## Project Markups and Review Note
Project Changemarks and Comments
38657
Cycle: | 1
Reviewer | File Name | Markup Name | Markup Description | Markup Text | Customer Response | WorkFlow Type
Craig Brown | C3.1.Util Plan BLDGS E F.pdf | C1 | 1. SHEET # C3.1 Utility Plan Building E F : Note #01; | 1. SHEET # C3.1 Utility Plan Building E F : Note #01; Please replace 2014 OPSC with 2017 OPSC and any new code section numbers as some have changed. CBR 03/08/18 | HWA | Primary Workflow
Craig Brown | P1.02.Underslab Plumbing Floor Plan-Building F.pdf | C1 | 5. SHEET # P1.02 UNERSLAB PLUMBING FLOOR PLAN - | 5. SHEET # P1.02 UNERSLAB PLUMBING FLOOR PLAN - BUILDING F: Note # 05; Two inch drains needed at all S-2 and S-4 sinks 2017 OPSC Table 702.1 CBR 03/08/18 C1 | All sinks have been revised to 2”W connection on P1.01 and connection schedule on P6.01. | Primary Workflow
Craig Brown | P1.01.Underslab Plumbing Floor Plan-Building E.pdf | C1 | 2. SHEET # P1.01 UNDERSLAB PLUMBING FLOOR PLAN - | 2. SHEET # P1.01 UNDERSLAB PLUMBING FLOOR PLAN - BUILDING E: Note # 02; Provide floor sink or floor drain for drainage of water heater temperature and pressure relief valve drain and drain from required reduced pressure backflow device for this section of the building to be installed on two and one half inch main cold water domestic riser. 2017 OPSC 608.5 / 602.3 CBR 03/08/18 C1 | There is already an existing floor drain serving drain from the existing water heater which was missing from the plan. The existing floor drain is now shown. Reduced Pressure Backflow Device has been added to the plan. See revised P1.01 and P6.01 | Primary Workflow
Craig Brown | P1.01.Underslab Plumbing Floor Plan-Building E.pdf | C1 | 3. SHEET # P1.01 UNDERSLAB PLUMBING FLOOR PLAN - | 3. SHEET # P1.01 UNDERSLAB PLUMBING FLOOR PLAN - BUILDING E: Note # 03;Two inch drains needed at all S-1 S-2 and S-3 sinks 2017 OPSC Table 702.1 CBR 03/08/18 C1 | All sinks have been revised to 2”W connection on P1.01 and connection schedule on P6.01. | Primary Workflow
Craig Brown | P1.01.Underslab Plumbing Floor Plan-Building E.pdf | C1 | 4.SHEET # P1.01 UNDERSLAB PLUMBING FLOOR PLAN - | 4.SHEET # P1.01 UNDERSLAB PLUMBING FLOOR PLAN - BUILDING E: Note # 04; Provide acid waste pretreatment system 2017 OPSC 306.1 CBR 03/08/18 C1 | Any chemicals used, if any, is diluted prior to dumping into the sink. If in any case, chemicals are drained into the sewer system, the discharge in the pipe is is diluted by waste discharge from a WC flush valve. This strategy has be approved and utilized at other middle schools in in Bend LaPine School District. | Primary Workflow
Donna Hamilton | A0.1.DATA SHEET.pdf | BR1 | A0.1.Data Sheet | No Alternates. Please remove any alternates. Revisions can be done after issuance if changes are needed. | BLRB | Primary Workflow
Donna Hamilton | A2.0A.WALL TYPES.pdf | BR1 | A2.0A Wall Types | This firewall most resembles "GA FILE NO. WP 3514" as there is not verification findable regarding "3614". Please clarify. 107.2 OSSC | BLRB | Primary Workflow
Donna Hamilton | A2.01.FLOOR PLAN.pdf | BR1 | A2.01 Floor Plan | Please label/describe the use for this "Flex" space off of the Choir room as it might require a second exit because of the 1230 sq ft. 107.2 OSSC | BLRB | Primary Workflow
Donna Hamilton | A2.01.FLOOR PLAN.pdf | BR1 | A2.01 Floor Plan | Reagrding science classrooms: Table 1015.1 "spaces with one exit or exit access" requires occupancy E with more than 49 occupants to have a secondary exit and the door shall swing in the direction of travel where serving a room or area containing an occupant load of 50 or more persons.. 1008.1.2 | BLRB | Primary Workflow
Donna Hamilton | A2.11.ENLARGED PLAN - AREA 1.pdf | BR1 | A2.11 Enlarged Plan | Please provide a detail showing compliance with 2009 ANSI 602. | BLRB | Primary Workflow
Donna Hamilton | A2.12.ENLARGED PLAN - AREA 2.pdf | BR1 | A2.12 Enlarged Plan | Please check the details and the designations provided for this submittal as a lot of them are incorrect. (like B5 /A8.5A.\) | BLRB | Primary Workflow
Donna Hamilton | A2.14.ENLARGED PLAN - AREA 4.pdf | BR1 | A2.14 Enlarged Plan | Per the demolition plans both the choir room and the band room had ramps to these classrooms. The entrances from the stage area will now be stairs? Per 3411.3, Alterations shall not reduce or have the effect of reducing accessibility of a facility or portion of a facility. | BLRB | Primary Workflow
Donna Hamilton | A6.13.RCP - AREA 3.pdf | BR1 | A6.13 RCP- Area 3 | Please provide supply and return air in the proposed Custodian breakroom and storgae room. 403.1 OMSC | Supply and exhaust have been added on M2.03. | Primary Workflow
Donna Hamilton | A6.14.RCP - AREA 4.pdf | BR1 | A6.14 RCP Area 4 | Is there no supply or return air in this revised area (Band and choir rooms)? 403.1 OMSC | Supply system is fed by existing sidewall grilles to remain as-is, not work shown. Return grilles(low returns) are adjusted to new floor elevation. This is shown on M2.03. | Primary Workflow
Donna Hamilton | A7.0.DOOR SCHEDULE.pdf | BR1 | A7.0 Door Schedule | Provide specifications of panic hardware/fire exit hardware (UL 305, UL 10C, UL 305 to be used and show locations of required hardware onto plan sheets. 1008.1.10 | BLRB | Primary Workflow
Donna Hamilton | A9.6C.ADA LIFT DETAILS.pdf | BR1 | A9.6C ADA Lift Details | Please provide manufacturers installation instructions/specifications. Is the system electric or hydrolic? 107.2 OSSC | BLRB | Primary Workflow
Donna Hamilton | PBMS_Bldg EF_Deferred Submittal Agreement.pdf | BR1 | PBMS Bldg EF Deferred Submittal Agreement | Provide all signatures per the deferred submittal agreement. | BLRB | Primary Workflow
Donna Hamilton | PBMS_Bldg EF_Special Inspection Agreement.pdf | BR1 | PBMS Bldg EF Special Inspection Agreement | Provide all signatures per the acknowledgement agreement of the special inspection form/agreement. | BLRB | Primary Workflow
Donna Hamilton | PBMS_Bldg EF_Special Inspection Agreement.pdf | BR1 | PBMS Bldg EF Special Inspection Agreement | Please mark all the applicable boxes of the schedules that are filled out for special inspection requirements. Specifically Schedule K. | BLRB | Primary Workflow
Donna Hamilton | S.2.2 E-F Roof Framing Plan.pdf | BR1 | S.2.2 E-F Roof Framing Plan | There is no detail 11 on sheet S-3.1. Please revise. 107.2 OSSC | A-V | Primary Workflow
Donna Hamilton | S.2.2 E-F Roof Framing Plan.pdf | BR1 | S.2.2 E-F Roof Framing Plan | Detail 14 is for the New ADA Lift Pit in the cafeteria. Please revise. 107.2 OSSC | A-V | Primary Workflow
Donna Hamilton | S.2.2 E-F Roof Framing Plan.pdf | BR1 | S.2.2.E-F Roof Framing Plan | Detail 15 on sheet S 3.1 is "Not Used" and there isn't a detail at all. Please revise. 107.2 OSSC | A-V | Primary Workflow
Donna Hamilton | S.2.2 E-F Roof Framing Plan.pdf | BR1 | S.2.2 E-F Roof Framing Plan | There is no detail 12 on sheet S.3.1. Please revise. 107.2 OSSC | A-V | Primary Workflow
Donna Hamilton | S.2.2 E-F Roof Framing Plan.pdf | BR1 | S.2.2 E-F Roof Framing Plan | Please check all the detail designations on this sheet and resubmit. 107.2 OSSC | A-V | Primary Workflow
Project Status & Notes
38657
Cycle: | 1
Reviewer Name | Status / Notes Comments |  |  |  |  | WorkFlow Type
Craig Brown | Hello Chris, Please review the correction letter (C1) in the ePlans Documentation folder and provide a written response to all required information with related sheet numbers and correction items of this review letter prior to the Building Safety Division performing additional reviews or issuing a building permit. Do not use the ePlans Change Marked Applicant Response box. Thank you, Craig Brown |  |  |  |  | Primary Workflow
Shannon Levine | On your SDC applications under BP-18-0645 your enrollment says 800 students under this permit it says 890. Please clarify which one is correct. |  |  |  |  | Primary Workflow
Kerry Bell | Provide a GC, field contact for inspections and subcontractor applications |  |  |  |  | Primary Workflow