March 14, 2014

City of Bend Building Division Plan Reviewer,

Re: Pilot Butte Middle Scohol – City of Bend Review comments, Project Permit Number: 18-0646

Mr. Craig Brown,

Please see the below responses to the Plumbing review comments from the referenced project #18-0646.

PLUMBING

General:

1. Item #3: See Civil response.
2. Item #2: There is already an existing floor drain serving drain from the existing water heater which was missing from the plan. The existing floor drain is now shown.

Reduced Pressure Backflow Device has been added to the plan. See revised P1.01 and P6.01

1. Item #3: All sinks have been revised to 2”W connection on P1.01 and connection schedule on P6.01.
2. Item #4: Any chemicals used, if any, is diluted prior to dumping into the sink.

If in any case, chemicals are drained into the sewer system, the discharge in the pipe is is diluted by waste discharge from a WC flush valve. This strategy has be approved and utilized at other middle schools in in Bend LaPine School District.

Sincerely,

Takako Baker

Takako Baker

MFIA