# SECTION 22 1000

# plumbing PIPing AND PumpS

## PART 1  GENERAL

1.1	DESCRIPTION

A.	Provide pipe, pipe fittings, piping specialties, pumps and related items required for complete piping system.

B.	Related Work:  The requirements of Section 22 05 00, Common Plumbing Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	General:  ASTM, and ANSI Standards are indicated.  In addition, special standards are referenced where neither ASTM nor ANSI Standards are applicable.

B.	Labeling:  All piping shall be continuously and legibly labeled on each length as required by codes and standards and including as a minimum, country of origin, manufacturer’s identification marking, wall thickness designation, and applicable standards and approvals.  Fittings shall be labeled as required by the referenced standard. Tubular fixture traps shall be stamped with manufacturer’s mark and material thickness.

C.	Potable Water Valves:  Potable water piping materials not limited to faucets, mixing valves, or pressure reducing valves.  Valves shall meet NSF/ANSI Standard 61, Section 9, for drinking water faucets and shall be brass construction.

D.	Plastic Piping:  All plastic piping systems including potable water and drain-waste-vent (DWV) shall meet NSF/ANSI Standard 14.

E.	Definitions:  Where piping fluid is not indicated in the following paragraphs, provide similar piping materials for similar fluids (i.e., "make-up water" = "domestic water"; "wet stand pipe" = "fire sprinkler pipe"; "drainage piping" = "sanitary/storm sewer piping").

F.	Plumbing System Disinfection shall be performed by an experienced, qualified, chemical treatment agency.  Mt. Hood Chemical, Chemcoa, or approved alternate.

1.3	STORAGE AND HANDLING

A.	Provide factory-applied end caps on each length of pipe and tube.  Maintain end caps through shipping, storage and handling as required to prevent pipe-end damage and eliminate dirt and moisture from inside of pipe and tube.  Protect flanges and fittings from moisture and dirt by inside storage and enclosure, or by packaging with durable, waterproof wrapping.

1.4	SUBMITTALS

A.	Submit catalog data for each product specified.

## PART 2  PRODUCTS

2.1	PIPING MATERIALS

A.	Copper Pipe and Tube:

1.	Application:

a.	Domestic water

b.	Priming lines

2.	Pipe:  ASTM B88.

a.	Above Ground Domestic Water:  Type L hard temper copper with soldered joints.

b.	Underground Domestic Water and Priming Lines:  Type L soft annealed with no joints or type K hard tempered copper with silver soldered joints.

3.	Fittings:  Wrought copper solder-joint fittings, ANSI B16.22.

B.	Plastic Pipe – Drain, Waste, Vent (DWV):

1.	Application:  Three-story or less structures and where allowed by Code only.

a.	Sanitary waste  (Not allowed for Grease Waste)

b.	Plumbing vent

2.	Pipe:

a.	Acrylonitrile-butadiene-styrene (ABS) (ASTM D3965) plastic drain, waste and vent piping (ASTM F628) and fittings (ASTM D2661) (DWV).

b.	Poly(vinyl chloride) (ASTM D1784) (PVC) plastic drain, waste and vent pipe (ASTM D2665 and D1785) and fittings (ASTM D2665) (DWV).

3.	Fittings:  Provide fittings of the type indicated, matching piping manufacture.  Where not otherwise indicated, provide socket style, solvent weld fittings produced and recommended for the service indicated by the piping manufacturer.

C.	Cast Iron DWV Pipe:

1.	Application:  1-1/2”" and larger.

a.	Sanitary waste

b.	 Grease Waste

c.	Plumbing vent

2.	Pipe:  Hubless cast iron soil pipe, CISPI 301-05/ASTM A 888-05.

3.	Fittings:	Hubless cast iron fittings:  CISPI 301-05/ASTM A 888-05.

4.	Couplings:

a.	Light Duty:  Standard couplings meeting CISPI 310/ASTM A 1277.

b.	Medium Duty: No-hub couplings meeting CISPI 310/ASTM A 1277 and incorporating ASTM C 564 gasket, type 304 SS corrugated shield and type 304 SS clamping bands.  Two clamping bands on 1-1/2” thru 4” pipe and four bands on 6” thru 10” pipe.

c.	Heavy Duty: No-hub couplings meeting ASTM C 1540, and FM 1680. ASTM C 564 neoprene gasket, type 304 SS corrugated shield and type 304 SS clamping bands. Four bands on 1-1/2” thru 4” pipe and 6 bands on 5” thru 10” pipe.

d.	Couplings to Dissimilar Pipe in Concealed Locations:  Fernco "LowFlex" or approved substitute.

5.	Manufacturers:  Cast iron pipe and fittings – AB&I, Charlotte Pipe, Tyler Pipe, or approved.  All pipe shall be labeled by the manufacturer.

D.	Cast Iron Pressure Pipe:

1.	Application:  4" and larger.

a.	Pressure sewer

2.	Pipe:  Ductile iron coated outside with bitumastic enamel, ANSI A21.51.

3.	Fittings:  Gray or ductile iron bolted stuffing box mechanical joint or rubber ring joints, ANSI A21.1.  Rubber gaskets, lubricants, bolts, and nuts, ANSI A21.11.

G.	Plastic Pipe:

1.	Application:  Where approved by Code.

a.	Domestic water

b.	Cooling coil condensate drain

2.	Pipe:

a.	Polyvinyl Chloride and Chlorinated Polyvinyl Chloride Plastic Pipe for Water Service:  SDR-PR pipe, ASTM D2241; Schedules 40, 80 and 120, ASTM D1785.

3.	Fittings:  Provide fittings of the type indicated, matching piping manufacturer.  Where not otherwise indicated, provide socket style, solvent weld fittings produced and recommended by the piping manufacturer for the service indicated.

2.2	MISCELLANEOUS PIPING MATERIALS

A.	Insulating (Dielectric) Fittings:  Provide standard products recommended by the manufacturer for use in the service indicated, and which effectively isolate ferrous from non-ferrous piping (electrical conductance), prevent galvanic action, and reduce corrosion.  Victaulic "Clear Flow."

B.	Soldering and Brazing Materials:  Provide soldering materials as determined by the installer to comply with installation requirements.

1.	Tin-Antimony Solder:  ASTM B32, Grade 95TA.

2.	Lead-Free Solder:  ASTM B32, Grade HB.  Harris "Bridgit" approved.

3.	Silver Solder:  ASTM B32, Grade 96.5TS.

4.	Flux: Water soluble paste flux.

5.	Brazing filler rod: BCuP  rod to suit conditions.

C.	Gaskets for Flanged Joints:  ANSI B16.21; full-faced for cast-iron flanges; raised-face for steel flanges.  Pressure and temperature rating required for the service indicated.

D.	Pipe Sleeves:  For installation in cast in place concrete floor systems.  UL 1479 listed with ratings for fire, smoke, and water intrusion.  Cast in place pipe sleeve with external waterstop collar and interior pipe seal and intumescent collar.  Holdrite “Hydroflame”.

E.	Sleeve Seal:  Rubber-link pipe wall and casing closure.  Thunderline Link-Seal.  For fire rated wall, floor or ceiling penetrations, 3-M "CP-25" caulk, "No. 303" putty and/or "PSS 7904" sealing system.

F.	Strainers:  "Y-pattern," Class 125 [epoxy coated iron body] [bronze body] with tapped blow-off connection and removable 20 mesh stainless steel screen.  NIBCO or equal.

G.	Tracer Wire:  14 gauge, single strand, copper wire with blue insulation for water, green for sanitary and storm sewers, and yellow for gas.  3M "DBY" direct bury splice kit required at all splices.

2.3	PIPING specialties

A.	Cleanouts:

1.	Manufacturer:  J.R. Smith, Zurn, Wade, Watts, Josam, Mifab, Sioux Chief, or approved substitute.

2.	Types:

a.	Tile Floor Cleanouts:  Smith 4053-U with square heavy-duty nickel bronze top, bronze plug, and vandalproof screws.  Adjustable top where cast into floor slab.

b.	Carpeted Floor Cleanout:  Smith 4023-U-X with round heavy-duty nickel bronze top, bronze plug, carpet clamping device, and vandalproof screws. Adjustable top where cast into floor slab.

c.	Concrete Floor Cleanout:  Smith 4023 with round heavy-duty nickel bronze top. [, stainless steel shallow cover and vandalproof screws.] Adjustable top where cast into floor slab.

d.	Wall Cleanouts:  Smith 4472-U, bronze ferrule with raised head bronze plug, stainless steel shallow cover and vandalproof screws.

e.	Outside Area Walks and Drives:  Smith 4253-U-G with galvanized cast iron body, top secured with vandalproof screws, and bronze plug.  Install in 18” x 18” x 6” deep concrete pad flush with grade.

f.	Plastic Body Cleanouts:  At contractor’s option, where ABS-DWV or PVC-DWV piping is approved, compatible plastic body cleanouts may be substituted.  Cleanouts shall have finished tops of style and material as specified above.

B.	Drains:

1.	Manufacturers: Zurn, Jay R. Smith, Josam, Watts, Wade, Froet Industries, Mifab, Sioux Chief, or approved substitute.  Where numbers are scheduled on the drawings they represent minimum the acceptable standard for locations involved.

2.	Cast iron construction with acid resistant coating, anchor flange, and other options as indicated by model number listed on the drawings.  PVC drains where specifically noted.  Cast iron dome strainers on roof drains.

3.	Install sheet flashing, extending not less than 10" from and clamped to all drains not completely cast-in-place in a homogeneous material.

C.	Trench Drain "":  Polyester concrete material, cast channels with 0.6% sloped bottom and with cast iron grate.  Length as indicated on the Drawings.  ACO Drain Incorporated "Channel Slope" NW-100 with No. 603 catch basins where indicated or approved substitute.

D.	Trench Drain "":  UV and chemical resistant HDPE interlocking [4”, 6”, 12” wide] channel sections  in flat and presloped styles with bottom or end outlets as shown.  Provide with grate anchors and construction covers.  [Ductile iron frame and grate] [Perforated stainless steel grate] [HDPE grate] Sioux Chief, Zurn.

E.	Catch Basin:  Code approved, fabricated of minimum 10 gauge steel plate welded and asphalt coated.  Sleeve for connection of inlets and outlets as shown with trap and cleanout access on outlets.  Fabricated steel grate as shown on the Drawings. Code approved concrete catch basins may be substituted with prior approval.

F.	Oil Separator:  Governing Authorities approved precast concrete basin with 10 gauge galvanized sheet metal baffles and 5/16" galvanized diamond plate steel cover with spring locks of size shown on the Drawings.  Utility Vault Co. [ Model 25TA oil-water separator ].

G.	Grease Trap:  Model and capacity as listed on the drawings.  Fabricated steel, with interior and exterior corrosion resistant coating for [on floor/recessed] mounting with [extension/receiving cradle.]  Interior separation baffles, air relief, and gasketed cover.  Furnish with flow control fitting for inlet.  Zurn, Jay R. Smith, Josam, Watts, Wade.

H.	Hydromechanical Grease Interceptor:  The interceptor vessel shall be formed of seamless chemical resistant thermoplastic suitable for underground installation with up to 72” of cover and 160 deg. F influent.  Interceptor shall incorporate an internal flow control device and inlet diffusion baffle and operate with a balanced air environment.  Average unit efficiency shall be not less than 95%. Vessel shall include 3 optional outlet locations and shall provide for a discharge sampling point.  Service access to be provided via H-20 traffic rated access rings and secured covers. When required by the installation, unit shall include cut-to-length riser extensions with watertight connections.  Schier, Endura, or approved substitute.

I.	Gravity Grease Interceptor:  Precast concrete vault as indicated on the drawings.  Provide with 2 [3] traffic weight manhole rings and covers and discharge sampling port, extended to grade.

J.	Flashing:  Minimum 4# sheet lead; to extend horizontally 10” from edge of vent penetrations or rain drain body and vertically 12” minimum up from roof turned over and down into hub of vent or finished with bronze cap providing counterflashing for screwed pipe.

K.	Downspout Boot:  Smith No. 1787-12, 4” diameter by 18”, offset type.  Smith No. 1785 or 1786 for rectangular downspouts.

L.	Shock Arrester:  Precharged bellows or sealed piston type manufactured to meet PDI WH-201 and ASSE 1010 Standards.  Size in accordance with PDI procedures.  J. R. Smith, PPP, Sioux Chief, Wade, Zurn, Watts, Josam, or approved substitute.

M.	Priming Valves:  Smith 2699, Josam 88250, Wade W8800T, Zurn Z1022, Watts MS810 or equivalent Precision Plumbing, Mifab.  Locate in closets, under counters or in walls behind access panels as specified in Section 22 05 00.  Use copper specified previously for all underground priming lines.

N.	Traps:  Except chrome plated fixture traps.  Recessed drainage pattern for threaded pipe and same grade as pipe for cast iron and plastic pipe; with cleanout plugs in trap body in all above grade locations.

O.	Pressure Reducing Valve:  Single seat type with in-line renewable stainless steel seat diaphragm, and valve.  Size and capacity as shown on Drawings.  Bronze bodies with screwed connections on valves 2-1/2” and smaller and flanged steel bodies on valves 3” and larger.  Install each PRV with strainer on inlet or internal strainer.  Select for 15 psi fall-off at indicated flow.  Leslie, Watts, Apollo, Cash-Acme, Zurn-Wilkins, or approved substitute.

P.	Backflow Preventer:  Where indicated on the Drawings, install a reduced pressure backflow preventer complete with [strainer on inlet,] shutoff valves, two separate check valves, differential relief valve with drain funnel, and test cocks.  USC Foundation for Cross Connection Control, State Health Officials, and serving utility approved.  Bronze bodies on units 2” and smaller, cast iron bodies with bronze trim on units 2-1/2” and larger, and stainless steel construction for carbonated beverage service.

Q.	Backflow Preventer:  Where indicated on the Drawings, install a double check backflow preventer complete with [strainer on inlet,] shutoff valves, two separate check valves, and test cocks.  USC Foundation for Cross Connection Control, State Health Officials, and serving utility approved.  Bronze bodies on units 2” and smaller, and cast iron bodies with bronze trim on units 2-1/2” and larger.

R.	Master Mixing Valve:  All brass or bronze body with stainless steel parts, thermostatic [bimetallic] [wax-filled] master control element to fail safe upon cold water or control element failure meeting ASSE 1017.  Provide with external union angle check stops, strainers, volume control, shutoff valves, dial thermometer.  Valve location, arrangement and capacity as shown on plans. Leonard, Lawler, Powers, Acorn, Bradley, Symmons, or approved substitute.  See section 3 for factory start-up procedures.

S.	Master Mixing Valve Station:

1.	Mixing valve station shall be fully factory assembled and tested incorporating type L copper tube with solder fittings, isolation ball valves on all inlet and outlet connections, check valves on inlet lines, recirculating pump with aquastat and timeclock wired to a junction box for single point power connection, circulating line balancing valve, check valve, [strainer,]and thermometer, all mounted [in a hinged door, stainless steel cabinet for] [to an assembled mounting frame for floor or] wall mounting.  Provide pressure reducing valves on multiple mixing valve stations.  All piping connections shall be labeled.

2.	Master Mixing Valve(s) of all brass or bronze body with stainless steel parts, [electronic] [bimetallic] [wax-filled] thermostatic master control element to fail safe upon cold water or control element failure meeting ASSE 1017.  Provide with strainers on inlets, and dial thermometer(s) on [inlets and] outlet.  Valve location, arrangement and capacity as shown on plans.

3.	Manufacturers:  Leonard, Bradley, Powers, Acorn, Symmons, or approved substitute.

T.	Backwater and Gate:  Cast iron body with brass wedge gate, brass swing check, and separate handle. Provide with proper extension to set floor plate flush with finished floor.  Smith 7150 or equivalent Josam, Wade, Watts or Zurn.

U.	Domestic Water Balancing Valve:  Balancing fitting with differential pressure taps, brass or bronze body and trim. B&G “Circuit Setter” or equivalent Taco, Armstrong, Thrush, Wheatley, Flow Design or approved substitute.  At contractor’s option, balancing valves 3” and larger may be butterfly style, Jenkins No. 222 EL or approved substitute as specified in Section 15100.

V.	Building Shut Off Valve Box:  10” round concrete enclosure with cast iron traffic weight cover. Brooks 3RT or approved substitute.

2.4	pumps

A.	Domestic Hot Water Circulator:  Bronze body, bronze fitted, in-line circulator with sleeve bearing.  Bell & Gossett [1” HV] or equivalent Grundfos, Thrush, Wilo, Taco, or Armstrong.  Provide with 7-day programmable electronic time clock and aquastat to start and stop the pump.

B.	Elevator Sump Pump: Submersible, 50 gpm at 17 ft. head, minimum 1/2 horsepower sump pump with integral float switch.  Myers, Paco, Hydronix, Zoeller, Viking, Liberty, or approved.

C.	Submersible Sump Pump:  Single submersible unit, bronze fitted with inlet strainer, direct connected to a permanently lubricated, ball bearing type motor with overload protection.  Provide liquid level control and "Man-Off-Auto" switch.  Make discharge pipe connection with union, swing check and gate valve.  Pump size and capacity as shown on Drawings.  PACO, Chicago, Gould, Hydr-O-Matic, Kenco, Federal, Peerless, Weinman, Zoeller or approved substitute.

D.	Sump Pump:  Duplex pump unit mounted on a gas-tight cover over a 3/16" black, steel bitumastic coated sump.  Vertical, submerged bronze fitted pump with inlet strainer, directly connected to a permanently lubricated, ball bearing motor with overload protection.  Gas-tight liquid level control, together with automatic alternator with override feature and audible high water alarm.  Mount alternator and motor starters on rigid stand on sump cover, making an integral assembly, with level control, alternator, control circuit transformer and starters prewired at factory, needing only power connection to be operable.  Starters as specified herein and with "Man-Off-Auto" switch in the cover for each pump.  Provide 11" x 15" manhole in sump cover.  Make discharge pipe connection with union, swing check and gate valve.  Pump capacity and sump size as shown on Drawings.  Paco, Aurora, Kenco, Chicago, Federal, Peerless, Weinman, Swaby, or approved substitute.

E.	Sewage Pumps:

1.	General:  Provide two vertical frame mount non-clog sewage pumps with flexible drives, deck mounted motors and complete control system.  Size, capacity and arrangement as shown on the Drawings.

2.	Impeller:  Heavy cast iron of single port design, balanced at the factory to ensure hydraulic and mechanical balance and threaded to the shaft to maintain smooth water passageway.  Well rounded vane edges for smooth flow.

3.	Volute:  Heavy cast iron sections with bolted contoured cleanout plug.

4.	Wear Rings:  Peripheral type requiring no vertical adjustment and pressed into the case for ready placement in the field.

5.	Shafts:  Stressproof steel with stainless steel sleeve to protect the area from the impeller hub through the stuffing box.

6.	Bearings:  Ball type bearings of sufficient size to withstand all thrust loads applied and arranged so that excessive lubrication will not build up excessive pressure but will be passed to the frame chamber.

7.	Stuffing Box:  An extra deep split gland type stuffing box with bronze lantern ring is required and shall be designed for grease seal.

8.	Vertical Frame:  One piece cast iron, minimum 40,000 pounds tensile strength, normalized to prevent post machining distortion.  Lined, bored bearing fits for exact concentricity and to prevent misalignment and roller finished to exact size for further alignment and heat transfer.

9.	Motor:  Vertical, solid shaft type.  Horsepower and electrical characteristics as indicated.

10.	Control:

a.	Provide complete operating controls including pump start and stop float switches, high level alarm, control panel and automatic alternator.  NEMA 1 enclosed type [NEMA 3R outdoor rated]  control panel with control circuit transformer, electric alternator, circuit breaker for each motor, pump motor magnetic starters with three-leg overload and undervoltage protection.  Include float controls to stop pump, start lead pump, start lag pump (both running together) and signal high level alarm.

b.	Include audible alarm with silencing switch and red light.  Light to remain on until high level is corrected.  [ Provide a remote red light on the outside of the pump house. / Locate the alarm panel as shown on the Drawings. ]  Locate the alarm in a location designated by the [ Architect ].

11.	Manufacturers:  Cornell, Allis Chalmers, Crane-Deming, Aurora, or approved substitute equal (note high discharge head requirements).

F.	Water Pressure Booster:  Factory assembled and tested duplex water booster unit complete with pumps, controls, hydro-pneumatic tank, suction and discharge manifolds and all necessary valves, fittings and gauges all mounted on steel support base.

1.	Pumps:  Bronze fitted centrifugal pumps of capacities and types indicated on the Drawings.  Provide with low/no flow thermal protection system.

2.	Manifolds:  Standard schedule 40 galvanized steel piping.

3.	Hydro-Pneumatic Tank:  Precharged ASME 125 psi code steel tank with replaceable butyl rubber bladder FDA approved for potable water. Equip tank with system connections, bladder access flange, drain, air charging valve, ASME code relief valve and lifting lugs.

4.	Control Panel:  NEMA I enclosure pre-wired with magnetic starters with 3-leg overload protection, fused disconnects, individual pump hand-off-auto selector switches, automatic alternator, 115V control transformer, operating pressure switches, terminal strip for single field power connection, motor run indicator lights, lead pump failure alarm and protection and low suction pressure shut down with manual reset.

5.	Acceptable Manufacturers:  Paco Pacoflo 9000 or approved.

2.5	BACKFILL MATERIALS

A.	Subbase Materials:  A graded mixture of gravel, sand, crushed stone or crushed slag.

B.	Finely-Graded Subbase Material:  Well graded sand, gravel, crushed stone or crushed slag, with 100% passing a 3/8" sieve.

C.	Backfill Material:  Soil material suitable for compacting to the required densities, and complying with AASHTO designation M145, Group A-1, A-2-4, A-2-5. or A-3.

D.	Drain Field Fill Material:  Washed and uniformly graded gravel crushed stone or crushed slag, with 100% passing a 1-1/2" sieve and not more than 5% passing a No. 4 sieve.

E.	Stabilization Fabric:  Nonwoven stabilization and drainage fabric.  Mirafi 140S or 140M.

## PART 3  EXECUTION

3.1	UTILITY SERVICE

A.	Plumbing Utility Connections: Complete installation.  Contact local serving utilities to determine conditions involved and make or arrange to have connection made at proper time and pay all costs involved.

B.	Sanitary and Storm Sewers:  Connect to or arrange for connection to [existing/  public] sanitary and storm sewers as shown on the Drawings and as required by the serving utility.  Verify depth, size and location prior to installation of the new sewer systems.

C.	Water Service:  Connect to or arrange for connection to [existing/public] water service.  Verify serving utility requirements prior to beginning any installation.  Verify water main size, depth, pressure and location prior to starting work.   Install water meter furnished by the serving utility and valve in vault provided under the fire sprinkler work specified in Section 21 13 00.  Coordinate vault size and piping arrangement.

D.	Fire Service:  Connect to or arrange for connection to existing public water main. Contact local serving utilities to determine conditions involved and make or arrange to have connection made at proper time and pay all costs involved.

Provide vault and install backflow preventer provided under the fire sprinkler work specified in Section 21 13 00.  Coordinate vault size and piping arrangement.  Installation of meters and vault by the serving utility.

3.2	PIPE INSTALLATION

A.	General:  Install pipe, tube and fittings in accordance with recognized industry practices, manufacturers instructions, and plumbing code standards.  Install each run accurately aligned with a minimum of joints and couplings, but with adequate and accessible unions and flanges for disassembly, maintenance and/or replacement of valves and equipment.  Reduce sizes (where indicated) by use of reducing fittings.

Comply with ANSI B31 Code for Pressure Piping.

B.	Piping Runs:  Route piping close to and parallel with walls, overhead construction, columns and other structural and permanent-enclosure elements of the building.  Install piping plumb and level except where pitched for drainage.  If not otherwise indicated, run piping in the shortest route which does not obstruct usable space or block access for servicing the building or equipment and avoid diagonal runs.  Wherever possible in finished and occupied spaces, conceal piping from view.  Do not encase horizontal runs in solid (concrete or CMU) partitions.

C.	Changes in Direction:  Use fittings for all changes in direction.  Run lines parallel with building surfaces.

D.	Line Grades:

1.	Drainage Lines:  Run at maximum possible grade and in no case less than 1/4" per foot within building.

2.	Vents:  Pitch for drainage 1/4" per 10'.

3.	Water:  Pitch to low points and install hose bib drains.  3' minimum depth of ground cover for all lines outside building unless otherwise noted.

E.	Unions and Flanges:  At all equipment to permit dismantling and elsewhere as consistent with good installation practice.

F.	Expansion:  Provide loops, swing joints, anchors, runouts and spring pieces to prevent damage to piping or equipment.

G.	Insulating (Dielectric) Fittings:  Comply with manufacturer's instructions for installing unions or fittings.  Install in a manner which will prevent galvanic action and stop corrosion where the "joining of ferrous and non-ferrous piping" is indicated.

H.	Tracer Wire:  Install tracer wire as close to underground non-metallic water, sanitary and storm sewers and gas pipe in the trench as possible.  Tracer wire shall be accessible at grade via all services, valve and meter boxes, curb cocks, cleanouts at the building, manholes (inside the cover near the top), etc.  Locate all points on the record as-installed drawings.  Splice into utility tracer system where available.  Comply with code requirements.

I.	Piping:  Install for services as specified in Part 2.  The following are special requirements:

1.	Underground Drainage Pipe:  Install cast iron soil pipe for the following conditions.  When specified in Part 2 of this Section and where allowed by Code, plastic piping may be installed in lieu of cast iron piping.

a.	Under the building to 5' outside the building structure.

b.	5' each way from a potable water line crossing.

c.	First section (minimum 5') from any connection to underground structures such as catch basins, manholes, disposal well or tank, etc.

d.	Through all fill areas where pipe cannot be rested on undisturbed earth.

e.	Where the top of the pipe is less than 12 inches below finish grade.

f.	At contractor's option in lieu of concrete or clay sewer pipe.

2.	Acid Waste Piping:  Install acid resisting piping and corresponding fittings in accordance with the manufacturer's recommendations.  Use acid resisting fittings in connecting to standard waste lines.  Install acid vent-thru-roof separately per Code.  Install steel sleeves at all fire-rated wall penetrations as approved.

3.	Demineralized, Deionized and/or Distilled Water Piping:  GSR polypropylene piping with "Fuseal" joints or Nalgene polyethylene piping with "polyfusion" joints.  Piping and joints installed in accordance with manufacturer's recommendations.  Install steel sleeves at all fire rated wall penetrations as approved.

4.	Existing Domestic Water Piping:  Piping materials as specified in Part 2 except where existing domestic water piping to be connected to is galvanized steel, new galvanized steel piping for short branches and rough-ins may be installed.

3.3	PIPING JOINTS

A.	General:  Provide joints of the type indicated in each piping system, and where piping and joint as manufactured form a system, utilize only that manufacturer's material.

B.	Cast Iron "No-Hub":  All joints in accordance with the Cast Iron Soil Pipe Institute (CISPI) Designation No. 310-97 "Installation Procedures for Hubless Cast Iron Soil Pipe and Fittings For Sanitary and Storm Drain, Waste and Vent Piping Applications.”  Horizontal runs of 5” and greater shall be braced as indicated in Figure 4 for “rodding” restraints.  Application of couplings as follows:

1.	Light Duty Couplings: All vent piping and all drainage and waste piping above grade and serving the uppermost floor of the structure.

2.	Medium Duty Couplings: All aboveground waste and drainage piping unless indicated otherwise.

3.	Heavy Duty Couplings:

a.	All underground installations.

b.	All rain drain leader joints located more than 20 feet below the roof drain.

c.	Above all patient critical care areas, operating rooms, delivery rooms, nurseries, and food storage, preparation, and serving areas in health care facilities.

C.	Solder Copper Tube and Fitting Joints:  In accordance ANSI B 828 with recognized industry practice.  Cut tube ends squarely, ream to full inside diameter, and clean outside of tube ends and inside of fittings.  Apply solder flux to joint areas of both tubes and fittings.  Insert tube full depth into fitting, and solder in a manner which will draw solder full depth and circumference of joint.  Wipe excess solder from joint before it hardens.  "T-Drill" field formed tees may be utilized where the main is at least two pipe sizes larger than the branch.

D.	Plastic Pipe/Tube Joints:  Comply with manufacturer's instructions and recommendations, and with applicable industry standards:

1.	Heat Joining of Thermoplastic Pipe:  ASTM D-2657.

2.	Making Solvent-Cemented Joints:  ASTM D-2865 and ASTM F-402.

E.	Braze Copper Tube and Fitting Joints:  Where indicated.  Pass a slow stream of dry nitrogen gas through the tubing at all times while brazing to eliminate formation of copper oxide.

F.	Flanged Joints:  Match flanges within piping system, and at connections with valves and equipment.  Clean flange faces and install gaskets.  Tighten bolts to provide uniform compression of gasket.

G.	Concrete Sewer Pipe Joints:  Comply with applicable provisions of "Concrete Pipe Field Manual" by the American Concrete Pipe Assoc.

H.	Ferrous Threaded Piping:  Thread pipe in accordance with ASME B1.20.1; cut threads full and clean using sharp dies.  Ream threaded ends to remove burrs and restore full inside diameter.  Apply pipe joint compound or pipe joint tape (Teflon) where recommended by pipe/fitting manufacturer, on male threads at each joint and tighten joint to leave no more than three threads exposed.

I.	Glass Pipe Joints:  Comply with manufacturer's instructions and recommendations.

J.	Grooved Pipe Joints:  Comply with fitting manufacturer's instructions for making grooves in pipe ends.  Remove burrs and ream pipe ends.  Assemble joints in accordance with manufacturer's instructions.  Visually inspect the assembled joint to ensure proper gasket seating.

3.4	CLEANOUTS

A.	Where required by code, at each change of sewer direction 45 degrees or greater and more than 10’ long, at end of each branch or main and spaced not greater than 100’ apart, as required by code and/or as shown on Drawings.  Provide cleanouts beneath all sinks.

3.5	MANHOLES

Where required by code, at each change of 8" or larger sewer direction 45 degrees or greater and more than 200' in length or where shown on the Drawings, manholes shall be constructed as follows:

A.	Concrete Base:  Construct the concrete bases for the manholes so that the first section of the precast manhole has a uniform bearing throughout the full circumference of the manhole wall.  Deposit sufficient mortar on the concrete base to provide a watertight seal between the base and the manhole wall.  Set base slab on undisturbed earth and compact backfill of original or better material as directed.  Verify inverts and accurately form to grades.  Shape concrete in base to provide uniform flow.

B.	Placing Precast Manhole Sections:  Make the joints for the precast concrete manholes of cement mortar consisting of one part cement to two parts sand.  Construct the walls true to line and grade.  Place mortar on the groove of the lower section of pipe prior to placing the next section of pipe and fill the entire joint completely with mortar and trowel to a smooth finish.

C.	Manhole Invert:  The manhole invert shall provide a smooth flow-through characteristic.  No sharp edges or rough section which will tend to obstruct the flow of sewage will be permitted.  Where a full section of sewer pipe is laid through the manhole, break out the top and cover the exposed edge of the pipe completely with mortar.  Trowel all cement and/or mortar used in the construction of the invert smooth.  Provide flexible connectors at piping inlet and outlet.

D.	Manhole Rings and Covers:  Install the cast iron manhole rings and covers on the tops of the manholes so as to positively prevent any infiltration of surface or ground water into the manholes.  Set the manhole rings so the tops of the covers are just flush with the surface of the adjoining pavement or ground surface unless otherwise shown on the Plans or as directed.

3.6	DRYWELL, CATCH BASIN, LEACHING WELL OR CESSPOOLS

A.	Set bottom ring on undisturbed earth and backfill around sides with not less than 24” of clean coarse gravel or crushed rock (1-1/2” to 2” size).

3.7	MISCELLANEOUS PIPING EQUIPMENT

A.	Floor, Wall and Ceiling Plates:  Chrome plated pressed steel or brass screw locked split plates on all pipe penetrations in finished spaces.

B.	Strainers:  Install in a manner to permit access for cleaning and screen removal and with blow-off valve.

C.	Sleeves:  At all penetrations of masonry or cast in place concrete construction.   PVC, 24 gauge galvanized steel tube or Schedule 40 galvanized steel pipe.  Use steel pipe sleeves through beams, footings, girders or columns and for all penetrations of walls or floors below grade.  Where floor finish is ceramic tile, terrazzo, or similar material extend standard steel pipe sleeves 1-1/2" above finished floor.  Fabricate sleeves 1" diameter larger than pipe or insulation.  PVC and sheet metal sleeves at non-structural penetrations only.  Use specified sleeve system for all above grade concrete floor applications.

D.	Sleeve Caulking:  Caulk below grade pipe with rubber link seal.  Grout above grade pipe with cement mortar or approved waterproof mastic.  All caulking or grouting shall extend full depth of sleeve.  Utilize rubber sealing links in lieu of caulking.  Install UL sealing caulk, putty and/or system at all penetrations of fire rated walls, floors and ceiling.

E.	Shock Arrestors:  Install at end of mains, in a battery of three or more flush valve-operated fixtures water header, ahead of quick closing and solenoid operated valves.  Size per PDI recommendations where size is not indicated.  Provide access panels.

F.	Trap Priming:  Traps serving floor drains, floor sinks, catch basins, and similar fixtures shall be primed in accordance with Code requirements.

G.	Domestic Hot Water Mixing Valves:  Install in accordance with manufacturers installation instructions and piping diagrams.

3.8	EXCAVATING

A.	General:  Do not excavate for mechanical work until the work is ready to proceed without delay, to minimize the total time lapse from excavation to completion of backfilling.  Comply with all applicable Federal and state safety regulations and local erosion control requirements.

B.	Width:  Excavate for piping with 6" to 9" clearance on both sides of pipe, except where otherwise shown or required for proper installation of pipe joints, fittings, valves and other work.  Excavate for other work to provide minimum practical but adequate working clearances.

C.	Depth for Direct Support:  For work to be supported directly on undisturbed soil, do not excavate beyond indicated depths, and hand-excavate the bottom cut to accurate elevations.  Support the following work on undisturbed soil at the bottom of the excavations:

1.	Piping of 5" and less pipe/tube size.

2.	Cast-in-place concrete.

D.	Depth for Subbase Support:  For large piping (6" pipe size and larger), tanks and where indicated for other mechanical work, excavate for installation of subbase material in the depth indicated, or, if not otherwise indicated, 6" below bottom of work to be supported.

E.	Depth for Exterior Piping:  Excavate for exterior water-bearing piping (water and  drainage) so that the top of piping will not be less than [ 3' ] vertical distance below finished grade.

F.	Depth for Unsatisfactory Soil Conditions:  Where unsatisfactory soil condition at the bottom of excavation exists, excavate additional depth as directed to reach satisfactory soil-bearing condition.  Backfill with subbase material, compacted as directed, to indicated excavation depth.

G.	Rock and Boulder Removal:  Refer to Division 1 for procedure on additional work, including additional excavating and backfilling, rock removal, etc.  [ Include removal of unusual rock and/or boulders in the contract. ]

H.	Protection of Trees:  Excavate near large trees (within the drip line) by hand, and protect the root system from damage or dryout to the greatest extent possible.  Maintain moist condition for root system and cover exposed roots with burlap.  Paint root cuts of 1" diameter and larger with asphaltic tree paint.

I.	Excavated Materials:  Store excavated material (temporarily) near the excavation, in a manner which will not interfere with or damage the excavation or other work.  Do not store under trees (within the drip line).  Retain excavated material which complies with the requirements for backfill material.  Dispose of excavated material which is either in excess of quantity needed for backfilling or does not comply with requirements for backfill material.

Move unused material to another location on Owner's property, or adjacent to the project site, and dispose of as directed by the [ Architect ][ /Engineer.]

Remove unused material from project site, and dispose of in a lawful manner.

3.9	DEWATERING

A.	Maintain dry excavation for mechanical work by removing water.  Protect excavations from inflow of surface water.  Pump minor inflow of ground water from excavations; protect excavations from major inflow of ground water by installing temporary sheeting and waterproofing.  Provide adequate barriers which will protect other excavations and below-grade property from being damaged by water, sediment or erosion from or through mechanical work excavations.  Comply with local erosion control regulations where applicable.

3.10	BASE PREPARATION

A.	Subbase Installation:  Where indicated, install subbase material to receive mechanical work, and compact by tamping to form a firm base for the work.  For 4" and larger piping, horizontal cylindrical tanks and similar work, shape the subbase to fit the bottom 90 degrees of the cylinder, for uniform continuous support.  Provide finely-graded subbase material for wrapped, coated and plastic pipe and tank.  Shape subbases and bottoms of excavation with recesses to receive pipe bells, flanged connections, valves and similar enlargements in the piping systems and set bottom of trench at proper pitch and correct elevations with subbase material.

B.	Concrete Encasement:  Where piping under roadways is less than 2'-6" below surface of roadway, provide 4" base slab of concrete to support piping. After piping is installed and tested, provide 4" thick encasement (sides and top) of concrete before backfilling.  Provide Class 2500 concrete for encasement and slab.

C.	Previous Excavations:  Where piping crosses over an area more than 5' wide which has been previously excavated to a greater depth than required for the piping installation, provide suitable subsidence-proof support for the piping.  Comply with the details shown, or where not otherwise shown, provide the following support system:

1.	Excavate to undisturbed soil, in a width equal to the pipe diameter plus 2'.  Install 8" courses of subbase material, each compacted to 95% of maximum density, as required to fill excavation and support piping.

3.11	BACKFILLING

A.	General:  Bedding and backfilling of plastic DWV piping shall comply with ASTM D2321, Standard practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity Flow Applications.

B.	Do not backfill until installed mechanical work has been tested and accepted wherever testing is indicated.  Install drainage fill where indicated, and tamp to a uniform firm density.  Backfill with finely-graded subbase material to 6" above wrapped, coated and plastic piping and tanks, and to center line of other tanks (where recommended by tank manufacturer, use "pea gravel" backfill).  Condition backfill material by either drying or adding water uniformly, to whatever extent may be necessary to facilitate compaction to the required densities.  Do not backfill with frozen materials.

3.12	CLEANING

A.	General:  Clean all dirt and construction dust and debris from all mechanical piping systems and leave in a new condition.  Touch up paint where necessary.

B	Disinfection of Domestic Water Piping System:

1.	Prior to starting work, verify system is complete and clean.

2.	Open all drains and fixtures valves in the building starting with the valve nearest the water service line and permit the water to run clear for 10 minutes to eliminate grease, cuttings, flux, and foreign matter.

3.	Disinfect piping system in accordance with ANSI/AWWA C651-92 standard.

4.	Take samples from 10 percent of outlets and from water entry, and analyze in accordance with AWWA C601.  If any sample fails the analysis, repeat the procedure.

5.	Include a copy of the bacteriological analysis in the Operating and Maintenance manuals.

C.	Sanitary and Storm Drainage System:

1.	Remove construction debris from cleanouts, drains, strainers, baskets, traps, etc., and leave same accessible and operable.  Place plugs in the end of uncompleted piping at the end of the day or whenever work stops.

2.	Before final acceptance of completed sewer system, flush and clean the entire system with water.  Trap and remove solid material obtained from flushing and cleaning from the new system.  Do not allow debris to enter the existing sewer system.

D.	Deionized Water Piping:  Remove all foreign material from piping and flush with clean water.  Sanitize and clean in accordance with procedure recommended by deionized water equipment manufacturer.  After system is ready to be operated, test water purity and certify that water quality is within allowable limits.

3.13	TEST

A.	General:

1.	Minimum duration of two hours or longer, as directed for all tests.  Furnish report of test observation signed by qualified inspector.  Make all tests before applying insulation, backfilling, or otherwise concealing piping or connecting fixtures or equipment.  Where part of the system must be tested to avoid concealment before the entire system is complete, test that portion separately, same as for entire system.

2.	Provide all necessary temporary equipment for testing, including pump and gauges.  Remove control devices before testing and do not use piping system valves to isolate sections where test pressure exceeds valve pressure rating.  Fill each section with water and pressurize for the indicated pressure and time.

3.	Observe each test section for leakage at end of test period.  Test fails if leakage is observed or if pressure drop exceeds 5% of test pressure.

B.	Repair:

1.	Repair piping system sections which fail the required piping test by disassembly and re-installation, using new materials to the extent required to overcome leakage.  Do not use chemical stop-leak compounds, solder, mastics, or other temporary repair methods.

2.	Drain test water from piping systems after testing and repair work has been completed.

C.	Sewer:  Furnish all facilities and personnel for conducting the test.  Test in accordance with the requirements of the State Plumbing Inspector and local authorities.

D.	Plumbing Waste and Vent Piping:  Hydrostatic test by filling to highest point, but not less than 10' water column on major horizontal portion.

E.	Water Piping:  Hydrostatic pressure of 100 psig without loss for four hours.

F.	Tanks and Equipment:  Hydrostatic pressure to 1.5 times operating pressure but do not exceed maximum rated pressure.

G.	Deionized (PVDF) Piping:

1.	Test Medium:  Water only.  No compressed air or gases.

2.	Initial Low Pressure Test:  Maximum 50 psig for four hours with no loss.

3.	High Pressure Test:  Maximum of 150 percent of the system operating pressure or the piping/fitting pressure ratings, whichever is lower. Test a minimum of 12 hours at the above pressure.  Observe safety precautions indicated by the manufacturer.

4.	Repair of Leaks:  Re-fuse leaky joints in accordance with the manufacturer's recommendations.  Replace defective sections of piping.

3.14	SUPERVISION AND START-UP

A.	Adjust flush valves, pressure reducing valves, mixing valves, water heater thermostats, domestic hot water circulating system balancing valves, and similar equipment.

B.	Domestic hot water system balancing:  Adjust domestic hot water recirculating balancing valves to equalize return temperatures from each branch line.

C.	The installation, start-up, and adjustment of the [sewage lift station /water pressure booster/Thermostatic mixing valve/master mixing valve] shall be supervised by an authorized agent of the manufacturer.  The manufacturer's agent shall check out and approve the installation and shall also approve and be responsible for adjusting the operating and control system and instructing the Owner's representatives on the system operation.

D.	Master mixing valve start-up procedure:  Provide a factory authorized representative to review the installation of the mixing valve and verify that the adjustment has been completed by an authorized agent of the manufacture.  Provide documentation in the O&M documents showing adjustment has been completed per manufacture instructions.  Record supply and return temperatures.  Work shall be completed prior to substantial completion.

END OF SECTION 22 1000