# SECTION 22 4000

# PLUMBING fixtures

## PART 1  GENERAL

1.1	DESCRIPTION

A.	The requirements of this section apply to the plumbing fixtures and trim.

B.	Provide fixtures as shown on the Drawings and specified herein.  Provide all required fixture trim and accessories for a complete, finished installation.

C.	Related Work:  The requirements of Section 22 0500, Common Plumbing Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	Code:  Comply with requirements of the Oregon State Plumbing Specialty Code.

B.	Fixture color: White unless indicated otherwise.

C.	Potable Water Valves:  Potable water valves not limited to faucets, mixing valves, or pressure reducing valves.  Valves shall meet NSF Standard 61, Section 9, for drinking water faucets and shall be brass construction.  Brass components which contact water within the faucet shall be from brass which contains no more than 0.25 percent lead by dry weight.

## PART 2  PRODUCTS

2.1	PIPING

A.	Piping, fittings, and related items as specified in related Sections 22 1000.

2.2	INTERIOR PLUMBING MATERIALS

A.	Shock Arrester:  Precharged bellows or sealed piston type manufactured to meet PDI WH-201 and ASSE 1010 Standards.  Size in accordance with PDI procedures.  J. R. Smith, PPP, Sioux Chief, Wade, Zurn, Watts, Josam, or approved substitute.

B.	Dishwasher and Cooking Equipment Pressure Reducing Valve:  For installation with dishwasher booster heater and other kitchen equipment, all brass, single seat type for dead end service, with renewable stainless steel seat and valve.  Designed for service on hot water to reduce pressure from [50 to psi to 20 psi].  Leslie, Watts, Cash-Acme, Zurn-Wilkins, or approved substitute.

C.	Handsink Tempering Valve:  Pressure compensating water mixing valve. Precision Plumbing Products “Tempera” valve or approved substitute.

D.	Secondary piping supports: Install manufactured secondary piping supports for support and positioning of fixture rough-in piping from framing members.  Hubbard, Sioux-Chief,  or approved substitute.

2.3	PLUMBING FIXTURES and trim

A.	Stops:  Furnish stop valves for all fixtures.  Loose key style, in wall, angle or straight through pattern to fit installation.  Stops to be all brass with full turn brass stem and replaceable washer, no plastic.  Compression nuts to be high copper content brass.  Finish to be copper nickel chrome plate.  Product to carry manufacturer’s name.  Risers to be chrome plated copper.  Provide chrome plated shallow escutcheons.  McGuire, Chicago, Brasskraft, Keeney, Zurn, or approved substitute.

B.	Fixture Traps:  Exposed fixture tailpieces, traps, and wastes shall be chrome plated 17 gauge seamless brass tube with cast brass nuts and deep or box style escutcheons as required to conceal rough piping.  Products to be stamped with manufacturer’s name and material gauge.  McGuire, Keeney, Zurn, or approved.

C.	Provide insulating covers on all exposed accessible lavatory and sink fixture traps and water supplies.  Covers to be ASTM C1822 compliant.

D.	Fixtures Furnished by Owner (and/or Under Another Section):  Some fixtures will be furnished by the Owner (and/or under another specification section).  Include under this section the required rough-ins, 3/8" chrome plated supplies with stops, 1-1/2" chrome plated cast brass "P" trap (or, on kitchen sinks, 2" cast iron "P" traps) for each sink compartment, and make final connection.  Verify all rough-ins and connection requirements before commencing work.

## PART 3  EXECUTION

3.1	PIPING

A.	Install in accordance with Section 22 1000.

B.	Install secondary pipe supports at rough-ins for all plumbing fixtures.

3.2	FIXTURE INSTALLATION AND CONNECTION

A.	All exposed fixture hardware and piping shall be plated with polished chrome unless otherwise directed in these specifications.

B.	All fixtures in contact with finished walls and floors shall be caulked with waterproof, white, non-hardening sealant which will not crack, shrink or change color with age.

C.	All fixtures and component parts shall conform to governing codes.

D.	All fixtures shall be securely mounted level and plumb or as recommended by the manufacturer.  Mount fixtures intended to be accessible to the handicapped at the dimensions required by code.

3.3	startup

A.	Adjust flush valves, pressure reducing valves, mixing valves, water heater thermostats, hot water circulating system balancing valves, and similar equipment.

B.	Remove construction protection, tags and labels and thoroughly clean all plumbing equipment and trim. Scour all fixtures just prior to building acceptance.

END OF SECTION  22 4000