# fSECTION 23 21 00 – Hydronic Piping and Pumps

## PART 1 – GENERAL

1.1	DESCRIPTION

A.	The requirements of this section apply to the HVAC heating and cooling water systems.  Provide pipe, pipe fittings, pumps, and related items required for complete piping system.

B.	Related Work:  The requirements of Section 23 05 00, Common HVAC Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	General:  ASTM and ANSI Standards are indicated.  In addition, special standards are referenced where neither ASTM nor ANSI Standards are applicable.

B.	Labeling:  All piping shall be continuously and legibly labeled on each length as required by codes and standards and including as a minimum, country of origin, manufacturers identification marking, wall thickness designation, and applicable standards and approvals.  Fittings shall be labeled as required by the referenced standard.

C.	Concealed Plastic Piping:  No concealed plastic piping inside the building unless approved by Code or Governing Authorities.

D.	Definitions:  Where piping fluid is not indicated in the following paragraphs, provide similar piping materials for similar fluids.

E.	All grooved couplings, and fittings, valves and specialties shall be the products of a single manufacturer.  Grooving tools shall be of the same manufacturer as the grooved components.

1.	All castings used for coupling housings, fittings, valve bodies, etc., shall be date stamped for quality assurance and traceability.

1.3	STORAGE AND HANDLING

A.	Provide factory-applied end caps on each length of pipe and tube.  Maintain end caps through shipping, storage and handling as required to prevent pipe-end damage and eliminate dirt and moisture from inside of pipe and tube.  Protect flanges and fittings from moisture and dirt by inside storage and enclosure, or by packaging with durable, waterproof wrapping.

1.4	SUBMITTALS

A.	Submit catalog data, construction details, performance characteristics for all equipment.

B.	Submit operating and maintenance data.

C.	Grooved joint couplings and fitting shall be referred to on drawings and product submittals, and be identified by the manufacturer’s listed model or series designation.

## PART 2 – PRODUCTS

2.1	PIPING MATERIALS

A.	Black Steel Pipe:

1.	Applications:

a.	Condensing water

2.	Pipe:  Systems 10" or smaller, operating below 400 psi, schedule 40, standard black steel pipe ASTM A-106 or A-53.

3.	Threaded Fittings:  For above ground installations only.

a.	Banded class 120 cast iron fittings, ANSI B16.4 to 125 psi.

b.	Banded class 150 malleable iron fittings, ANSI B16.3 to 150 psi.

4.	Welding Fittings:  Beveled ends, seamless fittings of the same type and class of piping above.

5.	Flanged Fittings:  For above ground installations only.

a.	Class 125 cast iron fittings, ANSI B16.2 including bolting to 125 psi.

b.	Class 150 steel welding neck flanges, ANSI B16.9 to 150 psi.

c.	Class 250 cast iron fittings, ANSI B16.1 including bolting to 250 psi.

d.	Class 300 steel welding neck flanges, ANSI B16.9 to 300 psi.

e.	Facing and Gasketing:  Selected for service pressures and temperatures.  Full-faced for cast iron and raised face for steel flanges.

6.	Grooved Fittings:  For above ground liquid installations only, of grooved or shouldered end designed to accept grooved mechanical couplings without field preparation.  Match gaskets for service and temperature indicated.

a.	Ductile Iron:  ASTM A-536.

b.	Factory-Fabricated Steel:  ASTM A-53, 3/4" to 1-1/2" Type F; 2"-20" Type E or S, Grade B.

c.	Steel:  ASTM A-234, Grade WPB. -

d.	Manufacturers:  Victaulic Company or accepted substitute.

7.	Victaulic Standard Mechanical Couplings: Manufactured in two segments of cast ductile iron, conforming to ASTM A-536, Grade 65-45-12. Gaskets shall be pressure-responsive synthetic rubber, grade to suit the intended service, conforming to ASTM D-2000. Mechanical Coupling bolts shall be zinc plated (ASTM B-633) heat treated carbon steel track head conforming to ASTM A-449 and ASTM A-183. Couplings shall comply with ASTM F1476 – Standard Specification for Performance of Gasketed Mechanical Couplings for Use in Piping Applications.

a.	Rigid Type: Coupling housings with offsetting, angle-pattern bolt pads shall be used to provide system rigidity and support and hanging in accordance with ANSI B31.1 and B31.9. Victaulic Style 107H/107N (Quick-Vic™), Installation ready rigid coupling for direct stab installation without field disassembly.  Gasket shall be Grade “EHP” EPDM designed for operating temperatures from -30 deg F (-34 deg C) to +250 deg F (+120 deg C).

b.	Flexible Type: Use in locations where vibration attenuation and stress relief are required. Flexible couplings may be used in lieu of flexible connectors at equipment connections. Three couplings, for each connector, shall be placed in close proximity to the vibration source.  Victaulic Style 177 (Quick-Vic™).  Installation ready flexible coupling.

B.	Plastic Pipe:

1.	Application:  Where approved by Code.

b.	Condensing water

2.	Pipe:

a.	Polyvinyl Chloride and Chlorinated Polyvinyl Chloride Plastic Pipe for Water Service:  SDR-PR pipe, ASTM D2241; Schedules 40, 80 and 120, ASTM D1785.

3.	Fittings:  Provide fittings of the type indicated, matching piping manufacture.  Where not otherwise indicated, provide fittings produced and recommended by the piping manufacturer for the service indicated.

2.2	MISCELLANEOUS PIPING MATERIALS/PRODUCTS

A.	Insulating (Dielectric) Fittings:  Provide standard products recommended by the manufacturer for use in the service indicated, and which effectively isolate ferrous from non-ferrous piping (electrical conductance), prevent galvanic action, and reduce corrosion.  Victaulic "Clear Flow."

B.	Welding Materials:  Provide welding materials as determined by the installer to comply with installation requirements

C.	Soldering and Brazing Materials:  Provide soldering materials as determined by the installer to comply with installation requirements.

1.	Tin-Antimony Solder:  ASTM B32, Grade 95TA.

2.	Lead-Free Solder:  ASTM B32, Grade HB.  Harris "Bridgit" approved.

3.	Silver Solder:  ASTM B32, Grade 96.5TS.

D.	Gaskets for Flanged Joints:  ANSI B16.21; full-faced for cast-iron flanges; raised-face for steel flanges.  Pressure and temperature rating required for the service indicated.

E.	Grooved Joint Lubricants: Lubricate gaskets in accordance with the manufacturer’s published installation instructions, using lubricant compatible with the gasket elastomer and fluid media. Basis of Design: Victaulic Vic-Lube.

F.	Sleeve Seal:  Rubber-link pipe wall and casing closure.  Thunderline Link-Seal.  For fire rated wall, floor or ceiling penetrations, 3-M "CP-25" caulk, "No. 303" putty and/or "PSS 7904" sealing system.

G.	Strainers:  "Y-pattern," 300-psig ductile iron body, or Class 125 [cast iron body] [bronze body] with tapped blow-off connection and removable [20 mesh] [1/16” perforations] [1/8” perforations] stainless steel screen.  Victaulic Style 732 / W732, NIBCO, or engineer approved equal.

H.	Tracer Wire:  14 gauge, single strand, copper wire with blue insulation for water, green for sanitary and storm sewers, and yellow for gas.  3M "DBY" direct bury splice kit required at all splices.

I.	Valves up to 12":

1.	Ball (to 2”):

a.	Two-piece, cast bronze body, full port, 600 psi WOG, T/S 585-70.

b.	Two-piece, forged bras body, standard port, 300 psi CWP, Victaulic P589.

2.	Gate (to 3”):  Bronze body, non-rising stem, 200 psi WOG, T/S-133.

3.	Gate (4” to 12”):  Iron body, non-rising stem, solid wedge, bolted bonnet, 200 psi WOG, F-619.

4.	Globe (shutoff):  Bronze body, Teflon disc, 200 psi WOG, T/S-211Y.

5.	Globe (throttling):  Bronze body, full plug stainless steel disc, 600 psi WOG,  T-276AP.

6.	Butterfly:  Ductile iron body, aluminum bronze, stainless steel, or electroless-nickel coated ductile iron disc, pressure responsive seat, and stem offset from the disc centerline to provide complete 360-degree circumferential seating. 300 psi WOG, Lugged body – LD-2000, Wafer body – WD-2000, Grooved body-Victaulic Vic-300 MasterSeal / AGS-Vic300.

7.	Check:  Bronze or iron body spring-assisted swing check for vertical or horizontal installation, 230 psi WOG, T/S-413B and F-918B, or Victaulic Series 716 and W715.

2.3	EXPANSION JOINT

A.	Stainless steel bellows type with flanged ends, controlled flexing, internal liner rated at a minimum of 28,000 average life cycles.  Provide amount of expansion indicated at each joint as shown on Drawings.  Carefully align joint and make proper allowance for temperature of pipe at time of installation.  Flexonics, Hyspan, or approved substitute.

B.	Grooved End Expansion Joints:

1.	Packless, Gasketed, Type: 350-psig maximum, grooved ends, telescoping type expansion joint consisting of a ductile iron housing, carbon steel ends, with PPS modified PTFE slide section coating. Suitable for axial end movement to 3” / 80mm. Basis of Design: Victaulic Style 150.

2.	Expansion fitting consisting of a series of grooved end nipple sections joined in tandem with Victaulic flexible type couplings. Pressure rating and total joint movement dependent on pipe size and the number of couplings used in the joint. Basis of Design: Victaulic Series 155.

2.4	PIPE ALIGNMENT GUIDES

A.	Manufactured steel guide which consists of heavy steel spider rigidly attached to pipe and housed in steel which is rigidly anchored.  Guides same as expansion joint manufacturer.

2.5	BACKFILL MATERIALS

A.	Subbase Materials:  A graded mixture of gravel, sand, crushed stone or crushed slag.

B.	Finely-Graded Subbase Material:  Well graded sand, gravel, crushed stone or crushed slag, with 100% passing a 3/8" sieve.

C.	Backfill Material:  Soil material suitable for compacting to the required densities, and complying with AASHTO designation M145, Group A-1, A-2-4, A-2-5, or A-3.

## PART 3 – EXECUTION

3.1	PIPE INSTALLATION

A.	General:  Install pipe, tube and fittings in accordance with recognized industry practices.  Install each run accurately aligned with a minimum of joints and couplings, but with adequate and accessible unions and flanges for disassembly, maintenance and/or replacement of valves and equipment.  Reduce sizes (where indicated) by use of reducing fittings.

B.	Piping Runs:  Route piping close to and parallel with walls, overhead construction, columns and other structural and permanent-enclosure elements of the building (pitched for drainage).  If not otherwise indicated, run piping in the shortest route which does not obstruct usable space or block access for servicing the building or equipment and avoid diagonal runs.  Wherever possible in finished and occupied spaces, conceal piping from view.  Do not encase horizontal runs in solid partitions.

3.2	PIPING JOINTS

A.	General:  Provide joints of the type indicated in each piping system, and where piping and joint as manufactured form a system, utilize only that manufacturer's material.

B.	Ferrous Threaded Piping:  Thread pipe in accordance with ANSI 82.l; cut threads full and clean using sharp dies.  Ream threaded ends to remove burrs and restore full inside diameter.  Apply pipe joint compound or pipe joint tape (Teflon) where recommended by pipe/fitting manufacturer, on male threads at each joint and tighten joint to leave no more than 3 threads exposed.

C.	Solder Copper Tube and Fitting Joints:  In accordance with recognized industry practice.  Cut tube ends squarely, ream to full inside diameter, and clean outside of tube ends and inside of fittings.  Apply solder flux to joint areas of both tubes and fittings.  Insert tube full depth into fitting, and solder in a manner which will draw solder full depth and circumference of joint.  Wipe excess solder from joint before it hardens.  "T-Drill" field formed tees may be utilized where the main is at least two pipe sizes larger than the branch.

D.	Braze Copper Tube and Fitting Joints:  Where indicated, in accordance with ANSI/ASME B31.5.  Pass a slow stream of dry nitrogen gas through the tubing at all times while brazing to eliminate formation of copper oxide.

E.	Weld Pipe Joints:  In accordance with recognized industry practice and as follows:

1.	Weld pipe joints only when ambient temperature is above 0 degrees F.

2.	Bevel pipe ends at a 37.5 degree angle, smooth rough cuts, and clean to remove slag, metal particles and dirt.

3.	Install welding rings for buttwelded joints.

4.	Use pipe clamps or tack-weld joints with 1" long welds; 4 welds for pipe sizes to 10"; 8 welds for pipe sizes up to 20".

5.	Build up welds with a stringer-bead pass, followed by a hot pass, followed by a cover of filler pass.  Eliminate valleys at center and edges of each weld.  Weld by procedures which will ensure elimination of unsound or unfused metal, cracks, oxidation, blow-holes and non-metallic inclusion.

6.	Do not weld out piping system imperfections by tack-welding procedures; refabricate to comply with requirements.

7.	Install forged branch-connection fittings wherever branch pipe is indicated, or install regular "T" fitting at Contractor's option.

F.	Flanged Joints:  Match flanges within piping system, and at connections with valves and equipment.  Clean flange faces and install gaskets.  Tighten bolts to provide uniform compression of gasket.

G.	Plastic Pipe/Tube Joints:  Comply with manufacturer's instructions and recommendations, and with applicable industry standards:

1.	Heat Joining of Thermoplastic Pipe:  ASTM D-2657.

2.	Making Solvent-Cemented Joints:  ASTM D-2865 and ASTM F-402.

H.	Grooved Pipe Joints:  Comply with fitting manufacturer's instructions for making grooves in pipe ends.  Assemble joints in accordance with manufacturer's instructions. Grooved ends shall be clean and free from indentations, projections, and roll marks. Remove burrs and ream pipe ends. Gaskets shall be molded and produced by the coupling manufacturer, and shall be verified as suitable for the intended service. A factory-trained field representative (direct employee) of the mechanical joint manufacture shall provide on-site training for contractor's field personnel in the proper use of grooving tools and installation of grooved piping products.  The factory-trained representative shall periodically review the product installation and ensure best practices are being followed.  Contractor shall remove and replace any improperly installed products. A distributor’s representative is not considered qualified to conduct the training.

I.	Insulating (Dielectric) Fittings:  Comply with manufacturer's instructions for installing unions or fittings.  Install in a manner which will prevent galvanic action and stop corrosion where the "joining of ferrous and non-ferrous piping" is indicated.

J.	Changes in Direction:  Use fittings for all changes in direction.  Run lines parallel with building surfaces.

K.	Line Grades:  Pitch hydronic piping 1" to 40' minimum to low point drips or drains.

L.	Unions and Flanges:  At all equipment to permit dismantling and elsewhere as consistent with good installation practice.

M.	Unions and flanges for servicing and disconnect are not required in installations with grooved mechanical joint couplings. (The couplings shall serve as disconnect points.)

N.	Expansion:  Provide loops, swing joints, anchors, runouts and spring pieces to prevent damage to piping or equipment.

1.	For water systems, Victaulic flexible couplings may be used to accommodate thermal growth, contraction, and for the elimination of expansion loops. (In accordance with the manufacturer’s written recommendations.) Where loops are required, use flexible couplings on the loop.

3.3	MISCELLANEOUS PIPING EQUIPMENT

A.	Floor, Wall and Ceiling Plates:  Chrome plated pressed steel or brass screw locked split plates on all pipe penetrations in finished spaces.

B.	Strainers:  Install in a manner to permit access for cleaning and screen removal and with blow-off valve.

C.	Sleeves:  At all penetrations of concrete or masonry construction.   PVC, 24 gauge galvanized steel or Schedule 40 galvanized steel pipe.  Use steel pipe sleeves through beams, footings, girders or columns and for all penetrations of walls or floors below grade.  Where floor finish is ceramic tile, terrazzo, or similar material extend standard steel pipe sleeves 1-1/2" above finished floor.  Fabricate sleeves 1" diameter larger than pipe or insulation.  PVC and sheet metal sleeves at non-structural penetrations only.

D.	Sleeve Caulking:  Grout uninsulated pipe with cement mortar or approved waterproof mastic.  All caulking or grouting shall extend full depth of sleeve.     Install UL sealing caulk, putty and/or system at all penetrations of fire rated walls, floors and ceiling.

E.	Valves:  Install valves in accordance with Section 23 05 00.  Install control valves specified in other division 23 sections.

3.4	EXCAVATING

A.	General:  Do not excavate for mechanical work until the work is ready to proceed without delay, to minimize the total time lapse from excavation to completion of backfilling.  Comply with all applicable Federal and state safety regulations.

B.	Width:  Excavate for piping with 6" to 9" clearance on both sides of pipe, except where otherwise shown or required for proper installation of pipe joints, fittings, valves and other work.  Excavate for other mechanical work to provide minimum practical but adequate working clearances.

C.	Depth for Direct Support:  For work to be supported directly on undisturbed soil, do not excavate beyond indicated depths, and hand-excavate the bottom cut to accurate elevations.  Support the following work on undisturbed soil at the bottom of the excavations:

1.	Piping of 5" and less pipe/tube size.

2.	Cast-in-place concrete.

D.	Depth for Subbase Support:  For large piping (6" pipe size and larger), tanks and where indicated for other mechanical work, excavate for installation of subbase material in the depth indicated, or, if not otherwise indicated, 6" below bottom of work to be supported.

E.	Depth for Exterior Piping:  Excavate for exterior water-bearing piping so that the top of piping will not be less than 3'  vertical distance below finished grade.

F.	Depth for Unsatisfactory Soil Conditions:  Where unsatisfactory soil condition at the bottom of excavation exists, excavate additional depth as directed to reach satisfactory soil-bearing condition.  Backfill with subbase material, compacted as directed, to indicated excavation depth.

G.	Rock and Boulder Removal:  Refer to Division 1 for procedure on additional work, including additional excavating and backfilling, rock removal, etc.

H.	Protection of Trees:  Excavate near large trees (within the drip line) by hand, and protect the root system from damage or dryout to the greatest extent possible.  Maintain moist condition for root system and cover exposed roots with burlap.  Paint root cuts of 1" diameter and larger with asphaltic tree paint.

I.	Excavated Materials:  Store excavated material (temporarily) near the excavation, in a manner which will not interfere with or damage the excavation or other work.  Do not store under trees (within the drip line).  Retain excavated material which complies with the requirements for backfill material.  Dispose of excavated material which is either in excess of quantity needed for backfilling or does not comply with requirements for backfill material.

3.5	DEWATERING

A.	Maintain dry excavation for mechanical work, by removing water.  Protect excavations from inflow of surface water.  Pump minor inflow of ground water from excavations; protect excavations from major inflow of ground water, by installing temporary sheeting and waterproofing.  Provide adequate barriers which will protect other excavations and below-grade property from being damaged by water, sediment or erosion from or through mechanical work excavations.  Comply with local erosion control regulations where applicable.

3.6	BASE PREPARATION

A.	Subbase Installation:  Where indicated, install subbase material to receive mechanical work, and compact by tamping to form a firm base for the work.  For 4" and larger piping, horizontal cylindrical tanks and similar work, shape and subbase to fit the shape of the bottom 90 degrees of the cylinder, for uniform continuous support.  Provide finely-graded subbase material for wrapped, coated and plastic pipe and tank.  Shape subbases and bottoms of excavation with recesses to receive pipe bells, flanged connections, valves and similar enlargements in the piping systems and set bottom of trench at proper pitch and correct elevations with subbase material.

B.	Concrete Encasement:  Where piping under roadways is less than 2'-6" below surface of roadway, provide 4" base slab of concrete to support piping. After piping is installed and tested, provide 4" thick encasement (sides and top) of concrete before backfilling.  Provide Class 250 concrete for encasement and slab.

3.7	BACKFILLING

A.	Do not backfill until installed mechanical work has been tested and accepted wherever testing is indicated.  Install drainage fill where indicated, and tamp to a uniform firm density.  Backfill with finely-graded subbase material to 6" above wrapped, coated and plastic piping and tanks, and to center line of other tanks (where recommended by tank manufacturer, use "pea gravel" backfill).  Condition backfill material by either drying or adding water uniformly, to whatever extent may be necessary to facilitate compaction to the required densities.  Do not backfill with frozen materials.

3.8	EQUIPMENT INSTALLATION

A.	Installation and Arrangement:  Install and arrange as shown on the Drawings.  Comply with manufacturer's recommendations for installation connections and start-up.

B.	Lubrication:  Lubricate all moving and rotating parts in accordance with the manufacturer's recommendations prior to start-up.

C.	Expansion Joint and Compensator Installation:  Carefully align joint or compensator and make proper allowance for temperature of pipe at time of installation.

3.9	CLEANING

A.	General:  Clean all dirt and construction dust and debris from all mechanical piping systems and equipment and leave in a new condition.  Touch up paint where necessary.

B.	Heating, Solar, Chilled and Condensing Water Piping Systems:

1.	Add cleaning chemical in proper concentration to clean system of manufacturing and installation contamination and residue.

2.	Fill, vent and circulate the system with this solution at design operating temperature.  After circulating for four hours, bleed out cleaning solution by the addition of fresh water to the system.

3.	Test for pH and add sufficient amount of the cleaning chemical to obtain a pH between 7 and 8.

4.	Clean all strainers and remove start-up strainers (from suction diffusers) after the system has operated for one week.

3.10	TEST

A.	General:

1.	Minimum duration of two hours or longer, as directed for all tests.  Furnish report of test observation signed by qualified inspector.  Make all tests before applying insulation, backfilling, or otherwise concealing piping or connecting fixtures or equipment.  Where part of the system must be tested to avoid concealment before the entire system is complete, test that portion separately, same as for entire system.

2.	Provide all necessary temporary equipment for testing, including pump and gauges.  Remove control devices before testing and do not use piping system valves to isolate sections where test pressure exceeds valve pressure rating.  Fill each section with water and pressurize for the indicated pressure and time.

3.	Observe each test section for leakage at end of test period.  Test fails if leakage is observed or if pressure drop exceeds 5% of test pressure.

B.	Repair:

1.	Repair piping system sections which fail the required piping test by disassembly and re-installation, using new materials to the extent required to overcome leakage.  Do not use chemical stop-leak compounds, solder, mastics, or other temporary repair methods.

2.	Drain test water from piping systems after testing and repair work has been completed.

C.	Heating, Solar, Chilled and Condensing Water Piping:  75 psig hydrostatic for 30 psig systems without loss for four hours.

D.	Tanks and Equipment:  Hydrostatic pressure to 1.5 times operating pressure.

END OF SECTION