# SECTION 22 30 00 - PLUMBING equipment

## PART 1 - GENERAL

1.1 DESCRIPTION

A. The requirements of this section apply to the plumbing equipment.

B. Provide plumbing equipment specified and shown on the Drawings.

C. Related Work: The requirements of Section 22 05 00, Common Plumbing Materials and Methods, also apply to this section.

1.2 QUALITY ASSURANCE

A. Code: Comply with requirements of the Oregon State Plumbing Specialty Code.

B. All equipment and component parts shall conform to governing codes.

C. Labeling: All equipment shall have permanent labels affixed by the manufacturer listing model number, capacity, efficiency, approvals, and similar characteristics of the product.

## PART 2 - PRODUCTS

2.1 PIPING

A. Piping, fittings, pumps, and related items are specified in Section 22 10 00.

2.2 Commercial High Efficiency Gas-fired INSTANTANEOUS Water Heater:

A. Design Built Contractor responsible for design and selection of water heaters to fit the needs of the building and the space constraints of the water heater rooms.

2.3 Water Heater accessories

A. Water Heater and Tank Seismic Restraints: For water heaters and tanks, Spacemaker, Holdrite “Quickstrap,” or approved.

B. Domestic Water Expansion Tank: Plastic lined drawn steel tank for potable water with epoxy exterior finish, air charging valve and system piping connection. Butyl rubber diaphragm with steel retaining ring. Provide with relief valve where working pressure rating is less than 150 psi.

C. Water Heater drain pan: Fabricated metal drain pan with reinforced rim and outlet connection.

D. Water heater vent: Provide venting materials complying with water heater manufacturers installation requirements (Use CPVC where plastic pipe is allowed).

## PART 3 - EXECUTION

3.1 UTILITY SERVICE

A. Plumbing Utility Connections: Complete installation. Verify rough in dimensions of equipment prior to installing piping.

3.2 equipment INSTALLATION AND CONNECTION

A. All equipment shall be installed plumb and level unless otherwise recommended by the manufacturer.

B. Arrange piping connections to equipment to allow removal and replacement of the equipment without disassembly of connecting piping. Provide valves, unions, flanges, etc. at connection points.

C. Arrange equipment for adequate service access as recommended by the manufacturer and as required by code.

D. Anchor equipment to resist displacement due to seismic events as detailed on the drawings, recommended by the manufacturer, and as required by code and as specified in other sections of these specifications. Provide seismic straps as specified above for tank type water heaters.

E. Drip Pans: Provide drip pans under all domestic hot water heaters. Provide 3/4" drainage piping, properly discharged to over floor drain, other approved receptor, or as shown on the Drawings.

3.3 equipment CLEANING

A. Remove construction and shipping protection and thoroughly clean all plumbing equipment just prior to building acceptance.

3.4 SUPERVISION AND START-UP

A. Do not place equipment onto operation until required work of other trades is complete, e.g. venting systems, combustion air ducts, etc.

B. Follow manufacturer’s instructions for start-up and adjustment of equipment.

END OF SECTION 22 30 00