# SECTION 23 77 00 - VRV HEAT RECOVERY

## PART 1 - GENERAL

1.1	System: VARIABLE REFRIGERANT VOLUME (VRV IV) AIR CONDITIONING

SPECIFICATION – Three Pipe Heat Recovery

1.2	SYSTEM DESCRIPTION

A.	The variable capacity, heat recovery air conditioning system shall be a Daikin Variable Refrigerant Volume Series (heat and cool model) split system as specified.  The system shall consist of multiple evaporators, branch selector boxes, REFNET™ joints and headers, a three pipe refrigeration distribution system using PID control and Daikin VRV condenser unit. The condenser shall be a direct expansion (DX), air-cooled heat recovery, multi-zone air-conditioning system with variable speed inverter driven compressors using R-410A refrigerant.  The condensing unit may connect an indoor evaporator capacity up to 200% of the condensing unit capacity.  All zones are each capable of operating separately with individual temperature control.  A dedicated hot gas pipe shall be required to ensure optimum heating operation performance.  Two-pipe, heat recovery systems utilizing a lower temperature mixed liquid/gas refrigerant to perform heat recovery are not acceptable due to reduced heating capabilities.

B.	The Daikin condensing unit shall be interconnected to indoor unit models FXFQ, FXHQ, FXMQ, FXLQ, FXNQ, FXTQ, FXDQ, FXZQ, FXAQ, FXMQ_MF and FXUQ and shall range in capacity from 7,500 Btu/h to 96,000 Btu/h in accordance with Daikin’s engineering data book detailing each available indoor unit.  The indoor units shall be connected to the condensing unit utilizing Daikin’s REFNET™ specified piping joints and headers to ensure correct refrigerant flow and balancing.  T style joints are not acceptable for a variable refrigerant system.

C.	Operation of the system shall permit either individual cooling or heating of each indoor unit simultaneously or all of the indoor units associated with each branch of the cool/heat selector box (BSQ_T / BS_Q54T).  Each indoor unit or group of indoor units shall be able to provide set temperature independently via a local remote controller, an Intelligent Controller, an Intelligent Manager or a BMS interface.

D.	Branch selector boxes shall be located as shown on the drawing. The branch selector boxes shall have the capacity to control up to 290 MBH (cooling) downstream of the branch selector box.  Each branch of the branch selector box shall consist of three electronic expansion valves, refrigerant control piping and electronics to facilitate communications between the box and main processor and between the box and indoor units.  The branch selector box shall control the operational mode of the subordinate indoor units.  The use of three EEV’s ensures continuous heating during defrost (multiple condenser systems), no heating impact during changeover and reduced sound levels.  The use of solenoid valves for changeover and pressure equalization shall not be acceptable due to refrigerant noise.

E.	The REYQ_T condensing unit model numbers and the associated number of connectable indoor units per REYQ_T condensing unit is indicated in the following table.  Each indoor unit or group of indoor units shall be independently controlled.

| Model Number | Nominal Capacity (Tons) | Number of Connectable Indoor Units |
| --- | --- | --- |
| REYQ72TTJU | 6 | 12 |
| REYQ96TTJU | 8 | 16 |
| REYQ120TTJU | 10 | 20 |
| REYQ144TTJU | 12 | 25 |
| REYQ168TTJU | 14 | 29 |
| REYQ192TTJU | 16 | 33 |
| REYQ216TTJU | 18 | 37 |
| REYQ240TTJU | 20 | 41 |
| REYQ264TTJU | 22 | 45 |
| REYQ288TTJU | 24 | 49 |
| REYQ312TTJU | 26 | 54 |
| REYQ336TTJU | 28 | 58 |
| REYQ360TTJU | 30 | 64 |
| REYQ384TTJU | 32 | 64 |
| REYQ408TTJU | 34 | 64 |
| REYQ432TTJU | 36 | 64 |
| REYQ456TTJU | 38 | 64 |

1.3	VRV IV FEATURES AND BENEFITS

A.	Voltage Platform –Heat recovery condensing units shall be available with a 208-230V/3/60 power supply.

B.	Advanced Zoning – A single system shall provide for up to 64 zones.

C.	Independent Control – Each indoor unit shall use a dedicated electronic expansion valve with 2000 positions for independent control.

D.	VFD Inverter Control and Variable Refrigerant Temperature – Each condensing unit shall use high efficiency, variable speed all “inverter” compressor(s) coupled with inverter fan motors to optimize part load performance. The system capacity and refrigerant temperatures shall be modulated automatically to set suction and condensing pressures while varying the refrigerant volume for the needs of the cooling or heating loads. The control will be automatic and customizable depending on load and weather conditions.

E.	Indoor units shall use PID to control superheat to deliver a comfortable room temperature condition and optimize efficiency.

F.	Configurator software – Each system shall be available with configurator software package to allow for remote configuration of operational settings and also for assessment of operational data and error codes. If this software is not provided by an alternate manufacturer, for each individual outdoor unit the contractor shall do the settings manually and keep detailed records for future maintenance purposes.

G.	Autocharging – Each system shall have a refrigerant auto-charging function.

H.	Defrost Heating – Multiple condenser VRV systems shall maintain continuous heating during defrost operation.  Reverse cycle (cooling mode) defrost operation shall not be permitted due to the potential reduction in space temperature.

I.	Oil Return Heating – Multiple condenser VRV systems shall maintain continuous heating during oil return operation.  Reverse cycle (cooling mode) oil return during heating operation shall not be permitted due to the potential reduction in space temperature.

J.	Low Ambient Cooling – Each system shall be capable of low ambient cooling operation to -4°F DB.

K.	Independent Control – Each indoor unit shall use a dedicated electronic expansion valve for independent control.

L.	Flexible Design –

1.	Systems shall be capable of up to 540ft (623ft equivalent) of linear piping between the condensing unit and furthest located indoor unit.

2.	Systems shall be capable of up to 3,280ft total “one-way” piping in the piping network.

3.	Systems shall have a vertical (height) separation of up to 295ft between the condensing unit and the indoor units.

4.	Systems shall be capable of up to 295ft from the first REFNET™ / branch point.

5.	The condensing unit shall have the ability to connect an indoor unit evaporator capacity of up to 200% of the condensing unit capacity.

6.	Systems shall be capable of 98ft vertical separation between indoor units.

7.	Condensing units shall be supported with a fan motor ESP up to 0.32”. WG as standard to allow connection of discharge ductwork and to prevent discharge air short circuiting.

M.	Oil Return – Each system shall be furnished with a centrifugal oil separator and active oil recovery cycle.

N.	Simple Wiring – Systems shall use 16/18 AWG, 2 wire, multi-stranded, non-shielded and non-polarized daisy chain control wiring.

O.	Outside Air – Systems shall provide outside air capability.

P.	Space Saving – Each system shall have a condensing unit module footprint as small as 36-5/8’’ x 30-1/8’’.

Q.	Advanced Diagnostics – Systems shall include a self-diagnostic, auto-check function to detect a malfunction and display the type and location.

R.	Each condensing unit shall incorporate contacts for electrical demand shedding with optional 3 stage demand control with 12 customizable demand settings.

S.	Advanced Controls – Each system shall have at least one remote controller capable of controlling up to 16 indoor units.

T.	Each system shall be capable of integrating with open protocol BACnet and LonWorks building management systems.

U.	Low Sound Levels – Each system shall use indoor and condensing units with quiet operation as low as 27 dB(A).

1.4	QUALITY ASSURANCE

A.	The units shall be tested by a Nationally Recognized Testing Laboratory (NRTL), in accordance with ANSI/UL 1995 – Heating and Cooling Equipment and bear the Listed Mark.

B.	All wiring shall be in accordance with the National Electric Code (NEC).

C.	The system will be produced in an ISO 9001 and ISO 14001 facility, which are standards set by the International Standard Organization (ISO).  The system shall be factory tested for safety and function.

D.	Mechanical equipment for wind-born debris regions shall be designed in accordance with ASCE 7-2010 and installed to resist the wind pressures on the equipment and the supports.

E.	The condensing unit will be factory charged with R-410A.

1.5	DELIVERY, STORAGE AND HANDLING

A.	Unit shall be stored and handled according to the manufacturer’s     recommendations.

1.6	INSTALLATION REQUIREMENTS

A.	The system must be installed by a Daikin factory trained contractor/dealer.

1.7	STANDARD LIMITED WARRANTY

A.	Daikin North America LLC warrants original owner of the non-residential building, multifamily residence or residence in which the Daikin products are installed that under normal use and maintenance for comfort cooling and conditioning applications such products (the “Products”) will be free from defects in material and workmanship. This warranty applies to compressor and all parts and is limited in duration to ten (10) years starting from the ‘’installation date’’ which is one of the two dates below:

1.	The installation date is the date that the unit is originally commissioned, but no later than 18 months after the manufacture date noted on the unit’s rating plate.

2.	If the date the unit is originally commissioned cannot be verified, the installation date is three months after the manufacture date.

## PART 2 - PRODUCTS

See Appendix for product cut sheets and system layouts.

2.1	BaSIS of design/Acceptable manufactures

A.	The HVAC equipment basis of design is Daikin.  All bidders shall furnish the minimum system standards as defined by the base bid model numbers, model families or as otherwise specified herein (see Key General Specifications Alternate Supplier Checklist).  In any event the contractor shall be responsible for all specified items and intents of this document without further compensation.

B.	Sanyo, LG, Trane, Samsung, Mitsubishi or approved

2.2	The VRV IV REYQ_T system shall perform as indicated below:

| Model Number | System IEER* (part load - ducted) | System IEER* (part load – non-ducted) | System IEER* (part load - mixed) |
| --- | --- | --- | --- |
| REYQ72TTJU | 20.80 | 26.20 | 23.50 |
| REYQ96TTJU | 21.00 | 29.30 | 25.15 |
| REYQ120TTJU | 20.70 | 25.40 | 23.05 |
| REYQ144TTJU | 20.70 | 24.20 | 22.45 |
| REYQ168TTJU | 19.50 | 22.00 | 20.75 |
| REYQ192TTJU | 20.40 | 22.90 | 21.65 |
| REYQ216TTJU | 20.20 | 22.90 | 21.55 |
| REYQ240TTJU | 19.20 | 21.90 | 20.55 |
| REYQ264TTJU | 18.10 | 21.60 | 19.85 |
| REYQ288TTJU | 18.20 | 21.40 | 19.80 |
| REYQ312TTJU | 17.80 | 20.20 | 19.00 |
| REYQ336TTJU | 17.00 | 19.00 | 18.00 |
| REYQ360TTJU | 17.90 | 19.60 | 18.75 |
| REYQ384TTJU | 16.60 | 18.30 | 17.45 |
| REYQ408TTJU | 16.50 | 17.20 | 16.85 |
| REYQ432TTJU | 16.50 | 16.20 | 16.35 |
| REYQ456TTJU | 15.90 | 16.20 | 16.05 |

| Model Number | System SCHE* (part load - ducted) | System SCHE* (part load – non-ducted) | System SCHE* (part load - mixed) |
| --- | --- | --- | --- |
| REYQ72TTJU | 22.60 | 27.80 | 25.20 |
| REYQ96TTJU | 23.00 | 27.30 | 25.15 |
| REYQ120TTJU | 25.10 | 27.90 | 26.50 |
| REYQ144TTJU | 23.80 | 25.50 | 24.65 |
| REYQ168TTJU | 22.80 | 26.60 | 24.70 |
| REYQ192TTJU | 22.90 | 26.60 | 24.75 |
| REYQ216TTJU | 22.50 | 25.60 | 24.05 |
| REYQ240TTJU | 22.70 | 25.60 | 24.15 |
| REYQ264TTJU | 22.00 | 24.40 | 23.20 |
| REYQ288TTJU | 21.40 | 23.30 | 22.35 |
| REYQ312TTJU | 20.30 | 23.60 | 21.95 |
| REYQ336TTJU | 20.40 | 23.20 | 21.80 |
| REYQ360TTJU | 20.20 | 22.60 | 21.40 |
| REYQ384TTJU | 18.70 | 22.40 | 20.55 |
| REYQ408TTJU | 18.30 | 21.80 | 20.05 |
| REYQ432TTJU | 18.10 | 21.10 | 19.60 |
| REYQ456TTJU | 17.90 | 20.90 | 19.40 |

| Model Number | System EER* (full load - ducted) | System EER* (full load – non-ducted) | System EER* (full load - mixed) |
| --- | --- | --- | --- |
| REYQ72TTJU | 13.40 | 15.80 | 14.60 |
| REYQ96TTJU | 13.10 | 15.10 | 14.10 |
| REYQ120TTJU | 12.60 | 13.90 | 13.25 |
| REYQ144TTJU | 11.90 | 12.90 | 12.40 |
| REYQ168TTJU | 11.30 | 11.70 | 11.50 |
| REYQ192TTJU | 12.60 | 12.50 | 12.55 |
| REYQ216TTJU | 12.40 | 12.50 | 12.45 |
| REYQ240TTJU | 11.60 | 12.20 | 11.90 |
| REYQ264TTJU | 10.50 | 11.80 | 11.15 |
| REYQ288TTJU | 10.90 | 11.80 | 11.35 |
| REYQ312TTJU | 10.60 | 11.30 | 10.95 |
| REYQ336TTJU | 10.00 | 10.70 | 10.35 |
| REYQ360TTJU | 11.00 | 10.80 | 10.90 |
| REYQ384TTJU | 9.80 | 9.80 | 9.80 |
| REYQ408TTJU | 9.70 | 9.80 | 9.75 |
| REYQ432TTJU | 9.70 | 9.80 | 9.75 |
| REYQ456TTJU | 9.50 | 9.50 | 9.50 |

| Model Number | System COP@17F* (full load - ducted) | System COP@17F* (full load – non-ducted) | System COP@17F* (full load - mixed) |
| --- | --- | --- | --- |
| REYQ72TTJU | 2.63 | 2.77 | 2.70 |
| REYQ96TTJU | 2.31 | 2.63 | 2.47 |
| REYQ120TTJU | 2.32 | 2.54 | 2.43 |
| REYQ144TTJU | 2.35 | 2.56 | 2.46 |
| REYQ168TTJU | 2.15 | 2.32 | 2.24 |
| REYQ192TTJU | 2.38 | 2.55 | 2.47 |
| REYQ216TTJU | 2.28 | 2.45 | 2.37 |
| REYQ240TTJU | 2.31 | 2.48 | 2.40 |
| REYQ264TTJU | 2.26 | 2.42 | 2.34 |
| REYQ288TTJU | 2.24 | 2.41 | 2.33 |
| REYQ312TTJU | 2.24 | 2.41 | 2.33 |
| REYQ336TTJU | 2.06 | 2.18 | 2.12 |
| REYQ360TTJU | 2.17 | 2.42 | 2.30 |
| REYQ384TTJU | 2.06 | 2.34 | 2.20 |
| REYQ408TTJU | 2.06 | 2.09 | 2.08 |
| REYQ432TTJU | 2.06 | 2.08 | 2.07 |
| REYQ456TTJU | 2.05 | 2.07 | 2.06 |

| Model Number | System COP@47F* (full load - ducted) | System COP@47F* (full load – non-ducted) | System COP@47F* (full load - mixed) |
| --- | --- | --- | --- |
| REYQ72TTJU | 3.82 | 4.29 | 4.06 |
| REYQ96TTJU | 3.72 | 4.25 | 3.99 |
| REYQ120TTJU | 3.51 | 3.98 | 3.75 |
| REYQ144TTJU | 3.55 | 3.81 | 3.68 |
| REYQ168TTJU | 3.33 | 3.77 | 3.55 |
| REYQ192TTJU | 3.67 | 3.84 | 3.76 |
| REYQ216TTJU | 3.67 | 3.73 | 3.70 |
| REYQ240TTJU | 3.55 | 3.67 | 3.61 |
| REYQ264TTJU | 3.38 | 3.55 | 3.47 |
| REYQ288TTJU | 3.26 | 3.51 | 3.39 |
| REYQ312TTJU | 3.22 | 3.56 | 3.39 |
| REYQ336TTJU | 3.20 | 3.52 | 3.36 |
| REYQ360TTJU | 3.31 | 3.51 | 3.41 |
| REYQ384TTJU | 3.21 | 3.21 | 3.21 |
| REYQ408TTJU | 3.20 | 3.21 | 3.21 |
| REYQ432TTJU | 3.20 | 3.21 | 3.21 |
| REYQ456TTJU | 3.20 | 3.21 | 3.21 |

A.	Performance Conditions

1.	Cooling:  indoor temp. of 80°F DB, 67°F WB and outdoor temp. of 95°F DB.

2.	Heating:  indoor temp. of 70°F DB and outdoor temp. of 47°F DB, 43°F WB.

3.	Equivalent piping length:  25ft

2.3	OPERATING RANGE

A.	The operating range in cooling or cooling dominant simultaneous cooling/heating will be (-4°F) 23°F DB ~ 122°F DB.

B.	Each system as standard shall be capable of onsite reprogramming to allow low ambient cooling operation down to -4°F DB.

C.	The operating range in heating or heating dominant simultaneous cooling/heating will be -13°F WB – 60°F WB.

D.	If an alternate equipment manufacturer is selected, the mechanical contractor shall provide, at their own risk and cost, all additional material and labor to meet low ambient operating condition and performance.

1.	Cooling mode indoor room temperature range will be 57°F-77°F WB.

2.	Heating mode indoor room temperature range will be 59°F-80°F DB.

2.4	REFRIGERANT PIPING

A.	The system shall be capable of refrigerant piping up to 540 actual feet or 623 equivalent feet from the condensing unit to the furthest indoor unit, a total combined liquid line length of 3,280 feet of piping between the condensing and indoor units with 295 feet maximum vertical difference, without any oil traps.

B.	REFNET™ piping joints and headers shall be used to ensure proper refrigerant balance and flow for optimum system capacity and performance.  T style joints shall not be acceptable as this will negatively impact proper refrigerant balance and flow for optimum system capacity and performance.

2.5	CONDENSING UNIT

A.	General:  The condensing unit is designed specifically for use with VRV IV series components.

1.	The condensing unit shall be factory assembled in the USA and pre-wired with all necessary electronic and refrigerant controls.  The refrigeration circuit of the condensing unit shall consist of Daikin inverter scroll compressors, motors, fans, condenser coil, electronic expansion valves, solenoid valves, 4-way valve, distribution headers, capillaries, filters, shut off valves, oil separators, service ports, liquid receiver and suction accumulator.

2.	High/low pressure gas line, liquid and suction lines must be individually insulated between the condensing and indoor units.

3.	The condensing unit can be wired and piped with access from the left, right, rear or bottom.

4.	The connection ratio of indoor units to condensing unit shall be permitted up to 200%.

5.	Each condensing system shall be able to support the connection of up to 64 indoor units dependent on the model of the condensing unit.

6.	The sound pressure level standard shall be that value as listed in the Daikin engineering manual for the specified models at 3 feet from the front of the unit.  The condensing unit shall be capable of operating automatically at further reduced noise during night time or via an external input.

7.	The system will automatically restart operation after a power failure and will not cause any settings to be lost, thus eliminating the need for reprogramming.

8.	The unit shall incorporate an auto-charging feature. Manual changing should be support with a minimum of 2 hours of system operation data to ensure correct operation.

9.	The condensing unit shall be modular in design and should allow for side-by-side installation with minimum spacing.

10.	The following safety devices shall be included on the condensing unit; high pressure sensor and switch, low pressure sensor, control circuit fuses, crankcase heaters, fusible plug, overload relay, inverter overload protector, thermal protectors for compressor and fan motors, over current protection for the inverter and anti-recycling timers.

11.	To ensure the liquid refrigerant does not flash when supplying to the various indoor units, the circuit shall be provided with a sub-cooling feature.

12.	Oil recovery cycle shall be automatic occurring 2 hours after start of operation and then every 8 hours of operation.  Each system shall maintain continuous heating during oil return operation.

13.	The condensing unit shall be capable of heating operation at  -13°F wet bulb ambient temperature without additional low ambient controls or an auxiliary heat source.

14.	The multiple condenser VRV systems shall continue to provide heat to the indoor units in heating operation while in the defrost mode.

B.	Unit Cabinet:

1.	The condensing unit shall be completely weatherproof and corrosion resistant.  The unit shall be constructed from rust-proofed mild steel panels coated with a baked enamel finish.

C.	Fan:

1.	The condensing unit shall consist of one or more propeller type, direct-drive 350 or 750 W fan motors that have multiple speed operation via a DC (digitally commutating) inverter.

| Model Number | Fan Motor Output (kW) & Quantity |
| --- | --- |
| REYQ72TTJU | 0.40 |
| REYQ96TTJU | 0.35 x 2 |
| REYQ120TTJU | 0.35 x 2 |
| REYQ144TTJU | 0.65 x 2 |
| REYQ168TTJU | 0.65 x 2 |
| REYQ192TTJU | (0.40 x 1) + (0.35 x 2) |
| REYQ216TTJU | (0.35 x 2) x 2 |
| REYQ240TTJU | (0.35 x 2) + (0.65 x 2) |
| REYQ264TTJU | (0.35 x 2) + (0.65 x 2) |
| REYQ288TTJU | (0.65 x 2) x 2 |
| REYQ312TTJU | (0.65 x 2) x 2 |
| REYQ336TTJU | (0.65 x 2) x 2 |
| REYQ360TTJU | (0.35 x 2) x 3 |
| REYQ384TTJU | (0.35 x 2) x 2 + (0.65 x 2) |
| REYQ408TTJU | (0.35 x 2) + (0.65 x 2) x 2 |
| REYQ432TTJU | (0.65 x 2) x 3 |
| REYQ456TTJU | (0.65 x 2) x 3 |

2.	The condensing unit fan motor shall have multiple speed operation of the DC (digitally commutating) inverter type, and be of high external static pressure and shall be factory set as standard at 0.12 in. WG.  A field setting switch to a maximum 0.32 in. WG pressure is available to accommodate field applied duct for indoor mounting of condensing units.

3.	The fan shall be a vertical discharge configuration with a nominal airflow maximum range of 5,544 CFM to 24,684 CFM dependent on model specified.

4.	Nominal sound pressure levels shall be as shown below.

| Model Number | Sound Pressure Level dB(A) |
| --- | --- |
| REYQ72TTJU | 58 |
| REYQ96TTJU | 61 |
| REYQ120TTJU | 61 |
| REYQ144TTJU | 65 |
| REYQ168TTJU | 65 |
| REYQ192TTJU | 63 |
| REYQ216TTJU | 64 |
| REYQ240TTJU | 66 |
| REYQ264TTJU | 66 |
| REYQ288TTJU | 68 |
| REYQ312TTJU | 68 |
| REYQ336TTJU | 68 |
| REYQ360TTJU | 66 |
| REYQ384TTJU | 68 |
| REYQ408TTJU | 69 |
| REYQ432TTJU | 70 |
| REYQ456TTJU | 70 |

5.	The fan motor shall have inherent protection and permanently lubricated bearings and be mounted.

6.	The fan motor shall be provided with a fan guard to prevent contact with moving parts.

7.	Night setback control of the fan motor for low noise operation by way of automatically limiting the maximum speed shall be a standard feature.  Operation sound level shall be selectable from 3 steps as shown below.

| Operation Sound dB(A) | Night Mode Sound Pressure Level dB(A) |
| --- | --- |
| Step 1 max. | 55 |
| Step 2 max. | 50 |
| Step 3 max. | 45 |

D.	Condenser Coil:

1.	The condenser coil shall be manufactured from copper tubes expanded into aluminum fins to form a mechanical bond.

2.	The heat exchanger coil shall be of a waffle louver fin and rifled bore tube design to ensure high efficiency performance.

3.	The heat exchanger on the condensing units shall be manufactured from Hi-X seamless copper tube with N-shape internal grooves mechanically bonded on to aluminum fins to an e-Pass Design.

4.	The fins are to be covered with an anti-corrosion Ulta Gold coating as standard with a salt spray test rating of 1000hr (ASTM B117 & Blister Rating:10), Acetic acid salt spray test: 500hr (ASTM G85 & Blister Rating:10)

5.	The pipe plates shall be treated with powdered polyester resin for corrosion prevention.  The thickness of the coating must be between 2.0 to 3.0 microns.

6.	The outdoor coil shall have three-circuit heat exchanger design eliminating the need for bottom plate heater. The lower part of the coil shall be used for inverter cooling and be on or off during heating operation enhancing the defrost operation.

7.	The condensing unit shall be factory equipped with condenser coil guards on all sides.

E.	Compressor:

1.	The Daikin inverter scroll compressors shall be variable speed (PVM inverter) controlled which is capable of changing the speed to follow the variations in total cooling and heating load as determined by the suction gas pressure as measured in the condensing unit.  In addition, samplings of evaporator and condenser temperatures shall be made so that the high/low pressures detected are read every 20 seconds and calculated.  With each reading, the compressor capacity (INV frequency) shall be controlled to eliminate deviation from target value. Non inverter-driven compressors, which may cause starting motor current to exceed the nominal motor current (RLA) and require larger wire sizing, shall not be allowed.

2.	The inverter driven compressor in each condensing unit shall be of highly efficient reluctance DC (digitally commutating), hermetically sealed scroll “G-type” or “J-type”.

3.	Neodymium magnets shall be adopted in the rotor construction to yield a higher torque and efficiency in the compressor instead of the normal ferrite magnet type.  At complete stop of the compressor, the neodymium magnets will position the rotor into the optimum position for a low torque start.

4.	The capacity control range shall be as low as 3% to 100%.

5.	The compressors’ motors shall have a cooling system using discharge gas, to avoid sudden changes in temperature resulting in significant stresses on winding and bearings.

6.	Each compressor shall be equipped with a crankcase heater, high pressure safety switch, and internal thermal overload protector.

7.	Oil separators shall be standard with the equipment together with an intelligent oil management system.

8.	The compressor shall be spring mounted to avoid the transmission of vibration eliminating the standard need for spring insolation.

9.	Compressor configurations

| Tonnage | Number of Compressors | Compressor Types |
| --- | --- | --- |
| 6 | 1 | Inverter controlled |
| 8 | 2 | All inverter controlled |
| 10 | 2 | All inverter controlled |
| 12 | 2 | All inverter controlled |
| 14 | 2 | All inverter controlled |
| 16 | 3 | All inverter controlled |
| 18 | 4 | All inverter controlled |
| 20 | 4 | All inverter controlled |
| 22 | 4 | All inverter controlled |
| 24 | 4 | All inverter controlled |
| 26 | 4 | All inverter controlled |
| 28 | 4 | All inverter controlled |
| 30 | 6 | All inverter controlled |
| 32 | 6 | All inverter controlled |
| 34 | 6 | All inverter controlled |
| 36 | 6 | All inverter controlled |
| 38 | 6 | All inverter controlled |

10.	In the event of compressor failure the remaining compressors shall continue to operate and provide heating or cooling as required at a proportionally reduced capacity.  The microprocessor and associated controls shall be designed to specifically address this condition.

11.	In the case of multiple condenser modules, conjoined operation hours of the compressors shall be balanced by means of the Duty Cycling Function, ensuring sequential starting of each module at each start/stop cycle, completion of oil return, completion of defrost or every 8 hours and extending the operating life of the system. When connected to a central control system, sequential start is activated for all system on each DIII network.

F.	Electrical:

1.	The power supply to the condensing unit shall be 208-230 volts, 3 phase, 60 hertz +/- 10%.

| Power Supply Voltage | Voltage Range |
| --- | --- |
| 208-230V/3/60 | 187V-253V |

| Model | MCA | MOP | Compressor RLA |
| --- | --- | --- | --- |
| REYQ72TTJU | 30.2 | 35 | 20.7 |
| REYQ96TTJU | 38.0 | 45 | 13.7 + 13.7 |
| REYQ120TTJU | 43.0 | 50 | 15.0 + 15.0 |
| REYQ144TTJU | 55.0 | 70 | 16.2 + 22.6 |
| REYQ168TTJU | 61.9 | 70 | 17.4 + 24.4 |
| REYQ192TTJU | 30.2 + 43.0 | 35 + 50 | 20.7 + (15.0 + 15.0) |
| REYQ216TTJU | 38.0 + 43.0 | 45 + 50 | (13.7 + 13.7) + (15.0 + 15.0) |
| REYQ240TTJU | 38.0 + 55.0 | 45 + 70 | (13.7 + 13.7) + (16.2 + 22.6) |
| REYQ264TTJU | 43.0 + 55.0 | 50 + 70 | (15.0 + 15.0) + (16.2 + 22.6) |
| REYQ288TTJU | 55.0 + 55.0 | 70 + 70 | (16.2 + 22.6) x 2 |
| REYQ312TTJU | 55.0 + 61.9 | 70 + 70 | (16.2 + 22.6) + (17.4 + 24.4) |
| REYQ336TTJU | 61.9 + 61.9 | 70 + 70 | (17.4.2 + 24.4) x 2 |
| REYQ360TTJU | 43.0 + 43.0 + 43.0 | 50 + 50 + 50 | (15.0 + 15.0) x 3 |
| REYQ384TTJU | 38.0 + 43.0 + 61.9 | 45 + 50 + 70 | (13.7 + 13.7) + (15.0 + 15.0) + (17.4 + 24.4) |
| REYQ408TTJU | 38.0 + 55.0 + 43.0 | 45 + 70 + 70 | (13.7 + 13.7) + (16.2 + 22.6) + (17.4 + 24.4) |
| REYQ432TTJU | 55.0 + 55.0 + 55.0 | 70 + 70 + 70 | (16.2 + 22.6) x 3 |
| REYQ456TTJU | 55.0 + 55.0 + 61.9 | 70 + 70 + 70 | (16.2 + 22.6) x 2 + (17.4 + 24.4) |

1.	The control voltage between the indoor and condensing unit shall be 16VDC non-shielded, stranded 2 conductor cable.

2.	The control wiring shall be a two-wire multiplex transmission system, making it possible to connect multiple indoor units to one condensing unit with one 2-cable wire, thus simplifying the wiring installation.

3.	The control wiring lengths shall be as shown below.

|  | Condenser to Indoor Unit | Condenser to Central Controller | Indoor Unit to Remote Control |
| --- | --- | --- | --- |
| Control Wiring Length | 6,665 ft | 3,330 ft | 1,665 ft |
| Wire Type | 16/18 AWG, 2 wire, non-polarity, non-shielded, stranded |  |  |

2.6	BS(4/6/8/10/12)Q_T BRANCH SELECTOR BOX FOR VRV IV HEAT RECOVERY SYSTEM

A.	General:  The BSQ36TVJ, BSQ60TVJ, BSQ96TVJ, BS4Q54TVJ, BS6Q54TVJ, BS8Q54TVJ, BS10Q54TVJ and BS12Q54TVJ branch selector boxes are designed specifically for use with VRV IV series heat recovery system components.

1.	These selector boxes shall be factory assembled, wired, and piped.

2.	These BSQ_T / BS(4/6/8/10/12)Q54T branch controllers must be run tested at the factory.

3.	These selector boxes must be mounted indoors.

4.	When simultaneously heating and cooling, the units in heating mode shall energize their subcooling electronic expansion valve.

5.	The number of connectable indoor units shall be in accordance with the table below:

| Model Number | Maximum Connectable Cooling Capacity | Maximum Number of Connectable Indoor Units Per Branch |
| --- | --- | --- |
| BSQ36TVJ | 36,000 Btu/h | 4 |
| BSQ60TVJ | 60,000 Btu/h | 8 |
| BSQ96TVJ | 96,000 Btu/h | 8 |
| BS4Q54TVJ | 144,000 Btu/h | 5 |
| BS6Q54TVJ | 216,000 Btu/h | 5 |
| BS8Q54TVJ | 290,000 Btu/h | 5 |
| BS10Q54TVJ | 290,000 Btu/h | 5 |
| BS12Q54TVJ | 290,000 Btu/h | 5 |

B.	Unit Cabinet:

1.	These units shall have a galvanized steel plate casing.

2.	Each cabinet shall house 3 electronic expansion valves for refrigerant control per branch.

3.	The cabinet shall contain one subcooling heat exchanger per branch.

4.	The unit shall have sound absorption thermal insulation material made of flame and heat resistant foamed polyethylene.

5.	Nominal sound pressure levels must be measured and published on the submittals by the manufacturer. These sound levels must not exceed the values below.

| Model Number | Sound Level dB(A) Operating | Sound Level dB(A) Max |
| --- | --- | --- |
| BSQ36TVJ | 42 | 32 |
| BSQ60TVJ | 43 | 32 |
| BSQ96TVJ | 44 | 34 |
| BS4Q54TVJ | 38 | 45 |
| BS6Q54TVJ | 39 | 47 |
| BS8Q54TVJ | 39 | 47 |
| BS10Q54TVJ | 40 | 48 |
| BS12Q54TVJ | 40 | 48 |

a.	If an alternate manufacturer is selected, the mechanical contractor shall provide, at their own cost and expense, any additional material and labor to meet the published sound levels above.

C.	Dimensions:

1.	Each BSQ_T unit shall be no larger than 8-1/8” x 15-1/4” x 12-13/16”.

2.	Each BS4Q_T shall be no larger than 11-3/4” x 14-9/16” x 18-15/16”.

3.	Each BS(6/8)Q_T shall be no larger than 11-3/4” x 22-13/16” x 18-15/16”.

4.	Each BS(10/12)Q_T shall be no larger than 11-3/4” x 32-5/16” x 18-15/16”.

D.	Refrigerant Valves:

1.	The unit shall be furnished with 3 electronic expansion valves per branch to control the direction of refrigerant flow.  The use of solenoid valves for changeover and pressure equalization shall not be acceptable due to refrigerant noise.

2.	The refrigerant connections must be of the braze type.

3.	In multi-port units, each port shall have its own electronic expansion valves. If common expansion/solenoid valves are used, redundancy must be provided.

4.	Each circuit shall have at least one (36,000 Btu/h indoor unit or smaller for the BSQ36TVJ, 54,000 Btu/h indoor unit or smaller for the BS(4/6/8/10/12)Q54TVJ, 60,000 Btu/h indoor unit or smaller for the BSQ60TVJ and 96,000 Btu/h indoor unit or smaller for the BSQ96TVJ) branch selector box.

5.	Multiple indoor units may be connected to a branch selector box with the use of a REFNET™ joint provided they are within the capacity range of the branch selector.

E.	Condensate Removal:

1.	The unit shall not require provisions for condensate removal. A safety device or secondary drain pan shall be installed by the mechanical contractor to comply with the applicable mechanical code, if an alternate manufacturer is selected.

F.	Electrical:

1.	The unit electrical power shall be 208/230 volts, 1 phase, 60 hertz.

2.	The unit shall be capable of operation within the limits of 187 volts to 255 volts.

3.	The minimum circuit amps (MCA) shall be 0.1 and the maximum overcurrent protection amps (MOP) shall be 15.

4.   	The control voltage between the indoor and condensing unit shall be 16VDC non-shielded 2 conductor cable.

## Part 3 - Execution

3.1	See specification section 23 00 00 for general HVAC/Air Handling installation.

## PART 4 - APPENDIX

4.1	Cut Sheets and General System Layout.

END OF SECTION 23 77 00