# SECTION 21 13 50 - ELECTRIC-DRIVE HORIZONTAL FIRE PUMPS

## PART 1   GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.02	SUMMARY

A.	This Section includes electric-drive, horizontal fire pumps for building fire-suppression systems and the following:

1.	In-line fire pumps.

2.	Pressure-maintenance pumps.

3.	Full-service, fire-pump controllers.

4.	Automatic transfer switches.

5.	Pressure-maintenance-pump controllers.

6.	Fire-pump specialties and accessories.

7.	Pressure-maintenance-pump specialties and accessories.

8.	Alarm panels.

9.	Flow-measuring systems.

B.	Related Sections include the following:

1.	Division 21 Section for Fire Suppression System.

2.	Division 26 Sections for Fire Alarm System.

1.03	DEFINITIONS

A.	Fire Pump:  Horizontal-type fire pump used to supply water at rated capacity and total head required for fire-suppression service.

B.	Fire-Pump Unit:  Assembly with fire pump, driver, controller, and related accessories.

C.	In-Line Fire Pump:  Radially split-case, horizontal fire pump with drive unit supported by pump, suction and discharge flanges on same centerline, and pump shaft in vertical position.

D.	Pressure-Maintenance Pump (or Jockey Pump):  Electric-drive pump used to maintain water pressure in fire-suppression piping system.

E.	Pressure-Maintenance-Pump Unit:  Assembly with pressure-maintenance pump, driver, controller, and related accessories.

1.04	SYSTEM PERFORMANCE REQUIREMENTS

A.	Fire-Pump Systems:  Fire-pump and pressure-maintenance-pump units that comply with performance requirements specified and are compatible with building fire-suppression systems.

B.	Pump, Equipment, Accessory, and Piping Pressure Rating:  175-psig (1200-kPa) minimum working-pressure rating, unless higher rating is indicated.

1.05	SUBMITTALS

A.	Product Data:  Include rated capacities; certified pump performance curves with each selection point indicated; shipping, installed, and operating weights; furnished specialties; and accessories for each fire-pump and pressure-maintenance-pump unit and flow-measuring system.

B.	Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, methods of field assembly, components, and location and size of each field connection for each fire-pump and pressure-maintenance-pump unit.

1.	Wiring Diagrams:  Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.

2.	Shop Drawings may be incorporated into other Division 13 fire-suppression piping system Shop Drawings.

C.	Product Certificates:  Signed by manufacturers of fire pumps and fire-pump controllers certifying that products furnished comply with requirements.

D.	Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.

E.	Maintenance Data:  For each fire-pump and pressure-maintenance-pump unit to include in maintenance manuals specified in Division 1.

1.06	QUALITY ASSURANCE

A.	Manufacturer Qualifications:  Firms whose fire pumps, pressure-maintenance pumps, drivers, controllers, and accessories are listed by product name and manufacturer in UL's "Fire Protection Equipment Directory" and FM's "Fire Protection Approval Guide" and that comply with requirements indicated.  The following are exceptions and are not required:

1.	UL listing and FM approval of fire pump assembly.

B.	Source Limitations:  Obtain fire-pump and pressure-maintenance-pump units through one source with responsibility and accountability to respond to and resolve problems regarding compatibility, installation, performance, and acceptance of units.

C.	Provide listing/approval stamp, label, or other marking on equipment made to specified standards.

D.	Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

E.	Comply with standards of authorities having jurisdiction pertaining to materials, hose threads, and installation.

F.	Comply with NFPA 20, "Centrifugal Fire Pumps," for fire pumps, drivers, controllers, accessories, and installation.

1.07	DELIVERY, STORAGE, AND HANDLING

A.	Preparation for Shipping:  After assembling and testing fire pumps and pressure-maintenance pumps, protect flanges and exposed machined metal surfaces, pipe openings, and nozzles.

B.	Retain shipping flange protective covers and protective coatings during storage.

C.	Protect bearings and couplings against damage from sand, grit, or other foreign matter.

## pART 2   PRODUCTS

2.01	MANUFACTURERS

A.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B.	Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1.	Fire Pump Assemblies:  Peerless Pump, Aurora Pump.

2.02	IN-LINE FIRE PUMPS

A.	Description:  UL 448, factory-assembled and -tested, in-line, horizontal fire pump with electric-motor driver directly mounted to pump casing.

1.	Characteristics:  Capable of furnishing not less than 150 percent of rated capacity at not less than 65 percent of total rated head.  Shutoff head is limited to 140 percent of total rated head.

2.	Casing:  Radially split cast iron with suction and discharge flanges machined to ASME B16.1, Class 125 dimensions.

3.	Impeller:  Cast bronze, statically and dynamically balanced, closed, overhung, single suction, and keyed to shaft.

4.	Wear Rings:  Replaceable, bronze.

5.	Shaft and Sleeve:  Steel shaft with bronze sleeve.

6.	Shaft Bearings:  Grease-lubricated ball bearings in cast-iron housing.

7.	Seals:  Stuffing box with minimum of four rings of graphite-impregnated braided yarn and bronze packing gland.

8.	Finish:  Manufacturer's standard red paint applied to factory-assembled and -tested units before shipping.

9.	Nameplate:  Complete with capacities, characteristics, and other pertinent data.

2.03	PRESSURE-MAINTENANCE PUMPS

A.	Description:  Factory-assembled and -tested, electric-drive pumps with cast-iron or stainless-steel casing and bronze or stainless-steel impellers and mechanical seals.  Include flanged suction and discharge flanges machined to ASME B16.1, Class 125 dimensions, unless Class 250 flanges are indicated and except that connections may be threaded in sizes where flanges are not available.

1.	Multistage, Pressure-Maintenance Pumps:  Multiple-impeller type complying with HI 1.1-1.5 requirements for multistage centrifugal pumps.  Include base.

a.	Finish:  Manufacturer's standard color paint applied to factory-assembled and -tested unit before shipping.

b.	Nameplate:  Complete with capacity, characteristics, and other pertinent data.

2.04	PUMP DRIVERS

A.	Description:  NEMA MG 1, open-dripproof, squirrel-cage, induction motor.  Include construction complying with NFPA 20 and NFPA 70, and include wiring compatible with controller used.

1.	Finish:  Manufacturer's standard red paint applied to factory-assembled and -tested unit before shipping.

2.	Nameplate:  Complete with motor horsepower, characteristics, and other pertinent data.

2.05	PUMP CONTROLLERS, GENERAL

A.	Description:  Combined automatic and nonautomatic operation; factory assembled and wired; factory tested for capacities and electrical characteristics; and with the following features:

1.	Enclosure:  UL 50, Type 2, dripproof, indoor, unless special-purpose enclosure is indicated.

2.	Controls, devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used, and specific items listed for each controller type.

3.	Nameplate:  Complete with capacity, characteristics, approvals and listings, and other pertinent data.

4.	Controller Sensing Pipes:  Fabricate pipe and fittings according to NFPA 20 with nonferrous-metal sensing piping, NPS 1/2 (DN15), with globe valves for testing controller mechanism from system to pump controller as indicated.  Include bronze check valve with 3/32-inch (2.4-mm) orifice in clapper or ground-face union with noncorrosive diaphragm having 3/32-inch (2.4-mm) orifice.

2.06	FULL-SERVICE, FIRE-PUMP CONTROLLERS

A.	Description:  UL 218 and NFPA 20; listed for electric-drive, fire-pump service and service entrance.

1.	Type Starting:  Across the line.

B.	Rate controllers for scheduled horsepower.  Include short-circuit withstand rating at least equal to short-circuit current available at controller location.  Take into account cable size and distance from substation or supply transformers.

C.	Automatic Transfer Switches:  UL 218 and UL 1008 and requirements for and attached to fire-pump controllers.  Include enclosure complying with UL 50, Type 2, with automatic transfer switch with rating at least equal to fire-pump driver-motor horsepower.  Include ampere rating not less than 115 percent of motor full-load current and suitable for switching motor-locked rotor current.

D.	Controllers:  As follows:

1.	Isolating means and circuit breaker.

2.	"Power on" pilot lamp.

3.	Fire alarm system connections for indicating motor running condition, loss-of-line power, and line-power phase reversal.

4.	Automatic and manual operation, and minimum run-time relay to prevent short cycling.

5.	Water-pressure-actuated switch with independent high and low calibrated adjustments responsive to water pressure in fire-suppression system.

6.	Automatic and manual shutdown.

7.	System pressure recorder, electric ac driven with spring backup.

8.	Mounting:  Skid mounted on fire pump assembly for field electrical connections.

9.	Enclosure Finish:  Manufacturer's standard red paint applied to factory-assembled and -tested unit before shipping.

2.07	PRESSURE-MAINTENANCE-PUMP CONTROLLERS

A.	Description:  UL 508; factory-assembled, -wired, and -tested across-the-line type for combined automatic and nonautomatic operation.

1.	Enclosure:  UL 508 and NEMA 250, Type 2, wall-mounting type for field electrical wiring.

B.	Rate controller for scheduled horsepower and include the following:

1.	Fusible disconnect switch.

2.	Pressure switch.

3.	Hand-off-auto selector switch.

4.	Pilot light.

5.	Running period timer.

6.	Enclosure Finish:  Manufacturer's standard color paint applied to factory-assembled and -tested unit before shipping.

2.08	FIRE-PUMP SPECIALTIES AND ACCESSORIES

A.	Match fire-pump suction and discharge ratings as required for fire-pump capacity rating.  Include the following:

1.	Automatic air-release valve.

2.	Circulation relief valve.

3.	Suction and discharge pressure gages.

4.	Eccentric-tapered reducer at suction inlet.

5.	Concentric-tapered reducer at discharge outlet.

6.	Test-Header Manifold:  Ductile-iron or brass body for hose valves.  Include nozzle outlets arranged in single line; horizontal, flush-wall mounting attachment; and rectangular, brass escutcheon plate with lettering equivalent to "PUMP TEST CONNECTION."

a.	Escutcheon Plate Finish:  Rough brass.

7.	Hose Valves:  UL 668, straightway pattern, bronze with cap and chain.  Include NFPA 1963 hose thread that complies with local fire department standards and finish same as for test-header-manifold escutcheon plate.

8.	Ball Drip Valve:  UL 1726.

2.09	PRESSURE-MAINTENANCE-PUMP SPECIALTIES AND ACCESSORIES

A.	Match pressure-maintenance-pump suction and discharge ratings as required for pump capacity rating.  Include the following:

1.	Circulation relief valve.

2.	Suction and discharge pressure gages.

2.10	ALARM PANELS

A.	Description:  Factory-assembled and -wired remote panel complying with UL 508 and requirements in NFPA 20.  Include audible and visible alarms matching controller type.

1.	Enclosure:  NEMA 250, Type 2, remote wall-mounting type.

2.	Enclosure Finish:  Manufacturer's standard red paint applied to factory-assembled and -tested unit before shipping.

B.	Features:  Include manufacturer's standard features and the following:

1.	Motor-operating condition.

2.	Loss-of-line power.

3.	Phase reversal.

2.11	FLOW-MEASURING SYSTEMS

A.	Description:  FM-approved, fire-pump, flow-measuring systems that indicate flow to not less than 175 percent of fire-pump rated capacity.  Include sensor of size to match pipe, tubing, flow meter, and fittings.

1.	Pressure Rating:  175 psig (1200 kPa) minimum.

2.	Sensor:  Venturi, annular probe, or orifice plate, unless otherwise indicated.

3.	Flow Meter:  Compatible with flow sensor with dial not less than 4-1/2 inches (115 mm) in diameter or manufacturer's equivalent size.

4.	Permanently Mounted:  Flow meter suitable for wall mounting with copper tubing to connect to flow sensor.

5.	Include complete operating instructions.

2.12	SOURCE QUALITY CONTROL

A.	Factory Tests:  Hydrostatically test and test run fire pumps before shipping.  Test at 150 percent of shutoff head plus suction head, but not less than 250 psig (1725 kPa).  Produce certified test curves showing head capacity and brake horsepower of each pump.

2.13	SYSTEM SKID

A.	Mount fire pump, pressure maintenance pump controllers, flow test devices and associated valves, piping and supports on a single skid.  Skid shall be rated for seismic attachment to concrete floor (seismic Zone 4 equivalent rated assembly).

## PART 3   EXECUTION

3.01	EXAMINATION

A.	Examine areas, equipment foundations, and conditions, with Installer present, for compliance with requirements for installation and other conditions affecting fire-pump performance.

1.	Proceed with installation only after unsatisfactory conditions have been corrected.

B.	Examine roughing-in of fire-suppression piping systems.  Verify actual locations of piping connections before pump installation.

3.02	INSTALLATION

A.	Install pump system to provide access for periodic maintenance, including removal of motors, impellers, couplings, and accessories.

3.03	ALIGNMENT

A.	Make piping connections, check alignment, and make required corrections.

3.04	CONNECTIONS

A.	Piping installation requirements are specified in other Division 21 Section.  Drawings indicate general arrangement of piping and specialties.  The following are specific connection requirements:

1.	Install piping adjacent to fire and pressure-maintenance pumps to allow service and maintenance.

2.	Connect water supply to fire pumps assembly.

3.	Connect fire-pump discharge piping to building fire-suppression piping.

4.	Connect relief-valve discharge to point of disposal.

B.	Connect flow-measuring-system meters and sensors according to manufacturer's written instructions.

C.	Connect fire-pump controllers to building fire alarm system.  Refer to Division 26 Section "Fire Alarm Systems."

D.	Electrical wiring and connections are specified in Division 26 Sections.

3.05	FIELD QUALITY CONTROL

A.	Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including fire-pump and pressure-maintenance-pump units, piping, and electrical connections.  Report results in writing.

1.	Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

2.	Check suction line connections for tightness so no air gets into pumps.

3.	Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.  Remove malfunctioning units, replace with new units, and retest.

4.	Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

5.	Furnish fire hoses in number, size, and length required to reach storm drain or other acceptable location to dispose of fire-pump test water.  Fire hoses are for field-acceptance tests only and are not property of Owner.

6.	Final Checks before Startup:  Perform the following preventive-maintenance operations and checks:

a.	Lubricate oil-lubrication-type bearings.

b.	Remove grease-lubrication-type bearing covers, flush bearings with kerosene, and clean thoroughly.  Fill with new lubricant according to manufacturer's written instructions.

c.	Disconnect coupling and check electric motor for proper rotation.  Rotation shall match direction of rotation marked on pump casing.

d.	Verify that pump is free to rotate by hand.  If pump is bound or if it drags even slightly, do not operate until cause of trouble is determined and corrected.

7.	Starting procedure for pumps is as follows:

a.	Prime pump by opening suction valve and closing drains, and prepare pump for operation.

b.	Open sealing liquid supply valves if pump is so fitted.

c.	Start motor.

d.	Open discharge valve slowly.

e.	Observe leakage from stuffing boxes and adjust sealing liquid valve for proper flow to ensure lubrication of packing.  Do not tighten gland immediately but let packing run in before reducing leakage through stuffing boxes.

f.	Check general mechanical operation of pump and motor.

B.	Perform field tests for each fire-pump unit and system piping when installation is complete.  Comply with operating instructions and procedures in NFPA 20 to demonstrate compliance with requirements.  Where possible, field correct malfunctioning equipment, then retest to demonstrate compliance.  Replace equipment that cannot be satisfactorily corrected or that does not perform as indicated, then retest to demonstrate compliance.  Verify that each fire-pump unit performs as indicated.  Report test results in writing.

3.06	DEMONSTRATION

A.	Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units as specified below:

1.	Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining units.

2.	Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

3.	Schedule training with Owner with at least seven days' advance notice.

END OF SECTION

THIS PAGE INTENTIONALLY BLANK