## Section 1.4.1A
Project sq ft | 21729 (19594 conditioned)
Section 1.4 - Comparison of Baseline Design Versus Proposed Design
General Building Info Measure | Baseline Case ASHRAE 90.1-2010 |  |  | Proposed Case
Climate Zone | 4c |  |  | 4c
Building Area | 21729 | sq ft |  | 21729 | sq ft
Building Roof Area | 9399 |  |  | 9399 | sq ft
General System Type | System 3 Packaged Single Zone (PSZ-AC) |  |  | Chilled Beam and Steam Boiler
Total Energy Cost (subtracting Renewable) | 29118 |  |  | 24963
Building Energy Cost | 29118 |  |  | 24963
Total Energy | 1277 | Kbtu |  | 1130 | Kbtu
EUI | 58.7694 | Kbtu/sq ft |  | 52.0042 | Kbtu/sq ft
Energy Savings |  |  |  | 11.51% | % savings
Cost Savings |  |  |  | 14.27% | % savings | 28 | green globe points
[6 empty] | X | points under Energy Star
Steam Rate | 1.323 | $/therm |  | 1.323 | $/therm
Elect rate | 0.061 | $/Kwh |  | 0.061 | $/Kwh
Elect Consumption | 336728 | Kwh |  | 281680 | Kwh
Steam Consumption | 1141 | Therms |  | 1674 | Therms
Solar Production | 0 |  |  | 0 | therms
Solar Cost | 0 |  |  | 0
PV Production | 0 |  |  | 0 | KWH
PV Cost | 0 |  |  | 0
Solar Percentage |  |  |  | 0%
Section 1.4 - Comparison of Baseline Design Versus Proposed Design
1.4.1A -ASHRAE 90.1 Section 5: Building Envelope (Construction Assemblies)
Model Input Parameter / Energy Efficiency Measure | Baseline Case |  |  | Proposed Case
| Description | Insulation R-value | Assembly U-factor/ C-factor/ F-factor | Description | Insulation R-value | Assembly U-factor/ C-factor/ F-factor
Roofs | 90.1-10 Min Roof Zone 4-8 | R-20 ci | Insulation Entirely above Deck U=0.048 | 2x12 Frame roof with R-38 | R-38 | U=0.0281174
Roof SRI | Reflect = 0.3 & a=0.7 |  |  | Reflect = 0.3 & a=0.7
Walls - Above Grade | 90.1-10 Min Wall non res Zone 4-6 | Steel Frame R=13 + R7.5 ci | Steel Frame U=0.064 | Wood Frame 2x6-R21-with Face Brick | R=21 | U=0.0590438
Walls - Below Grade | none |  |  | none
Semiheated Exterior Envelope | none |  |  | none
Floors | Steel Joist R-30 (90.1 min floor zone 4-7) | R-30 | U=0.038 | 2x10 Wood Frame Floor with R-30 | R-30 | U=0.0343
Slab-On-Grade Floors | slab |  | F-0.73 | slab |  | F=0.73
Opaque doors
Other

## Section 1.4.1B to 1.4.7
1.4.1B - ASHRAE 90.1 Section 5: Fenestration and Shading
Include units for all relevant inputs
Model Input Parameter / Energy Efficiency Measure | Baseline Case | Proposed Case
Vertical fenestration Area (% of Wall area) | Wall = 11,281 Window = 1906 = =16.9% | Wall = 11,281 Window = 1906 = =16.9% | Old Window
Vertical Glazing Description-Residential | 90.1 Metal Framing | Pella Wood Clad | Jeld-Wen Premium Aluminum model A-500 Low e Argon filled
Vertical Glazing U-factor-Residential | U = 0.55 | U = 0.33 (assembly) | U = 0.37 (assembly)
Vertical Glazing SHGC - North -Residential | SHGC = 0.40 & SC = 0.46 | SHGC = 0.268 & SC = 0.308 | SHGC = 0.38 & SC = 0.44
Vertical Glazing SHGC Non-North - Residential | SHGC = 0.40 & SC = 0.46 | SHGC = 0.268 & SC = 0.308 | SHGC = 0.38 & SC = 0.44
Shading Devices | none | none
Fenestration Visual Light Transmittance-Residential | VT = 0.70 | VT = 0.48
Skylight Fenestration Area (percent of roof area) | none | none
Skylight Description | none | none
Skylight U-factor | none | none
Skylight SHGC | none | none
Building Self-Shading Description | none | none
Building Orientation & Shape1 | less than 5% difference | NA
Other
1 If energy cost by Baseline Rotation (0, 90, 180, 270) varies by more than 5%, describe the factors
contributing towards this variation (e.g. fenestration percentage by orientation, building form, etc.)
1.4.2 - ASHRAE 90.1 Section 6: HVAC (Air-Side)
Include units for all relevant inputs
Model Input Parameter / Energy Efficiency Measure | Baseline Case | Proposed Case
Primary HVAC Type1 | System 3 PSZ-AC (Packaged Rooftop AC) | 4 pipe chilled beam with air cooled chiller and hot water provided by a steam to water converter. Steam is from a campus steam boiler
Other HVAC Type2 | none | none
Semi-conditioned Space HVAC Type | none | none
Semi-conditioned Area (Gross SF) | none | none
Semi-conditioned Heating Capacity (Btuh) | none | none
Total Cooling Capacity | 53.4 tons | 45.6 tons (design) - 41.0 tons (simulation) - 40 ton nominal chiller operating at 43 tons
Unitary Cooling Capacity Ranges3 | 90.1-10 Min AC SS/SP Other 65-135 MBH & 90.1-10 LESS THAN 65 MBH | 40 ton air cooled chiller, see below for information
Unitary Cooling Efficiency4 | 11.0 EER & 13.0 SEER(MODELED AS 11.1 EER) | see below for chiller efficiences
Total Heating Capacity | 462 MBH | 168 MBH (simulation)
Unitary Heating Capacity Ranges5 | 462 MBH purchased gas heat | 1086 MBH steam to hot water converter (campus steam boiler)
Unitary Heating Efficiency6 | Purchased Campus heat 100% efficiency | Purchased Campus Steam
Fan System Operation | Cycles with Occupancy 7 day a week operation | Cycles with Occupancy 7 day a week operation
Outdoor Air Design Min Ventilation7 | 3521 cfm (total of ventilation unit) | 3521 cfm (total of ventilation unit)
Outdoor Air Design Min Ventilation dwelling units7 - | NA | NA
HVAC Air-side Economizer Cycle | dry bulb | dry Bulb
Economizer High-Limit Shutoff | 75 F | 75 F
Design Airflow Rates (Conditioned Space) | 18,161 cfm | 3638 + 3287 cfm of active air to chilled beams
Total System Fan Power (Conditioned)8 | 90.1-2007 ECB Fan Rules 16.25 KW | 7.32 KW (9.82 BHP) (sum of all design fan systems)
Total Supply Fan Power | 1.3 + 1.53 + .63 + 1.11 + .38 + 1.43 + 1.49 + .96 + 1.59 + = 10.42 KW | 6.64 hp = 4.95 KW
Total Return / Relief Fan Power | .66 + .77 + .32 + .56 + .76 + .72 + .75 + .49 + .8 = 5.83 KW | 3.18 hp = 2.37 KW
Total Exhaust Fan Power (tied to AHUs) | 0 | 0
6.5.3.1.1B Pressure Drop Adjusmtents9 | 0.5 ducted return | na
Zone Terminal Boxes Fan Power | na | na
Unconditioned Total Fan Power10 | na | na
Unconditioned Total Fan Flow10 | na | na
Semi-conditioned Total Fan Power10 | na
Semi-conditioned Total Fan Flow10 | na | na
Exhaust Air Energy Recovery11 | none | none
Demand Control Ventilation12 | none | none
Supply Air Temperature Reset Parameters | none | Yes, based on Relative Humidity - -chilled Beam system
Thermal Energy Storage | none | none
Other
1 Indicate the ASHRAE Baseline HVAC System Type Number From Table G3.1.1B (#1 - #8)
2 Indicate ASHRAE Baseline HVAC System Type Number From Table G3.1.1B (#1 - #8), and applicable exception to G3.1.1 that applies (indicate how the exception applies)
3 Unitary cooling capacity ranges should match tables 6.8.1A, 6.8.1B, or 6.8.1D
4 Efficiency should be reported per capacity range, and should match the units used for each capacity range in tables 6.8.1A, 6.8.1B, or 6.8.1D
5 Unitary heating capacity ranges should match tables 6.8.1B, 6.8.1D, or 6.8.1E
6 Efficiency should be reported per capacity range, and should match the units used for each capacity range in tables 6.8.1B, 6.8.1D, or 6.8.1E
7 Indicate Total System Fan Power including supply, return, exhaust and relief fan power
8 Indicate all pressure drop adjustments including devices for which credit is taken and the related adjustment.
9 Enter ventilation flow rate (not %). Baseline & Proposed ventilation rate must be equal unless Demand Control Ventilation is modeled for credit, in which case Baseline should reflect ASHRAE 62.1-2007 or local code minimum volumes.
10 Fan flow & power must be identical (except standard motor efficiencies from chapter 10 may be used in the Baseline). The exceptional calculation method may be used to show savings.
11 Indicate energy recovery efficiency, percentage of building served by ERV, and ERV bypass Mechanism, and verify that outside air is modeled with zero flow in both cases during unoccupied periods.
12 Indicate spaces with DCV, method of control used, and verify that outside air is modeled with zero flow in both cases during unoccupied periods.
1.4.3 - ASHRAE 90.1 Appendix G: HVAC (Water-side)
Include units for all relevant inputs
Model Input Parameter / Energy Efficiency Measure | Baseline Case | Proposed Case
The Project Has District Heating (Y/N) | Yes | Yes
The Project Has District Cooling (Y/N) | No | No
Number of Chillers | na | 1
Chiller Part-Load Controls1 | na | digital scroll
Chiller Capacity (Per Chiller) | na | 40 tons
Chiller Efficiency2 | na | 10.1 EER, IPLV = 14.9 (compressor 1.04 KW/ton)
Chilled Water Loop Supply Temperature | na | 44
Chilled Water (CHW) Loop Delta-T | na | 10
CHW Loop Temp Reset Parameters | na | Yes, based on OSA temp, and Humidity -10 deg reset
CHW Loop Configuration3 | na | primary & secondary
Number of Primary CHW Pumps | na | primary pump
Primary CHW Pump Power | na | 3.0 HP
Primary CHW Pump Flow | na | 110 gpm
Primary CHW Pump Speed Control | na | Constant
Secondary CHW Pump Power | na | 2.506 hp (ave of AHU and Chilled Beams)
Secondary CHW Pump Flow | na | 140
Secondary CHW Pump Speed Control | na | VFD
Number of Cooling Towers / Fluid Coolers | na | none
Cooling Tower Fan Power | na | na
Cooling Tower Fan Control | na | na
Condenser Water Leaving Temperature | na | na
Condenser Water (CW) Loop Delta-T | na | na
CW Loop Temp Reset Parameters | na | na
CW Loop Configuration3 | na | na
Number of CW Pumps | na | na
CW Pump Power | na | na
CW Pump Flow | na | na
CW Pump Speed Control | na | na
Number of Boilers | NA | 1 steam to water converter - Purchased Steam
Boiler Part-Load Controls | NA | control valve on converter
Boiler Capacity (Per Boiler) | NA | 1086 mbh converter
Boiler Efficiency2 | NA | Purchased Steam
Boiler Water Loop Supply Temperature | NA | 180
Hot Water or Steam (HHW) Loop Delta-T | NA | 47
HHW Loop Temp Reset Parameters | NA | none
HHW Loop Configuration3 | NA | primary & secondary
Number of Primary HHW Pumps | NA | Single primary pump
Primary HHW Pump Power | NA | 3/4 hp
Primary HHW Pump Flow | NA | 50 gpm
Primary HHW Pump Speed Control | NA | Constant
Secondary HHW Pump Power | na | 1 hp
Secondary HHW Pump Flow | na | 55 gpm
Secondary HHW Pump Speed Control | na | VFD
Thermal Energy Storage Capacity | na | na
Thermal Energy Storage Control Sequence | na | na
Thermal Energy Storage Charge Temp | na | na
Thermal Energy Storage Chiller Efficiency4 | na | na
Water-side Economizer | na | na
Water-side Energy Recovery | na | na
Other
1 Example - variable speed drive, dual compressors, etc.
2 Units of efficiency must match the units listed for the relevant equipment type in Tables 6.8.1F through 6.8.1J
3 Constant Primary / Variable Secondary, Variable Primary, etc.
4 The full-load efficiency of the chillers while charging the thermal energy storage tanks
1.4.4 - ASHRAE 90.1 Section 7: Service Water Heating
Include units for all relevant inputs
Model Input Parameter / Energy Efficiency Measure | Baseline Case | Proposed Case
SHW Equipment Type | Steam to Hot water Converter | Steam to Hot water Converter
SHW Storage Tank Capacity | Instantaneous | Instantaneous
SHW Heating Input Capacity1 | 1700 lbs/hr steam usage modeled as 23.03 MBH * | 1700 lbs/hr steam usage modeled as 23.03 MBH *
Equipment Efficiency1 | Purchased Steam | Purchased Steam
Temperature Controls | control valve set to 130 | control valve set to 130
SHW Energy Recovery | none | none
Hot Water Calculations | 217 persons x 106 btu/h = 23.03 MBH (based on EPACT modeling guidelines, using EPAC Non Residential schedule) | 217 persons x 106 btu/h = 23.03 MBH (based on EPACT modeling guidelines, using EPAC Non Residential schedule)
1 Units must match the relevant SWH Equipment Type in Table 7.8
1.4.5 - ASHRAE 90.1 Section 9: Lighting
Include units for all relevant inputs
Model Input Parameter / Energy Efficiency Measure | Baseline Case | Proposed Case
Automatic Lighting Shutoff Method | No Lighting Controls above code have been used | No Lighting Controls above code have been used
Gross Lighted Floor Area | 21729 sq ft | 21,729 sq ft
Interior Lighting Power Calc Method1 | Building Area Method | Building Area Method
Interior Lighting Power Density Dormitory | 0.90W/sq ft | 0.76 W/sq ft
Interior LPD per space (Space-by-Space)2 | no | no
Additional Lighting Power Allowance3 | 0 watts | 0 watts
Automatic Interior Space Shutoff Control in Required Spaces (Section 9.4.1.2)4 | yes | yes
Interior Lighting Power Adjustments (Table G3.2) 5 | none | none
Daylight Dimming Controls6 | none | none
Automatic Exterior Lighting Control | timeclock | timeclock
Total Exterior Lighting Power | 1.882 KW | 2.673 KW
Tradable Surface Exterior Lighting Power | 0.170 KW | 0.961 KW
Non-Tradable Surface Exterior Lighting Power7 | 1.712 KW | 1.712 KW
Other
1 Indicate whether Building Area Method or Space-by-Space Method was used. If Building Area Method
was used, indicate the Building Area Function (e.g. Office). If the Building includes a parking garage
or Tenant Spaces that differ from the main Building Area Function, indicate these separately.
2 If the Space-by-Space Method was used, indicate each space function, and the lighting power density per space function.
Alternatively, upload the lighting compliance documentation in Section 1.1B, and reference it in this table.
3 Indicate the total additional lighting power modeled, and the exceptions applied that allow additional lighting
(total additional lighting power modeled should be identical in the Baseline and Proposed case)
4 No credit may be taken for spaces where automated controls are required
5 Indicate the percentage credit taken, and the spaces for which the credit was applied.
6 Indicate the spaces where automated daylighting controls are included, and verify these were modeled
in the simulation program.
7 Values should be identical in the Baseline and Proposed Case
1.4.6 - Miscellaneous
Include units for all relevant inputs
Model Input Parameter / Energy Efficiency Measure | Baseline Case | Proposed Case
Receptacle equipment | 1.00 w/sq ft | 1.00 w/sq ft
Escalators and Elevators | none | none
Data Equipment | none | none
Process loads
Other