# SECTION 22 1000 – plumbing PIPing AND PumpS

## PART 1 - GENERAL

1.1	DESCRIPTION

A.	Provide pipe, pipe fittings, piping specialties, pumps and related items required for complete piping system.

B.	Related Work:  The requirements of Section 22 0500, Common Plumbing Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	General:  ASTM, and ANSI Standards are indicated.  In addition, special standards are referenced where neither ASTM nor ANSI Standards are applicable.

B.	Labeling:  All piping shall be continuously and legibly labeled on each length as required by codes and standards and including as a minimum, country of origin, manufacturer’s identification marking, wall thickness designation, and applicable standards and approvals.  Fittings shall be labeled as required by the referenced standard. Tubular fixture traps shall be stamped with manufacturer’s mark and material thickness.

C.	Potable Water Valves:  Potable water piping materials not limited to faucets, mixing valves, or pressure reducing valves.  Valves shall meet NSF/ANSI Standard 61, Section 9, for drinking water faucets and shall be brass construction.

D.	Plastic Piping:  All plastic piping systems including potable water and drain-waste-vent (DWV) shall meet NSF/ANSI Standard 14.

E.	Definitions:  Where piping fluid is not indicated in the following paragraphs, provide similar piping materials for similar fluids (i.e., "make-up water" = "domestic water"; "wet stand pipe" = "fire sprinkler pipe"; "drainage piping" = "sanitary/storm sewer piping").

F.	Plumbing System Disinfection shall be performed by an experienced, qualified, chemical treatment agency.  Mt. Hood Chemical, Chemcoa, Industrial Treatment of Water, or approved alternate.

1.3	STORAGE AND HANDLING

A.	Provide factory-applied end caps on each length of pipe and tube.  Maintain end caps through shipping, storage and handling as required to prevent pipe-end damage and eliminate dirt and moisture from inside of pipe and tube.  Protect flanges and fittings from moisture and dirt by inside storage and enclosure, or by packaging with durable, waterproof wrapping.

1.4	SUBMITTALS

A.	Submit catalog data for each product specified.

## PART 2 - PRODUCTS

2.1	PIPING MATERIALS

A.	Copper Pipe and Tube:

1.	Application:

a.	Domestic water

b.	Priming lines

2.	Pipe:  ASTM B88.

a.	Above Ground Domestic Water:  Type L hard temper copper with soldered joints.

b.	Underground Domestic Water and Priming Lines:  Type L soft annealed with no joints or type K hard tempered copper with silver soldered joints.

3.	Fittings:  Wrought copper solder-joint fittings, ANSI B16.22.

4.	Preinsulated Piping:  Type K solder joint copper piping with 1" thick urethane insulation protected by 20 gauge PVC outer jacket.  Rovanco "Insul/80," equivalent Rikwil or approved substitute.

5.	Domestic Water, 2-1/2” and Larger:  Rolled groove gasketed mechanical fittings with UPC approval.  Tyco-Grinnell CTS or Victaulic CTS, NIBCO Press System or approved.

6.	Domestic Water up to 4”:  UPC approved mechanically compressed copper or bronze fittings with EPDM O-ring seal.  Viega ProPress, Mueller approved.

B.	Plastic Pipe:

1.	Application:  Where approved by Code.

a.	Domestic water, systems operating at less than 80 psi and 140 degrees F.

2.	Pipe:

a.	Cross-linked polyethylene (PEX-a) tubing for Water Service: ASTM F877; SDR 9.  NSF-pw and NSF 61.

3.	Fittings:  Cold expansion (ASTM F1960) style fittings of the type indicated, matching piping manufacturer.  Where not otherwise indicated, provide fittings produced and recommended by the piping manufacturer for the service indicated.

C.	Plastic Pipe – Drain, Waste, Vent (DWV):

1.	Application:  Where allowed by Code only.

a.	Sanitary waste

b.	Plumbing vent

c.	Rain drain

2.	Pipe:

a.	Poly(vinyl chloride) (ASTM D1784) (PVC) solid core plastic drain, waste and vent pipe (ASTM D2665 and D1785) and fittings (ASTM D2665) (DWV).

3.	Fittings:  Provide fittings of the type indicated, matching piping manufacture.  Where not otherwise indicated, provide socket style, solvent weld fittings produced and recommended for the service indicated by the piping manufacturer.

D.	Cast Iron DWV Pipe:

1.	Application:  1-1/2”" and larger.

a.	Sanitary waste

b.	Plumbing vent

c.	Rain drain

2.	Pipe:  Hubless cast iron soil pipe, CISPI 301-05/ASTM A 888-05.

3.	Fittings:	Hubless cast iron fittings:  CISPI 301-05/ASTM A 888-05.

4.	Couplings:

a.	Standard Duty:  Standard couplings meeting CISPI 310/ASTM A 1277.

b.	Heavy Duty: No-hub couplings meeting ASTM C 1540, and FM 1680. ASTM C 564 neoprene gasket, type 304 SS corrugated shield and type 304 SS clamping bands.

d.	Couplings to Dissimilar Pipe in Concealed Locations:  Fernco "LowFlex" or approved substitute.

5.	Manufacturers:  Cast iron pipe and fittings – AB&I, Charlotte Pipe, Tyler Pipe, or approved.  All pipe shall be labeled by the manufacturer.

E.	Plastic Pipe:

1.	Application:  Where approved by Code.

a.	Cooling coil condensate drain

2.	Pipe:

a.	Polyvinyl Chloride and Chlorinated Polyvinyl Chloride Plastic Pipe for Water Service:  SDR-PR pipe, ASTM D2241; Schedules 40, 80 and 120, ASTM D1785.

3.	Fittings:  Provide fittings of the type indicated, matching piping manufacturer.  Where not otherwise indicated, provide socket style, solvent weld fittings produced and recommended by the piping manufacturer for the service indicated.

2.2	MISCELLANEOUS PIPING MATERIALS

A.	Insulating (Dielectric) Fittings:  Provide standard products recommended by the manufacturer for use in the service indicated, and which effectively isolate ferrous from non-ferrous piping (electrical conductance), prevent galvanic action, and reduce corrosion.  Victaulic "Clear Flow."

B.	Soldering and Brazing Materials:  Provide soldering materials as determined by the installer to comply with installation requirements.

1.	Tin-Antimony Solder:  ASTM B32, Grade 95TA.

2.	Lead-Free Solder:  ASTM B32, Grade HB.  Harris "Bridgit" approved.

3.	Silver Solder:  ASTM B32, Grade 96.5TS.

4.	Flux: Water soluble paste flux.

5.	Brazing filler rod: BCuP  rod to suit conditions.

C.	Gaskets for Flanged Joints:  ANSI B16.21; full-faced for cast-iron flanges; raised-face for steel flanges.  Pressure and temperature rating required for the service indicated.

D.	Pipe Sleeves:  For installation in cast in place concrete floor systems.  UL 1479 listed with ratings for fire, smoke, and water intrusion.  Cast in place pipe sleeve with external waterstop collar and interior pipe seal and intumescent collar.  Holdrite “Hydroflame”.

E.	Sleeve Seal:  Rubber-link pipe wall and casing closure.  Thunderline Link-Seal.  For fire rated wall, floor or ceiling penetrations, 3-M "CP-25" caulk, "No. 303" putty and/or "PSS 7904" sealing system.

F.	Strainers:  "Y-pattern," Class 125 [epoxy coated iron body] [bronze body] with tapped blow-off connection and removable 20 mesh stainless steel screen.  NIBCO or equal.

G.	Tracer Wire:  14 gauge, single strand, copper wire with blue insulation for water, green for sanitary and storm sewers, and yellow for gas.  3M "DBY" direct bury splice kit required at all splices.

2.3	PIPING specialties

A.	Cleanouts:

1.	Manufacturer:  Jay R. Smith, Zurn, Wade, Watts, Josam, Mifab, Sioux Chief, or approved substitute.

2.	Types:

a.	Tile Floor Cleanouts:  Smith 4053-U with square heavy-duty nickel bronze top, bronze plug, and vandalproof screws.  Adjustable top where cast into floor slab.

b.	Carpeted Floor Cleanout:  Smith 4023-U-X with round heavy-duty nickel bronze top, bronze plug, carpet clamping device, and vandalproof screws. Adjustable top where cast into floor slab.

c.	Concrete Floor Cleanout:  Smith 4023 with round heavy-duty nickel bronze top. Adjustable top where cast into floor slab.

d.	Wall Cleanouts:  Smith 4472-U, bronze ferrule with raised head bronze plug, stainless steel shallow cover and vandalproof screws.

e.	Outside Area Walks and Drives:  Smith 4253-U-G with galvanized cast iron body, top secured with vandalproof screws, and bronze plug.  Install in 18” x 18” x 6” deep concrete pad flush with grade.

f.	Plastic Body Cleanouts:  At Contractor’s option, where ABS-DWV or PVC-DWV piping is approved, compatible plastic body cleanouts may be substituted.  Cleanouts shall have finished tops of style and material as specified above.

B.	Drains:

1.	Manufacturers: Zurn, Jay R. Smith, Josam, Watts, Wade, Froet Industries, Mifab, Sioux Chief, or approved substitute.  Where numbers are scheduled on the drawings they represent minimum the acceptable standard for locations involved.

2.	Cast iron construction with acid resistant coating, anchor flange, and other options as indicated by model number listed on the drawings.  PVC drains where specifically noted.  Cast iron dome strainers on roof drains.

3.	Install sheet flashing, extending not less than 10" from and clamped to all drains not completely cast-in-place in a homogeneous material.

C.	Trench Drain:  Polyester concrete material, cast channels with 0.6% sloped bottom and with cast iron grate.  Length as indicated on the Drawings.  ACO Drain Incorporated "Channel Slope" NW-100 with No. 603 catch basins where indicated or approved substitute.

D.	Trench Drain:  UV and chemical resistant HDPE interlocking 4”, channel sections in flat and presloped styles with bottom or end outlets as shown.  Provide with grate anchors and construction covers.  Coordinate grate choice with Owner.  Sioux Chief, Zurn or Mifab.

E.	Hydromechanical Grease Interceptor:  The interceptor vessel shall be formed of seamless chemical resistant thermoplastic suitable for underground installation with up to 72” of cover and 160 deg. F influent.  Interceptor shall incorporate an internal flow control device and inlet diffusion baffle and operate with a balanced air environment.  Average unit efficiency shall be not less than 95%. Vessel shall include 3 optional outlet locations and shall provide for a discharge sampling point.  Service access to be provided via H-20 traffic rated access rings and secured covers. When required by the installation, unit shall include cut-to-length riser extensions with watertight connections.  Schier, Endura, Mifab or approved substitute.

F.	Flashing:  Minimum 4# sheet lead; to extend horizontally 10” from edge of vent penetrations or rain drain body and vertically 12” minimum up from roof turned over and down into hub of vent or finished with bronze cap providing counterflashing for screwed pipe.

G.	Shock Arrester:  Precharged bellows or sealed piston type manufactured to meet PDI WH-201 and ASSE 1010 Standards.  Size in accordance with PDI procedures.  Jay R. Smith, PPP, Sioux Chief, Wade, Zurn, Watts, Josam, Mifab WHB or approved substitute.

H.	Priming Valves:  Smith 2699, Josam 88250, Wade W8800T, Zurn Z1022, Watts MS810 or equivalent Precision Plumbing, Mifab.  Locate in closets, under counters or in walls behind access panels as specified in Section 22 0500.  Use copper specified previously for all underground priming lines.

I.	Traps:  Except chrome plated fixture traps.  Recessed drainage pattern for threaded pipe and same grade as pipe for cast iron and plastic pipe; with cleanout plugs in trap body in all above grade locations.

J.	Pressure Reducing Valve:  Single seat type with in-line renewable stainless steel seat diaphragm, and valve.  Size and capacity as shown on Drawings.  Bronze bodies with screwed connections on valves 2-1/2” and smaller and flanged steel bodies on valves 3” and larger.  Install each PRV with strainer on inlet or internal strainer.  Select for 15 psi fall-off at indicated flow.  Leslie, Watts, Apollo, Cash-Acme, Zurn-Wilkins, or approved substitute.

K.	Backflow Preventer:  Where indicated on the Drawings, install a reduced pressure backflow preventer complete with strainer on inlet, shutoff valves, two separate check valves, differential relief valve with drain funnel, and test cocks.  USC Foundation for Cross Connection Control, State Health Officials, and serving utility approved.  Bronze bodies on units 2” and smaller, cast iron bodies with bronze trim on units 2-1/2” and larger, and stainless steel construction for carbonated beverage service.

L.	Master Mixing Valve Station:

1.	Mixing valve station shall be fully factory assembled and tested incorporating type L copper tube with solder fittings, isolation ball valves on all inlet and outlet connections, check valves on inlet lines, recirculating pump with aquastat and timeclock wired to a junction box for single point power connection, circulating line balancing valve, check valve, [strainer,]and thermometer, all mounted [in a hinged door, stainless steel cabinet for] [to an assembled mounting frame for floor or] wall mounting.  Provide pressure reducing valves on multiple mixing valve stations.  All piping connections shall be labeled.

2.	Master Mixing Valve(s) of all brass or bronze body with stainless steel parts, electronic thermostatic master control element to fail safe upon cold water or control element failure meeting ASSE 1017.  Provide with strainers on inlets, and dial thermometer(s) on [inlets and] outlet.  Valve location, arrangement and capacity as shown on plans.

3.	Manufacturers:  Leonard, Bradley, Powers, Acorn, Symmons, or approved substitute.

M.	Domestic Water Balancing Valve:  Balancing fitting with differential pressure taps, brass or bronze body and trim. B&G “Circuit Setter” or equivalent Taco, Armstrong, Thrush, Wheatley, Flow Design or approved substitute.  At Contractor’s option, balancing valves 3” and larger may be butterfly style, Jenkins No. 222 EL or approved substitute as specified in Section 15100.

N.	Thermostatically Controlled Balancing Valve:  Thermal Balancing Valve for domestic hot water recirculation circuits. Internal thermostatic balancing cartridge automatically modulates flow to ensure constant temperature which is adjustable from 95 degrees F to 140 degrees F.  Sizes ½” and ¾” with NPT female connections. Provided with DZR low-lead brass valve, stainless steel and copper adjustable thermostatic cartridge, peroxide-cured EPDM hydraulic seals, 300 Series stainless steel springs, adjustment knob with temperature adjustment scale and tamper-proof adjustment locking screw.  Provide with optional check valve and pre-formed insulation shell. Provide with optional (model dependent) outlet temperature gauge, 30 degrees F to 180 degrees F scale.

1.	Maximum working pressure: 230 psi.

2.	Maximum differential pressure: 15 psi.

3.	Maximum inlet temperature: 195 degrees F.

4.	Meets requirements of ANSI/NSF 372-2011. Certified to low-lead laws and listed by ICC-ES, file PMG-1360, for use in accordance with U.S. and Canadian plumbing codes.

5.	Certified to NSF/ANSI 61 (180 degrees F/82 degrees C Commercial Hot), Drinking Water System Component- Health Effects, by ICC-ES, file PMG-1512.

6.	Caleffi 1164 Series or approved.

** NOTE TO SPECIFIER ** Select one of the following paragraphs as required and delete those not required.

O.	Domestic Hot Water Demand Circulation Controller:  Hot water circulation pump controller with flow switch, temperature sensor, timer, and pump relay.  Controller to start circulation pump upon demand sensed by flow switch and stop pump when circulation loop return reaches setpoint (adjustable).  120 volt power cord and receptacle for circulation pump. Flow switch to activate at 0.3 gpm or less. Constant on override switch for troubleshooting. Enovative.

2.4	pumps

A.	Domestic Hot Water Circulator:  Bronze body, bronze fitted, in-line circulator with sleeve bearing.  Bell & Gossett 1” HV or equivalent Grundfos, Thrush, Wilo, Taco, or Armstrong.  Provide with 7-day programmable electronic time clock and aquastat to start and stop the pump.

## PART 3 - EXECUTION

3.1	UTILITY SERVICE

A.	Plumbing Utility Connections: Complete installation.  Contact local serving utilities to determine conditions involved and make or arrange to have connection made at proper time and pay all costs involved.

B.	Sanitary and Storm Sewers:  Connect to or arrange for connection to existing/  public sanitary and storm sewers as shown on the Drawings and as required by the serving utility.  Verify depth, size and location prior to installation of the new sewer systems.

C.	Water Service:  Connect to or arrange for connection to public water service.  Verify serving utility requirements prior to beginning any installation.  Verify water main size, depth, pressure and location prior to starting work.

D.	Fire Service:  Connect to or arrange for connection to existing public water main. Contact local serving utilities to determine conditions involved and make or arrange to have connection made at proper time and pay all costs involved.

Provide vault and install backflow preventer provided under the fire sprinkler work specified in Section 21 1300.  Coordinate vault size and piping arrangement.  Installation of meters and vault by the serving utility.

3.2	PIPE INSTALLATION

A.	General:  Install pipe, tube and fittings in accordance with recognized industry practices, manufacturer’s instructions, and plumbing code standards.  Install each run accurately aligned with a minimum of joints and couplings, but with adequate and accessible unions and flanges for disassembly, maintenance and/or replacement of valves and equipment.  Reduce sizes (where indicated) by use of reducing fittings.

B.	Piping Runs:  Route piping close to and parallel with walls, overhead construction, columns and other structural and permanent-enclosure elements of the building.  Install piping plumb and level except where pitched for drainage.  If not otherwise indicated, run piping in the shortest route which does not obstruct usable space or block access for servicing the building or equipment and avoid diagonal runs.  Wherever possible in finished and occupied spaces, conceal piping from view.  Do not encase horizontal runs in solid (concrete or CMU) partitions.  Do not locate piping within dedicated electrical spaces (six feet above switchgear and panelboards).  Provide drip pans below piping routed above dedicated electrical space.

C.	Changes in Direction:  Use fittings for all changes in direction.  Run lines parallel with building surfaces.

D.	Line Grades:

1.	Drainage Lines:  Run at maximum possible grade and in no case less than 1/4" per foot within building.

2.	Vents:  Pitch for drainage 1/4" per 10'.

3.	Water:  Pitch to low points and install hose bib drains.  3' minimum depth of ground cover for all lines outside building unless otherwise noted.

E.	Unions and Flanges:  At all equipment to permit dismantling and elsewhere as consistent with good installation practice.

F.	Expansion:  Provide loops, swing joints, anchors, runouts and spring pieces to prevent damage to piping or equipment.

G.	Insulating (Dielectric) Fittings:  Comply with manufacturer's instructions for installing unions or fittings.  Install in a manner which will prevent galvanic action and stop corrosion where the "joining of ferrous and non-ferrous piping" is indicated.

H.	Tracer Wire:  Install tracer wire as close to underground non-metallic water, sanitary and storm sewers and gas pipe in the trench as possible.  Tracer wire shall be accessible at grade via all services, valve and meter boxes, curb cocks, cleanouts at the building, manholes (inside the cover near the top), etc.  Locate all points on the record as-installed drawings.  Splice into utility tracer system where available.  Comply with code requirements.

I.	Piping:  Install for services as specified in Part 2.  The following are special requirements:

1.	Underground Drainage Pipe:  Install cast iron soil pipe for the following conditions.  When specified in Part 2 of this Section and where allowed by Code, plastic piping may be installed in lieu of cast iron piping.

a.	Under the building to 5' outside the building structure.

b.	5' each way from a potable water line crossing.

c.	First section (minimum 5') from any connection to underground structures such as catch basins, manholes, disposal well or tank, etc.

d.	Through all fill areas where pipe cannot be rested on undisturbed earth.

e.	Where the top of the pipe is less than 12 inches below finish grade.

f.	At Contractor's option in lieu of concrete or clay sewer pipe.

3.3	PIPING JOINTS

A.	General:  Provide joints of the type indicated in each piping system, and where piping and joint as manufactured form a system, utilize only that manufacturer's material.

B.	Cast Iron "No-Hub":  All joints in accordance with the Cast Iron Soil Pipe Institute (CISPI) Designation No. 310-97 "Installation Procedures for Hubless Cast Iron Soil Pipe and Fittings For Sanitary and Storm Drain, Waste and Vent Piping Applications.”  Horizontal runs of 5” and greater shall be braced as indicated in Figure 4 for “rodding” restraints.  Application of couplings as follows:

1.	Standard Duty Couplings: All vent piping and all drainage and waste piping above grade.

2.	Heavy Duty Couplings:

a.	All underground installations.

b.	All rain drain leader joints located more than 20 feet below the roof drain.

C.	Solder Copper Tube and Fitting Joints:  In accordance ANSI B 828 with recognized industry practice.  Cut tube ends squarely, ream to full inside diameter, and clean outside of tube ends and inside of fittings.  Apply solder flux to joint areas of both tubes and fittings.  Insert tube full depth into fitting, and solder in a manner which will draw solder full depth and circumference of joint.  Wipe excess solder from joint before it hardens.  "T-Drill" field formed tees may be utilized where the main is at least two pipe sizes larger than the branch.

D.	Plastic Pipe/Tube Joints:  Comply with manufacturer's instructions and recommendations, and with applicable industry standards:

1.	Heat Joining of Thermoplastic Pipe:  ASTM D-2657.

2.	Making Solvent-Cemented Joints:  ASTM D-2865 and ASTM F-402.

E.	Braze Copper Tube and Fitting Joints:  Where indicated.  Pass a slow stream of dry nitrogen gas through the tubing at all times while brazing to eliminate formation of copper oxide.

F.	Flanged Joints:  Match flanges within piping system, and at connections with valves and equipment.  Clean flange faces and install gaskets.  Tighten bolts to provide uniform compression of gasket.

G.	Ferrous Threaded Piping:  Thread pipe in accordance with ASME B1.20.1; cut threads full and clean using sharp dies.  Ream threaded ends to remove burrs and restore full inside diameter.  Apply pipe joint compound or pipe joint tape (Teflon) where recommended by pipe/fitting manufacturer, on male threads at each joint and tighten joint to leave no more than three threads exposed.

H.	Grooved Pipe Joints:  Comply with fitting manufacturer's instructions for making grooves in pipe ends.  Remove burrs and ream pipe ends.  Assemble joints in accordance with manufacturer's instructions.  Visually inspect the assembled joint to ensure proper gasket seating.

3.4	CLEANOUTS

A.	Where required by code, at each change of sewer direction 45 degrees or greater and more than 10’ long, at end of each branch or main and spaced not greater than 100’ apart, as required by code and/or as shown on Drawings.  Provide cleanouts beneath all sinks.

3.5	MISCELLANEOUS PIPING EQUIPMENT

A.	Floor, Wall and Ceiling Plates:  Chrome plated pressed steel or brass screw locked split plates on all pipe penetrations in finished spaces.

B.	Strainers:  Install in a manner to permit access for cleaning and screen removal and with blow-off valve.

C.	Sleeves:  At all penetrations of masonry or cast in place concrete construction.   PVC, 24 gauge galvanized steel tube or Schedule 40 galvanized steel pipe.  Use steel pipe sleeves through beams, footings, girders or columns and for all penetrations of walls or floors below grade.  Where floor finish is ceramic tile, terrazzo, or similar material extend standard steel pipe sleeves 1-1/2" above finished floor.  Fabricate sleeves 1" diameter larger than pipe or insulation.  PVC and sheet metal sleeves at non-structural penetrations only.  Use specified sleeve system for all above grade concrete floor applications.

D.	Sleeve Caulking:  Caulk below grade pipe with rubber link seal.  Grout above grade pipe with cement mortar or approved waterproof mastic.  All caulking or grouting shall extend full depth of sleeve.  Utilize rubber sealing links in lieu of caulking.  Install UL sealing caulk, putty and/or system at all penetrations of fire rated walls, floors and ceiling.

E.	Shock Arrestors:  Install at end of mains, in a battery of three or more flush valve-operated fixtures water header, ahead of quick closing and solenoid operated valves.  Size per PDI recommendations where size is not indicated.  Provide access panels.

F.	Trap Priming:  Traps serving floor drains, floor sinks, catch basins, and similar fixtures shall be primed in accordance with Code requirements.

G.	Domestic Hot Water Mixing Valves:  Install in accordance with manufacturers installation instructions and piping diagrams.

3.6	BASE PREPARATION

A.	Subbase Installation:  Where indicated, install subbase material to receive mechanical work, and compact by tamping to form a firm base for the work.  For 4" and larger piping, horizontal cylindrical tanks and similar work, shape the subbase to fit the bottom 90 degrees of the cylinder, for uniform continuous support.  Provide finely-graded subbase material for wrapped, coated and plastic pipe and tank.  Shape subbases and bottoms of excavation with recesses to receive pipe bells, flanged connections, valves and similar enlargements in the piping systems and set bottom of trench at proper pitch and correct elevations with subbase material.

B.	Concrete Encasement:  Where piping under roadways is less than 2'-6" below surface of roadway, provide 4" base slab of concrete to support piping. After piping is installed and tested, provide 4" thick encasement (sides and top) of concrete before backfilling.  Provide Class 2500 concrete for encasement and slab.

C.	Previous Excavations:  Where piping crosses over an area more than 5' wide which has been previously excavated to a greater depth than required for the piping installation, provide suitable subsidence-proof support for the piping.  Comply with the details shown, or where not otherwise shown, provide the following support system:

1.	Excavate to undisturbed soil, in a width equal to the pipe diameter plus 2'.  Install 8" courses of subbase material, each compacted to 95% of maximum density, as required to fill excavation and support piping.

3.7	BACKFILLING

A.	General:  Bedding and backfilling of plastic DWV piping shall comply with ASTM D2321, Standard practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity Flow Applications.

B.	Do not backfill until installed mechanical work has been tested and accepted wherever testing is indicated.  Install drainage fill where indicated, and tamp to a uniform firm density.  Backfill with finely-graded subbase material to 6" above wrapped, coated and plastic piping and tanks, and to center line of other tanks (where recommended by tank manufacturer, use "pea gravel" backfill).  Condition backfill material by either drying or adding water uniformly, to whatever extent may be necessary to facilitate compaction to the required densities.  Do not backfill with frozen materials.

3.8	CLEANING

A.	General:  Clean all dirt and construction dust and debris from all mechanical piping systems and leave in a new condition.  Touch up paint where necessary.

B	Disinfection of Domestic Water Piping System:

1.	Prior to starting work, verify system is complete and clean.

2.	Open all drains and fixtures valves in the building starting with the valve nearest the water service line and permit the water to run clear for 10 minutes to eliminate grease, cuttings, flux, and foreign matter.

3.	Disinfect piping system in accordance with ANSI/AWWA C651-92 standard.

4.	Take samples from 10 percent of outlets and from water entry, and analyze in accordance with AWWA C601.  If any sample fails the analysis, repeat the procedure.

5.	Include a copy of the bacteriological analysis in the Operating and Maintenance manuals.

C.	Sanitary and Storm Drainage System:

1.	Remove construction debris from cleanouts, drains, strainers, baskets, traps, etc., and leave same accessible and operable.  Place plugs in the end of uncompleted piping at the end of the day or whenever work stops.

2.	Before final acceptance of completed sewer system, flush and clean the entire system with water.  Trap and remove solid material obtained from flushing and cleaning from the new system.  Do not allow debris to enter the existing sewer system.

D.	Deionized Water Piping:  Remove all foreign material from piping and flush with clean water.  Sanitize and clean in accordance with procedure recommended by deionized water equipment manufacturer.  After system is ready to be operated, test water purity and certify that water quality is within allowable limits.

3.9	TEST

A.	General:

1.	Minimum duration of two hours or longer, as directed for all tests.  Furnish report of test observation signed by qualified inspector.  Make all tests before applying insulation, backfilling, or otherwise concealing piping or connecting fixtures or equipment.  Where part of the system must be tested to avoid concealment before the entire system is complete, test that portion separately, same as for entire system.

2.	Provide all necessary temporary equipment for testing, including pump and gauges.  Remove control devices before testing and do not use piping system valves to isolate sections where test pressure exceeds valve pressure rating.  Fill each section with water and pressurize for the indicated pressure and time.

3.	Observe each test section for leakage at end of test period.  Test fails if leakage is observed or if pressure drop exceeds 5% of test pressure.

B.	Repair:

1.	Repair piping system sections which fail the required piping test by disassembly and re-installation, using new materials to the extent required to overcome leakage.  Do not use chemical stop-leak compounds, solder, mastics, or other temporary repair methods.

2.	Drain test water from piping systems after testing and repair work has been completed.

C.	Sewer:  Furnish all facilities and personnel for conducting the test.  Test in accordance with the requirements of the State Plumbing Inspector and local authorities.

D.	Plumbing Waste and Vent Piping:  Hydrostatic test by filling to highest point, but not less than 10' water column on major horizontal portion.

E.	Water Piping:  Hydrostatic pressure of 100 psig without loss for four hours.

F.	Tanks and Equipment:  Hydrostatic pressure to 1.5 times operating pressure but do not exceed maximum rated pressure.

3.10	SUPERVISION AND START-UP

A.	Adjust flush valves, pressure reducing valves, mixing valves, water heater thermostats, domestic hot water circulating system balancing valves, and similar equipment.

B.	Domestic hot water system balancing:  Adjust domestic hot water recirculating balancing valves to equalize return temperatures from each branch line.

C.	The installation, start-up, and adjustment of  Master mixing valve shall be supervised by an authorized agent of the manufacturer.  The manufacturer's agent shall check out and approve the installation and shall also approve and be responsible for adjusting the operating and control system and instructing the Owner's representatives on the system operation.

D.	Master mixing valve start-up procedure:  Provide a factory authorized representative to review the installation of the mixing valve and verify that the adjustment has been completed by an authorized agent of the manufacture.  Provide documentation in the O&M documents showing adjustment has been completed per manufacture instructions.  Record supply and return temperatures.  Work shall be completed prior to substantial completion.

END OF SECTION