# SECTION 22 07 00 - plumbing INSULATION

## PART 1 – GENERAL

1.1	DESCRIPTION

A.	The requirements of this section apply to the insulation of plumbing systems specified elsewhere in these specifications.

B.	The requirements of Section 22 05 00, Common Plumbing Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	Minimum Insulation Thickness and Thermal Performance:  Comply with the State of Oregon Energy Efficiency Code except where more stringent requirements are specified herein.

B.	Composite (Insulation, Jacket or Facing and Adhesives) Fire and Smoke Hazard Ratings:  Not to exceed a flame spread of 25 or smoke development of 50 and containing less than 0.1% by weight deca-PDE fire retardant.

C.	Component Ratings of Accessories (Adhesives, Mastics, Cements, Tapes, Finishing Cloth for Fittings):  Same as "B" requirements above and permanently treated.  No water soluble treatments.

1.3	SUBMITTALS

A.	Submit catalog data and performance characteristics for each product specified.

1.4	PRODUCT DELIVERY, STORAGE AND HANDLING

A.	General:  In addition to the requirements specified in Section 22 05 00, the following apply:

1.	Deliver insulation, coverings, cements, adhesives and coatings to the site in factory-fabricated containers with the manufacturer's stamp or label affixed showing fire hazard ratings of the products.  Store insulation in original wrappings and protect from weather and construction traffic.

2.	Protect insulation against dirt, water, chemical and mechanical damage.  Do not install damaged insulation.  Remove such insulation from project site.

## PART 2 – PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

A.	Insulation Manufacturers:  Johns Manville, Owens-Corning, Knauf, Certain Teed, Armstrong, Pabco, Imcoa or Nomaco.  Johns Manville products are listed unless indicated otherwise.

B.	Adhesive Manufacturers:  Foster, 3M, Insul-Coustic, Borden, Kingco or Armstrong.

2.2	PIPING INSULATION

A.	Interior and Exterior Piping Systems 32 to 180 Deg. F:  Glass fiber preformed pipe insulation with a minimum K-value of 0.23 at 75 deg. F, a minimum density of 3.5 pounds per cubic foot within all-service vapor barrier jacket, vinyl or pre-sized finish and pressure sensitive seal containing less than 0.1% by weight deca-PDE fire retardant.

B.	Exterior Installations:  Same as for interior installations except 0.016" aluminum finish jacket

C.	Pipe Temperatures Minus 30 to 180 Deg. F:  Flexible, preformed, pre-slit, self-sealing elastomeric pipe insulation up to 2-1/8" ID, thermal conductivity of 0.27 BTU/hr. sq. ft./in. at 75 deg. F and vapor transmission rating of 0.2 perms/inch.    Armstrong "Armaflex 2000" or, in concealed locations, Imcoa or Nomaco also approved.

2.3	INSULATION ACCESSORIES

A.	Insulation Compounds and Materials:  Provide rivets, staples, bands, tapes, adhesives, cements, coatings, sealers, welded studs, etc., as recommended by the manufacturer for the insulation and conditions specified. No staples allowed on  cold water piping systems.

B.	PVC Protective Jacketing and Valve and Pipe Fitting Covers:  Johns Manville Zeston 2000, Proto LoSmoke, Speedline Smoke Safe, or Ceel-Co Ceel-Tite 100 Series with precut fitting fiberglass insulation or approved.

C.	Jacket Lap Sealing Adhesives:  Foster Drion 85-75 contact cement or approved substitute.

D.	Saddles and Shields:  Install to prevent crushing of insulation at support points.

1.	Protection Saddles:  MSS Type 39.

2.	Protection Shields:  MSS Type 40.

3.	Preinsulated Pipe Supports: Calcium silicate load bearing metal jacketed inserts.  Pipe Shields Inc. or accepted substitute.

a.	Pipe supported on rods - Models A1000, A2000, A3000, A4000.

b.	Pipe supported on flat surfaces - Models A1000, A2000, A3000, A4000.

c.	Pipe supported on pipe rolls - Models A3000, A4000, A5000,.

d.	Vertical riser clamp – Models E1000, E1100, E1200.

## PART 3 – EXECUTION

3.1	PIPING INSULATION

A.	General:  Insulate both metallic and non-metallic piping as subsequently specified. Insulation shall be continuous except where passing through structural members. Do not insulate underground piping except at joints and fittings on preinsulated piping unless indicated otherwise.

B.	At the contractor’s option and in accordance with Part 2 of this section, elastomeric insulation may be installed on domestic water piping in thicknesses providing overall thermal resistance equivalent to the glass fiber insulation.  Increased thickness is typically required.  Installation shall comply with the manufacturer’s recommendation with joints and seams completely sealed.

C.	Insulate Domestic Water Piping with glass fiber pipe covering:

1.	Cold Water piping: 1” thick for cold water piping.

- Hot Water Piping: 1/2” thick for 3/4” and smaller piping. 1” thick for 1” and 1-1/4” piping.  1-1/2” thick for 1-1/2” piping.  2”  thick for 2” and larger piping.

- Insulate hot water return piping same as hot water piping.

- Insulate all water piping exposed to outside weather and freezing temperatures with minimum 1” thickness of glass fiber pipe covering with weather-proof metal jacket.   Apply insulation after heat cable is installed.

D.	Pipe Fittings:

1.	Insulate and finish all fittings including valve bodies, bonnets, unions, flanges and expansion joints with precut fiberglass insulation and preformed PVC covers sealed to adjacent insulation jacket for continuous vapor barrier covering over all fittings.   Elastomeric insulation shall be cut and sealed at fittings.

2.	Use elastomeric insulation at flexible pipe connections.

3.	Provide removable/reusable insulation covers on 4" and larger valves, unions, flanges, pump casings, strainers and similar fittings or equipment requiring periodic service.

E.	Protective Covering:  Install continuous protective PVC or metal covering on all piping and fittings in mechanical rooms, accessible tunnels, attic spaces, accessible ceilings, etc., where insulation may be subject to damage.  Install with rivets or cement seams and joints.

F.	Piping Insulation Lap Seams and Butt Joints:  Install insulation jacket in accordance with manufacturer's recommendation and without staples on cold water lines.   Where jacket joint and lap seams have not adhered, remove affected section of insulation and reinstall or apply lap sealing adhesive in accordance with manufacturer's instructions.

END OF SECTION