# SECTION 23 10 00 – facility fuel gas systems

## PART 1 - GENERAL

1.1	description

- The requirements of this section apply to the fuel gas distribution systems for the facility.

B.	Related Work:  The requirements of Section 23 05 00, Common HVAC Materials and Methods, also apply to this section.

1.2	CODES AND STANDARDS

A.	Comply with the provisions of the following referenced codes, standards and specifications:

1.	National Fire Protection Association (NFPA)

2.	Underwriters Laboratories, Inc. (UL)

3.	Factory Mutual (FM)

4.	National Fuel Gas Code (NFPA 54)

5.	Liquefied Petroleum Gas Code (NFPA 58)

6.	International Mechanical Code (IMC) with State and Local Amendments

7.	American Society for Testing and Materials (ASTM)

8.	International Fire Code (IFC) with State and Local Amendments

9.	American Gas Association (AGA)

1.3	SUBMITTALS

A.	Required for all items.

## PART 2 - PRODUCTS

2.1	PIPING MATERIALS

A.	Black Steel Pipe:

- Applications: Indoors or underground.

  - Natural Gas.

  - LP gas (Propane).

- Pipe:  Systems 10” or smaller, operating below 400 psi, schedule 40, standard black steel pipe ASTM A-120 or A-53.

- Underground Piping:  Coated with a minimum of ten mils of factory applied 100% thermosetting epoxy resin.

4.	Threaded Fittings:  For above ground installations only.  Banded class 150 malleable iron fittings, ANSI B16.3 to 150 psi.

5.	Welding Fittings:  Standard weight, seamless steel, beveled end fittings, ANSI B16.9.

6.	Flanged Fittings:  For above ground installations only.

a.	Class 150 steel welding neck flanges, ANSI B16.9 to 150 psi.

b.	Facing and Gasketing:  Selected for service pressures and temperatures.  Raised face for steel flanges.

B.	Flexible Fuel Gas Piping (CSST):

1.	Application:  5 psi or less:

a.	Natural gas

b.	LPG (Propane gas)

2.	Pipe:  Corrugated 300 series stainless steel tubing with yellow polyethylene jacketing.

3.	Fittings:  Fittings shall be yellow brass and provide a self-flaring connection to the tubing.  Systems incorporating gaskets or o-rings are not acceptable.

4.	Underground Installations:  CSST pre-sleeved with heavy wall internally ribbed polyethylene secondary venting conduit with end seals and vent connection fittings.

5.	Approvals:  System shall be listed by an approved independent laboratory and approved for use by the local code officials.  TracPipe, Gastite, or approved.

D.	Copper Pipe and Tube:

- Application:

- Regulator vents.

2.	Pipe:  ASTM B88.

a.	Above Ground:  Type L hard temper copper with brazed joints.

b.	Underground:  Type L soft annealed with no joints or type K hard tempered copper with brazed joints.

3.	Fittings:  Wrought copper solder-joint fittings, ANSI B16.22.

2.2	piping accessories

A.	Fuel Gas Valves:  UL listed or AGA approved valves.

1.	10 psig or Less:

a.	Ball:  NIBCO bronze body T/S 585-70-UL, brass body FP-600.

B.	Strainers: Threaded bronze or iron body for 175 working pressure, Y pattern with 1/32” stainless steel perforated screen.

C.	Gas Pressure Regulators:  Size based on pressures indicated on the drawings and for 1.5 times connected load.  Style and model as approved by Northwest Natural Gas Co.  Maxitrol, Rockwell, Fisher, Reliance, or approved substitute.

D.	Gas Appliance Connectors:  For low pressure gas connection to indoor or outdoor rigidly mounted stationary appliances, AGA approved corrugated stainless steel tubing with zinc plated steel end fittings.  Brasscraft or approved substitute.

E.	Gas Connection Hose:  For low pressure gas connection to moveable appliances including cooking equipment, flexible hose consisting of inner tube, stainless steel braid, and outer protective jacket with swivel steel threaded end fittings. T & S Brass HG series, or approved substitute.

2.3	expansion joints and loops

A.	Flexible Expansion/Seismic Loop:  Factory fabricated assembly consisting of two elbows and return bend or three elbows, and two lengths of flexible hose to allow free movement in three axis.  Return bend or elbow shall include a drain/vent fitting.  Hose shall be corrugated metal style with metal overbraid compatible with the piping materials.  Connections to match piping system except connection 2” and larger shall be flanged style.  Listed for fuel gas use.  Metraflex “Metraloop” or Unisource “Uni-loops”.

## PART 3 - EXECUTION

3.1	equipment INSTALLATION

A.	Locating and Positioning Equipment:  Observe all Codes and Regulations and good common practice in locating and installing mechanical equipment and material so that complete installation presents the least possible hazard.  Maintain adequate clearances for repair and service to all equipment.  Installation of any equipment with less than minimum clearances shall not be accepted.

- Anchorage:  Anchor and/or brace mechanical equipment and piping to resist displacement due to seismic action.

- Gas Pressure Regulators:  Install with drip leg at regulator inlet and capped test tees at inlet and outlet piping connections.  Vent to exterior in accordance with code requirements except where vent limiting devices are installed.

3.3	PIPE INSTALLATION

A.	General:	Install pipe, tube and fittings in accordance with recognized industry practiced for each indicated service without piping failure.  Install each run with a minimum of joints and couplings, but with adequate and accessible unions and flanges for disassembly, maintenance and/or replacement of valves and equipment.  Reduce sizes (where indicated) by use of reducing fittings.  Align piping accurately at connections.

B.	Ferrous Threaded Piping:  Thread pipe in accordance with ANSI 82.1; cut threads full and clean using sharp dies.  Ream threaded ends to remove burrs and restore full inside diameter.  Apply pipe joint compound where recommended by pipe/fitting manufacturer, on male threads at each joint and tighten joint to leave no more than 3 threads exposed.

C.	Flexible Gas Piping (CSST):  Comply with manufacturer’s recommendations for system installation.  Provide striker plates and supports as required.  All penetrations of finished walls, including mechanical room walls, shall be accomplished using surface or recessed termination fittings.  Where installed underground below a building, vent the conduit to outdoors per Code.

D.	Changes in Direction:	Use fittings for all changes in direction.  Run lines parallel with building surfaces.

E.	Unions and Flanges:  At all equipment to permit dismantling and elsewhere as consistent with good installation practice.

F.	Expansion:  Provide loops, swing joints, anchors, runouts and spring pieces to prevent damage to piping or equipment.

G.	Underground Gas Piping:  Standard schedule 40 black steel pipe with welding fittings coated with a minimum of ten mils of 100% thermosetting epoxy resin, Scotchkote No. 203 factory applied per resin manufacturer's recommendations.  Wrap all joints with 10 mil polyvinyl chloride pipewrap tape to a total thickness of 40 mils.  Provide one 15 pound magnesium anode per each 100' of underground pipe, attached to coupling or other fitting with No. 10 copper wire.  No underfloor slab natural gas piping except as provided for by code.

3.7	CLEANING

A.	General:  Clean all dirt and construction dust and debris from all mechanical piping systems and leave in a new condition.  Touch up paint where necessary.

B.	Fuel Piping:  Blow clear of debris with nitrogen or oil free air.

3.9	TEST

A.	General:  Minimum duration of two hours or longer, as directed for all tests.  Furnish report of test observation signed by qualified inspector.  Make all tests before applying insulation, backfilling, or otherwise concealing piping or connecting fixtures or equipment.  Where part of the system must be tested to avoid concealment before the entire system is complete, test that portion separately, same as for entire system.

B.	Natural Gas Piping:  One half hour minimum air at 60 psig for 2 psig gas, and 15 minutes at 10 psig for 7" water gauge natural gas or as approved and certified by serving utility.

C.	Storage Tanks:  Test tank according to manufacturer’s recommendation.

3.10	MECHANICAL PAINTING

A.	Uninsulated Piping:  Paint black steel piping in moist equipment rooms, crawl spaces, inside of secondary containment piping, or exposed to weather two (2) coats black rust-inhibiting paint.

END OF SECTION