# SECTION 23 22 00 - steam Piping and Pumps

## PART 1 - GENERAL

1.1	DESCRIPTION

A.	The requirements of this section apply to steam and condensate return systems.  Provide pipe, pipe fittings, pumps, and related items required for complete piping system.

B.	Related Work:  The requirements of Section 23 05 00, Common HVAC Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	General:  ASTM, and ASME Standards are indicated.  In addition, special standards are referenced where neither ASTM nor ASME Standards are applicable.

B.	Labeling:  All piping shall be continuously and legibly labeled on each length as required by codes and standards and including as a minimum, country of origin, manufacturer’s identification marking, wall thickness designation, and applicable standards and approvals.  Fittings shall be labeled as required by the referenced standard.

C.	Definitions:  Where piping fluid is not indicated in the following paragraphs, provide similar piping materials for similar fluids.

D.	All welders and welding procedure specifications shall be qualified as required by ASME Standard B31.

1.3	STORAGE AND HANDLING

A.	Provide factory-applied end caps on each length of pipe and tube.  Maintain end caps through shipping, storage and handling as required to prevent pipe-end damage and eliminate dirt and moisture from inside of pipe and tube.  Protect flanges and fittings from moisture and dirt by inside storage and enclosure, or by packaging with durable, waterproof wrapping.

1.4	SUBMITTALS

A.	Submit catalog data, construction details, performance characteristics for all equipment.

B.	Submit operating and maintenance data.

## PART 2 - PRODUCTS

2.1	PIPING MATERIALS

A.	Systems:  Low pressure 15 psig or less, steam supply and condensate return systems.

1.	Applicable on 12 inches and smaller pipe:  black steel pipe ASTM A-106 or A-53, Grade B.

a.	Steam Pipe - 2 inches to 12 inches:  Schedule 40.

b. Condensate Pipe – 2 inches to 12 inches:  Schedule 80.

2.	Threaded Fittings:  2 inch and smaller pipe.

a.	Class 125 cast iron fittings, ASME B16.4 to 100 psig maximum pressure.

b.	Class 150 malleable iron fittings, ASME B16.3 to 125 psig maximum pressure.

3.	Welding Fittings:  Beveled ends, seamless fittings of the same type and class of piping above.

4.	Flanged Fittings:  2-1/2 to 12 inch, for above ground installations only.

a.	Class 125 cast iron threaded fittings, ASME B16.1 including bolting to 125 psi.  Maximum system pressure 100 psig.

b.	Class 150 steel welding neck flanges, ASME B16.9 to 200 psig maximum system pressure.

c.	Facing and Gaskets:  Selected for service pressures and temperatures.  Provide flat-faced flanges with full-faced gaskets for cast iron pipes.  Provide raised-face flanges with ring gaskets for steel pipes and gaskets of non-asbestos construction.

B.	Systems:  Medium pressure 15 psig to 125 psig steam supply and condensate return systems.

1.	Applicable on 12 inches and smaller pipe:   black steel pipe ASTM A-106 or A-53, Grade B.

a.	Steam Pipe - 2 inches to 12 inches:  Schedule 40.

b. Condensate Pipe – 2 inches to 12 inches:  Schedule 80.

2.	Threaded Fittings:  2 inch and smaller pipe.

a.	Class 250 cast iron fittings, ASME B16.4 .

b.	Class 150 malleable iron fittings, ASME B16.3 to .

3.	Welding Fittings:  Beveled ends, seamless fittings of the same type and class of piping above.

4.	Flanged Fittings:  2-1/2 to 12 inch, for above ground installations only.

a.	Class 250 cast iron threaded fittings, ASME B16.1 including bolting to 250 psi.

b.	Class 150 steel welding neck flanges, ASME B16.9 to 200 psi.

c.	Facing and Gaskets:  Selected for service pressures and temperatures.  Provide flat-faced flanges with full-faced gaskets for cast iron pipes.  Provide  raised-face flanges with ring gaskets for steel pipes and gaskets of non-asbestos construction.

2.2	MISCELLANEOUS PIPING MATERIALS/PRODUCTS

A.	Insulating (Dielectric) Fittings:  Provide standard products recommended by the manufacturer for use in the service indicated, and which effectively isolate ferrous from non-ferrous piping (electrical conductance), prevent galvanic action, and reduce corrosion.  Victaulic "Clear Flow."

B.	Welding Materials:  Provide welding materials as determined by the installer to comply with installation requirements.  Comply with Section 2-C, ASME Boiler Code for welding materials.

C.	Gaskets for Flanged Joints:  ASME B16.21; full-faced gaskets for cast-iron flat-faced flanges; ring gaskets for raised-face for steel flanges.  Provide non-asbestos gasket construction.  Pressure and temperature rating required for the service indicated.

D.	Sleeve Seal:  Rubber-link pipe wall and casing closure.  Thunderline Link-Seal.  For fire rated wall, floor or ceiling penetrations, 3-M "CP-25" caulk, "No. 303" putty and/or "PSS 7904" sealing system.

E.	Strainers:  "Y-pattern," tapped blow-off connection and removable 20 mesh stainless steel screen.  NIBCO or equal.

- Steam systems up to 15 psig and 250 deg. F:  Class 125 cast iron or bronze body.

- Steam systems up to 125 psig and 350 deg F:  Class 250 cast iron body.

- Provide threaded end connections for strainers 2 inches or less.

- Provide flanged end connections with non-asbestos gasket for strainers 2-1/2 inches and larger.

F.	Tracer Wire:  14 gauge, single strand, copper wire with blue insulation for water, green for sanitary and storm sewers, and yellow for gas.  3M "DBY" direct bury splice kit required at all splices.

G.	Valves:  Steam Systems:

1.	Systems up to 15 psi and  250 Deg. F:

a.	Ball (2 inches and smaller):  Two piece, cast bronze body, stainless steel ball and stem, reinforced Teflon seats, full port, 2 inch extended handle of non-thermal conductive material with protective sleeve, 150 psi SWP and 600 psi non-shock WOG, Nibco T 585-70-66-ST.

b.	Gate (to 2”):  Class 125, bronze body wedge and union bonnet, dezincification-resistant silicon bronze rising stem, solid wedge, non-asbestos packing and malleable or ductile iron handwheel, MSS SP-80 compliant, 125 psi WSP, Nibco T-134.

c.	Gate (2-1/2” to 12”):  Class 125, iron body, bronze trim, bolted bonnet, solid wedge, outside screw and yoke, 125 psi WSP, non-asbestos packing, Nibco F-617-O.

d.	Check (3/4 to 2 inches):  Class 125, horizontal swing, Y-pattern, renewable seat and disc, PTFE seat disc, ASTM B-62 bronze body, MSS SP-80 compliant, applicable to horizontal and vertical with upward flow installations, Nibco T413-Y.

e.	Check (2-1/2 to 12 inches):  Class 125, horizontal swing, lever and spring assisted, renewable seat and disc, bolted bonnet, ASTM Class B cast iron body with bronze trim, non-asbestos gasket, MSS SP-71, type 1 compliant, applicable to horizontal and vertical with upward flow installations, Nibco F-918-B.

2.	Systems up to 125 psi and 350 Deg. F:

a.	Gate (to 2”):  Class 150 bronze body, union bonnet, dezincification-resistant silicon bronze rising stem, solid wedge, non-asbestos packing and malleable or ductile iron handwheel, 150 psi WSP, Nibco T-134.

b.	Gate (2-1/2” to 12”):  Cast iron body, bronze trim, bolted bonnet, solid wedge, outside screw and yoke, MSS SP-70 compliant, non-asbestos packing, 250 psi WSP, Nibco F-667-O.

c.	Check (3/4 to 2 inches):  Class 150, horizontal swing, Y-pattern, renewable seat and disc, PTFE seat disc, ASTM B-62 bronze body, MSS SP-80 compliant, applicable to horizontal and vertical with upward flow installations, Nibco T433-Y.

d.	Check (2-1/2 to 6 inches):  Class 250, horizontal swing, lever and spring assisted, renewable bronze seat and disc, bolted bonnet, iron body with bronze trim, MSS SP-71 Type 1 compliant, non-asbestos gasket, applicable to horizontal and vertical with upward flow installations, Nibco F-968-B.

H.	Thermostatic Air Vents:

- Systems up to 125 psig and 350 deg. F:  Forged brass body and cover, welded stainless steel element, spring and seat, brass gasket, union nipple, union nut.  Watson McDaniel AVT125 or approved equal.

2.3	steam and condensate SPECIALTIES

A.	Blowdown Tank:  150 pound ASME Code steel blowdown tank with required tappings and installed as shown on Drawings.

B.	Flash Tank:  135 pound ASME Code construction.  Capacity, tappings and mounting as shown on Drawings.

C.	Float and Thermostatic Traps:  For 15 psig operation selected on 1.5 times condensing capacity of equipment served at 1/2 pound differential.  Cast iron body, non-corrosive internal parts, renewable float valve and seat of monel or stainless steel, renewable thermostatic element.  Marsh, Hoffman, Trane, Sarco, Webster, Dunham-Bush, Armstrong, or approved substitute.

D.	Thermostatic Steam Traps:  For 15 psig operation selected on 1.5 times condensing capacity of equipment served at 1/2 pound differential.  Install on direct radiation equipment.  Brass or bronze body with renewable stainless or monel steel seat and valve.  Marsh, Hoffman, Trane, Sarco, Webster, Dunham-Bush, Armstrong, or approved substitute.

E.	Inverted Bucket Steam Traps:  For 150 psig operation iron body, non-corrosive internal parts, renewable valve and seat of stainless steel.  Hoffman, Webster, Dunham-Bush, Armstrong, Sarco or approved substitute.

F.	[15] psig Steam Safety Valve:  ASME approved and of number and size required by ASME Code.  Install Grinnell No. 1538 drip pan elbow on safety valve outlet.

1)	Size as required by ASME and Boiler and Pressure Vessel Code.

G.	Medium [ High ] Pressure Safety Valve:  ASME approved and of a number and size required by ASME Code.  Steel body side outlet pattern with testing level.  Set at [ 60 ] [ 100 ] psig.

1)	Size as required by ASME and Boiler and Pressure Vessel Code.

H.	Pilot Operated Steam Pressure Reducing Valve:  Single-seated, main pressure reducing valve, with pilot operator designed to regulate accurately throughout the range of pressure and flow conditions scheduled and function quietly and close tight on a dead-end shutoff.

I.	Chemical Shot Feeder:  2 [5] gallon feeder rated for 125 psi working pressure complete with fill funnel and valve or cap, drain valve, air vent, and inlet and outlet connections. Mogul, J.L. Wingert, or approved

J.	Externally Controlled Steam Pressure Reducing Valve:

1.	Single-seated, main pressure reducing valve, with external controller, designed to  regulate accurately throughout the range of pressure and flow conditions scheduled and function quietly and close tight on a dead-end shutoff.

2.	Iron body with flanged ends on valve sizes 2-1/2" and larger.  Seats, discs and stems of stainless steel and diaphragms of bronze.  No springs in the path of the steam and no stuffing boxes.  All parts easily accessible without removal of the valve from the line.  Watts, Cash-Acme, Fisher, Hoffman, Leslie, Spence, Aerco or approved substitute.

3.	Fisher "Wizard II" pressure controller, yoke mounted, operated on 25 psig compressed air.  Close reducing valve on air pressure failure.

2.5	EXPANSION JOINT

A.	Stainless steel bellows type with flanged ends, controlled flexing, internal liner rated at a minimum of 28,000 average life cycles.  Provide amount of expansion indicated at each joint as shown on Drawings.  Carefully align joint and make proper allowance for temperature of pipe at time of installation.  Flexonics, Hyspan, or approved substitute.

2.6	PIPE ALIGNMENT GUIDES

A.	Manufactured steel guide which consists of heavy steel spider rigidly attached to pipe and housed in steel which is rigidly anchored.  Guides same as expansion joint manufacturer.

## PART 3 - EXECUTION

3.1	PIPE INSTALLATION

A.	General:  Install pipe, tube and fittings in accordance with recognized industry practices.  Install each run accurately aligned with a minimum of joints and couplings, but with adequate and accessible unions and flanges for disassembly, maintenance and/or replacement of valves and equipment.  Reduce sizes (where indicated) by use of reducing fittings.

Comply with ASME B31 Code for Pressure Piping.

B.	Piping Runs:  Route piping close to and parallel with walls, overhead construction, columns and other structural and permanent-enclosure elements of the building (pitched for drainage).  If not otherwise indicated, run piping in the shortest route which does not obstruct usable space or block access for servicing the building or equipment and avoid diagonal runs.  Wherever possible in finished and occupied spaces, conceal piping from view.  Do not encase horizontal runs in solid partitions.

C.	Piping:  Install for services as specified in Part 2.  The following are Contractor's options.

1.	Steam Piping:  Standard black schedule 40 steel pipe and 125 pound black cast screwed or approved welding fittings for pressures up to 75 psi.  Welded connections on all piping underground, piping in tunnel or tile or otherwise inaccessible and on all equipment room headers 4" and over.  Weldolets, Threadolets, or schedule 80 shaped nipples may be used for take-offs up to half the nominal size of main.

D.	Take off all branch lines from the top of the steam mains.

E.	Install eccentric reducer fitting with the level side on the bottom.

F.	Install drip legs at all low points and natural drainage points such as at the end of mains and the bottom of risers and ahead of pressure regulators, control valves, isolation valves, pipe bends, and expansion joints.

1.	On straight horizontal runs, space drip legs at intervals not exceeding 300 feet if the pipe is pitched down in the direction of steam flow.

2. Size drip leg pipes the same size as the mains.  In steam mains 6 inches and over the size can be reduced to half the diameter of the main, but no less than 4 inches.

3.2	PIPING JOINTS

A.	General:  Provide joints of the type indicated in each piping system, and where piping and joint as manufactured form a system, utilize only that manufacturer's material.

B.	Ferrous Threaded Piping:  Thread pipe in accordance with  ASME B1.20.1; cut threads full and clean using sharp dies.  Ream threaded ends to remove burrs and restore full inside diameter.  Apply pipe joint compound or pipe joint tape (Teflon) where recommended by pipe/fitting manufacturer, on male threads at each joint and tighten joint to leave no more than three threads exposed.

C.	Weld Pipe Joints:  In accordance with recognized industry practice and as follows:

1.	Weld pipe joints only when ambient temperature is above 0 degrees F.

2.	Bevel pipe ends at a 37.5 degree angle, smooth rough cuts, and clean to remove slag, metal particles and dirt.

3.	Install welding rings for buttwelded joints.

4.	Use pipe clamps or tack-weld joints with 1" long welds; 4 welds for pipe sizes to 10"; 8 welds for pipe sizes up to 20".

5.	Build up welds with a stringer-bead pass, followed by a hot pass, followed by a cover of filler pass.  Eliminate valleys at center and edges of each weld.  Weld by procedures which will ensure elimination of unsound or unfused metal, cracks, oxidation, blow-holes and non-metallic inclusion.

6.	Do not weld out piping system imperfections by tack-welding procedures; refabricate to comply with requirements.

7.	Install forged branch-connection fittings wherever branch pipe is indicated, or install regular "T" fitting at Contractor's option.

D.	Flanged Joints:  Match flanges within piping system, and at connections with valves and equipment.  Clean flange faces and install gaskets.  Tighten bolts to provide uniform compression of gasket.

E.	Insulating (Dielectric) Fittings:  Comply with manufacturer's instructions for installing unions or fittings.  Install in a manner which will prevent galvanic action and stop corrosion where the "joining of ferrous and non-ferrous piping" is indicated.

F.	Changes in Direction:  Use fittings for all changes in direction.  Run lines parallel with building surfaces.

G.	Steam Line Grades:  Pitch piping uniformly down 1" to 40' minimum in the direction of steam flow.

H.	Condensate Line Grades:  Pitch piping uniformly down 0.5" to 10' minimum in the direction of condensate flow.

I.	Unions and Flanges:  At all equipment to permit dismantling and elsewhere as consistent with good installation practice.

1.	Install unions on 2 inches and smaller piping.

2.	Install flanges on 2-1/2 inches and larger piping.

J.	Expansion:  Provide loops, swing joints, anchors, runouts and spring pieces to prevent damage to piping or equipment.

3.3	MISCELLANEOUS PIPING EQUIPMENT

A.	Floor, Wall and Ceiling Plates:  Chrome plated pressed steel or brass screw locked split plates on all pipe penetrations in finished spaces.

B.	Strainers:  Install in a manner to permit access for cleaning and screen removal and with blow-off valve.

1.	Steam or gas lines:  Install y-type strainer on horizontal lines with the pocket in the horizontal plane.  .

2.	Liquid lines:  Install y-type strainer on horizontal lines with the pocket pointing vertically downwards.

3.	On vertical lines the y-type strainer shall be installed with the pocket pointing downward when the flow is downward.

4.	Install strainers upstream of the [control valves,] [steam traps,] [pressure reducing valves,] [flowmeters].

C.	Sleeves:  At all penetrations of concrete or masonry construction.  PVC, 24 gauge galvanized steel or Schedule 40 galvanized steel pipe.  Use steel pipe sleeves through beams, footings, girders or columns and for all penetrations of walls or floors below grade.  Where floor finish is ceramic tile, terrazzo, or similar material extend standard steel pipe sleeves 1-1/2" above finished floor.  Fabricate sleeves 1" diameter larger than pipe or insulation.  PVC and sheet metal sleeves at non-structural penetrations only.

D.	Sleeve Caulking:  Grout uninsulated pipe with cement mortar or approved waterproof mastic.  All caulking or grouting shall extend full depth of sleeve.     Install UL sealing caulk, putty and/or system at all penetrations of fire rated walls, floors and ceiling.

E.	Valves:  Install valves in accordance with Section 23 05 00.  Install control valves specified in other division 23 sections.

F.	Pressure Gauges:  Install upstream and downstream of [pressure reducing valves,] [filters].  Install pressure gauge on [blowdown tank][flash tank] vessel(s).

G.	Safety Valves:  Install downstream of the pressure reducing valve.  Size the safety valve to prevent unsafe pressure rise in the system, if pressure reducing valve fails in the open position.

H.	Swing Check Valves:  Install in horizontal position.  Vertical installation shall be allowed on upflow systems only.

3.4	EQUIPMENT INSTALLATION

A.	Installation and Arrangement:  Install and arrange as shown on the Drawings.  Comply with manufacturer's recommendations for installation connections and start-up.

B.	Lubrication:  Lubricate all moving and rotating parts in accordance with the manufacturer's recommendations prior to start-up.

C.	Expansion Joint and Compensator Installation:  Carefully align joint or compensator and make proper allowance for temperature of pipe at time of installation.

D.	Steam Traps:  Provide where indicated on returns from steam using equipment and on drips from ends of mains and other low points in steam piping, whether indicated or not.  Install with union connections on both sides, "Y" type strainer same make as trap on inlet, and gate valve on inlet from main riser or end of main drips and where indicated.

For systems over 15 psig, install bucket type traps on all equipment and on drips from ends of main and other low points in steam piping, whether indicated or not, with gate, "Y" type strainer (same make as trap) and union on inlet side and check and gate on outlet.  3/4" minimum size in any location.

E.	Pressure Relief Valve Installation:  Install relief valves directly into pressure vessel tapping or with minimum length of pipe and no elbows. Inlet and outlet piping shall be the relief valve size or larger and have no shutoff valves. Support the discharge piping independently of relief valve.  Discharge pipe shall contain no more than one elbow and the outlet shall not be threaded. Terminate the discharge piping within 6 inches of the floor unless otherwise shown on the drawings.

F.	Steam Safety Relief Valve Installation:  Pipe discharge through roof two pipe sizes larger than safety valve outlet.  Support all piping free of safety valve and provide unions or flanges to allow removal of safety valve without disturbing drip pan elbow.  Where valve is mounted more than 6 feet above floor or testing lever is otherwise inaccessible, provide operating chain or cable with handle from testing lever to an accessible point 6 feet above the floor.  Support cable clear of any insulation.

G.	Air Vents:  Conduct 1/4" copper tubing from high end of air chambers to accessible locations and terminate with screwdriver cock.  Conduct 1/4" copper tubing from outlets of automatic air vents to floor drains indicated or to the outside when approved by Governing Authorities.

H.	Pumps:  Mount in a manner to allow disassembly of pump and motor without disturbing piping.

3.5	TEST

A.	General:

1.	Minimum duration of two hours or longer, as directed for all tests.  Furnish report of test observation signed by qualified inspector.  Make all tests before applying insulation, backfilling, or otherwise concealing piping or connecting fixtures or equipment.  Where part of the system must be tested to avoid concealment before the entire system is complete, test that portion separately, same as for entire system.

2.	Provide all necessary temporary equipment for testing, including pump and gauges.  Remove control devices before testing and do not use piping system valves to isolate sections where test pressure exceeds valve pressure rating.  Fill each section with water and pressurize for the indicated pressure and time.

3.	Observe each test section for leakage at end of test period.  Test fails if leakage is observed or if pressure drop exceeds 5% of test pressure.

B.	Repair:

1.	Repair piping system sections which fail the required piping test by disassembly and re-installation, using new materials to the extent required to overcome leakage.  Do not use chemical stop-leak compounds, solder, mastics, or other temporary repair methods.

2.	Drain test water from piping systems after testing and repair work has been completed.

C.	Steam and Condensate Return Piping:  75 psig hydrostatic without loss for four hours.

D.	Tanks and Equipment:  Hydrostatic pressure to 1.5 times operating pressure.

3.6	CLEANING

A.	General:  Clean all dirt and construction dust and debris from all mechanical piping systems and equipment and leave in a new condition.  Touch up paint where necessary.

B.	Flushing of Steam Heating System:

1.	After boilers have been cleaned and are ready to operate, remove all thermostatic elements from the traps and operate system with all condensate run to sewer until it shows clear at all drains, but not less than 8 hours.

2.	After system is all flushed out, including pumps and converters, clean all dirt pockets and strainers, and reinstall all thermostatic elements.  Furnish the fuel oil, operate the plant and cooperate with Owner to the end that the entire heating system throughout the project is thoroughly flushed out.

END OF SECTION