# SECTION 26 05 73

# electrical power system studies

## PART 1 - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.02	DESCRIPTION

A.	The electrical equipment manufacturer shall provide electrical power system studies for the project as specified herein.

1.03	SUBMITTAL AND RECORD DOCUMENTATION

A.	Submit five copies of the completed power system studies, bound and tabulated with table of contents and section & page numbers.

## PART 2 - PRODUCTS

2.01	SHORT-CIRCUIT ANALYSIS

A.	Calculation of the maximum rms symmetrical three-phase short-circuit current at each significant location in the electrical system shall be made using a digital computer and software.

B.	Appropriate motor short-circuit contribution shall be included at the appropriate locations in the system so that the computer-calculated values represent the highest short-circuit current the equipment will be subjected to under fault conditions.

C.	A tabular computer printout shall be included which lists the calculated short-circuit currents, X/R ratios, equipment short-circuit interrupting or withstand current ratings, and notes regarding the adequacy or inadequacy of the equipment.

D.	The study shall include a computer printout of input circuit data including conductor lengths, number of conductors per phase, conductor impedance values, insulation types, transformer impedances and X/R ratios, motor contributions, and other circuit information as related to the short-circuit calculations.

E.	Include a computer printout identifying the maximum available short-circuit current in rms symmetrical amperes and the X/R ratio of the fault current for each bus/branch calculation.

F.	The system one-line diagram shall be computer generated and shall clearly identify individual equipment buses, bus numbers/names used in the short-circuit analysis, cable and bus connections between equipment, calculated maximum short-circuit current at each bus location and other information pertinent to the computer analysis.

G.	A comprehensive discussion section evaluating the adequacy or inadequacy of the equipment must be provided and include recommendations as appropriate for improvements to the system.

H.	The analysis shall be based upon the actual available three-phase short-circuit rms symmetrical current from the serving utility's system. Include in the report this value on utility letterhead.

I.	The Contractor shall be responsible for supplying actual conductor information (lengths, types, number per phase, etc.) and other pertinent equipment information (transformer sizes and impedances, generator sizes and sub-transient reactances, etc.) to the equipment manufacturer in a timely manner to allow the short-circuit analysis to be completed, reviewed, and modified as necessary prior to ordering of equipment.

J.	Any inadequacies shall be called to the attention of the Engineer and recommendations made for improvements as soon as they are identified.

2.02	EMERGENCY SYSTEM PROTECTIVE DEVICE TIME-CURRENT COORDINATION ANALYSIS

A.	The time-current coordination analysis shall be performed on the emergency system with the aid of a digital computer and software and shall include the determination of settings, ratings, or types for the overcurrent protective devices supplied, to comply with NEC 700 and/or 701.

B.	Where necessary, the Engineer shall be consulted regarding the appropriate compromises to be made between system protection and service continuity.

C.	A sufficient number of computer-generated log-log plots shall be provided to indicate the degree of system protection and coordination by displaying the time-current characteristics of series-connected overcurrent devices and other pertinent system parameters.

D.	Computer printouts shall accompany the log-log plots and shall contain descriptions for each of the devices shown, settings of the adjustable devices, the short-circuit current availability at the device location when known, and device identification numbers to aid in locating the devices on the log-log plots and the system one-line diagram.

E.	The study shall include a separate, tabular computer printout containing the suggested device settings of all adjustable overcurrent protective devices, the equipment where the device is located, and the device number corresponding to the device on the system one-line diagram.

F.	A computer-generated system one-line diagram shall be provided which clearly identifies individual equipment buses, bus numbers, device identification numbers and the maximum available short-circuit current at each bus when known.

G.	A discussion section which evaluates the degree of system protection and service continuity with overcurrent devices, along with recommendations as required for increasing system protection or device coordination.

H.	The Contractor shall be responsible for supplying actual equipment and system information to the equipment manufacturer in a timely manner to allow the protective device time-current coordination analysis to be completed, reviewed, and modified as necessary prior to ordering of equipment.

I.	Significant deficiencies in protection and/or coordination shall be called to the attention of the Engineer and recommendations made for improvements as soon as they are identified.

2.03	ARC FLASH HAZARD ANALYSIS

A.	The arc flash hazard analysis shall be performed according to the IEEE 1584 equations that are presented in NFPA70E-2004, Annex D.

B.	The flash protection boundary and the incident energy shall be calculated at all significant locations in the electrical distribution system (switchboards, switchgear, motor-control centers, panelboards, busway and splitters) where work could be performed on energized parts.

C.	The Arc-Flash Hazard Analysis shall include all significant locations in 480 volt systems, and in all 240 volt and 208 volt systems fed from transformers equal to or greater than 125 kVA where work could be performed on energized parts.

D.	Safe working distances shall be based upon the calculated arc flash boundary considering an incident energy of 1.2 cal/cm^2.

E.	When appropriate, the short circuit calculations and the clearing times of the phase overcurrent devices shall be retrieved from the short-circuit and coordination study model. Ground overcurrent relays should not be taken into consideration when determining the clearing time when performing incident energy calculations.

F.	The short-circuit calculations and the corresponding incident energy calculations for multiple system scenarios must be compared and the greatest incident energy must be uniquely reported for each equipment location. Calculations must be performed to represent the maximum and minimum contributions of fault current magnitude for all normal and emergency operating conditions. The minimum calculation will assume that the utility contribution is at a minimum and will assume a minimum motor contribution (all motors off). Conversely, the maximum calculation will assume a maximum contribution from the utility and will assume the maximum amount of motors to be operating. Calculations shall take into consideration the parallel operation of synchronous generators with the electric utility, where applicable.

G.	The incident energy calculations must consider the accumulation of energy over time when performing arc flash calculations on buses with multiple sources. Iterative calculations must take into account the changing current contributions, as the sources are interrupted or decremented with time. Fault contribution from motors and generators should be decremented as follows:

1.	Fault contribution from induction motors should not be considered beyond 3-5 cycles.

2.	Fault contribution from synchronous motors and generators should be decayed to match the actual decrement of each as closely as possible (e.g. contributions from permanent magnet generators will typically decay from 10 per unit to 3 per unit after 10 cycles).

H.	For each equipment location with a separately enclosed main device (where there is adequate separation between the line side terminals of the main protective device and the work location), calculations for incident energy and flash protection boundary shall include both the line and load side of the main breaker.

I.	When performing incident energy calculations on the line side of a main breaker (as required per above), the line side and load side contributions must be included in the fault calculation.

J.	Mis-coordination should be checked amongst all devices within the branch containing the immediate protective device upstream of the calculation location and the calculation should utilize the fastest device to compute the incident energy for the corresponding location.

K.	Arc Flash calculation shall be based on actual overcurrent protective device clearing time. Maximum clearing time will be capped at 2 seconds based on IEEE 1584-2002 section B.1.2. Where it is not physically possible to move outside of the flash protection boundary in less than 2 seconds during an arc flash event, a maximum clearing time based on the specific location shall be utilized.

2.04	MANUFACTURERS/VENDORS

A.	The specified electrical power system studies shall be performed by the manufacturer(s) of the electrical distribution equipment.

## PART 3 - EXECUTION

3.01	ARC FLASH WARNING LABELS

A.	The Contractor of the Arc Flash Hazard Analysis shall provide a 3.5 in. x 5 in. thermal transfer type label of high adhesion polyester for each work location analyzed.

B.	All labels shall be based on recommended overcurrent device settings and shall be provided after the results of the analysis have been presented to the Owner and after any system changes, upgrades or modifications have been incorporated in the system.

C.	The label shall include the following information, at a minimum:

1.	Location designation

2.	Nominal voltage

3.	Flash protection boundary

4.	Hazard risk category

5.	Incident energy

6.	Working distance

7.	Engineering report number, revision number and issue date.

D.	Labels shall be machine printed, with no field markings.

E.	Arc flash labels shall be provided in the following manner and all labels shall be based on the recommended overcurrent device settings.

1.	For each 480 volt and applicable 208 volt (or 240 volt) panelboard, one arc flash label shall be provided.

2.	For each motor control center, one arc flash label shall be provided.

3.	For each low voltage switchboard, one arc flash label shall be provided.

4.	For each switchgear, one arc flash label shall be provided.

F.	ARC Flash Training

1.	The Contractor of the Arc Flash Hazard Analysis shall train the Owner’s qualified electrical personnel of the potential arc flash hazards associated with working on energized equipment (minimum of 4 hours). The training shall be certified for continuing education units (CEUs) by the International Association for Continuing Education Training (IACET) or equivalent.

END OF SECTION