## SECTION 224000 - PLUMBING FIXTURES

## PART 1 - GENERAL

1.1	DESCRIPTION

A.	The requirements of this section apply to the plumbing system.

B.	Provide fixtures specified and shown on the Drawings.

1.2	QUALITY ASSURANCE

A.	Code:  Comply with requirements of the Oregon State Plumbing Specialty Code.

B.	Fixture Color:  White unless indicated otherwise.

C.	Utility Connections:  Make utility and equipment connections and install distribution piping as shown on the Drawings and specified herein.  Verify size, location, depth, elevation and arrangement of connection points before bidding or starting work.

D.	Potable Water Valves:  Potable water valves not limited to faucets, mixing valves, or pressure reducing valves.  Valves shall meet NSF Standard 61, Section 9, for drinking water faucets and shall be brass construction.  Brass components which contact water within the faucet shall be from brass which contains no more than 3 percent lead by dry weight.

E.	Field Wiring:  Comply with requirements of Section 220500.

## PART 2 - PRODUCTS

2.1	PIPING

A.	Piping, fittings, supports and related items as specified in related Sections 220500, 221000, and 220700.

2.2	SITE WORK MATERIALS

A.	Precast concrete vaults of size required and indicated on the Drawings complete with access suitable for the installation and with suitable inspection plates.

2.3	INTERIOR PLUMBING MATERIALS

A.	Cleanouts:

1.	Manufacturer:  J.R. Smith, Zurn, Wade, Ancon, or accepted substitute.

2.	Types:

a.	Tile Floor Cleanouts:  Smith 4053-U with square heavy-duty nickel bronze top, taper thread, bronze plug, and vandalproof screws.

b.	Carpeted Floor Cleanout:  Smith 4023-U-X with round heavy-duty nickel bronze top, taper thread, bronze plug, carpet clamping device and vandalproof screws.

c.	Concrete Floor Cleanout:  Smith 4023 with round heavy-duty nickel bronze top.

d.	Wall Cleanouts:  Smith 4472-U, bronze ferrule with raised head bronze plug, stainless steel shallow cover and vandalproof screws.

e.	Outside Area Walks and Drives:  Smith 4253-U-G with galvanized cast iron body, top secured with vandalproof screws, taper thread and bronze plug.  Install in 18" x 18" x 6" deep concrete pad flush with grade.

B.	Flashing:  Minimum 4# sheet lead; to extend horizontally 10" from edge of vent penetrations or rain drain body and vertically 12" minimum up from roof turned over and down into hub of vent or finished with bronze cap providing counterflashing for screwed pipe.

C.	Air Chambers and Shock Arrester:  Precharged bellows or sealed piston type manufactured to meet PDI WH-201 and ASSE 1010 Standards.  Size in accordance with PDI procedures.  Jay R. Smith, PPP, Wade, Zurn, Ancon, or accepted substitute.

D.	Priming Valves:  Smith 2699, Wade W8800T, Zurn Z1022, Ancon MS810 or equivalent Precision Plumbing.  Locate in closets, under counters or in walls behind Milcor or access panels as specified in Section 220500.  Use copper specified in Section 221000, Pipe & Pipe Fittings, for all underground priming lines.

E.	Traps:  Except chrome plated fixture traps.  Recessed drainage pattern for threaded pipe and same grade as pipe for cast iron pipe; with cleanout plugs in trap body in all above grade locations.

F.	Domestic Hot Water Circulator:  Bronze body, bronze fitted, in-line circulator with sleeve bearing.  Bell and Gossett or equivalent Grundfos, Thrush, Taco or Armstrong.

G.	Single Fixture Tempering Valve:  Thermostatic mixing valve. Watts MMV. ASSE 1016 listed. Bronze/brass construction with stainless steel disc and springs, copper thermostat.

H.	Gas Fired Water Heater:

1.	AGA approved commercial gas fired heater complying with the State Energy Code requirements and of size and capacity shown on Drawings.  Glass lined steel tank equipped with sacrificial anode.  1-1/2" minimum of non-organic insulation, cold rolled enameled steel jacket to encase sides, top and combustion chamber.  Adjustable automatic thermostat, safety pilot, main and pilot gas cocks, automatic gas pressure regulator, all brass hose bib drain.  ASME Code pressure-temperature relief.  Unit shall be  high efficiency with PVC combustion air and exhaust.

2.	Coates, Rheem, PVI, Ruud, A.O. Smith, Bradford White, State, or accepted substitute.

I.	Water Heater and Tank Seismic Restraints:  For water heaters and tanks up to 100 gallons, Spacemaker restraints or approved.

J.	Pressure Reducing Valve:  Single seat type with renewable stainless steel seat and valve.  Size and capacity as shown on Drawings.  Bronze bodies with screwed connections on valves 2-1/2" and smaller and flanged steel bodies on valves 3" and larger.  Install each PRV with strainer on inlet or internal strainer.  Leslie, Spence, Fisher, Watts, Foster, Cash-Acme, or accepted substitute.

K.	Backflow Preventer:  Where indicated on the Drawings, install a reduced pressure backflow preventer complete with shutoff valves, two separate check valves, differential relief valve and test cocks.  USC Foundation for Cross Connection Control, State Health Officials and serving utilities approved.  Bronze bodies on units 2" and smaller, and cast iron bodies with bronze trim on units 2-1/2" and larger.

L.	Master Mixing Valve:  All brass or bronze body with stainless steel parts, thermostatic master control element to fail safe upon cold water or control element failure.  Provide with external union angle check stops, strainers, volume control, shutoff valves, dial thermometer.  Valve location, arrangement and capacity as shown on Plans.  Leonard, Lawler, Powers, or accepted substitute.

M.	Gas Pressure Regulators:  AGA approved size and capacity as required for connected load with propane fuel.  Maxitrol, Rockwell, Fisher, Reliance, or accepted substitute.

N.	Domestic Water Balancing Valve:  Balancing fitting with differential pressure taps, brass or bronze body and trim.  B&G "Circuit Setter" or equivalent Taco, Armstrong, Thrush, Wheatley, Flow Design or accepted substitute.

O.	Thermometers:  Mercury-in-glass, adjustable stem, separable sockets, plus 40 to 240 degrees F range (unless indicated otherwise) thermometers.  Weiss numbers are listed.  Equivalent Marshalltown, Taylor, Trerice, Wekler or accepted substitute.

1.	Wide case (9") in equipment rooms and all major equipment items.  Weiss "9VS" series.

2.	Narrow case (7") in all other locations.  Weiss "7VS" series.

P.	Dishwasher and Cooking Equipment Pressure Reducing Valve:  For installation with dishwasher booster heater and other kitchen equipment, all brass, single seat type for dead end service, with renewable stainless steel seat and valve.  Designed for service on hot water to reduce pressure from 50 to psi to 20 psi.  Leslie, Watts, Cash-Acme, Zurn-Wilkins, or approved substitute.

Q.	Tempering Valve:  Designed for single or banks of lavatories thermostatic mixing valve. ASSE 1070 listed. Lead free brass construction with integral check valves.

Incoming HT temperature is 140 degree F at Lavatories.

2.4	PLUMBING FIXTURES

A.	Stops:  Furnish stop valves for all fixtures. Loose key style, in wall, angle or straight through pattern to fit installation.  Kohler, Speedway, Chicago, Eastman, Brasskraft, or accepted substitute.

B.	Fixture Traps:  Exposed fixture tailpieces, traps, and wastes shall be chrome plated 17 gauge seamless brass tube with cast brass nuts and deep or box style escutcheons as required to conceal rough piping.  Products to be stamped with manufacturer’s name and material gauge.  McGuire, Keeney, Zurn, or approved.

C.	Provide compliant fixture piping protector kit on all exposed accessible fixture traps and water supplies.  White anti-microbial molded PVC.  IPS Truebro “Lav Guard 2”, McGuire “ProWrap”, Plumberex “Pro-extreme”, or approved substitute.

D.	1.28 Gallon, Water Closet, Elongated Type, Vitreous China:  Floor mounted two piece close coupled, gravity tank type water closet shall be specifically designed for 1.28 gallon siphon jet flush.  Provide stop, escutcheon, and flush lever.

1.	Seat:  Solid white heavy weight molded plastic seat, with molded-in bumpers; open front less cover for elongated bowl with check and self-sustaining hinge.  Hinge and hardware to be 300 series stainless steel. Church 295-SSC, Beneke 523-SS/CH-B,  Bemis 1955 SS/C, or Zurn Z5956SS-EL-STS.

2.	Kohler, Highline Model K-3999-UR, or approved equal.

E.	Urinal, Flush Valve, Vitreous China, "UR-1":

1.	Install each listed urinal line with the following:  Quiet acting, exposed chrome plated  0.5 GPF brass flush valve with ADA manual operation, screwdriver check/control stop with vandal resistant cap, cast wall flange, check/control stop with vandal resistant cap, cast wall flange,  synthetic rubber diaphragm, and vacuum breaker, as recommended by fixture manufacturer. Sloan, Zurn.

2.	Wall Hung:  Install with plate type carrier with bearing plate.  Zurn, Jay R. Smith, Wade, Ancon.  American Standard 6501.010, Kohler 4960 or Eljer 161-2030.

3.	Set one urinal at height required by code for the handicapped in each restroom.

F.	Lavatory :

1.	Faucet:  Chrome plated brass body with handle for the handicapped, vandal resistant 0.5 gpm aerator, tempering valve with grid strainer waste.  American Standard 1480.100, or equal Symmons, Delta, Moen.

2.	“LV-1”: 22”x19” Type 304 Stainless Steel wall mounted lavatory sink.  Elkay ELV2219, or approved equal.

3.	“LV-2”: 21”x18” vitreous china, wall hung lavatory sink. Kohler Kingston, K-2005, or approved equal.

G.	Drains:

1.	Zurn, Jay R. Smith, Wade and Ancon.  Numbers scheduled on drawings represent minimum acceptable standard for locations involved.

2.	Install 4 pound sheet lead flashing, extending not less than 10" from and clamped to all drains not completely cast-in-place in a homogeneous material.

H.	Fiber Glass, Single Stall, “SH-1”:  Install with concealed piping and 1.75 gpm maximum fixed head, handheld shower head with flex hose and quick connect wall mount diverter valve, vacuum breaker, and wall slide bar for ADA.  Pressure equalizing mixing valve with combination strainer/check stops and temperature limit stop.  Powers, Leonard, Lawler, Symmons approved.  Fiberglass shower stall with grid strainer outlet, grab bars and curtain rod reinforced for grab bar and curtain rod.  Aquatic 1363BFSC.

I.	Hose Bibs:

1.	Outside "HB-1":  Non-freeze type with vacuum breaker, bronze wall casing and wall clamp.  Zurn Z-1310-6, Wade W-8620, Woodford 67 series, Smith 5609-PB, or Watts HY420.

2.	Inside, “HB-2”: Indoor HW and CW mixing hose station,all exposed parts made of stainless steel.  Strahman M-750TG.

J.	Fixtures Furnished by Owner (and/or Under Another Section):  Some fixtures will be furnished by the Owner (and/or under another specification section).  Include under this section the required rough-ins, 3/8" chrome plated supplies with stops, 1-1/2" chrome plated cast brass "P" trap (or, on kitchen sinks, 2" cast iron "P" traps) for each sink compartment, and make final connection.  Verify all rough-ins and connection requirements before commencing work.

K. 	Ice Maker Connection, IM-1:  Guy Gray BIM 875 or approved.

L.	  Service Sump (Mop Basin)" ":

1.	Faucet exposed, brass body, rough plated, long spout, top brace, hose end spout with bucket hook, vacuum breaker and integral stops in shanks.  Chicago 897, T & S  B-0665-BSTP, or equal Zurn, Delta Commercial, mounted 24" above rim.  Install with 18 gauge type 302, No. 4 finish stainless steel splash on the two walls.

2.	Molded stone 24" x 24" x 10" deep with vinyl bumper guard and 3" brass body   strainer outlet.  Fiat, Mustee, Swan or approved substitute.

## PART 3 - EXECUTION

3.1	PIPING

A.	Install in accordance with Section 220500, 221000, 220700, and 223000.

B.	Shock Arrestors and Air Chambers:  Install at end of mains, in a battery of three or more flush valve-operated fixtures water header, ahead of quick closing and solenoid operated valves.  Size per PDI recommendations where size is not indicated.  Provide access panels.

C.	Trap Priming:  Traps serving floor drains, floor sinks, catch basins, and similar fixtures shall be primed in accordance with Code requirements.

3.2	CLEANOUTS

A.	Where required by code, at each change of sewer direction 45 degrees or greater and more than 10' long, at end of each branch or main and spaced not greater than 100' apart, as required by code and/or as shown on Drawings.

3.3	FIXTURE INSTALLATION AND CONNECTION

A.	All exposed fixture connections and piping shall be plated with polished chrome.  Where chair carriers or special carrier design are not indicated, provide 3/16" thick by 6" wide steel to waste or vent piping and to available building construction.

B.	All fixtures in contact with finished walls shall be caulked with waterproof, white, non-hardening sealant which will not crack, shrink or change color with age.

C.	All fixtures and component parts shall conform to governing codes.

3.4	FIXTURE CLEANING

A.	Remove construction protection, tags and labels and thoroughly clean all plumbing equipment and trim and scour all fixtures just prior to building acceptance.

3.5	CHEMICAL WATER TREATMENT

A.	Analyze the water condition and determine chemicals required for treatment.  Provide sufficient chemicals for the initial fill and provide a list of the chemicals required for the Operating and Maintenance Manuals specified.  The list shall include probable quantities of each chemical required for one year, availability of each chemical and the name and address of the supplier.

END OF SECTION 224000