CITY OF PORTLAND, OREGON – BUREAU OF DEVELOPMENT SERVICES

1900 SW Fourth Avenue, Suite 5000  Portland, Oregon  97201  www.portlandonline.com/bds

| MECHANICAL CHECKSHEET |  |  |  | Application # : | 16-164385-000-00-MT |  |
| --- | --- | --- | --- | --- | --- | --- |
| Mechanical Permit |  |  |  | Review Date : | May 10, 2016 |  |
| To: | APPLICANT | TIM RICHARD SITEWORKS DESIGN BUILD 240 SE 2ND AVE PORTLAND, OR 97214 |  | Cellular: |  | 503 449-7326 |
|  |  |  |  | Work: |  | 503 230-2337 |
|  |  |  |  | e-Mail: |  | tim@siteworksportland.com |
| From: | BDS Mechanical Engineer | Thomas Ng |  | Phone: Fax: |  | 503-823-7434 503-823-4591 |
| cc: | OWNER | POWELL LLC 533 DYKE RD DILLARD, OR 97432 |  |  |  |  |

| PROJECT INFORMATION |  |
| --- | --- |
| Street Address: |  |
| Description of Work: | MECHANICAL FOR NEW CONSTRUCTION OF 4 STORY MULTIFAMILY APARTMENT BUILDINGS. PTAC UNITS. ELEC HEATER IN BEDRM. BATHRM EF. DRYER EXHAUST. KIT HOOD EXH. GAS WATER HEATER. 2 PSIG GAS SYSTEM. |

| Based on the plans and specifications submitted, the following items appear to be missing or not in conformance with the Oregon Mechanical Specialty Code and / or other city, state, or federal requirements. |  |  |  |
| --- | --- | --- | --- |
| Item # | Location on plans | Code Section | Clarification / Correction Required |
| 1. | General | 2014 OMSC 505.2 | Kitchen hood information not provided. Please provide make up air to hood exhaust as required. |
| 2. | 2/M601 | 2014 OMSC 504.1 | Please provide independent dryer exhaust from the dryer to exterior wall. Provide baffles to separate from other systems as required. |
| 3. | General | 2014 OMSC 504.5 | Please provide make up air to the room dryer located. |
| 4. | General | 2014 OMSC 504.6.1 and 504.6.2 | Please add a note on plans for dryer duct material shall have a smooth interior finish and 0.016 inch think. Rivet or screw penetrates to the duct wall is not acceptable. Dryer Duct shall be support every 4 foot intervals. |
| 5. | G201, 3/M601 | 2016 OSSC 707.6 | Please provide fan in a box detail to maintain ceiling assembly rating. |
| 6. | M601 | 2014 OMSC Table 403.3 | Please provide ventilation table. |
| 7. |  |  |  |
| 8. |  |  |  |
| 9. |  |  |  |
| 10. |  |  |  |

INSTRUCTIONS

To respond to this checksheet, come to the Bureau of Development Services located at 1900 SW Fourth Ave. The Development Service Center (1st floor) and Permitting Services (2nd floor) are open Monday through Friday from 8:00 a.m. to 3:00 p.m. (close at noon on Thursday).  Please update all sets of submitted drawings by either replacing the original sheets with new sheets, or editing the originally submitted sheets.  You can review ''How to Update Your Plans in Response to a Checksheet'' at http://www.portlandoregon.gov/bds/article/93028  Visit the BDS website for more helpful information and a current listing of services available in the Development Services Center.

Please complete the attached Checksheet Response Form and include it with your re-submittal.

If you have specific questions concerning this Checksheet, please call me at the phone number listed above. To check the status of your project, go to http://www.portlandonline.com/bds/index.cfm?c=34194.  Or, you may request the status to be faxed to you by calling 503-823-7000 and selecting option 4.

You may receive separate Checksheets from other City agencies that will require separate responses.

NEW RECHECK FEE:  Please note that for plans submitted on or after July 1, 2010 plan review fees for Life Safety, Structural, Site Development and Planning and Zoning will cover the initial  review and up to two checksheets and the reviews of the applicant's responses to those checksheets. All additional checksheets and reviews of applicant responses will be charged $155 per checksheet.

Appeals:  Pursuant to City Code Chapters 24.10, 25.07, 26.03, 27.02, and 28.03, you may appeal any code provision cited in this Checksheet to the BDS Administrative Board of Appeal within 180 calendar days of the review date.  For information on the appeals process and costs, including forms, appeal fee, payment methods and fee waivers, go to www.portlandoregon.gov/bds/appeals, call (503) 823-7300 or come in to the Development Services Center.  Permit application expiration will not be extended pending resolution of any administrative appeal.

# Mechanical Checksheet Response

Permit #:    16-164385-000-00-MT	Date: __7-06-16___________________

Customer name and phone number: _Mark Denyer 503-234-0548_______

Note:	Please number each change in the ‘#’ column.  Use as many lines as necessary to describe your changes.  Indicate which reviewer’s checksheet you are responding to and the item your change addresses.  If the item is not in response to a checksheet, write customer in the last column.

| # | Description of changes, revisions, additions, etc. | Checksheet and item # |
| --- | --- | --- |
| 1 | The kitchen hoods are residential, and less than 400 cfm, thus make up air is not required - -see Architectural cut sheets on the hoods. |  |
| 2 | The dryer duct is independent - -that is exactly what detail 2/M601 shows. The dryer duct is routed independently to the exterior wall louver/screen. A Baffle has been added per the City of Portland requirements. |  |
| 3 | The dryers are residential and exhaust less than 200 cfm. The dryers are not located in closets, but are open to the bathrooms, which are open to the rest of the dwelling unit, thus make up air is not required. |  |
| 4 | The requested note has been added to the drawings for typical dryer duct installation requirements. |  |
| 5 | The bathroom ceiling fan is installed in a drop ceiling located below the floor ceiling rating, and thus does not penetrate any ratings, please see the architectural details for clarification. |  |
| 6 | This project is not mechanically ventilated, but instead uses natural ventilation under the procedures listed under section 402 Natural ventilation. The PTHP schedule on sheet M600 states that the ventilation is provided by natural means, and that operable windows have greater than 4% operable area. |  |

(for office use only)