# SECTION 22 40 00 – PLUMBING fixtures

## PART 1 - GENERAL

1.1	DESCRIPTION

A.	The requirements of this section apply to the plumbing fixtures and trim.

B.	Provide fixtures as shown on the Drawings and specified herein.  Provide all required fixture trim and accessories for a complete, finished installation.

C.	Related Work:  The requirements of Section 22 05 00, Common Plumbing Materials and Methods, also apply to this section.

1.2	QUALITY ASSURANCE

A.	Code:  Comply with requirements of the Oregon State Plumbing Specialty Code.

B.	Fixture color: White unless indicated otherwise.

C.	Potable Water Valves:  Potable water valves not limited to faucets, mixing valves, or pressure reducing valves.  Valves shall meet NSF Standard 61, Section 9, for drinking water faucets and shall be brass construction.  Brass components which contact water within the faucet shall be from brass which contains no more than 0.25 percent lead by dry weight.

## PART 2 - PRODUCTS

2.1	PIPING

A.	Piping, fittings, and related items as specified in related Sections 22 10 00.

2.2	INTERIOR PLUMBING MATERIALS

A.	Shock Arrester:  Precharged bellows or sealed piston type manufactured to meet PDI WH-201 and ASSE 1010 Standards.  Size in accordance with PDI procedures.  J. R. Smith, PPP, Sioux Chief, Wade, Zurn, Watts, Josam, or approved substitute.

B.	Dishwasher and Cooking Equipment Pressure Reducing Valve:  For installation with dishwasher booster heater and other kitchen equipment, all brass, single seat type for dead end service, with renewable stainless steel seat and valve.  Designed for service on hot water to reduce pressure from [50 to psi to 20 psi].  Leslie, Watts, Cash-Acme, Zurn-Wilkins, or approved substitute.

D.	Handsink Tempering Valve:  Pressure compensating water mixing valve. Precision Plumbing Products “Tempera” valve or approved substitute.

E.	Secondary piping supports: Install manufactured secondary piping supports for support and positioning of fixture rough-in piping from framing members.  Hubbard, Sioux-Chief,  or approved substitute.

2.3	PLUMBING FIXTURES and trim

A.	Stops:  Furnish stop valves for all fixtures.  Screwdriver  style, in wall, angle or straight through pattern to fit installation.  Stops to be all brass with full turn brass stem and replaceable washer, no plastic.  Compression nuts to be high copper content brass.  Finish to be copper nickel chrome plate.  Product to carry manufacturer’s name.  Risers to be chrome plated copper.  Provide chrome plated shallow escutcheons.  McGuire, Chicago, Brasskraft, Keeney, Zurn, or approved substitute.

B.	Fixture Traps:  Exposed fixture tailpieces, traps, and wastes shall be chrome plated 17 gauge seamless brass tube with cast brass nuts and deep or box style escutcheons as required to conceal rough piping.  Products to be stamped with manufacturer’s name and material gauge.  McGuire, Keeney, Zurn, or approved.

C.	Provide compliant fixture piping protector kit on all exposed accessible fixture traps and water supplies.  White anti-microbial molded PVC.  IPS Truebro “Lav Guard 2”, McGuire “ProWrap”, Plumberex “Pro-extreme”, or approved substitute.

D.	1.28 Gallon Flush Water Closet, Flush Valve, Vitreous China:  Elongated water closet bowl shall be designed for 1.6 gallon siphon jet flushing action.

1.	Install each listed water closet with the following:

a.	Flush Valve:  Quiet acting, exposed chrome plated brass with [ADA metal oscillating non-hold-open handle] [battery powered] [ low voltage powered with transformer] motion sensor and operating solenoid], screwdriver check/control stop with vandal resistant cap, cast wall flange, synthetic rubber diaphragm, and vacuum breaker, as recommended by closet manufacturer.  Sloan, Zurn.

b.	Seat:  Solid white [ black ] heavy weight molded plastic seat, with molded in bumpers; open front less cover for elongated bowl with check and self-sustaining hinge.  Hinge and hardware to be 300 series stainless steel. Church 295-SSC, Beneke 523-SS/CH-B, or Bemis 1955 SS/C, Zurn Z5956SS-EL-STS.

2.	Floor Mounted, Top Spud "WC-":  American Standard 2234.015, Kohler K-4350, or Eljer 111-2125.  [ Toto CT 705. ]

3.	Floor Mounted, Top Spud 18" High "WC-":  American Standard 3043.102, Kohler K-4368, Eljer 111-2145.  [ Toto CT 705L. ]

4.	Wall Hung, Top Spud "WC-":  Install with cantilevered design chair carrier for single or battery installation.  Zurn, Jay R. Smith, Josam, Watts, and Wade.  Set water closet " " for the handicapped at height required by code.  American Standard 2257.103,  Kohler K-4330, Eljer 111-2105.  [ Toto CT 708. ]

E.	Lavatory, Vitreous China, "LV-1":

1.	Faucet:  Chrome plated brass body with handle for the handicapped, vandal resistant 2.0 [0.5] gpm aerator, [temperature limit stop], with grid strainer waste.  Symmons "S-60-G-H" metering faucet, [ Delta 516WF HGM HDF, Grohe 33.024 w/07.542, Moen 8430 or Symmons S20-2G-FR-W ].

2.	Faucet:  Chrome plated brass body with handle for the handicapped, vandal resistant 2.0 [0.5] gpm aerator, [temperature limit stop], with pop-up waste. Symmons "S-60-P-H" metering faucet, [ Delta 515WF HGM HDF, Grohe 33.816 w/07.542, Moen 8420 or Symmons S20-2-FR-W ].

2.	Faucet:  Electronic chrome plated brass body, deck mounted, tempered water faucet with built-in sensor complete with solenoid valve, transformer, [mechanical mixing valve,] and [ grid strainer outlet / pop-up waste ].  Sloan Optima ETF-60, Delany SF1580 or Bradley Model 900.

3.	Wall Hung, 20" x 18" Size "LV-":  Provide with concealed arm hangers and wall backing plate (J.R. Smith, Josam, Wade, Watts, or Zurn).  American Standard 0355.012, Kohler K-2005, or Eljer 051-2104.

4.	Counter Mounted, Self-rimming, 19" Diameter Round "LV-":  American Standard 0491.019, Kohler K-2202, or Eljer 051-0174.

5.	Counter Mounted, Self-rimming, Oval "LV-":  American Standard 0476.028, Kohler K-2196, or Eljer 051-3514.

F.	Service Sump (Mop Basin)" ":

1.	Faucet exposed, brass body, rough plated, long spout, top brace, hose end spout with bucket hook, vacuum breaker and integral stops in shanks.  Chicago 897, T & S  B-0665-BSTP, or equal Zurn, Delta Commercial, mounted 24" above rim.  Install with 18 gauge type 302, No. 4 finish stainless steel splash on the two walls.

2.	Molded stone 24" x 36" x 10" deep with vinyl bumper guard and 3" brass body strainer outlet.  Fiat, Mustee, Swan or approved substitute.

2.	Enameled CI 28" x 28" service sump with vinyl rim guard and 3" strainer outlet.  American Standard 7740.020, Kohler K6710, Eljer 242-0050.

G.	Service Sink, " ":

1.	24" by 20" acid-resisting enameled cast iron and with stainless steel rim guard.  American Standard 7695.018, Kohler K-6716, or Eljer 242-0155.

2.	Cast iron, porcelain enamel inside, painted outside.  Three inch "P" trap to wall with cleanout plug and chrome plated strainer.  Stainless steel "U" type rim guard bolted to rim.  Provide wall hanger.

3.	Faucet exposed, brass body, rough plated, hose end spout with bucket hook, vacuum breaker, adjustable wall brace and integral stops in shanks, Chicago 897, T & S B-0665-BSTP, or equal Zurn, Delta Commercial.

## PART 3 – EXECUTION

3.1	PIPING

A.	Install in accordance with Section 22 10 00.

B.	Install secondary pipe supports at rough-ins for all plumbing fixtures.

3.2	FIXTURE INSTALLATION AND CONNECTION

A.	All exposed fixture hardware and piping shall be plated with polished chrome unless otherwise directed in these specifications.

B.	All fixtures in contact with finished walls and floors shall be caulked with waterproof, white, non-hardening sealant which will not crack, shrink or change color with age.

C.	All fixtures and component parts shall conform to governing codes.

D.	All fixtures shall be securely mounted level and plumb or as recommended by the manufacturer.  Mount fixtures intended to be accessible to the handicapped at the dimensions required by code.

3.3	startup

A.	Adjust flush valves, pressure reducing valves, mixing valves, water heater thermostats, hot water circulating system balancing valves, and similar equipment.

B.	Remove construction protection, tags and labels and thoroughly clean all plumbing equipment and trim. Scour all fixtures just prior to building acceptance.

END OF SECTION