# SECTION 23 01 00 – HVAC DESIGN REQUIREMENTS

## pART 1 - GENERAL

1.1	DESCRIPTION

A.	Provide detailed HVAC design and construction documents as indicated in these specifications.

1.2	QUALITY ASSURANCE

A.	All systems designs shall conform to all applicable local and state codes and all federal, state and other applicable laws and regulations.

B.	Whenever the requirements of the Specifications exceed those of the applicable code or standard, the requirements of the Specifications shall govern.

C.	Codes and Standards:  Comply with the provisions of the current edition of the following referenced codes, standards and specifications:

1.	American National Standards Institute (ANSI)

2.	Oregon Plumbing Specialty Code (OPSC)

3.	Oregon Mechanical Specialty Code (OMSC)

4.	Oregon Structural Specialty Code (OSSC)

5.	Oregon Energy Efficiency Specialty Code (OEESC)

6.	Oregon Uniform Fire Code (UFC)

7.	National Fire Codes (NFC) by National Fire Protection  Association (NFPA)

8.	All local amendments of the above codes.

9.	All other Codes and Standards referenced throughout these specifications.

D.	All electrical products specified shall in all cases be listed and labeled as an assembly by an approved nationally recognized safety testing organization.

E.	The contractor shall submit the drawings for plan review by the Authority having jurisdiction, pay any and all plan review fees, and respond to review comments and revise the drawings as required.

1.3	COORDINATION

A.	The HVAC contractor shall coordinate all aspects of the design and installation of the various HVAC systems included in these Specifications including but not limited to connections to utilities, scheduling, space allocation, interfacing of systems, submission of drawings and equipment submittals, and the successful operation of the completed systems.

B.	The HVAC contractor shall furnish the electrical contractor with the electrical power requirements of all mechanical equipment in a timely manner.

## PART 2 - DESIGN

2.1	DESIGN CRITERIA

A.	Scope:  Provide complete designs for the following mechanical systems:

1.	Complete mechanical system including heating, ventilation, and cooling of all areas utilizing packaged gas heating-electric cooling rooftop units, ductwork systems, exhaust systems, control system, and gas piping system.

B.	Heating, Ventilating, and Cooling System:

1.	Air Handling and Distribution:

a.	The following temperatures shall be the basis of design:

1)		Heating season:	70 deg. F DB inside

10 deg. F DB outdoors

2)	Cooling season:     75 deg. F inside

95 deg. F outdoors

b.	Zoning:  The building shall be zoned to allow accurate temperature control in areas that experience different heating and cooling loads.  Zoning is accomplished through the use of multiple heating and cooling units and independent duct systems.  Provide a minimum of 6 zones.

c.	Duct Design:  The duct system shall be designed to deliver the required air volumes to each space.  The maximum allowable duct pressure loss is 0.10” WG per 100 ft.  The maximum allowable velocity is 1200 ft/min.

d.	Provide supply and return air to each space except return air is not required where exhaust fans are provided.

e.	Provide exhaust for each toilet room at the rate of 10 air changes per hour.

f.	Air Diffusion:  Select air outlets based on a supply air temperature difference of 20 deg. F.  Air velocity within the occupied zone (6” to 6’ above floor) shall not exceed 50 ft/min.  The maximum temperature gradient from floor to 6’ shall not exceed 5º F between any two points in the room more than 2’ from exterior walls.

2.	Gas Piping: Design gas piping in accordance with the Code and to supply gas to all appliances simultaneously.  Include demand of building heating equipment, water heating equipment, and cooking appliances.  Contractor has the option of using a low pressure or 2 psi system.

C.	Acoustic Design:  The design shall include consideration of the acoustic characteristics of the equipment and systems.  The mechanical systems shall not produce noise levels in indicated spaces exceeding the following limits:

Space				NC Limit

Multi-use/Gym		30

Classrooms			35

Offices			35

Corridor/Foyer		35

Storage/Mechanical	40

Other				35

D.	Vibration:  The mechanical systems shall not generate noticeable vibration in any occupied space.  Provide vibration isolation equipment as required.

E.	Seismic Restraint:  The mechanical contractor is responsible for the design of seismic restraint systems for all portions of the mechanical systems and equipment in accordance with the requirements of the Code.

## PART 3 - CONSTRUCTION DOCUMENTS

3.1	CRITERIA

A.	Develop construction documents for the  Heating, Ventilating, Air Conditioning, Exhaust, and related mechanical systems.  The quality of the drawings shall be similar to those produced by the Architect and shall be sufficiently detailed to graphically represent the appearance of the installed mechanical systems.  Submit the drawings to the Architect for review.

B.	Installation Drawings:  Prepare complete installation drawings for approval prior to commencement of work. Do not begin installation of any portion of the work until approved drawings have been returned from the Architect.  Installation drawings shall be the same size, with overall floor plans at the same scale, as the architectural drawings, and shall include the following information:

1.	All HVAC piping sizes and pipe routing.

2.	All mechanical equipment located and identified.

3.	All ductwork sizes shown and routing through the structure indicated.  Provide enlarged floor plans of congested areas such as mechanical rooms and provide building sections indicating coordination of the mechanical systems with the building structure.

4.	Gas piping schematic including appliance demand, pipe length, delivery pressure, total building load, and code table used to size piping.

5.	Schedule of mechanical equipment including manufacturer’s name and model number, and equipment characteristics and capacities.

6.	Control systems including field wiring diagrams.

7.	Required airflow at all air inlets and outlets.

8.	Required ventilation airflow for each space with method of calculation.

9.	Legends identifying symbols used on the drawings.

10.	Submit heating and cooling load calculations used to establish equipment capacities and airflow rates (submit on separate 8-1/2” by 11” sheets).

11.	Energy code compliance forms (may be indicated on Drawings or on separate 8-1/2” by 11” sheets).

C.	Installation drawings shall be prepared by or under the supervision of a professional engineer or certified engineering technician registered in the state where the work is to be performed.  The Engineer or technician shall have been trained and presently be specializing and practicing in the field of mechanical system design.  The Engineer or technician shall stamp and sign all submitted drawings.  Drawings shall include a title block identifying the contractor, project name and address, drawing name, number, and submittal date and record of revisions to original drawings.

D.	Contractor shall submit equipment catalog data and shop drawings as specified in Division 23 specification sections for review by the Engineer.  HVAC submittals shall include all air handling equipment, air filters, air inlets and outlets, fire and smoke dampers, insulation, and controls.

END OF SECTION