# SECTION 23 05 90 - TESTING, ADJUSTING AND BALANCING

## pART 1 - GENERAL

1.1	DESCRIPTION

A.	Work Included:  After completion of the work of installation, test and regulate all components of the new heating, air conditioning and ventilating systems to verify air volumes and heating-cooling flow rates indicated on the Drawings.

B.	Related Work:  The requirements of Section 23 05 00, Common HVAC Materials and Methods, also apply to this section.

C.	Balancing Organization:

1.	Balancing of the Heating and Air Conditioning Systems:  Performed by a firm providing this service established in the State of [Oregon].

2.	Balancing Organization:  Approval by [Architect].  Air Balancing Specialties, Air Introduction & Regulation, Northwest Engineering Services, Neudorfer Engineers, Pacific Coast Air Balancing, or approved.

3.	Provide all necessary personnel, equipment, and services.

1.2	QUALITY ASSURANCE

A.	Balancing of the Heating and Air Conditioning Systems:  Agency shall be a current member of NEBB or AABC specializing in the adjusting and balancing of systems specified with a minimum of 10 years documented experience.

B.	Testing, adjusting, and balancing shall be performed under direct field supervision of a Certified NEBB Supervisor or a Certified AABC Supervisor.

1.3	SUBMITTALS

A.	Balancing Data:  Include the following minimum information in the Operation and Maintenance Data, as specified in Section 23 05 00.

1.	Names or initials of personnel performing the balancing.

2.	Dates balancing was performed.

3.	List of balancing instruments utilized.

4.	Weather conditions at the time of the test.

5.	Mechanical system descriptions.

6.	All motor rated voltages, amps, starter and overload protective device sizes.

7.	All motor operating data.

8.	Fan cfm, rpm, operating static pressures, driven and motor sheave data, and all drive changes necessitated to obtain design capacities.  List actual minimum outside air volumes measured for each system.

9.	Type and size of filters installed in each filter bank.

10.	All supply, return and exhaust air outlet cfm readings.

11.	Terminal unit cfm and static pressures on full [cooling] and [heating], and final settings.

12.	Coil steam pressure and entering and leaving air temperatures.

13.	Coil chilled water supply and return temperatures and entering and leaving air temperatures.

14.	Coil heating water entering and leaving temperatures and entering and leaving air temperatures.

15.	Condensing water supply and return temperatures.

16.	Pump gpm, rpm, pressure, horsepower and service.

17.	Electric heating elements voltage and amperage for each stage of heat.

18.	Power Exhaust fan settings – cfm or % of supply airflow and power exhaust fan start point (% of outside air damper position).

1.4	DETAILED REQUIREMENTS

A.	Adjusting and Balancing:

1.	Prior to beginning the balancing work, obtain from the Architect the latest version of the mechanical drawings including addenda, revisions, change orders, etc.

2.	Adjust and balance all portions of the mechanical systems to produce indicated results within limits of minus 5 or plus 10 percent or as subsequently directed by the [Architect].

3.	Balancing data may be spot checked with instruments similar to that used by the balancing firm.

4.	If, in the judgment of the [Architect], the discrepancies warrant additional adjustment, readjust and rebalance the systems at no additional project cost.

5.	Adjust diffuser throws as shown on the drawings (shown as directional arrows)

END OF SECTION