# SECTION 26 0521

# METAL-CLAD CABLE

## PART 1 GENERAL

1.01	WORK INCLUDED

A.	Metal-clad cable may be used for all concealed branch circuit wiring where permitted by local codes and NEC Article 330 except where otherwise noted.  Metal-clad cable shall be used only for concealed interior wiring and shall be exposed only in unfinished crawl spaces or attics.

1.02	SUBMITTAL AND RECORD DOCUMENTATION

A.	None required.

## PART 2 PRODUCTS

2.01	MATERIALS

A.	Cable shall be steel jacketed, interlock armor with internal, fully insulated, green grounding conductor and multi-conductor, thermoplastic, insulated, color-coded solid or stranded copper conductors No. 12 through No. 6 AWG, 600 volt.

B.	Connections, terminations, and fasteners shall be malleable iron or steel saddle-type with anti-short insulated bushings.

2.02	APPROVED MANUFACTURERS

A.	MC Cable:  AFC/A Nortek Company, type MC, HCF-90.

B.	Fittings:  T&B 3110 series connectors with 390 series bushings.

C.	Tools:  Cable manufacturer approved type with controlled depth rotary cutter.

## PART 3 EXECUTION

3.01	INSTALLATION

A.	Support horizontal and vertical cable 6 feet on center (maximum) and within 6" of boxes with approved cable clamps.

B.	Support cable above accessible ceilings; do not rest cables on ceiling tiles.  Attach cables with metal clips or plastic cable ties to support wires from structure on 6-foot centers maximum.

C.	Cable shall be cut with manufacturer-approved devices.

D.	Splice conductors only in accessible junction boxes.

E.	Cable shall not be supported from or come into contact with mechanical ducts, water, sprinkler or gas piping; maintain 6-inch separation minimum.

F.	Provide junction box at all cable penetrations of wall, ceiling, or floor surfaces for equipment connections; cable shall not be run directly through finished surfaces.

G.	Voltage Drop:  Conductors over 75 feet for 120-volt, and over 200 feet for 277-volt for branch or individual circuit home runs from equipment connection; receptacle or lighting fixture shall be No. 10 AWG minimum.

H.	Provide junction box at transition from concealed to exposed wiring.  Exposed wiring shall conform to Section 16110 - Raceways.

I.	Where cable penetrates fire-rated walls or floors, provide mechanical fire stop fitting with UL-listed fire rating equal to wall or floor rating.

J.	Provide junction box at transition from interior to exterior wiring.  Exterior wiring shall conform to Section 16110 - Raceways.

K.	Provide EMT risers from panelboards up into accessible ceiling/attic space and down into accessible crawl/ceiling space, terminating in accessible gutter(s) or junction box(es).

END OF SECTION