## Summary of Measurements
ASU-14 (M1) |  |  | ASU-14 (M1)
Unit Total | 24648 | cfm | Supply Airflow |  | Static Pres. (inwc)
Unit Discharge Pressure | 1.86 | inwc | Traverse Location | Airflow (cfm)
Unit Suction Pressure | -0.23 | inwc | 1st Floor | 5255 | 1.83
Supply Fan Suction Pressure | -1.4 | inwc | 2nd Floor | 10363 | 1.15
External Static Pressure | 2.09 | inwc | 3rd Floor | 7759 | 1.64
Supply Fan Total Static Pressure | 3.26 | inwc | Sum of Floors | 23377
OAT | 60 | °F | Measured Total | 24648 | -0.23
Hist. Design Full Capacity | 34000 | cfm
Hist. Design TSP | 4 | inwc | Return Airflow
Duct Static Pressure/Setpoint | 1.75/1.75 | inwc | Traverse Location | Airflow (cfm)
Fan Speed | 85-95 | % | 1st Floor (1) | 3503
|  |  | 1st Floor (2) | 1887
Supply Fans - Two 30HP |  |  | 2nd Floor (1) | 5172
Rated Voltage | 460 | Volts | 2nd Floor (2) | 1525
Measured Voltage | 480 | Volts | 3rd Floor (1) | 5723
Rated Full Load Amperage | 70/2Motors | Amps | 3rd Floor (2) | 6007
Measured Amperage | 35/2Motors | Amps | Sum of Floors | 23817
|  |  | Measured Total | 24648 | -0.23
Exhaust Fan
Total Airflow | 5745 | cfm
Static Pressure | -0.72 | inwc
Traverse Total | 5420 | cfm
Flowhood Total (RR on L3) | 345 | cfm
There are two different motors installed one is a Leeson and the other a Magnatek. The amperage is 22A to one motor and 14A to the other.
ASU-15 (M2) |  |  | ASU-15 (M2)
Unit Total | 18760 | cfm | Supply Airflow |  | Static Pres. (inwc)
Unit Discharge Pressure | 2.17 | inwc | Traverse Location | Airflow (cfm)
Unit Suction Pressure | -0.44 | inwc | 1st Floor | 6533 | 1.8
Supply Fan Suction Pressure | -1.3 | inwc | 2nd Floor | 6244 | 1.7
External Static Pressure | 2.61 | inwc | 3rd Floor | 6972 | 1.66
Supply Fan Total Static Pressure | 3.47 | inwc | Sum of Floors | 19749
OAT | 60 | °F | Measured Total | 18760 | -0.44
Duct Static Pressure/Setpoint | 1.75/1.75 | inwc
Fan Speed | 85-95 | %
Return Airflow
Supply Fan - One 40HP |  |  | Traverse Location | Airflow (cfm)
Rated Voltage | 460 | Volts | 1st Floor (1) | 1323
Measured Voltage | 480 | Volts | 1st Floor (2) | 2195
Rated Full Load Amperage | 47 | Amps | 2nd Floor (1) | 1890
Measured Amperage | 30 | Amps | 2nd Floor (2) | 2801
|  |  | 3rd Floor (1) | 2338
Exhaust Fan |  |  | 3rd Floor (2) | 636
Total Airflow | 2912 | cfm | 3rd Floor (3) | 4029
Static Pressure | -0.4 | inwc | Sum of Floors | 15212
|  |  | Measured Total | 18760 | -0.44
All measurements were taken with the unit fully recirculating. The MAD position was at 1.5Volts. The OSA damper was closed and the RA damper is at about 85% open. No measurable airflow was entering through OSA inlet.
There is around 19% unaccounted for airflow entering the ASU-15 (M2) system. This is in part due to the leakage in the architectural RA shaft and the duct connection.
Building pressure was measured at -0.02inwc. There are doors open to MOB(MP)2 that effect pressurization.
ASU-14 SA VFD is ABB located in electrical room across from level 3 elevators. It was recorded operating at 50.4Hz at 83.9% indicating that 100% speed is 60Hz.
There is roughly 8x8 hole cut in the side of the RA shaft at the first floor that can be seen through the RA opening.
The above data is a combination of new field readings taken 9/21/17 and verified readings from previous survey on 9/14/17.

## ASU-14 (M1) trends
|  | Duct Static Pressure | Exhaust Damper Position | Economizer Mode | Mixed Air Damper Position | Supply Fan Speed | Exhaust Fan Speed
Date | Time | A14DSP IN H2O | A14EAD VOLTS | A14ECM | A14MAD VOLTS | A14VFS PERCNT | A14EVS % | 50.4Hz | 24648 | 60Hz (100) | 0.84 | 29342.8571
2017-06-21 | 15:15 | 1.6438 | 0.054218 | 0 | 1.5 | 90.5894 | 0 | 26581.5165
2017-06-21 | 15:30 | 2.019 | 0 | 0 | 1.5 | 86.607 | 0 | 25412.9712
2017-06-21 | 15:45 | 1.7249 | 0 | 0 | 1.5 | 85.1303 | 0 | 24979.6629
2017-06-21 | 16:00 | 1.6095 | 0 | 0 | 1.5 | 87.8028 | 0 | 25763.8399
2017-06-21 | 16:15 | 1.6758 | 0 | 0 | 1.5 | 90.0396 | 0 | 26420.1903
2017-06-21 | 16:30 | 2.0198 | 0 | 0 | 1.5 | 87.8819 | 0 | 25787.0639
2017-06-21 | 16:45 | 1.8622 | 0 | 0 | 1.5 | 84.3504 | 0 | 24750.8159
2017-06-21 | 17:00 | 1.6781 | 0 | 0 | 1.5 | 84.2916 | 0 | 24733.5512
2017-06-21 | 17:15 | 1.6844 | 0 | 0 | 1.5 | 83.967 | 0 | 24638.3245
2017-06-21 | 17:30 | 1.8131 | 0 | 0 | 1.5 | 83.192 | 0 | 24410.9212
2017-06-21 | 17:45 | 1.7655 | 0 | 0 | 1.5 | 82.3524 | 0 | 24164.543
2017-06-21 | 18:00 | 1.7273 | 0 | 0 | 1.5 | 82.0419 | 0 | 24073.4466
2017-06-21 | 18:15 | 1.7499 | 0 | 0 | 1.5 | 81.6466 | 0 | 23957.4537
2017-06-21 | 18:30 | 1.7764 | 0 | 0 | 1.5 | 81.0773 | 0 | 23790.3943
2017-06-21 | 18:45 | 1.7499 | 0 | 0 | 1.5 | 80.6552 | 0 | 23666.5257
2017-06-21 | 19:00 | 1.8084 | 0 | 0 | 1.5 | 80.2322 | 0 | 23542.4269
2017-06-21 | 19:15 | 1.817 | 0.36005 | 0 | 1.5 | 79.5285 | 0 | 23335.9218
2017-06-21 | 19:30 | 1.7678 | 0 | 0 | 1.5 | 79.0934 | 0 | 23208.2698
2017-06-21 | 19:45 | 1.7507 | 0 | 0 | 1.5 | 78.5243 | 0 | 23041.2664
2017-06-21 | 20:00 | 1.8014 | 0 | 0 | 1.5 | 78.3248 | 0 | 22982.7224
2017-06-21 | 20:15 | 1.739 | 0 | 0 | 1.5 | 77.5489 | 0 | 22755.0509
2017-06-21 | 20:30 | 1.7803 | 0 | 0 | 1.5 | 77.2285 | 0 | 22661.0373
2017-06-21 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 76.9598 | 0 | 22582.2177
2017-06-21 | 20:57 |  |  | 1 |  |  |  | 0
2017-06-21 | 21:00 | 1.7842 | 0 | 0 | 10 | 76.4461 | 0 | 22431.4761
2017-06-21 | 21:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 21:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 21:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 22:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 22:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 22:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 22:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 23:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 23:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 23:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 23:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 0:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 0:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 0:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 1:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 2:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 3:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 3:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 3:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 5:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 5:00 |  |  | 1 |  |  |  | 0
2017-06-22 | 5:15 | 2.3216 | 7.7389 | 1 | 10 | 87.9129 | 81.504 | 25796.1643
2017-06-22 | 5:30 | 1.8989 | 5.8536 | 1 | 10 | 81.4162 | 0 | 23889.8366
2017-06-22 | 5:45 | 1.8045 | 5.2002 | 1 | 10 | 78.8022 | 0 | 23122.8038
2017-06-22 | 6:00 | 1.8255 | 4.728 | 1 | 10 | 77.4192 | 0 | 22717.0179
2017-06-22 | 6:15 | 1.7772 | 5.723 | 1 | 10 | 76.7334 | 0 | 22515.7781
2017-06-22 | 6:30 | 1.728 | 6.2434 | 1 | 10 | 76.6438 | 0 | 22489.4737
2017-06-22 | 6:45 | 1.7631 | 5.5552 | 1 | 10 | 76.1974 | 0 | 22358.5019
2017-06-22 | 7:00 | 1.7397 | 5.0124 | 1 | 10 | 76.0536 | 0 | 22316.296
2017-06-22 | 7:15 | 1.7249 | 5.5766 | 1 | 10 | 76.3408 | 0 | 22400.5666
2017-06-22 | 7:30 | 1.7546 | 6.2173 | 1 | 10 | 76.0888 | 0 | 22326.6408
2017-06-22 | 7:45 | 1.7951 | 6.8679 | 1 | 10 | 76.1181 | 0 | 22335.233
2017-06-22 | 8:00 | 1.8053 | 5.5528 | 1 | 10 | 76.1014 | 0 | 22330.3257
2017-06-22 | 8:15 | 1.7694 | 5.9225 | 1 | 10 | 76.5927 | 0 | 22474.488
2017-06-22 | 8:30 | 1.7764 | 5.995 | 1 | 10 | 76.9284 | 0 | 22572.9943
2017-06-22 | 8:45 | 1.7015 | 7.1363 | 1 | 10 | 77.2997 | 0 | 22681.9535
2017-06-22 | 9:00 | 1.7764 | 6.6448 | 1 | 10 | 77.6702 | 0 | 22790.6526
2017-06-22 | 9:15 | 1.6828 | 6.1596 | 1 | 10 | 78.3724 | 0 | 22996.6987
2017-06-22 | 9:30 | 1.7109 | 6.7465 | 1 | 10 | 79.4104 | 0 | 23301.2802
2017-06-22 | 9:45 | 1.6461 | 6.6924 | 1 | 10 | 80.703 | 0 | 23680.5625
2017-06-22 | 10:00 | 1.6547 | 7.3113 | 1 | 10 | 81.8018 | 0 | 24002.9841
2017-06-22 | 10:15 | 1.8248 | 7.5321 | 1 | 10 | 81.9408 | 0 | 24043.7775
2017-06-22 | 10:17 |  |  | 0 |  |  |  | 0
2017-06-22 | 10:30 | 1.7967 | 2.3766 | 0 | 1.5 | 81.2062 | 0 | 23828.226
2017-06-22 | 10:45 | 1.7709 | 0 | 0 | 1.5 | 80.8829 | 0 | 23733.3394
2017-06-22 | 11:00 | 1.739 | 0 | 0 | 1.5 | 81.0666 | 0 | 23787.2467
2017-06-22 | 11:15 | 1.7608 | 0 | 0 | 1.5 | 81.4059 | 0 | 23886.8257
2017-06-22 | 11:30 | 1.7787 | 0 | 0 | 1.5 | 82.4842 | 0 | 24203.2163
2017-06-22 | 11:45 | 1.7741 | 0 | 0 | 1.5 | 82.5339 | 0 | 24217.8102
2017-06-22 | 12:00 | 1.6953 | 0 | 0 | 1.5 | 83.2062 | 0 | 24415.0717
2017-06-22 | 12:15 | 1.7616 | 0 | 0 | 1.5 | 83.3767 | 0 | 24465.1198
2017-06-22 | 12:30 | 1.7468 | 0 | 0 | 1.5 | 83.6767 | 0 | 24553.1269
2017-06-22 | 12:45 | 1.7241 | 0 | 0 | 1.5 | 84.3443 | 0 | 24749.0295
2017-06-22 | 13:00 | 1.6415 | 0 | 0 | 1.5 | 85.296 | 0 | 25028.2805
2017-06-22 | 13:15 | 1.689 | 0 | 0 | 1.5 | 85.9851 | 0 | 25230.4962
2017-06-22 | 13:30 | 1.6984 | 0 | 0 | 1.5 | 85.7064 | 0 | 25148.6948
2017-06-22 | 13:45 | 1.7312 | 0 | 0 | 1.5 | 86.2206 | 0 | 25299.5775
2017-06-22 | 14:00 | 1.884 | 0 | 0 | 1.5 | 86.8758 | 0 | 25491.8533
2017-06-22 | 14:15 | 1.7226 | 0 | 0 | 1.5 | 84.2345 | 0 | 24716.7993
2017-06-22 | 14:30 | 1.7132 | 0 | 0 | 1.5 | 85.4699 | 0 | 25079.3024
2017-06-22 | 14:45 | 1.8825 | 0 | 0 | 1.5 | 87.0707 | 0 | 25549.0226
2017-06-22 | 15:00 | 1.6914 | 0 | 0 | 1.5 | 86.1201 | 0 | 25270.0985
2017-06-22 | 15:15 | 1.8903 | 0 | 0 | 1.5 | 87.5597 | 0 | 25692.5133
2017-06-22 | 15:30 | 1.714 | 0 | 0 | 1.5 | 86.1666 | 0 | 25283.7344
2017-06-22 | 15:45 | 1.8817 | 0 | 0 | 1.5 | 86.3919 | 0 | 25349.838
2017-06-22 | 16:00 | 1.7296 | 0 | 0 | 1.5 | 84.691 | 0 | 24850.7665
2017-06-22 | 16:15 | 1.8599 | 0 | 0 | 1.5 | 84.9954 | 0 | 24940.0653
2017-06-22 | 16:30 | 1.7912 | 0 | 0 | 1.5 | 83.2251 | 0 | 24420.6348
2017-06-22 | 16:45 | 1.6906 | 0 | 0 | 1.5 | 84.1747 | 0 | 24699.2502
2017-06-22 | 17:00 | 1.9113 | 0 | 0 | 1.5 | 83.2747 | 0 | 24435.1639
2017-06-22 | 17:15 | 1.7366 | 0 | 0 | 1.5 | 82.223 | 0 | 24126.5707
2017-06-22 | 17:30 | 1.7826 | 0 | 0 | 1.5 | 81.9811 | 0 | 24055.6067
2017-06-22 | 17:45 | 1.7787 | 0 | 0 | 1.5 | 81.7334 | 0 | 23982.921
2017-06-22 | 18:00 | 1.7592 | 0 | 0 | 1.5 | 81.4064 | 0 | 23886.9689
2017-06-22 | 18:15 | 1.8123 | 0 | 0 | 1.5 | 81.2298 | 0 | 23835.148
2017-06-22 | 18:30 | 1.7772 | 0 | 0 | 1.5 | 81.1192 | 0 | 23802.6936
2017-06-22 | 18:45 | 1.7702 | 0 | 0 | 1.5 | 80.817 | 0 | 23714.0283
2017-06-22 | 19:00 | 1.7491 | 0 | 0 | 1.5 | 80.6077 | 0 | 23652.6146
2017-06-22 | 19:15 | 1.7795 | 0 | 0 | 1.5 | 80.1095 | 0 | 23506.4065
2017-06-22 | 19:30 | 1.8029 | 0 | 0 | 1.5 | 79.4847 | 0 | 23323.0694
2017-06-22 | 19:45 | 1.7647 | 0 | 0 | 1.5 | 78.8559 | 0 | 23138.5638
2017-06-22 | 20:00 | 1.7756 | 0 | 0 | 1.5 | 78.2178 | 0 | 22951.3496
2017-06-22 | 20:15 | 1.7429 | 0 | 0 | 1.5 | 77.7099 | 0 | 22802.2938
2017-06-22 | 20:30 | 1.7928 | 0 | 0 | 1.5 | 77.2077 | 0 | 22654.948
2017-06-22 | 20:45 | 1.7858 | 0 | 0 | 1.5 | 76.5816 | 0 | 22471.2239
2017-06-22 | 21:00 | 1.7179 | 0 | 0 | 1.5 | 77.1571 | 0 | 22640.0856
2017-06-22 | 21:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 21:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 21:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 22:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 22:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 22:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 22:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 23:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 23:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 23:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-22 | 23:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 0:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 0:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 0:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 0:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 1:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 1:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 1:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 1:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 5:00 | 0.02998 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-23 | 5:15 | 2.267 | 10 | 1 | 10 | 92.8054 | 100 | 27231.7642
2017-06-23 | 5:30 | 2.0049 | 8.4998 | 1 | 10 | 84.4886 | 85.9586 | 24791.383
2017-06-23 | 5:45 | 1.7975 | 7.2665 | 1 | 10 | 81.6519 | 73.7478 | 23958.9895
2017-06-23 | 6:00 | 1.7413 | 7.0931 | 1 | 10 | 80.6097 | 71.5396 | 23653.1832
2017-06-23 | 6:15 | 1.7694 | 7.6227 | 1 | 10 | 79.4414 | 77.0649 | 23310.3762
2017-06-23 | 6:30 | 1.7858 | 7.0048 | 1 | 10 | 78.3181 | 71.4328 | 22980.7547
2017-06-23 | 6:45 | 1.831 | 6.4078 | 1 | 10 | 77.3516 | 65.9246 | 22697.1607
2017-06-23 | 6:46 |  |  | 0 |  |  |  | 0
2017-06-23 | 7:00 |  |  | 1 |  |  |  | 0
2017-06-23 | 7:00 | 1.6695 | 0 | 1 | 10 | 78.0205 | 0 | 22893.4371
2017-06-23 | 7:15 | 1.8006 | 4.385 | 1 | 10 | 77.4733 | 0 | 22732.8654
2017-06-23 | 7:30 | 1.7881 | 4.7827 | 1 | 10 | 76.9648 | 0 | 22583.6707
2017-06-23 | 7:45 | 1.8053 | 5.2299 | 1 | 10 | 76.9132 | 0 | 22568.5237
2017-06-23 | 8:00 | 1.6742 | 4.2833 | 1 | 10 | 77.3549 | 0 | 22698.1302
2017-06-23 | 8:15 | 1.7124 | 4.8205 | 1 | 10 | 78.329 | 0 | 22983.956
2017-06-23 | 8:30 | 1.7725 | 5.5636 | 1 | 10 | 78.9571 | 0 | 23168.2667
2017-06-23 | 8:33 |  |  | 0 |  |  |  | 0
2017-06-23 | 8:45 | 1.7304 | 1.4016 | 0 | 1.5 | 80.2824 | 0 | 23557.1438
2017-06-23 | 9:00 | 1.7 | 0 | 0 | 1.5 | 80.9323 | 0 | 23747.8594
2017-06-23 | 9:15 | 1.7951 | 0 | 0 | 1.5 | 80.8525 | 0 | 23724.4315
2017-06-23 | 9:30 | 1.739 | 0 | 0 | 1.5 | 80.8338 | 0 | 23718.9379
2017-06-23 | 9:45 | 1.7296 | 0 | 0 | 1.5 | 81.5093 | 0 | 23917.144
2017-06-23 | 10:00 | 1.6758 | 0 | 0 | 1.5 | 82.3121 | 0 | 24152.7207
2017-06-23 | 10:15 | 1.6688 | 0 | 0 | 1.5 | 83.7435 | 0 | 24572.7221
2017-06-23 | 10:30 | 1.7514 | 0 | 0 | 1.5 | 84.4342 | 0 | 24775.419
2017-06-23 | 10:45 | 1.7631 | 0 | 0 | 1.5 | 85.0932 | 0 | 24968.7808
2017-06-23 | 11:00 | 1.721 | 0 | 0 | 1.5 | 85.9701 | 0 | 25226.0836
2017-06-23 | 11:15 | 1.6555 | 0 | 0 | 1.5 | 87.6756 | 0 | 25726.5278
2017-06-23 | 11:30 | 1.6851 | 0 | 0 | 1.5 | 88.7421 | 0 | 26039.4776
2017-06-23 | 11:45 | 1.9722 | 0 | 0 | 1.5 | 86.2176 | 0 | 25298.709
2017-06-23 | 12:00 | 1.6711 | 0 | 0 | 1.5 | 85.7248 | 0 | 25154.1033
2017-06-23 | 12:15 | 1.6773 | 0 | 0 | 1.5 | 86.8999 | 0 | 25498.9097
2017-06-23 | 12:30 | 1.9776 | 0 | 0 | 1.5 | 85.4034 | 0 | 25059.8079
2017-06-23 | 12:45 | 1.7093 | 0 | 0 | 1.5 | 83.6946 | 0 | 24558.3945
2017-06-23 | 13:00 | 1.6344 | 0 | 0 | 1.5 | 85.8441 | 0 | 25189.1096
2017-06-23 | 13:15 | 1.9644 | 0 | 0 | 1.5 | 85.658 | 0 | 25134.5172
2017-06-23 | 13:30 | 1.7273 | 0 | 0 | 1.5 | 84.5508 | 0 | 24809.6061
2017-06-23 | 13:45 | 1.6937 | 0 | 0 | 1.5 | 86.4807 | 0 | 25375.9165
2017-06-23 | 14:00 | 1.7881 | 0 | 0 | 1.5 | 84.461 | 0 | 24783.2635
2017-06-23 | 14:15 | 1.5978 | 0 | 0 | 1.5 | 87.6869 | 0 | 25729.8544
2017-06-23 | 14:30 | 1.8981 | 0 | 0 | 1.5 | 85.8175 | 0 | 25181.3102
2017-06-23 | 14:45 | 1.6243 | 0 | 0 | 1.5 | 86.9927 | 0 | 25526.1454
2017-06-23 | 15:00 | 1.8708 | 0 | 0 | 1.5 | 84.9176 | 0 | 24917.2641
2017-06-23 | 15:15 | 1.6695 | 0 | 0 | 1.5 | 86.1077 | 0 | 25266.4741
2017-06-23 | 15:30 | 1.9004 | 0 | 0 | 1.5 | 83.9108 | 0 | 24621.8276
2017-06-23 | 15:45 | 1.5939 | 0 | 0 | 1.5 | 85.4819 | 0 | 25082.8327
2017-06-23 | 16:00 | 1.8528 | 0 | 0 | 1.5 | 84.3926 | 0 | 24763.2027
2017-06-23 | 16:15 | 1.6017 | 0 | 0 | 1.5 | 85.6234 | 0 | 25124.347
2017-06-23 | 16:30 | 1.8271 | 0 | 0 | 1.5 | 83.9386 | 0 | 24629.9899
2017-06-23 | 16:45 | 1.611 | 0 | 0 | 1.5 | 84.4614 | 0 | 24783.3912
2017-06-23 | 17:00 | 1.9371 | 0 | 0 | 1.5 | 83.7837 | 0 | 24584.5402
2017-06-23 | 17:15 | 1.7327 | 0 | 0 | 1.5 | 82.2367 | 0 | 24130.5889
2017-06-23 | 17:30 | 1.7507 | 0 | 0 | 1.5 | 82.9739 | 0 | 24346.9106
2017-06-23 | 17:45 | 1.7881 | 0 | 0 | 1.5 | 81.3246 | 0 | 23862.9591
2017-06-23 | 18:00 | 1.7179 | 0 | 0 | 1.5 | 81.5801 | 0 | 23937.9325
2017-06-23 | 18:15 | 1.7163 | 0 | 0 | 1.5 | 82.2434 | 0 | 24132.5748
2017-06-23 | 18:30 | 1.845 | 0 | 0 | 1.5 | 81.9891 | 0 | 24057.955
2017-06-23 | 18:45 | 1.7608 | 0 | 0 | 1.5 | 80.5659 | 0 | 23640.3267
2017-06-23 | 19:00 | 1.7093 | 0 | 0 | 1.5 | 81.0672 | 0 | 23787.4259
2017-06-23 | 19:15 | 1.7148 | 0 | 0 | 1.5 | 81.4234 | 0 | 23891.9634
2017-06-23 | 19:30 | 1.728 | 0 | 0 | 1.5 | 81.7728 | 0 | 23994.475
2017-06-23 | 19:45 | 1.7241 | 0 | 0 | 1.5 | 81.6457 | 0 | 23957.194
2017-06-23 | 20:00 | 1.7686 | 0 | 0 | 1.5 | 81.3891 | 0 | 23881.8736
2017-06-23 | 20:15 | 1.7764 | 0 | 0 | 1.5 | 80.9512 | 0 | 23753.3979
2017-06-23 | 20:30 | 1.7982 | 0 | 0 | 1.5 | 80.2026 | 0 | 23533.7206
2017-06-23 | 20:45 | 1.7803 | 0 | 0 | 1.5 | 79.5063 | 0 | 23329.4318
2017-06-23 | 21:00 | 1.7803 | 0 | 0 | 1.5 | 78.8761 | 0 | 23144.5055
2017-06-23 | 21:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 21:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 21:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 22:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 22:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 22:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 22:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 23:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 23:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 23:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 23:45 | 0.02452 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 0:00 | 0.02452 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 0:15 | 0.02452 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 0:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 0:30 | 0.02452 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 0:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 0:45 | 0.02452 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 0:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 1:00 | 0.02374 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 1:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 1:15 | 0.02452 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 1:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 1:30 | 0.02452 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 1:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 1:45 | 0.02374 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 1:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 2:00 | 0.02452 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 2:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 2:15 | 0.02452 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 2:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 2:30 | 0.02374 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 2:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 2:45 | 0.0253 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 2:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 3:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 3:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 3:15 | 0.0253 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 3:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 3:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 3:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 3:45 | 0.0253 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 3:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 4:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 4:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 4:15 | 0.02608 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 4:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 4:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 4:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 4:45 | 0.02608 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 4:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 5:00 | 0.02608 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-06-24 | 5:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 5:01 |  |  | 1 |  |  |  | 0
2017-06-24 | 5:15 | 2.0845 | 9.9964 | 1 |  | 94.6941 | 100 | 27785.9609
2017-06-24 | 5:15 |  |  |  | 10 |  |  | 0
2017-06-24 | 5:30 | 2.0627 | 9.8106 | 1 | 10 | 87.1108 | 98.446 | 25560.8026
2017-06-24 | 5:30 |  |  |  | 10 |  |  | 0
2017-06-24 | 5:45 | 1.8911 | 8.3121 | 1 |  | 82.2996 | 83.943 | 24149.0491
2017-06-24 | 5:45 |  |  |  | 10 |  |  | 0
2017-06-24 | 6:00 | 1.8708 | 7.2729 | 1 | 10 | 79.9752 | 73.6145 | 23466.9967
2017-06-24 | 6:00 |  |  |  | 10 |  |  | 0
2017-06-24 | 6:15 | 1.7748 | 7.4809 | 1 |  | 79.3078 | 75.6142 | 23271.1856
2017-06-24 | 6:15 |  |  |  | 10 |  |  | 0
2017-06-24 | 6:30 | 1.7608 | 7.3079 | 1 | 10 | 78.7855 | 73.7378 | 23117.912
2017-06-24 | 6:30 |  |  |  | 10 |  |  | 0
2017-06-24 | 6:35 |  |  | 0 |  |  |  | 0
2017-06-24 | 6:45 | 1.8076 | 0 | 0 |  | 78.7017 | 0 | 23093.3268
2017-06-24 | 6:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 7:00 | 1.7787 | 0 | 0 | 1.5 | 77.8886 | 0 | 22854.7304
2017-06-24 | 7:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 7:15 | 1.7429 | 0 | 0 |  | 78.0584 | 0 | 22904.5633
2017-06-24 | 7:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 7:30 | 1.7202 | 0 | 0 | 1.5 | 77.3203 | 0 | 22687.9978
2017-06-24 | 7:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 7:45 | 1.7678 | 0 | 0 |  | 76.9789 | 0 | 22587.799
2017-06-24 | 7:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 8:00 | 1.7483 | 0 | 0 | 1.5 | 77.1411 | 0 | 22635.3954
2017-06-24 | 8:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 8:15 | 1.7062 | 0 | 0 |  | 77.0023 | 0 | 22594.6852
2017-06-24 | 8:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 8:30 | 1.7592 | 0 | 0 | 1.5 | 77.1941 | 0 | 22650.9565
2017-06-24 | 8:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 8:45 | 1.7514 | 0 | 0 |  | 77.0687 | 0 | 22614.1682
2017-06-24 | 8:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 9:00 | 1.7569 | 0 | 0 | 1.5 | 76.9735 | 0 | 22586.225
2017-06-24 | 9:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 9:15 | 1.76 | 0 | 0 |  | 77.2364 | 0 | 22663.3656
2017-06-24 | 9:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 9:30 | 1.7452 | 0 | 0 | 1.5 | 77.5668 | 0 | 22760.3138
2017-06-24 | 9:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 9:45 | 1.7413 | 0 | 0 |  | 77.705 | 0 | 22800.8677
2017-06-24 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 10:00 | 1.7429 | 0 | 0 | 1.5 | 77.8114 | 0 | 22832.0838
2017-06-24 | 10:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 10:15 | 1.7358 | 0 | 0 |  | 77.9745 | 0 | 22879.9335
2017-06-24 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 10:30 | 1.7374 | 0 | 0 | 1.5 | 78.1831 | 0 | 22941.1615
2017-06-24 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 10:45 | 1.7436 | 0 | 0 |  | 78.3827 | 0 | 22999.7298
2017-06-24 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 11:00 | 1.7452 | 0 | 0 | 1.5 | 78.5904 | 0 | 23060.6802
2017-06-24 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 11:15 | 1.7273 | 0 | 0 |  | 78.8375 | 0 | 23133.1641
2017-06-24 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 11:30 | 1.7405 | 0 | 0 | 1.5 | 79.2524 | 0 | 23254.9305
2017-06-24 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 11:45 | 1.7382 | 0 | 0 |  | 79.5176 | 0 | 23332.7452
2017-06-24 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 12:00 | 1.76 | 0 | 0 | 1.5 | 79.6659 | 0 | 23376.2583
2017-06-24 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 12:15 | 1.7413 | 0 | 0 |  | 79.86 | 0 | 23433.2013
2017-06-24 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 12:30 | 1.7507 | 0 | 0 | 1.5 | 80.0135 | 0 | 23478.2573
2017-06-24 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 12:45 | 1.7444 | 0 | 0 |  | 80.2665 | 0 | 23552.4762
2017-06-24 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 13:00 | 1.8279 | 0 | 0 | 1.5 | 79.5401 | 0 | 23339.3491
2017-06-24 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 13:15 | 1.7631 | 0 | 0 |  | 78.7278 | 0 | 23100.9853
2017-06-24 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 13:30 | 1.7234 | 0 | 0 | 1.5 | 79.2046 | 0 | 23240.9008
2017-06-24 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 13:45 | 1.7717 | 0 | 0 |  | 79.6058 | 0 | 23358.6197
2017-06-24 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 14:00 | 1.76 | 0 | 0 | 1.5 | 78.75 | 0 | 23107.4865
2017-06-24 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 14:15 | 1.7234 | 0 | 0 |  | 79.1332 | 0 | 23219.9512
2017-06-24 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 14:30 | 1.8053 | 0 | 0 | 1.5 | 79.2247 | 0 | 23246.7817
2017-06-24 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 14:45 | 1.7397 | 0 | 0 |  | 78.8333 | 0 | 23131.9464
2017-06-24 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 15:00 | 1.6953 | 0 | 0 | 1.5 | 79.5291 | 0 | 23336.1231
2017-06-24 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 15:15 | 1.7873 | 0 | 0 |  | 78.6543 | 0 | 23079.4224
2017-06-24 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 15:30 | 1.7265 | 0 | 0 | 1.5 | 78.7728 | 0 | 23114.1846
2017-06-24 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 15:45 | 1.7772 | 0 | 0 |  | 79.1711 | 0 | 23231.0507
2017-06-24 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 16:00 | 1.746 | 0 | 0 | 1.5 | 78.3077 | 0 | 22977.7192
2017-06-24 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 16:15 | 1.7241 | 0 | 0 |  | 78.7951 | 0 | 23120.726
2017-06-24 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 16:30 | 1.7686 | 0 | 0 | 1.5 | 79.224 | 0 | 23246.5893
2017-06-24 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 16:45 | 1.7522 | 0 | 0 |  | 78.2484 | 0 | 22960.3224
2017-06-24 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 17:00 | 1.7187 | 0 | 0 | 1.5 | 78.6488 | 0 | 23077.7951
2017-06-24 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 17:15 | 1.7826 | 0 | 0 |  | 78.9761 | 0 | 23173.8457
2017-06-24 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 17:30 | 1.7709 | 0 | 0 | 1.5 | 78.0025 | 0 | 22888.1695
2017-06-24 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 17:45 | 1.7249 | 0 | 0 |  | 78.3 | 0 | 22975.4715
2017-06-24 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 18:00 | 1.7031 | 0 | 0 | 1.5 | 79.0401 | 0 | 23192.6304
2017-06-24 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 18:15 | 1.7663 | 0 | 0 |  | 78.7337 | 0 | 23102.7271
2017-06-24 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 18:30 | 1.7608 | 0 | 0 | 1.5 | 78.7771 | 0 | 23115.4405
2017-06-24 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 18:45 | 1.7132 | 0 | 0 |  | 79.3737 | 0 | 23290.5032
2017-06-24 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 19:00 | 1.7975 | 0 | 0 | 1.5 | 79.4588 | 0 | 23315.4737
2017-06-24 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 19:15 | 1.7452 | 0 | 0 |  | 78.7901 | 0 | 23119.2756
2017-06-24 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 19:30 | 1.707 | 0 | 0 | 1.5 | 79.4599 | 0 | 23315.8049
2017-06-24 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 19:45 | 1.7218 | 0 | 0 |  | 80.0198 | 0 | 23480.0997
2017-06-24 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 20:00 | 1.7226 | 0 | 0 | 1.5 | 80.2044 | 0 | 23534.2599
2017-06-24 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 20:15 | 1.7561 | 0 | 0 |  | 79.9669 | 0 | 23464.5653
2017-06-24 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 20:30 | 1.7717 | 0 | 0 | 1.5 | 79.594 | 0 | 23355.1408
2017-06-24 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 20:45 | 1.7694 | 0 | 0 |  | 79.1412 | 0 | 23222.2928
2017-06-24 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-06-24 | 21:00 | 1.7912 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 21:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 21:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 21:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 21:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 21:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 21:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 21:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 22:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 22:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 22:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 22:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 22:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 22:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 22:45 | 0.02686 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 22:45 |  |  |  | 0 |  |  | 0
2017-06-24 | 23:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 23:00 |  |  |  | 0 |  |  | 0
2017-06-24 | 23:15 | 0.02608 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 23:15 |  |  |  | 0 |  |  | 0
2017-06-24 | 23:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-24 | 23:30 |  |  |  | 0 |  |  | 0
2017-06-24 | 23:45 | 0.02608 | 0 | 0 |  | 0 | 0 | 0
2017-06-24 | 23:45 |  |  |  | 0 |  |  | 0
2017-06-25 | 0:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 0:00 |  |  |  | 0 |  |  | 0
2017-06-25 | 0:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 0:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 0:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 1:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 1:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 1:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 1:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 2:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 2:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 2:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 2:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 3:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 3:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 3:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 3:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 4:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 4:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 4:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 4:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 5:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 5:01 |  |  | 1 |  |  |  | 0
2017-06-25 | 5:15 | 1.8895 | 10 | 1 | 10 | 96.9999 | 100 | 28462.5491
2017-06-25 | 5:30 | 2.0829 | 10 | 1 | 10 | 91.1648 | 100 | 26750.3644
2017-06-25 | 5:45 | 1.9394 | 9.1564 | 1 | 10 | 84.7376 | 92.2398 | 24864.4247
2017-06-25 | 6:00 | 1.8458 | 7.6393 | 1 | 10 | 81.4557 | 77.4746 | 23901.4197
2017-06-25 | 6:15 | 1.8068 | 6.8566 | 1 | 10 | 79.7 | 69.6738 | 23386.2674
2017-06-25 | 6:30 | 1.76 | 6.379 | 1 | 10 | 78.7671 | 65.0368 | 23112.5302
2017-06-25 | 6:33 |  |  | 0 |  |  |  | 0
2017-06-25 | 6:45 | 1.7686 | 0 | 0 | 1.5 | 78.8164 | 0 | 23126.9854
2017-06-25 | 7:00 | 1.7826 | 0 | 0 | 1.5 | 78.1625 | 0 | 22935.1101
2017-06-25 | 7:15 | 1.778 | 0 | 0 | 1.5 | 78.0958 | 0 | 22915.5308
2017-06-25 | 7:30 | 1.7678 | 0 | 0 | 1.5 | 77.6694 | 0 | 22790.4264
2017-06-25 | 7:45 | 1.7694 | 0 | 0 | 1.5 | 77.2441 | 0 | 22665.6288
2017-06-25 | 8:00 | 1.7702 | 0 | 0 | 1.5 | 76.9798 | 0 | 22588.0607
2017-06-25 | 8:15 | 1.7522 | 0 | 0 | 1.5 | 76.9369 | 0 | 22575.4929
2017-06-25 | 8:30 | 1.7468 | 0 | 0 | 1.5 | 76.9387 | 0 | 22576.021
2017-06-25 | 8:45 | 1.7421 | 0 | 0 | 1.5 | 77.2053 | 0 | 22654.2338
2017-06-25 | 9:00 | 1.7187 | 0 | 0 | 1.5 | 77.9324 | 0 | 22867.5916
2017-06-25 | 9:15 | 1.721 | 0 | 0 | 1.5 | 78.3188 | 0 | 22980.9698
2017-06-25 | 9:30 | 1.7226 | 0 | 0 | 1.5 | 78.5264 | 0 | 23041.8908
2017-06-25 | 9:45 | 1.7234 | 0 | 0 | 1.5 | 79.0628 | 0 | 23199.2704
2017-06-25 | 10:00 | 1.721 | 0 | 0 | 1.5 | 79.557 | 0 | 23344.2854
2017-06-25 | 10:15 | 1.7312 | 0 | 0 | 1.5 | 80.08 | 0 | 23497.7741
2017-06-25 | 10:30 | 1.7234 | 0 | 0 | 1.5 | 80.8519 | 0 | 23724.2502
2017-06-25 | 10:45 | 1.7257 | 0 | 0 | 1.5 | 81.3482 | 0 | 23869.8967
2017-06-25 | 11:00 | 1.7265 | 0 | 0 | 1.5 | 81.7616 | 0 | 23991.1819
2017-06-25 | 11:15 | 1.7748 | 0 | 0 | 1.5 | 80.591 | 0 | 23647.7052
2017-06-25 | 11:30 | 1.7109 | 0 | 0 | 1.5 | 80.8775 | 0 | 23731.7611
2017-06-25 | 11:45 | 1.7865 | 0 | 0 | 1.5 | 81.2956 | 0 | 23854.4386
2017-06-25 | 12:00 | 1.7312 | 0 | 0 | 1.5 | 80.7141 | 0 | 23683.8354
2017-06-25 | 12:15 | 1.7834 | 0 | 0 | 1.5 | 81.0493 | 0 | 23782.1671
2017-06-25 | 12:30 | 1.7499 | 0 | 0 | 1.5 | 80.0406 | 0 | 23486.2045
2017-06-25 | 12:45 | 1.7039 | 0 | 0 | 1.5 | 80.6615 | 0 | 23668.3952
2017-06-25 | 13:00 | 1.778 | 0 | 0 | 1.5 | 81.1054 | 0 | 23798.6528
2017-06-25 | 13:15 | 1.7468 | 0 | 0 | 1.5 | 80.0089 | 0 | 23476.8984
2017-06-25 | 13:30 | 1.6914 | 0 | 0 | 1.5 | 80.6332 | 0 | 23660.0941
2017-06-25 | 13:45 | 1.8302 | 0 | 0 | 1.5 | 80.2381 | 0 | 23544.1616
2017-06-25 | 14:00 | 1.7616 | 0 | 0 | 1.5 | 79.2388 | 0 | 23250.9235
2017-06-25 | 14:15 | 1.6875 | 0 | 0 | 1.5 | 80.2081 | 0 | 23535.3347
2017-06-25 | 14:30 | 1.7663 | 0 | 0 | 1.5 | 81.0015 | 0 | 23768.1418
2017-06-25 | 14:45 | 1.7546 | 0 | 0 | 1.5 | 79.8324 | 0 | 23425.1086
2017-06-25 | 15:00 | 1.6766 | 0 | 0 | 1.5 | 80.4075 | 0 | 23593.8626
2017-06-25 | 15:15 | 1.7787 | 0 | 0 | 1.5 | 81.2317 | 0 | 23835.6985
2017-06-25 | 15:30 | 1.7858 | 0 | 0 | 1.5 | 79.8905 | 0 | 23442.1427
2017-06-25 | 15:45 | 1.6797 | 0 | 0 | 1.5 | 80.5669 | 0 | 23640.6175
2017-06-25 | 16:00 | 1.7826 | 0 | 0 | 1.5 | 81.2922 | 0 | 23853.4515
2017-06-25 | 16:15 | 1.8154 | 0 | 0 | 1.5 | 79.7832 | 0 | 23410.6645
2017-06-25 | 16:30 | 1.7093 | 0 | 0 | 1.5 | 79.7373 | 0 | 23397.1877
2017-06-25 | 16:45 | 1.6859 | 0 | 0 | 1.5 | 80.977 | 0 | 23760.9669
2017-06-25 | 17:00 | 1.8115 | 0 | 0 | 1.5 | 80.7436 | 0 | 23692.4698
2017-06-25 | 17:15 | 1.7429 | 0 | 0 | 1.5 | 79.9197 | 0 | 23450.719
2017-06-25 | 17:30 | 1.6797 | 0 | 0 | 1.5 | 80.9536 | 0 | 23754.1121
2017-06-25 | 17:45 | 1.8006 | 0 | 0 | 1.5 | 80.7034 | 0 | 23680.681
2017-06-25 | 18:00 | 1.7078 | 0 | 0 | 1.5 | 80.6038 | 0 | 23651.4438
2017-06-25 | 18:15 | 1.6968 | 0 | 0 | 1.5 | 81.7604 | 0 | 23990.8303
2017-06-25 | 18:30 | 1.8263 | 0 | 0 | 1.5 | 81.2398 | 0 | 23838.0694
2017-06-25 | 18:45 | 1.7351 | 0 | 0 | 1.5 | 80.7519 | 0 | 23694.9191
2017-06-25 | 19:00 | 1.7319 | 0 | 0 | 1.5 | 81.1991 | 0 | 23826.1215
2017-06-25 | 19:15 | 1.7553 | 0 | 0 | 1.5 | 81.5179 | 0 | 23919.6672
2017-06-25 | 19:30 | 1.7288 | 0 | 0 | 1.5 | 81.871 | 0 | 24023.2868
2017-06-25 | 19:45 | 1.721 | 0 | 0 | 1.5 | 82.1968 | 0 | 24118.894
2017-06-25 | 20:00 | 1.7421 | 0 | 0 | 1.5 | 82.2791 | 0 | 24143.0294
2017-06-25 | 20:15 | 1.7631 | 0 | 0 | 1.5 | 81.9751 | 0 | 24053.8224
2017-06-25 | 20:30 | 1.7741 | 0 | 0 | 1.5 | 81.5469 | 0 | 23928.1807
2017-06-25 | 20:45 | 1.7873 | 0 | 0 | 1.5 | 80.847 | 0 | 23722.8109
2017-06-25 | 21:00 | 1.7663 | 0 | 0 | 1.5 | 80.0928 | 0 | 23501.5127
2017-06-25 | 21:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 21:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 21:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 22:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 22:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 22:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 22:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 23:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 23:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 23:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 23:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 0:00 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 0:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 0:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 0:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 1:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 1:15 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 1:30 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 1:45 | 0.0253 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 2:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 2:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 2:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 2:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 3:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 3:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 3:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 3:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 4:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 4:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 4:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 4:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 5:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 5:00 |  |  | 1 |  |  |  | 0
2017-06-26 | 5:15 | 1.9737 | 10 | 1 | 10 | 95.1682 | 100 | 27925.0728
2017-06-26 | 5:30 | 2.0276 | 10 | 1 | 10 | 89.2284 | 99.98 | 26182.1511
2017-06-26 | 5:45 | 1.909 | 9.0565 | 1 | 10 | 83.9631 | 91.3507 | 24637.1828
2017-06-26 | 6:00 | 1.8544 | 7.9341 | 1 | 10 | 81.5383 | 80.7419 | 23925.6601
2017-06-26 | 6:15 | 1.7881 | 8.2769 | 1 | 10 | 80.4613 | 83.414 | 23609.6499
2017-06-26 | 6:30 | 1.7561 | 7.8964 | 1 | 10 | 79.668 | 79.8463 | 23376.8651
2017-06-26 | 6:45 | 1.7577 | 7.5027 | 1 | 10 | 79.09 | 76.0126 | 23207.2645
2017-06-26 | 7:00 | 1.785 | 7.0757 | 1 | 10 | 78.8718 | 71.7371 | 23143.2317
2017-06-26 | 7:15 | 1.7709 | 6.5793 | 1 | 10 | 79.0458 | 67.1778 | 23194.2938
2017-06-26 | 7:30 | 1.6953 | 5.6867 | 1 | 10 | 78.8872 | 0 | 23147.7517
2017-06-26 | 7:45 | 1.7296 | 6.5725 | 1 | 10 | 79.127 | 0 | 23218.1358
2017-06-26 | 8:00 | 1.7733 | 5.5143 | 1 | 10 | 79.0149 | 0 | 23185.2292
2017-06-26 | 8:15 | 1.7288 | 5.3997 | 1 | 10 | 79.1778 | 0 | 23233.0161
2017-06-26 | 8:30 | 1.7195 | 4.1715 | 1 | 10 | 79.3657 | 0 | 23288.1775
2017-06-26 | 8:45 | 1.6563 | 5.4332 | 1 | 10 | 82.1637 | 0 | 24109.1648
2017-06-26 | 9:00 | 1.8115 | 4.6266 | 1 | 10 | 81.7148 | 0 | 23977.4541
2017-06-26 | 9:15 | 1.7499 | 4.4914 | 1 | 10 | 81.583 | 0 | 23938.7922
2017-06-26 | 9:30 | 1.6836 | 5.2404 | 1 | 10 | 81.7271 | 0 | 23981.0586
2017-06-26 | 9:45 | 1.7023 | 4.4899 | 1 | 10 | 81.4767 | 0 | 23907.5782
2017-06-26 | 10:00 | 1.7499 | 3.7164 | 1 | 10 | 81.4037 | 0 | 23886.1585
2017-06-26 | 10:15 | 1.611 | 3.7152 | 1 | 10 | 82.7414 | 0 | 24278.6958
2017-06-26 | 10:29 |  |  | 0 |  |  |  | 0
2017-06-26 | 10:30 | 1.6906 | 4.708 | 0 | 1.5 | 83.9205 | 0 | 24624.6619
2017-06-26 | 10:38 |  |  | 1 |  |  |  | 0
2017-06-26 | 10:45 | 1.8411 | 1.444 | 1 | 10 | 83.6984 | 0 | 24559.516
2017-06-26 | 10:53 |  |  | 0 |  |  |  | 0
2017-06-26 | 11:00 | 1.7436 | 0 | 0 | 1.5 | 83.8686 | 0 | 24609.4341
2017-06-26 | 11:15 | 1.6547 | 0 | 0 | 1.5 | 85.1225 | 0 | 24977.3595
2017-06-26 | 11:30 | 1.7397 | 0 | 0 | 1.5 | 85.9863 | 0 | 25230.8342
2017-06-26 | 11:45 | 1.6274 | 0 | 0 | 1.5 | 86.7809 | 0 | 25463.9864
2017-06-26 | 12:00 | 1.7 | 0 | 0 | 1.5 | 87.392 | 0 | 25643.3203
2017-06-26 | 12:15 | 1.6929 | 0 | 0 | 1.5 | 88.4779 | 0 | 25961.952
2017-06-26 | 12:30 | 1.7218 | 0 | 0 | 1.5 | 88.7506 | 0 | 26041.9536
2017-06-26 | 12:45 | 1.7156 | 0 | 0 | 1.5 | 88.6225 | 0 | 26004.3841
2017-06-26 | 13:00 | 1.6469 | 0 | 0 | 1.5 | 90.2063 | 0 | 26469.101
2017-06-26 | 13:15 | 1.7039 | 0 | 0 | 1.5 | 92.1507 | 0 | 27039.6359
2017-06-26 | 13:30 | 1.6204 | 0 | 0 | 1.5 | 94.5114 | 0 | 27732.3424
2017-06-26 | 13:45 | 1.8747 | 0 | 0 | 1.5 | 94.4923 | 0 | 27726.7523
2017-06-26 | 14:00 | 1.8669 | 0 | 0 | 1.5 | 89.2909 | 0 | 26200.4971
2017-06-26 | 14:15 | 1.622 | 0 | 0 | 1.5 | 90.0001 | 0 | 26408.5961
2017-06-26 | 14:30 | 1.5775 | 0 | 0 | 1.5 | 93.053 | 0 | 27304.4159
2017-06-26 | 14:45 | 1.7577 | 0 | 0 | 1.5 | 94.0896 | 0 | 27608.5634
2017-06-26 | 15:00 | 1.9308 | 0 | 0 | 1.5 | 90.5051 | 0 | 26556.781
2017-06-26 | 15:15 | 1.7405 | 0 | 0 | 1.5 | 89.3826 | 0 | 26227.4083
2017-06-26 | 15:30 | 1.5572 | 0 | 0 | 1.5 | 92.0856 | 0 | 27020.5443
2017-06-26 | 15:45 | 1.7561 | 0 | 0 | 1.5 | 95.3523 | 0 | 27979.0989
2017-06-26 | 16:00 | 2.0338 | 0 | 0 | 1.5 | 90.5165 | 0 | 26560.1279
2017-06-26 | 16:15 | 1.682 | 0 | 0 | 1.5 | 88.4609 | 0 | 25956.9485
2017-06-26 | 16:30 | 1.5627 | 0 | 0 | 1.5 | 91.5456 | 0 | 26862.0838
2017-06-26 | 16:45 | 1.792 | 0 | 0 | 1.5 | 94.7009 | 0 | 27787.9557
2017-06-26 | 17:00 | 2.15 | 0 | 0 | 1.5 | 89.4316 | 0 | 26241.774
2017-06-26 | 17:15 | 1.6836 | 0 | 0 | 1.5 | 86.1848 | 0 | 25289.0757
2017-06-26 | 17:30 | 1.7741 | 0 | 0 | 1.5 | 86.0156 | 0 | 25239.4241
2017-06-26 | 17:45 | 1.7631 | 0 | 0 | 1.5 | 86.0353 | 0 | 25245.2178
2017-06-26 | 18:00 | 1.7928 | 0 | 0 | 1.5 | 86.0968 | 0 | 25263.2569
2017-06-26 | 18:15 | 1.8099 | 0 | 0 | 1.5 | 85.0756 | 0 | 24963.6027
2017-06-26 | 18:30 | 1.8419 | 0 | 0 | 1.5 | 84.0912 | 0 | 24674.768
2017-06-26 | 18:45 | 1.7834 | 0 | 0 | 1.5 | 82.8974 | 0 | 24324.4701
2017-06-26 | 19:00 | 1.7678 | 0 | 0 | 1.5 | 82.2138 | 0 | 24123.8864
2017-06-26 | 19:15 | 1.792 | 0 | 0 | 1.5 | 81.0607 | 0 | 23785.5207
2017-06-26 | 19:30 | 1.8201 | 0 | 0 | 1.5 | 80.1093 | 0 | 23506.3639
2017-06-26 | 19:45 | 1.7951 | 0 | 0 | 1.5 | 78.9692 | 0 | 23171.833
2017-06-26 | 20:00 | 1.7897 | 0 | 0 | 1.5 | 78.0898 | 0 | 22913.7667
2017-06-26 | 20:15 | 1.7444 | 0 | 0 | 1.5 | 77.6182 | 0 | 22775.4116
2017-06-26 | 20:30 | 1.7858 | 0 | 0 | 1.5 | 76.9503 | 0 | 22579.4037
2017-06-26 | 20:45 | 1.7748 | 0 | 0 | 1.5 | 76.6548 | 0 | 22492.6997
2017-06-26 | 21:00 | 1.7483 | 0 | 0 | 1.5 | 76.3474 | 0 | 22402.5188
2017-06-26 | 21:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 21:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 21:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 22:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 22:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 22:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 22:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 23:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 23:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 23:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-26 | 23:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 0:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 0:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 0:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 0:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 1:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 1:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 1:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 1:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 2:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 2:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 2:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 2:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 3:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 3:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 3:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 3:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 4:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 4:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 4:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 4:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 5:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 5:00 |  |  | 1 |  |  |  | 0
2017-06-27 | 5:15 | 2.189 | 10 | 1 | 10 | 94.2228 | 100 | 27647.6686
2017-06-27 | 5:30 | 2.0556 | 9.499 | 1 | 10 | 86.0042 | 95.3195 | 25236.1042
2017-06-27 | 5:45 | 1.7803 | 8.1055 | 1 | 10 | 82.1742 | 81.7387 | 24112.2587
2017-06-27 | 6:00 | 1.8302 | 7.1313 | 1 | 10 | 80.1268 | 72.6781 | 23511.506
2017-06-27 | 6:15 | 1.8372 | 7.4013 | 1 | 10 | 78.9357 | 75.0558 | 23161.9762
2017-06-27 | 6:30 | 1.7803 | 6.9136 | 1 | 10 | 78.3008 | 69.9369 | 22975.6796
2017-06-27 | 6:45 | 1.7148 | 6.3917 | 1 | 10 | 77.7446 | 65.1704 | 22812.4998
2017-06-27 | 7:00 | 1.739 | 5.965 | 1 | 10 | 77.1314 | 0 | 22632.548
2017-06-27 | 7:15 | 1.8224 | 6.8113 | 1 | 10 | 76.7028 | 0 | 22506.781
2017-06-27 | 7:30 | 1.7787 | 5.8705 | 1 | 10 | 76.7636 | 0 | 22524.6256
2017-06-27 | 7:45 | 1.6929 | 5.7597 | 1 | 10 | 77.0012 | 0 | 22594.3424
2017-06-27 | 8:00 | 1.6914 | 4.6969 | 1 | 10 | 77.1548 | 0 | 22639.4274
2017-06-27 | 8:15 | 1.7413 | 5.1827 | 1 | 10 | 77.3718 | 0 | 22703.0932
2017-06-27 | 8:30 | 1.6867 | 4.978 | 1 | 10 | 78.4966 | 0 | 23033.1578
2017-06-27 | 8:45 | 1.6469 | 5.6422 | 1 | 10 | 79.5821 | 0 | 23351.6663
2017-06-27 | 9:00 | 1.6719 | 5.4632 | 1 | 10 | 81.0236 | 0 | 23774.6251
2017-06-27 | 9:15 | 1.7592 | 6.5422 | 1 | 10 | 81.2508 | 0 | 23841.3088
2017-06-27 | 9:30 | 1.7787 | 7.0455 | 1 | 10 | 81.3831 | 0 | 23880.1341
2017-06-27 | 9:45 | 1.7998 | 6.351 | 1 | 10 | 81.1047 | 0 | 23798.4448
2017-06-27 | 10:00 | 1.6344 | 5.7797 | 1 | 10 | 82.2396 | 0 | 24131.4554
2017-06-27 | 10:15 | 1.7795 | 7.1208 | 1 | 10 | 82.8944 | 0 | 24323.586
2017-06-27 | 10:30 | 1.6555 | 7.8273 | 1 | 10 | 84.3061 | 0 | 24737.8249
2017-06-27 | 10:45 | 1.6337 | 8.0507 | 1 | 10 | 85.1758 | 0 | 24993.0057
2017-06-27 | 11:00 | 1.7912 | 7.8134 | 1 | 10 | 86.1069 | 0 | 25266.2299
2017-06-27 | 11:15 | 1.7616 | 7.7657 | 1 | 10 | 85.5218 | 0 | 25094.5522
2017-06-27 | 11:30 | 1.8076 | 7.7972 | 1 | 10 | 84.4198 | 0 | 24771.1678
2017-06-27 | 11:45 | 1.6352 | 8.1512 | 1 | 10 | 86.08 | 0 | 25258.3364
2017-06-27 | 11:47 |  |  | 0 |  |  |  | 0
2017-06-27 | 11:51 |  |  | 1 |  |  |  | 0
2017-06-27 | 11:53 |  |  | 0 |  |  |  | 0
2017-06-27 | 12:00 | 1.6181 | 0 | 0 | 1.5 | 85.9607 | 0 | 25223.3257
2017-06-27 | 12:15 | 1.8037 | 0 | 0 | 1.5 | 85.8665 | 0 | 25195.6756
2017-06-27 | 12:30 | 1.7834 | 0 | 0 | 1.5 | 85.2832 | 0 | 25024.5328
2017-06-27 | 12:45 | 1.8162 | 0 | 0 | 1.5 | 84.3498 | 0 | 24750.6504
2017-06-27 | 13:00 | 1.8107 | 0 | 0 | 1.5 | 83.6571 | 0 | 24547.3713
2017-06-27 | 13:15 | 1.7421 | 0 | 0 | 1.5 | 83.6398 | 0 | 24542.2938
2017-06-27 | 13:30 | 1.7912 | 0 | 0 | 1.5 | 84.411 | 0 | 24768.5977
2017-06-27 | 13:45 | 1.7304 | 0 | 0 | 1.5 | 85.8735 | 0 | 25197.7241
2017-06-27 | 14:00 | 1.7374 | 0 | 0 | 1.5 | 87.6036 | 0 | 25705.3901
2017-06-27 | 14:15 | 1.778 | 0 | 0 | 1.5 | 88.8808 | 0 | 26080.1767
2017-06-27 | 14:30 | 1.7351 | 0 | 0 | 1.5 | 89.2838 | 0 | 26198.4308
2017-06-27 | 14:45 | 1.7733 | 0 | 0 | 1.5 | 89.6535 | 0 | 26306.8949
2017-06-27 | 15:00 | 1.707 | 0 | 0 | 1.5 | 90.131 | 0 | 26447.0117
2017-06-27 | 15:15 | 1.7124 | 0 | 0 | 1.5 | 90.1783 | 0 | 26460.8894
2017-06-27 | 15:30 | 1.7507 | 0 | 0 | 1.5 | 90.6615 | 0 | 26602.663
2017-06-27 | 15:45 | 1.7468 | 0 | 0 | 1.5 | 90.6144 | 0 | 26588.8504
2017-06-27 | 16:00 | 1.7101 | 0 | 0 | 1.5 | 91.2522 | 0 | 26776.0042
2017-06-27 | 16:15 | 1.7686 | 0 | 0 | 1.5 | 91.2173 | 0 | 26765.7556
2017-06-27 | 16:30 | 1.7873 | 0 | 0 | 1.5 | 90.1214 | 0 | 26444.1957
2017-06-27 | 16:45 | 1.7351 | 0 | 0 | 1.5 | 90.7252 | 0 | 26621.3626
2017-06-27 | 17:00 | 1.7756 | 0 | 0 | 1.5 | 90.269 | 0 | 26487.5052
2017-06-27 | 17:15 | 1.8684 | 0 | 0 | 1.5 | 88.2785 | 0 | 25903.4306
2017-06-27 | 17:30 | 1.8146 | 0 | 0 | 1.5 | 86.0207 | 0 | 25240.9173
2017-06-27 | 17:45 | 1.8177 | 0 | 0 | 1.5 | 84.4714 | 0 | 24786.3081
2017-06-27 | 18:00 | 1.767 | 0 | 0 | 1.5 | 83.4803 | 0 | 24495.5099
2017-06-27 | 18:15 | 1.7865 | 0 | 0 | 1.5 | 82.8253 | 0 | 24303.3212
2017-06-27 | 18:30 | 1.7967 | 0 | 0 | 1.5 | 82.4079 | 0 | 24180.8183
2017-06-27 | 18:45 | 1.8006 | 0 | 0 | 1.5 | 81.9086 | 0 | 24034.3235
2017-06-27 | 19:00 | 1.7507 | 0 | 0 | 1.5 | 81.3714 | 0 | 23876.6957
2017-06-27 | 19:15 | 1.799 | 0 | 0 | 1.5 | 81.1854 | 0 | 23822.1054
2017-06-27 | 19:30 | 1.7858 | 0 | 0 | 1.5 | 80.7086 | 0 | 23682.201
2017-06-27 | 19:45 | 1.753 | 0 | 0 | 1.5 | 80.0109 | 0 | 23477.4847
2017-06-27 | 20:00 | 1.7943 | 0 | 0 | 1.5 | 79.2807 | 0 | 23263.236
2017-06-27 | 20:15 | 1.7702 | 0 | 0 | 1.5 | 78.54 | 0 | 23045.8803
2017-06-27 | 20:30 | 1.7764 | 0 | 0 | 1.5 | 77.7064 | 0 | 22801.2683
2017-06-27 | 20:45 | 1.7748 | 0 | 0 | 1.5 | 77.2361 | 0 | 22663.2782
2017-06-27 | 21:00 | 1.7234 | 0 | 0 | 1.5 | 76.8747 | 0 | 22557.2296
2017-06-27 | 21:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 21:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 22:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 22:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 22:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 23:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 23:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 0:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 0:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 0:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 0:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 0:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 1:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 1:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 1:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 1:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 1:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 1:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 2:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 2:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 2:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 2:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 2:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 2:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 2:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 3:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 3:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 3:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 3:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 3:45 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 3:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 4:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 4:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 4:15 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 4:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 4:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 4:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 4:45 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 4:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 5:00 | 0.02998 | 0 | 1 | 0 | 25.375 | 0 | 7445.75
2017-06-28 | 5:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 5:15 | 2.2694 | 10 | 1 |  | 90.457 | 100 | 26542.6774
2017-06-28 | 5:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 5:30 | 1.9519 | 8.5333 | 1 | 10 | 83.7219 | 86.1236 | 24566.409
2017-06-28 | 5:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 5:45 | 1.8622 | 7.7527 | 1 |  | 81.6102 | 78.1801 | 23946.755
2017-06-28 | 5:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 6:00 | 1.7717 | 6.9364 | 1 | 10 | 79.9636 | 70.1651 | 23463.6005
2017-06-28 | 6:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 6:15 | 1.8552 | 7.2002 | 1 |  | 79.287 | 72.7303 | 23265.0852
2017-06-28 | 6:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 6:30 | 1.7858 | 6.5641 | 1 | 10 | 78.1162 | 66.594 | 22921.537
2017-06-28 | 6:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 6:45 | 1.7803 | 6.5935 | 1 |  | 78.0991 | 66.7202 | 22916.5135
2017-06-28 | 6:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 7:00 | 1.7265 | 5.8998 | 1 | 10 | 77.6547 | 0 | 22786.1147
2017-06-28 | 7:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 7:15 | 1.7741 | 6.6133 | 1 |  | 77.3767 | 0 | 22704.5281
2017-06-28 | 7:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 7:30 | 1.7631 | 4.9876 | 1 | 10 | 77.1537 | 0 | 22639.0982
2017-06-28 | 7:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 7:45 | 1.7241 | 4.8357 | 1 |  | 77.0318 | 0 | 22603.3331
2017-06-28 | 7:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 8:00 | 1.7421 | 4.0972 | 1 | 10 | 77.1617 | 0 | 22641.4512
2017-06-28 | 8:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 8:15 | 1.7413 | 4.8025 | 1 |  | 78.1963 | 0 | 22945.0389
2017-06-28 | 8:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 8:30 | 1.7054 | 4.7883 | 1 | 10 | 78.6221 | 0 | 23069.964
2017-06-28 | 8:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 8:45 | 1.6914 | 5.5899 | 1 |  | 79.3954 | 0 | 23296.87
2017-06-28 | 8:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 9:00 | 1.6976 | 5.4282 | 1 | 10 | 79.8291 | 0 | 23424.1482
2017-06-28 | 9:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 9:15 | 1.7616 | 4.976 | 1 |  | 80.163 | 0 | 23522.1152
2017-06-28 | 9:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 9:30 | 1.6968 | 5.6133 | 1 | 10 | 81.0043 | 0 | 23768.9793
2017-06-28 | 9:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 9:45 | 1.7312 | 5.5905 | 1 |  | 81.6564 | 0 | 23960.317
2017-06-28 | 9:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 10:00 | 1.6672 | 5.0577 | 1 | 10 | 82.3428 | 0 | 24161.7337
2017-06-28 | 10:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 10:15 | 1.7031 | 5.9415 | 1 |  |  | 0 | 0
2017-06-28 | 10:15 |  |  |  | 10 | 83.6279 |  | 24538.8284
2017-06-28 | 10:30 | 1.7826 | 5.9471 | 1 | 10 | 84.0191 | 0 | 24653.5989
2017-06-28 | 10:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 10:45 | 1.7912 | 5.7152 | 1 |  | 83.6336 | 0 | 24540.4983
2017-06-28 | 10:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 11:00 | 1.7351 | 5.8438 | 1 | 10 | 83.5542 | 0 | 24517.1848
2017-06-28 | 11:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 11:15 | 1.7538 | 5.6501 | 1 |  | 83.7714 | 0 | 24580.9357
2017-06-28 | 11:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 11:30 | 1.76 | 6.1633 | 1 | 10 | 84.1867 | 0 | 24702.7828
2017-06-28 | 11:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 11:45 | 1.785 | 6.019 | 1 |  | 83.8718 | 0 | 24610.3924
2017-06-28 | 11:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 12:00 | 1.6695 | 6.2134 | 1 | 10 | 83.8831 | 0 | 24613.6856
2017-06-28 | 12:00 |  |  |  | 10 |  |  | 0
2017-06-28 | 12:15 | 1.6758 | 5.8441 | 1 |  | 83.657 | 0 | 24547.3511
2017-06-28 | 12:15 |  |  |  | 10 |  |  | 0
2017-06-28 | 12:19 |  |  | 0 |  |  |  | 0
2017-06-28 | 12:28 |  |  | 1 |  |  |  | 0
2017-06-28 | 12:30 | 1.792 | 0 | 1 | 10 | 83.211 | 0 | 24416.4978
2017-06-28 | 12:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 12:32 |  |  | 0 |  |  |  | 0
2017-06-28 | 12:33 |  |  | 1 |  |  |  | 0
2017-06-28 | 12:38 |  |  | 0 |  |  |  | 0
2017-06-28 | 12:42 |  |  | 1 |  |  |  | 0
2017-06-28 | 12:45 | 1.6898 | 0 | 1 |  | 82.8164 | 0 | 24300.6842
2017-06-28 | 12:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 12:49 |  |  | 0 |  |  |  | 0
2017-06-28 | 13:00 | 1.7015 | 0 | 0 | 1.5 | 83.3712 | 0 | 24463.5012
2017-06-28 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 13:08 |  |  | 1 |  |  |  | 0
2017-06-28 | 13:10 |  |  | 0 |  |  |  | 0
2017-06-28 | 13:15 | 1.7327 | 0 | 0 |  | 83.4892 | 0 | 24498.1023
2017-06-28 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 13:30 | 1.8115 | 0 | 0 | 1.5 | 83.4637 | 0 | 24490.6431
2017-06-28 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 13:45 | 1.7109 | 0 | 0 |  | 83.3466 | 0 | 24456.2703
2017-06-28 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 14:00 | 1.6688 | 0 | 0 | 1.5 | 83.6005 | 0 | 24530.7759
2017-06-28 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 14:15 | 1.6836 | 0 | 0 |  | 85.1658 | 0 | 24990.0796
2017-06-28 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 14:30 | 1.7889 | 0 | 0 | 1.5 | 85.1336 | 0 | 24980.6233
2017-06-28 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 14:45 | 1.6664 | 0 | 0 |  | 85.2744 | 0 | 25021.9339
2017-06-28 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 15:00 | 1.7195 | 0 | 0 | 1.5 | 85.2707 | 0 | 25020.8614
2017-06-28 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 15:15 | 1.7553 | 0 | 0 |  | 86.1371 | 0 | 25275.0727
2017-06-28 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 15:30 | 1.7608 | 0 | 0 | 1.5 | 85.9198 | 0 | 25211.3198
2017-06-28 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 15:45 | 1.7397 | 0 | 0 |  | 86.0942 | 0 | 25262.4981
2017-06-28 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 16:00 | 1.6984 | 0 | 0 | 1.5 | 86.7915 | 0 | 25467.1138
2017-06-28 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 16:15 | 1.8123 | 0 | 0 |  | 86.5028 | 0 | 25382.3954
2017-06-28 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 16:30 | 1.7312 | 0 | 0 | 1.5 | 85.5392 | 0 | 25099.6362
2017-06-28 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 16:45 | 1.7538 | 0 | 0 |  | 85.1711 | 0 | 24991.6222
2017-06-28 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 17:00 | 1.7 | 0 | 0 | 1.5 | 85.4651 | 0 | 25077.9098
2017-06-28 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 17:15 | 1.8294 | 0 | 0 |  | 84.4571 | 0 | 24782.1218
2017-06-28 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 17:30 | 1.8318 | 0 | 0 | 1.5 | 82.835 | 0 | 24306.1419
2017-06-28 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 17:45 | 1.7795 | 0 | 0 |  | 81.5181 | 0 | 23919.7276
2017-06-28 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 18:00 | 1.7717 | 0 | 0 | 1.5 | 80.6094 | 0 | 23653.114
2017-06-28 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 18:15 | 1.778 | 0 | 0 |  | 79.7678 | 0 | 23406.1446
2017-06-28 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 18:30 | 1.8107 | 0 | 0 | 1.5 | 79.0636 | 0 | 23199.5075
2017-06-28 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 18:45 | 1.792 | 0 | 0 |  | 78.2582 | 0 | 22963.181
2017-06-28 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 19:00 | 1.8029 | 0 | 0 | 1.5 | 77.8365 | 0 | 22839.4401
2017-06-28 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 19:15 | 1.792 | 0 | 0 |  | 77.298 | 0 | 22681.4408
2017-06-28 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 19:30 | 1.7046 | 0 | 0 | 1.5 | 77.716 | 0 | 22804.1025
2017-06-28 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 19:45 | 1.7483 | 0 | 0 |  | 77.4946 | 0 | 22739.1315
2017-06-28 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 20:00 | 1.7647 | 0 | 0 | 1.5 | 77.1949 | 0 | 22651.2027
2017-06-28 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 20:15 | 1.7616 | 0 | 0 |  | 77.3055 | 0 | 22683.6571
2017-06-28 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-06-28 | 20:19 |  |  | 1 |  |  |  | 0
2017-06-28 | 20:30 | 1.8099 | 0.47368 | 1 | 10 | 76.4128 | 0 | 22421.6952
2017-06-28 | 20:30 |  |  |  | 10 |  |  | 0
2017-06-28 | 20:45 | 1.7132 | 1.3607 | 1 |  | 76.158 | 0 | 22346.9323
2017-06-28 | 20:45 |  |  |  | 10 |  |  | 0
2017-06-28 | 21:00 | 1.7725 | 6.4307 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 21:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 21:15 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 21:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 21:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 21:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 21:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 22:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 22:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 22:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 22:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 22:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 22:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 22:45 |  |  |  | 0 |  |  | 0
2017-06-28 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 23:00 |  |  |  | 0 |  |  | 0
2017-06-28 | 23:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 23:15 |  |  |  | 0 |  |  | 0
2017-06-28 | 23:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 23:30 |  |  |  | 0 |  |  | 0
2017-06-28 | 23:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-06-28 | 23:45 |  |  |  | 0 |  |  | 0
2017-06-29 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 0:00 |  |  |  | 0 |  |  | 0
2017-06-29 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 2:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 2:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 3:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 4:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 4:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 5:00 | 0.03154 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-29 | 5:15 | 2.2545 | 8.9919 | 1 | 10 | 87.5774 | 92.131 | 25697.7137
2017-06-29 | 5:30 | 1.9043 | 7.4595 | 1 | 10 | 81.3212 | 76.9021 | 23861.9539
2017-06-29 | 5:45 | 1.8154 | 6.6628 | 1 | 10 | 79.0209 | 69.0597 | 23186.9889
2017-06-29 | 6:00 | 1.8185 | 6.1414 | 1 | 10 | 77.9102 | 64.1566 | 22861.0681
2017-06-29 | 6:15 | 1.7834 | 6.9876 | 1 | 10 | 77.3496 | 0 | 22696.5876
2017-06-29 | 6:30 | 1.7156 | 7.1992 | 1 | 10 | 77.3001 | 0 | 22682.0518
2017-06-29 | 6:45 | 1.8076 | 6.9375 | 1 | 10 | 77.1708 | 0 | 22644.1285
2017-06-29 | 7:00 | 1.7826 | 5.9321 | 1 | 10 | 76.3164 | 0 | 22393.4187
2017-06-29 | 7:15 | 1.7858 | 6.3822 | 1 | 10 | 75.9383 | 0 | 22282.4628
2017-06-29 | 7:30 | 1.7421 | 5.7522 | 1 | 10 | 76.1664 | 0 | 22349.3836
2017-06-29 | 7:45 | 1.7475 | 5.852 | 1 | 10 | 76.5887 | 0 | 22473.3058
2017-06-29 | 8:00 | 1.7787 | 5.0095 | 1 | 10 | 76.9804 | 0 | 22588.2623
2017-06-29 | 8:15 | 1.7764 | 7.1445 | 1 | 10 | 77.7006 | 0 | 22799.5737
2017-06-29 | 8:30 | 1.7085 | 6.427 | 1 | 10 | 77.7901 | 0 | 22825.8403
2017-06-29 | 8:45 | 1.6633 | 6.3999 | 1 | 10 | 78.6201 | 0 | 23069.3798
2017-06-29 | 9:00 | 1.792 | 7.1499 | 1 | 10 | 79.4054 | 0 | 23299.8028
2017-06-29 | 9:15 | 1.7202 | 6.7019 | 1 | 10 | 79.7399 | 0 | 23397.9667
2017-06-29 | 9:30 | 1.6446 | 6.8349 | 1 | 10 | 80.9562 | 0 | 23754.8574
2017-06-29 | 9:45 | 1.7031 | 7.5413 | 1 | 10 | 81.9232 | 0 | 24038.5993
2017-06-29 | 10:00 | 1.792 | 7.2938 | 1 | 10 | 82.153 | 0 | 24106.0307
2017-06-29 | 10:15 | 1.7304 | 7.1248 | 1 | 10 | 81.5526 | 0 | 23929.8485
2017-06-29 | 10:30 | 1.7912 | 7.7181 | 1 | 10 | 82.8816 | 0 | 24319.8315
2017-06-29 | 10:45 | 1.7577 | 6.8533 | 1 | 10 | 81.8037 | 0 | 24003.5461
2017-06-29 | 11:00 | 1.7265 | 6.0329 | 1 | 10 | 81.8976 | 0 | 24031.0908
2017-06-29 | 11:04 |  |  | 0 |  |  |  | 0
2017-06-29 | 11:15 | 1.7405 | 0 | 0 | 1.5 | 82.5517 | 0 | 24223.013
2017-06-29 | 11:30 | 1.7312 | 0 | 0 | 1.5 | 83.2299 | 0 | 24422.023
2017-06-29 | 11:45 | 1.7647 | 0 | 0 | 1.5 | 83.6283 | 0 | 24538.9358
2017-06-29 | 12:00 | 1.799 | 0 | 0 | 1.5 | 83.4463 | 0 | 24485.5298
2017-06-29 | 12:15 | 1.8162 | 0 | 0 | 1.5 | 82.9236 | 0 | 24332.1397
2017-06-29 | 12:30 | 1.6789 | 0 | 0 | 1.5 | 82.9579 | 0 | 24342.2184
2017-06-29 | 12:45 | 1.668 | 0 | 0 | 1.5 | 83.2435 | 0 | 24426.0213
2017-06-29 | 13:00 | 1.7218 | 0 | 0 | 1.5 | 83.6357 | 0 | 24541.094
2017-06-29 | 13:15 | 1.7327 | 0 | 0 | 1.5 | 83.9287 | 0 | 24627.0929
2017-06-29 | 13:30 | 1.6898 | 0 | 0 | 1.5 | 84.5991 | 0 | 24823.7969
2017-06-29 | 13:45 | 1.6321 | 0 | 0 | 1.5 | 86.3595 | 0 | 25340.335
2017-06-29 | 14:00 | 1.7124 | 0 | 0 | 1.5 | 87.554 | 0 | 25690.8542
2017-06-29 | 14:15 | 1.7592 | 0 | 0 | 1.5 | 88.1547 | 0 | 25867.1012
2017-06-29 | 14:30 | 1.6688 | 0 | 0 | 1.5 | 88.6817 | 0 | 26021.7451
2017-06-29 | 14:45 | 1.7405 | 0 | 0 | 1.5 | 87.0894 | 0 | 25554.5209
2017-06-29 | 15:00 | 1.7117 | 0 | 0 | 1.5 | 86.9786 | 0 | 25522.0128
2017-06-29 | 15:15 | 1.7148 | 0 | 0 | 1.5 | 88.5651 | 0 | 25987.5314
2017-06-29 | 15:30 | 1.9152 | 0 | 0 | 1.5 | 85.9304 | 0 | 25214.438
2017-06-29 | 15:45 | 1.7085 | 0 | 0 | 1.5 | 85.6176 | 0 | 25122.6366
2017-06-29 | 16:00 | 1.6313 | 0 | 0 | 1.5 | 87.7751 | 0 | 25755.7357
2017-06-29 | 16:15 | 1.8887 | 0 | 0 | 1.5 | 88.7729 | 0 | 26048.5041
2017-06-29 | 16:30 | 1.8833 | 0 | 0 | 1.5 | 85.3613 | 0 | 25047.4346
2017-06-29 | 16:45 | 1.6274 | 0 | 0 | 1.5 | 85.8066 | 0 | 25178.0954
2017-06-29 | 17:00 | 1.739 | 0 | 0 | 1.5 | 87.0455 | 0 | 25541.6394
2017-06-29 | 17:15 | 2.0065 | 0 | 0 | 1.5 | 84.4934 | 0 | 24792.7645
2017-06-29 | 17:30 | 1.8466 | 0 | 0 | 1.5 | 81.7982 | 0 | 24001.9275
2017-06-29 | 17:45 | 1.7928 | 0 | 0 | 1.5 | 80.6493 | 0 | 23664.8177
2017-06-29 | 18:00 | 1.7592 | 0 | 0 | 1.5 | 80.2024 | 0 | 23533.6824
2017-06-29 | 18:15 | 1.7702 | 0 | 0 | 1.5 | 80.0498 | 0 | 23488.8976
2017-06-29 | 18:30 | 1.7499 | 0 | 0 | 1.5 | 80.1508 | 0 | 23518.5468
2017-06-29 | 18:45 | 1.76 | 0 | 0 | 1.5 | 80.2557 | 0 | 23549.3286
2017-06-29 | 19:00 | 1.7725 | 0 | 0 | 1.5 | 80.5889 | 0 | 23647.094
2017-06-29 | 19:15 | 1.7787 | 0 | 0 | 1.5 | 80.8311 | 0 | 23718.1477
2017-06-29 | 19:30 | 1.76 | 0 | 0 | 1.5 | 80.7952 | 0 | 23707.6348
2017-06-29 | 19:45 | 1.7639 | 0 | 0 | 1.5 | 80.5151 | 0 | 23625.4214
2017-06-29 | 20:00 | 1.7647 | 0 | 0 | 1.5 | 80.165 | 0 | 23522.6926
2017-06-29 | 20:15 | 1.753 | 0 | 0 | 1.5 | 79.6301 | 0 | 23365.7453
2017-06-29 | 20:30 | 1.7678 | 0 | 0 | 1.5 | 78.9408 | 0 | 23163.4917
2017-06-29 | 20:45 | 1.7764 | 0 | 0 | 1.5 | 78.354 | 0 | 22991.3102
2017-06-29 | 21:00 | 1.7717 | 0 | 0 | 1.5 | 77.8623 | 0 | 22847.0091
2017-06-29 | 21:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 21:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 22:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 22:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 22:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 22:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 23:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 23:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 23:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-29 | 23:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 0:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 0:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 0:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 0:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 1:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 1:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 1:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 1:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 2:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 2:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 2:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 3:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 3:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 3:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 3:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 4:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 4:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 4:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 4:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 5:00 | 0.02764 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-30 | 5:15 | 2.118 | 10 | 1 | 10 | 94.5772 | 100 | 27751.6509
2017-06-30 | 5:30 | 2.0861 | 9.593 | 1 | 10 | 86.7396 | 96.4506 | 25451.8752
2017-06-30 | 5:45 | 1.8723 | 8.1576 | 1 | 10 | 83.1802 | 82.3998 | 24407.4379
2017-06-30 | 6:00 | 1.8162 | 7.6278 | 1 | 10 | 81.5876 | 77.0011 | 23940.14
2017-06-30 | 6:15 | 1.7312 | 7.5445 | 1 | 10 | 80.7589 | 76.1224 | 23696.9584
2017-06-30 | 6:30 | 1.7241 | 7.5785 | 1 | 10 | 80.312 | 76.7174 | 23565.8343
2017-06-30 | 6:45 | 1.8333 | 7.2466 | 1 | 10 | 79.7242 | 73.4533 | 23393.3663
2017-06-30 | 6:54 |  |  | 0 |  |  |  | 0
2017-06-30 | 7:00 | 1.7647 | 1.8661 | 0 | 1.5 | 79.1822 | 0 | 23234.3257
2017-06-30 | 7:01 |  |  | 1 |  |  |  | 0
2017-06-30 | 7:15 | 1.7031 | 5.6401 | 1 | 10 | 78.6443 | 0 | 23076.4831
2017-06-30 | 7:30 | 1.7202 | 5.3772 | 1 | 10 | 78.595 | 0 | 23062.0324
2017-06-30 | 7:45 | 1.7546 | 5.1087 | 1 | 10 | 78.2692 | 0 | 22966.4116
2017-06-30 | 8:00 | 1.7499 | 3.6002 | 1 | 10 | 78.4968 | 0 | 23033.196
2017-06-30 | 8:15 | 1.7148 | 4.1866 | 1 | 10 | 78.9884 | 0 | 23177.4677
2017-06-30 | 8:30 | 1.7101 | 3.9899 | 1 | 10 | 79.3539 | 0 | 23284.703
2017-06-30 | 8:45 | 1.7062 | 4.3597 | 1 | 10 | 80.0943 | 0 | 23501.9537
2017-06-30 | 9:00 |  |  | 0 |  |  |  | 0
2017-06-30 | 9:00 | 1.7288 | 5.3119 | 0 | 1.5 | 81.0716 | 0 | 23788.7264
2017-06-30 | 9:15 | 1.6188 | 0 | 0 | 1.5 | 82.5183 | 0 | 24213.2345
2017-06-30 | 9:30 | 1.6454 | 0 | 0 | 1.5 | 83.581 | 0 | 24525.0649
2017-06-30 | 9:45 | 1.7171 | 0 | 0 | 1.5 | 84.3059 | 0 | 24737.7601
2017-06-30 | 10:00 | 1.8333 | 0 | 0 | 1.5 | 84.7932 | 0 | 24880.7423
2017-06-30 | 10:15 | 1.6812 | 0 | 0 | 1.5 | 85.9049 | 0 | 25206.9565
2017-06-30 | 10:30 | 1.6922 | 0 | 0 | 1.5 | 86.9904 | 0 | 25525.4829
2017-06-30 | 10:45 | 1.7078 | 0 | 0 | 1.5 | 87.2469 | 0 | 25600.7206
2017-06-30 | 11:00 | 1.7101 | 0 | 0 | 1.5 | 88.5197 | 0 | 25974.1953
2017-06-30 | 11:15 | 1.6586 | 0 | 0 | 1.5 | 90.7027 | 0 | 26614.7519
2017-06-30 | 11:30 | 1.6142 | 0 | 0 | 1.5 | 92.4308 | 0 | 27121.8335
2017-06-30 | 11:45 | 1.9589 | 0 | 0 | 1.5 | 90.5219 | 0 | 26561.6995
2017-06-30 | 12:00 | 1.7592 | 0 | 0 | 1.5 | 88.0863 | 0 | 25847.0451
2017-06-30 | 12:15 | 1.6914 | 0 | 0 | 1.5 | 89.0302 | 0 | 26123.9968
2017-06-30 | 12:30 | 1.8053 | 0 | 0 | 1.5 | 89.2062 | 0 | 26175.6499
2017-06-30 | 12:45 | 1.817 | 0 | 0 | 1.5 | 85.9288 | 0 | 25213.9703
2017-06-30 | 13:00 | 1.6243 | 0 | 0 | 1.5 | 87.1329 | 0 | 25567.2903
2017-06-30 | 13:15 | 1.8006 | 0 | 0 | 1.5 | 88.8896 | 0 | 26082.7492
2017-06-30 | 13:30 | 1.9574 | 0 | 0 | 1.5 | 87.1584 | 0 | 25574.7651
2017-06-30 | 13:45 | 1.7241 | 0 | 0 | 1.5 | 86.1839 | 0 | 25288.8319
2017-06-30 | 14:00 | 1.572 | 0 | 0 | 1.5 | 89.656 | 0 | 26307.6426
2017-06-30 | 14:15 | 1.8497 | 0 | 0 | 1.5 | 88.3839 | 0 | 25934.3536
2017-06-30 | 14:30 | 1.8489 | 0 | 0 | 1.5 | 86.4566 | 0 | 25368.8267
2017-06-30 | 14:45 | 1.6181 | 0 | 0 | 1.5 | 86.4705 | 0 | 25372.9077
2017-06-30 | 15:00 | 1.7039 | 0 | 0 | 1.5 | 90.4178 | 0 | 26531.1527
2017-06-30 | 15:15 | 1.8521 | 0 | 0 | 1.5 | 88.7031 | 0 | 26028.0222
2017-06-30 | 15:30 | 1.8209 | 0 | 0 | 1.5 | 86.3449 | 0 | 25336.0656
2017-06-30 | 15:45 | 1.8068 | 0 | 0 | 1.5 | 84.4835 | 0 | 24789.8721
2017-06-30 | 16:00 | 1.6344 | 0 | 0 | 1.5 | 86.6988 | 0 | 25439.898
2017-06-30 | 16:15 | 1.799 | 0 | 0 | 1.5 | 86.7707 | 0 | 25460.9976
2017-06-30 | 16:30 | 1.7819 | 0 | 0 | 1.5 | 84.7126 | 0 | 24857.1063
2017-06-30 | 16:45 | 1.7826 | 0 | 0 | 1.5 | 85.0037 | 0 | 24942.5143
2017-06-30 | 17:00 | 1.9207 | 0 | 0 | 1.5 | 84.7032 | 0 | 24854.3416
2017-06-30 | 17:15 | 1.7561 | 0 | 0 | 1.5 | 82.7497 | 0 | 24281.1336
2017-06-30 | 17:30 | 1.7624 | 0 | 0 | 1.5 | 82.941 | 0 | 24337.2597
2017-06-30 | 17:45 | 1.7592 | 0 | 0 | 1.5 | 83.7568 | 0 | 24576.6464
2017-06-30 | 18:00 | 1.7023 | 0 | 0 | 1.5 | 84.3786 | 0 | 24759.0856
2017-06-30 | 18:15 | 1.7764 | 0 | 0 | 1.5 | 84.5228 | 0 | 24801.4147
2017-06-30 | 18:30 | 1.8193 | 0 | 0 | 1.5 | 81.979 | 0 | 24054.9709
2017-06-30 | 18:45 | 1.7226 | 0 | 0 | 1.5 | 81.3214 | 0 | 23862.0143
2017-06-30 | 19:00 | 1.7358 | 0 | 0 | 1.5 | 81.6845 | 0 | 23968.5532
2017-06-30 | 19:15 | 1.7663 | 0 | 0 | 1.5 | 81.9404 | 0 | 24043.6522
2017-06-30 | 19:30 | 1.7904 | 0 | 0 | 1.5 | 81.8032 | 0 | 24003.3961
2017-06-30 | 19:45 | 1.7725 | 0 | 0 | 1.5 | 81.5644 | 0 | 23933.3386
2017-06-30 | 20:00 | 1.746 | 0 | 0 | 1.5 | 80.8554 | 0 | 23725.2889
2017-06-30 | 20:15 | 1.7928 | 0 | 0 | 1.5 | 79.9603 | 0 | 23462.6378
2017-06-30 | 20:30 | 1.7663 | 0 | 0 | 1.5 | 79.4064 | 0 | 23300.1118
2017-06-30 | 20:45 | 1.785 | 0 | 0 | 1.5 | 78.5229 | 0 | 23040.8477
2017-06-30 | 21:00 | 1.7429 | 0 | 0 | 1.5 | 77.9855 | 0 | 22883.1595
2017-06-30 | 21:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 21:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 21:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 22:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 22:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 22:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 22:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 23:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 23:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 23:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-30 | 23:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-01 | 0:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-01 | 0:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 0:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 0:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 0:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 0:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 0:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 1:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 1:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 1:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 1:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 1:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 1:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 1:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 1:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 2:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 2:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 2:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 2:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 2:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 2:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 2:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 2:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 3:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 3:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 3:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 3:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 3:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 3:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 3:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 3:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 4:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 4:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 4:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 4:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 4:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 4:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 4:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 4:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 5:00 | 0.02842 | 0 | 1 | 0 |  | 0 | 0
2017-07-01 | 5:00 |  |  |  | 0 | 25.375 |  | 7445.75
2017-07-01 | 5:15 | 2.1695 | 10 | 1 |  | 91.2759 | 100 | 26782.9663
2017-07-01 | 5:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 5:30 | 1.9067 | 9.3425 | 1 | 10 |  | 94.0211 | 0
2017-07-01 | 5:30 |  |  |  | 10 | 84.8824 |  | 24906.9281
2017-07-01 | 5:45 | 1.767 | 8.2713 | 1 |  | 82.281 | 83.3258 | 24143.5845
2017-07-01 | 5:45 |  |  |  | 10 |  |  | 0
2017-07-01 | 6:00 |  | 7.7134 |  | 10 |  | 78.0529 | 0
2017-07-01 | 6:00 | 1.8154 |  | 1 | 10 | 80.9515 |  | 23753.483
2017-07-01 | 6:15 | 1.8255 | 7.6914 | 1 |  | 79.7192 | 77.9594 | 23391.8775
2017-07-01 | 6:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 6:30 | 1.785 | 7.4295 | 1 | 10 |  | 75.2254 | 0
2017-07-01 | 6:30 |  |  |  | 10 | 78.9871 |  | 23177.0848
2017-07-01 | 6:45 | 1.7655 | 7.0649 | 1 |  | 78.7945 | 71.4318 | 23120.5717
2017-07-01 | 6:45 |  |  |  | 10 |  |  | 0
2017-07-01 | 7:00 | 1.7834 | 6.9936 | 1 | 10 |  | 70.8291 | 0
2017-07-01 | 7:00 |  |  |  | 10 | 78.1661 |  | 22936.1556
2017-07-01 | 7:15 | 1.8224 | 6.7267 | 1 |  | 77.5308 | 68.4231 | 22749.7519
2017-07-01 | 7:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 7:30 | 1.7351 | 6.6995 | 1 | 10 |  | 68.0906 | 0
2017-07-01 | 7:30 |  |  |  | 10 | 77.3849 |  | 22706.926
2017-07-01 | 7:45 | 1.6883 | 6.718 | 1 |  |  | 68.1618 | 0
2017-07-01 | 7:45 |  |  |  | 10 | 77.4096 |  | 22714.1769
2017-07-01 | 8:00 | 1.7717 | 6.3327 | 1 | 10 |  | 64.676 | 0
2017-07-01 | 8:00 |  |  |  | 10 | 76.6927 |  | 22503.8438
2017-07-01 | 8:15 | 1.7803 | 6.0941 | 1 |  | 76.6367 | 62.1606 | 22487.3895
2017-07-01 | 8:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 8:30 | 1.7234 | 6.195 | 1 | 10 |  | 0 | 0
2017-07-01 | 8:30 |  |  |  | 10 | 76.5779 |  | 22470.1538
2017-07-01 | 8:45 | 1.7569 | 6.6882 | 1 |  | 76.3584 | 0 | 22405.7356
2017-07-01 | 8:45 |  |  |  | 10 |  |  | 0
2017-07-01 | 9:00 | 1.7694 | 6.6649 | 1 | 10 |  | 0 | 0
2017-07-01 | 9:00 |  |  |  | 10 | 76.6886 |  | 22502.6146
2017-07-01 | 9:15 | 1.7296 | 6.5889 | 1 |  | 76.4971 | 0 | 22446.4371
2017-07-01 | 9:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 9:30 | 1.746 | 6.7746 | 1 | 10 |  | 0 | 0
2017-07-01 | 9:30 |  |  |  | 10 | 76.2829 |  | 22383.575
2017-07-01 | 9:45 | 1.7553 | 6.5105 | 1 |  | 76.1455 | 0 | 22343.2585
2017-07-01 | 9:45 |  |  |  | 10 |  |  | 0
2017-07-01 | 10:00 | 1.7865 | 6.2748 | 1 | 10 |  | 0 | 0
2017-07-01 | 10:00 |  |  |  | 10 | 76.3044 |  | 22389.9037
2017-07-01 | 10:15 | 1.728 | 6.464 | 1 |  | 76.2036 | 0 | 22360.3264
2017-07-01 | 10:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 10:30 | 1.7748 | 6.7164 | 1 | 10 |  | 0 | 0
2017-07-01 | 10:30 |  |  |  | 10 | 76.2051 |  | 22360.7516
2017-07-01 | 10:45 | 1.7772 | 6.6448 | 1 |  | 76.3917 | 0 | 22415.5121
2017-07-01 | 10:45 |  |  |  | 10 |  |  | 0
2017-07-01 | 11:00 | 1.7335 | 6.2034 | 1 | 10 |  | 0 | 0
2017-07-01 | 11:00 |  |  |  | 10 | 76.351 |  | 22403.5508
2017-07-01 | 11:15 | 1.7335 | 6.3791 | 1 |  | 76.3668 | 0 | 22408.194
2017-07-01 | 11:15 |  |  |  | 10 |  |  | 0
2017-07-01 | 11:30 | 1.7249 | 6.5898 | 1 | 10 |  | 0 | 0
2017-07-01 | 11:30 |  |  |  | 10 | 76.3749 |  | 22410.5669
2017-07-01 | 11:45 | 1.7296 | 6.3948 | 1 |  | 76.4182 | 0 | 22423.2827
2017-07-01 | 11:45 |  |  |  | 10 |  |  | 0
2017-07-01 | 12:00 | 1.7444 | 6.2386 | 1 | 10 | 76.1232 | 0 | 22336.733
2017-07-01 | 12:00 |  |  |  | 10 |  |  | 0
2017-07-01 | 12:00 |  |  | 0 |  |  |  | 0
2017-07-01 | 12:05 |  |  | 1 |  |  |  | 0
2017-07-01 | 12:14 |  |  | 0 |  |  |  | 0
2017-07-01 | 12:15 | 1.7655 | 4.551 | 0 |  | 76.3281 | 0 | 22396.855
2017-07-01 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 12:30 | 1.7663 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 12:30 |  |  |  | 1.5 | 76.6299 |  | 22485.4038
2017-07-01 | 12:45 | 1.7725 | 0 | 0 |  | 76.6828 | 0 | 22500.9113
2017-07-01 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 13:00 | 1.7546 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 13:00 |  |  |  | 1.5 | 76.5384 |  | 22458.5642
2017-07-01 | 13:15 | 1.7655 | 0 | 0 |  | 76.6974 | 0 | 22505.205
2017-07-01 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 13:30 | 1.7553 | 0 | 0 | 1.5 | 76.5762 | 0 | 22469.6344
2017-07-01 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 13:45 | 1.7062 | 0 | 0 |  | 77.1038 | 0 | 22624.4617
2017-07-01 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 14:00 | 1.7553 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 14:00 |  |  |  | 1.5 | 77.5486 |  | 22754.9726
2017-07-01 | 14:15 | 1.7725 | 0 | 0 |  | 77.5042 | 0 | 22741.9455
2017-07-01 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 14:30 | 1.728 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 14:30 |  |  |  | 1.5 | 77.5262 |  | 22748.4153
2017-07-01 | 14:45 | 1.7273 | 0 | 0 |  | 77.6096 | 0 | 22772.8708
2017-07-01 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 15:00 | 1.767 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 15:00 |  |  |  | 1.5 | 77.5694 |  | 22761.0817
2017-07-01 | 15:15 | 1.8263 | 0 | 0 |  | 77.2714 | 0 | 22673.6389
2017-07-01 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 15:30 | 1.7249 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 15:30 |  |  |  | 1.5 | 77.1794 |  | 22646.6291
2017-07-01 | 15:45 | 1.7273 | 0 | 0 |  | 77.1855 | 0 | 22648.4289
2017-07-01 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 16:00 | 1.7351 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 16:00 |  |  |  | 1.5 | 77.3109 |  | 22685.2399
2017-07-01 | 16:15 | 1.8084 | 0 | 0 |  | 77.024 | 0 | 22601.052
2017-07-01 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 16:30 | 1.728 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 16:30 |  |  |  | 1.5 | 76.9856 |  | 22589.7755
2017-07-01 | 16:45 | 1.6922 | 0 | 0 |  | 77.1155 | 0 | 22627.8801
2017-07-01 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 17:00 | 1.746 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 17:00 |  |  |  | 1.5 | 77.1 |  | 22623.3291
2017-07-01 | 17:15 | 1.7881 | 0 | 0 |  |  | 0 | 0
2017-07-01 | 17:15 |  |  |  | 1.5 | 76.9108 |  | 22567.8276
2017-07-01 | 17:30 | 1.7475 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 17:30 |  |  |  | 1.5 | 76.8592 |  | 22552.6738
2017-07-01 | 17:45 | 1.7085 | 0 | 0 |  | 76.995 | 0 | 22592.5449
2017-07-01 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 18:00 | 1.7234 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 18:00 |  |  |  | 1.5 | 77.1369 |  | 22634.173
2017-07-01 | 18:15 | 1.7748 | 0 | 0 |  | 77.0606 | 0 | 22611.7953
2017-07-01 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 18:30 | 1.7709 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 18:30 |  |  |  | 1.5 | 76.9928 |  | 22591.8776
2017-07-01 | 18:45 | 1.6984 | 0 | 0 |  | 77.1967 | 0 | 22651.7133
2017-07-01 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 19:00 | 1.7179 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 19:00 |  |  |  | 1.5 | 77.3335 |  | 22691.8505
2017-07-01 | 19:15 | 1.7717 | 0 | 0 |  |  | 0 | 0
2017-07-01 | 19:15 |  |  |  | 1.5 | 77.2644 |  | 22671.586
2017-07-01 | 19:30 | 1.7538 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 19:30 |  |  |  | 1.5 | 77.1474 |  | 22637.2649
2017-07-01 | 19:45 | 1.7171 | 0 | 0 |  | 77.1865 | 0 | 22648.718
2017-07-01 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 20:00 | 1.7358 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 20:00 |  |  |  | 1.5 | 77.2201 |  | 22658.5816
2017-07-01 | 20:15 | 1.7842 | 0 | 0 |  | 77.0399 | 0 | 22605.6949
2017-07-01 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 20:30 | 1.7943 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-01 | 20:30 |  |  |  | 1.5 | 76.575 |  | 22469.2829
2017-07-01 | 20:45 | 1.7132 | 0 | 0 |  | 76.4311 | 0 | 22427.0793
2017-07-01 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-07-01 | 21:00 | 1.739 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 21:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 21:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 21:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 21:30 | 0.03232 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 21:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 21:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 21:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 22:00 | 0.02998 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 22:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 22:15 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 22:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 22:30 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 22:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 22:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 22:45 |  |  |  | 0 |  |  | 0
2017-07-01 | 23:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 23:00 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 23:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 23:15 |  |  |  | 0 |  |  | 0
2017-07-01 | 23:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-01 | 23:30 |  |  |  | 0 | 0 |  | 0
2017-07-01 | 23:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-01 | 23:45 |  |  |  | 0 |  |  | 0
2017-07-02 | 0:00 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-02 | 0:00 |  |  |  | 0 | 0 |  | 0
2017-07-02 | 0:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 0:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 1:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 2:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 2:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 3:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 5:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 5:00 |  |  | 1 |  |  |  | 0
2017-07-02 | 5:15 | 2.2062 | 9.3847 | 1 | 10 | 87.7986 | 95.9161 | 25762.6242
2017-07-02 | 5:30 | 1.8848 | 7.9525 | 1 | 10 | 82.0346 | 81.9652 | 24071.2908
2017-07-02 | 5:45 | 1.8513 | 7.0003 | 1 | 10 | 79.7029 | 72.7057 | 23387.1113
2017-07-02 | 6:00 | 1.8045 | 6.4804 | 1 | 10 | 78.5387 | 67.5399 | 23045.5065
2017-07-02 | 6:15 | 1.7436 | 6.915 | 1 | 10 | 78.1311 | 71.5754 | 22925.8959
2017-07-02 | 6:30 | 1.7452 | 6.8133 | 1 | 10 | 77.8283 | 70.698 | 22837.0448
2017-07-02 | 6:45 | 1.8232 | 6.7583 | 1 | 10 | 77.5117 | 70.1327 | 22744.1327
2017-07-02 | 7:00 | 1.7936 | 6.3248 | 1 | 10 | 76.6258 | 66.0711 | 22484.1858
2017-07-02 | 7:15 | 1.7078 | 6.2328 | 1 | 10 | 76.9116 | 64.9167 | 22568.0583
2017-07-02 | 7:30 | 1.7195 | 6.3484 | 1 | 10 | 76.5669 | 66.2733 | 22466.9302
2017-07-02 | 7:45 | 1.7967 | 6.155 | 1 | 10 | 76.694 | 64.2336 | 22504.222
2017-07-02 | 8:00 | 1.7616 | 6.1038 | 1 | 10 | 76.4114 | 0 | 22421.3014
2017-07-02 | 8:15 | 1.7132 | 6.4709 | 1 | 10 | 76.4604 | 0 | 22435.6783
2017-07-02 | 8:30 | 1.6711 | 6.8565 | 1 | 10 | 76.765 | 0 | 22525.0531
2017-07-02 | 8:45 | 1.7249 | 7.3706 | 1 | 10 | 77.0039 | 0 | 22595.1417
2017-07-02 | 9:00 | 1.8224 | 7.0995 | 1 | 10 | 76.9066 | 0 | 22566.6029
2017-07-02 | 9:15 | 1.7241 | 6.7215 | 1 | 10 | 77.0319 | 0 | 22603.3645
2017-07-02 | 9:30 | 1.7187 | 6.7315 | 1 | 10 | 77.445 | 0 | 22724.5869
2017-07-02 | 9:45 | 1.7507 | 6.9915 | 1 | 10 | 77.661 | 0 | 22787.9528
2017-07-02 | 10:00 | 1.7678 | 7.1178 | 1 | 10 | 77.5846 | 0 | 22765.5504
2017-07-02 | 10:08 |  |  | 0 |  |  |  | 0
2017-07-02 | 10:15 | 1.7156 | 3.5791 | 0 | 1.5 | 77.856 | 0 | 22845.1646
2017-07-02 | 10:23 |  |  | 1 |  |  |  | 0
2017-07-02 | 10:30 |  |  | 0 |  |  |  | 0
2017-07-02 | 10:30 | 1.7468 | 3.0309 | 0 | 1.5 | 78.2501 | 0 | 22960.8127
2017-07-02 | 10:45 | 1.7382 | 0 | 0 | 1.5 | 78.9356 | 0 | 23161.9671
2017-07-02 | 11:00 | 1.8021 | 0 | 0 | 1.5 | 78.6485 | 0 | 23077.7053
2017-07-02 | 11:15 | 1.7733 | 0 | 0 | 1.5 | 78.2854 | 0 | 22971.171
2017-07-02 | 11:30 | 1.7374 | 0 | 0 | 1.5 | 78.3308 | 0 | 22984.498
2017-07-02 | 11:45 | 1.7202 | 0 | 0 | 1.5 | 78.4479 | 0 | 23018.8505
2017-07-02 | 12:00 | 1.7756 | 0 | 0 | 1.5 | 78.3221 | 0 | 22981.9548
2017-07-02 | 12:15 | 1.8006 | 0 | 0 | 1.5 | 78.0322 | 0 | 22896.8623
2017-07-02 | 12:30 | 1.7904 | 0 | 0 | 1.5 | 77.8165 | 0 | 22833.5906
2017-07-02 | 12:45 | 1.7686 | 0 | 0 | 1.5 | 77.2649 | 0 | 22671.7204
2017-07-02 | 13:00 | 1.76 | 0 | 0 | 1.5 | 77.067 | 0 | 22613.6556
2017-07-02 | 13:15 | 1.7491 | 0 | 0 | 1.5 | 77.0005 | 0 | 22594.1611
2017-07-02 | 13:30 | 1.7709 | 0 | 0 | 1.5 | 76.9342 | 0 | 22574.6801
2017-07-02 | 13:45 | 1.7452 | 0 | 0 | 1.5 | 76.924 | 0 | 22571.7006
2017-07-02 | 14:00 | 1.7436 | 0 | 0 | 1.5 | 76.9688 | 0 | 22584.8348
2017-07-02 | 14:15 | 1.7585 | 0 | 0 | 1.5 | 76.9898 | 0 | 22591.0047
2017-07-02 | 14:30 | 1.7561 | 0 | 0 | 1.5 | 76.9928 | 0 | 22591.8732
2017-07-02 | 14:45 | 1.7483 | 0 | 0 | 1.5 | 76.9785 | 0 | 22587.6913
2017-07-02 | 15:00 | 1.7382 | 0 | 0 | 1.5 | 77.0008 | 0 | 22594.2262
2017-07-02 | 15:15 | 1.76 | 0 | 0 | 1.5 | 77.0061 | 0 | 22595.8022
2017-07-02 | 15:30 | 1.7569 | 0 | 0 | 1.5 | 77.0221 | 0 | 22600.481
2017-07-02 | 15:45 | 1.7499 | 0 | 0 | 1.5 | 77.0078 | 0 | 22596.2791
2017-07-02 | 16:00 | 1.739 | 0 | 0 | 1.5 | 76.9922 | 0 | 22591.7077
2017-07-02 | 16:15 | 1.7514 | 0 | 0 | 1.5 | 77.004 | 0 | 22595.1799
2017-07-02 | 16:30 | 1.7577 | 0 | 0 | 1.5 | 77.0023 | 0 | 22594.6737
2017-07-02 | 16:45 | 1.76 | 0 | 0 | 1.5 | 77.0278 | 0 | 22602.1711
2017-07-02 | 17:00 | 1.7577 | 0 | 0 | 1.5 | 77.0976 | 0 | 22622.6328
2017-07-02 | 17:15 | 1.76 | 0 | 0 | 1.5 | 77.0517 | 0 | 22609.1603
2017-07-02 | 17:30 | 1.7491 | 0 | 0 | 1.5 | 77.0381 | 0 | 22605.1755
2017-07-02 | 17:45 | 1.7421 | 0 | 0 | 1.5 | 77.0657 | 0 | 22613.2662
2017-07-02 | 18:00 | 1.7366 | 0 | 0 | 1.5 | 77.1392 | 0 | 22634.8315
2017-07-02 | 18:15 | 1.7491 | 0 | 0 | 1.5 | 77.2243 | 0 | 22659.8105
2017-07-02 | 18:30 | 1.753 | 0 | 0 | 1.5 | 77.3313 | 0 | 22691.2102
2017-07-02 | 18:45 | 1.7475 | 0 | 0 | 1.5 | 77.4212 | 0 | 22717.5865
2017-07-02 | 19:00 | 1.7709 | 0 | 0 | 1.5 | 77.4794 | 0 | 22734.6609
2017-07-02 | 19:15 | 1.7483 | 0 | 0 | 1.5 | 77.4822 | 0 | 22735.4916
2017-07-02 | 19:30 | 1.7483 | 0 | 0 | 1.5 | 77.389 | 0 | 22708.1393
2017-07-02 | 19:45 | 1.7686 | 0 | 0 | 1.5 | 77.2485 | 0 | 22666.905
2017-07-02 | 20:00 | 1.767 | 0 | 0 | 1.5 | 76.947 | 0 | 22578.45
2017-07-02 | 20:15 | 1.7538 | 0 | 0 | 1.5 | 76.5829 | 0 | 22471.6203
2017-07-02 | 20:30 | 1.7351 | 0 | 0 | 1.5 | 76.2642 | 0 | 22378.0859
2017-07-02 | 20:45 | 1.7795 | 0 | 0 | 1.5 | 75.8425 | 0 | 22254.3605
2017-07-02 | 21:00 | 1.7678 | 0 | 0 | 1.5 | 75.8483 | 0 | 22256.0463
2017-07-02 | 21:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 21:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 21:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 22:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 22:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 22:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 23:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-02 | 23:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 0:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 0:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 0:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 1:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 1:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 4:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 4:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 4:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 5:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-03 | 5:15 | 2.2662 | 10 | 1 | 10 | 89.0908 | 100 | 26141.79
2017-07-03 | 5:30 | 1.9589 | 9.1056 | 1 | 10 | 82.9485 | 91.0842 | 24339.4736
2017-07-03 | 5:45 | 1.8287 | 7.7501 | 1 | 10 | 80.2838 | 78.5263 | 23557.5514
2017-07-03 | 6:00 | 1.8084 | 7.1029 | 1 | 10 | 78.7666 | 72.0656 | 23112.3624
2017-07-03 | 6:15 | 1.8404 | 7.1607 | 1 | 10 | 77.5993 | 72.3936 | 22769.8485
2017-07-03 | 6:30 | 1.792 | 6.6431 | 1 | 10 | 76.9207 | 67.7346 | 22570.7402
2017-07-03 | 6:45 | 1.7413 | 7.2453 | 1 | 10 | 76.762 | 73.1628 | 22524.1531
2017-07-03 | 7:00 | 1.7546 | 6.8097 | 1 | 10 | 76.5892 | 69.2391 | 22473.4604
2017-07-03 | 7:15 | 1.8224 | 6.1899 | 1 | 10 | 76.1879 | 63.4476 | 22355.7125
2017-07-03 | 7:30 | 1.792 | 6.1996 | 1 | 10 | 75.9291 | 0 | 22279.7808
2017-07-03 | 7:45 | 1.7234 | 6.6442 | 1 | 10 | 76.1102 | 0 | 22332.9114
2017-07-03 | 8:00 | 1.7226 | 6.1665 | 1 | 10 | 76.219 | 0 | 22364.8373
2017-07-03 | 8:15 | 1.7811 | 6.6078 | 1 | 10 | 76.229 | 0 | 22367.7633
2017-07-03 | 8:30 | 1.7631 | 6.0053 | 1 | 10 | 76.2726 | 0 | 22380.5483
2017-07-03 | 8:45 | 1.7351 | 6.3637 | 1 | 10 | 76.5425 | 0 | 22459.7641
2017-07-03 | 9:00 | 1.7093 | 5.1594 | 1 | 10 | 76.916 | 0 | 22569.3432
2017-07-03 | 9:15 | 1.7452 | 5.3009 | 1 | 10 | 77.2173 | 0 | 22657.7755
2017-07-03 | 9:30 | 1.7538 | 4.6118 | 1 | 10 | 77.6655 | 0 | 22789.2893
2017-07-03 | 9:45 | 1.7163 | 4.6099 | 1 | 10 | 77.7806 | 0 | 22823.0418
2017-07-03 | 10:00 | 1.7507 | 4.9005 | 1 | 10 | 78.3479 | 0 | 22989.5171
2017-07-03 | 10:15 | 1.7187 | 5.4714 | 1 | 10 | 78.5763 | 0 | 23056.5385
2017-07-03 | 10:30 | 1.8029 | 5.6985 | 1 | 10 | 78.6761 | 0 | 23085.8162
2017-07-03 | 10:45 | 1.7179 | 4.6778 | 1 | 10 | 78.7488 | 0 | 23107.162
2017-07-03 | 11:00 | 1.6391 | 5.2984 | 1 | 10 | 79.764 | 0 | 23405.0322
2017-07-03 | 11:07 |  |  | 0 |  |  |  | 0
2017-07-03 | 11:09 |  |  | 1 |  |  |  | 0
2017-07-03 | 11:15 | 1.7444 | 4.9614 | 1 | 10 | 79.8904 | 0 | 23442.1339
2017-07-03 | 11:30 | 1.7897 | 4.917 | 1 | 10 | 79.1755 | 0 | 23232.3671
2017-07-03 | 11:39 |  |  | 0 |  |  |  | 0
2017-07-03 | 11:45 | 1.6812 | 1.4087 | 0 | 1.5 | 79.9952 | 0 | 23472.8866
2017-07-03 | 12:00 | 1.7351 | 0 | 0 | 1.5 | 80.0887 | 0 | 23500.3237
2017-07-03 | 12:15 | 1.7741 | 0 | 0 | 1.5 | 80.3187 | 0 | 23567.7999
2017-07-03 | 12:30 | 1.8115 | 0 | 0 | 1.5 | 80.2433 | 0 | 23545.6863
2017-07-03 | 12:45 | 1.7039 | 0 | 0 | 1.5 | 80.0209 | 0 | 23480.4219
2017-07-03 | 13:00 | 1.6859 | 0 | 0 | 1.5 | 80.0719 | 0 | 23495.3853
2017-07-03 | 13:15 | 1.7468 | 0 | 0 | 1.5 | 80.8429 | 0 | 23721.6243
2017-07-03 | 13:30 | 1.7803 | 0 | 0 | 1.5 | 80.6839 | 0 | 23674.9724
2017-07-03 | 13:45 | 1.6937 | 0 | 0 | 1.5 | 80.9506 | 0 | 23753.2189
2017-07-03 | 14:00 | 1.7093 | 0 | 0 | 1.5 | 81.5532 | 0 | 23930.0299
2017-07-03 | 14:15 | 1.7249 | 0 | 0 | 1.5 | 82.4127 | 0 | 24182.2355
2017-07-03 | 14:30 | 1.7951 | 0 | 0 | 1.5 | 82.6757 | 0 | 24259.4228
2017-07-03 | 14:45 | 1.7257 | 0 | 0 | 1.5 | 83.9965 | 0 | 24646.9657
2017-07-03 | 15:00 | 1.6633 | 0 | 0 | 1.5 | 85.0844 | 0 | 24966.186
2017-07-03 | 15:15 | 1.7358 | 0 | 0 | 1.5 | 85.982 | 0 | 25229.5895
2017-07-03 | 15:30 | 1.8482 | 0 | 0 | 1.5 | 86.5714 | 0 | 25402.5322
2017-07-03 | 15:45 | 1.8037 | 0 | 0 | 1.5 | 85.6908 | 0 | 25144.1255
2017-07-03 | 16:00 | 1.6103 | 0 | 0 | 1.5 | 86.151 | 0 | 25279.1628
2017-07-03 | 16:15 | 1.7569 | 0 | 0 | 1.5 | 85.8567 | 0 | 25192.7945
2017-07-03 | 16:30 | 1.8248 | 0 | 0 | 1.5 | 85.5158 | 0 | 25092.7814
2017-07-03 | 16:45 | 1.8279 | 0 | 0 | 1.5 | 84.4443 | 0 | 24778.3809
2017-07-03 | 17:00 | 1.7624 | 0 | 0 | 1.5 | 84.0039 | 0 | 24649.1552
2017-07-03 | 17:15 | 1.7538 | 0 | 0 | 1.5 | 83.7342 | 0 | 24569.9952
2017-07-03 | 17:30 | 1.8255 | 0 | 0 | 1.5 | 83.1421 | 0 | 24396.2802
2017-07-03 | 17:45 | 1.8232 | 0 | 0 | 1.5 | 82.2918 | 0 | 24146.7724
2017-07-03 | 18:00 | 1.7374 | 0 | 0 | 1.5 | 81.5652 | 0 | 23933.5672
2017-07-03 | 18:15 | 1.721 | 0 | 0 | 1.5 | 81.1268 | 0 | 23804.9301
2017-07-03 | 18:30 | 1.7546 | 0 | 0 | 1.5 | 80.9821 | 0 | 23762.4602
2017-07-03 | 18:45 | 1.8154 | 0 | 0 | 1.5 | 80.4996 | 0 | 23620.87
2017-07-03 | 19:00 | 1.7616 | 0 | 0 | 1.5 | 80.5313 | 0 | 23630.1852
2017-07-03 | 19:15 | 1.7351 | 0 | 0 | 1.5 | 80.5007 | 0 | 23621.1992
2017-07-03 | 19:30 | 1.778 | 0 | 0 | 1.5 | 80.1475 | 0 | 23517.5685
2017-07-03 | 19:45 | 1.8279 | 0 | 0 | 1.5 | 79.4664 | 0 | 23317.7055
2017-07-03 | 20:00 | 1.7655 | 0 | 0 | 1.5 | 78.7666 | 0 | 23112.3803
2017-07-03 | 20:15 | 1.7647 | 0 | 0 | 1.5 | 78.3131 | 0 | 22979.2972
2017-07-03 | 20:30 | 1.7702 | 0 | 0 | 1.5 | 77.9808 | 0 | 22881.7915
2017-07-03 | 20:45 | 1.8107 | 0 | 0 | 1.5 | 77.7027 | 0 | 22800.1917
2017-07-03 | 21:00 | 1.7491 | 0 | 0 | 1.5 | 77.3157 | 0 | 22686.6413
2017-07-03 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 22:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 22:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 22:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 23:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 1:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 2:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 2:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 2:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 2:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 3:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 4:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 4:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 5:00 | 0.03232 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-04 | 5:15 | 2.2304 | 9.1462 | 1 | 10 | 89.7913 | 93.6706 | 26347.3411
2017-07-04 | 5:30 | 1.9129 | 7.4102 | 1 | 10 | 83.6134 | 76.5881 | 24534.5705
2017-07-04 | 5:45 | 1.8107 | 6.4968 | 1 | 10 | 80.9875 | 67.5049 | 23764.0564
2017-07-04 | 6:00 | 1.8068 | 5.9728 | 1 | 10 | 79.574 | 0 | 23349.2778
2017-07-04 | 6:15 | 1.7967 | 6.7552 | 1 | 10 | 78.8407 | 0 | 23134.1201
2017-07-04 | 6:30 | 1.7218 | 6.793 | 1 | 10 | 78.4563 | 0 | 23021.3106
2017-07-04 | 6:45 | 1.7241 | 6.8168 | 1 | 10 | 78.3651 | 0 | 22994.5473
2017-07-04 | 7:00 | 1.7429 | 6.8424 | 1 | 10 | 78.3655 | 0 | 22994.6706
2017-07-04 | 7:15 | 1.7811 | 6.6584 | 1 | 10 | 78.3197 | 0 | 22981.2271
2017-07-04 | 7:30 | 1.76 | 6.3666 | 1 | 10 | 77.6039 | 0 | 22771.1939
2017-07-04 | 7:45 | 1.7507 | 7.3886 | 1 | 10 | 77.4711 | 0 | 22732.2363
2017-07-04 | 8:00 | 1.7663 | 7.2842 | 1 | 10 | 77.375 | 0 | 22704.0381
2017-07-04 | 8:15 | 1.7975 | 7.6536 | 1 | 10 | 77.3313 | 0 | 22691.2193
2017-07-04 | 8:30 | 1.7468 | 7.2431 | 1 | 10 | 77.5148 | 0 | 22745.0506
2017-07-04 | 8:45 | 1.6898 | 7.2562 | 1 | 10 | 77.8615 | 0 | 22846.7875
2017-07-04 | 9:00 | 1.7288 | 7.8411 | 1 | 10 | 78.0092 | 0 | 22890.1261
2017-07-04 | 9:15 | 1.778 | 6.8596 | 1 | 10 | 78.3753 | 0 | 22997.545
2017-07-04 | 9:30 | 1.7444 | 7.1109 | 1 | 10 | 78.4939 | 0 | 23032.3676
2017-07-04 | 9:45 | 1.6953 | 7.5044 | 1 | 10 | 79.249 | 0 | 23253.9144
2017-07-04 | 10:00 | 1.7335 | 7.1289 | 1 | 10 | 79.2882 | 0 | 23265.4189
2017-07-04 | 10:15 | 1.7936 | 6.7173 | 1 | 10 | 79.1091 | 0 | 23212.8837
2017-07-04 | 10:20 |  |  | 0 |  |  |  | 0
2017-07-04 | 10:30 | 1.7709 | 0 | 0 | 1.5 | 79.116 | 0 | 23214.9051
2017-07-04 | 10:45 | 1.6992 | 0 | 0 | 1.5 | 79.2538 | 0 | 23255.3226
2017-07-04 | 11:00 | 1.7265 | 0 | 0 | 1.5 | 79.2016 | 0 | 23240.0076
2017-07-04 | 11:15 | 1.7967 | 0 | 0 | 1.5 | 79.0066 | 0 | 23182.7914
2017-07-04 | 11:30 | 1.778 | 0 | 0 | 1.5 | 78.9029 | 0 | 23152.3723
2017-07-04 | 11:45 | 1.7296 | 0 | 0 | 1.5 | 78.9801 | 0 | 23175.012
2017-07-04 | 12:00 | 1.7288 | 0 | 0 | 1.5 | 79.0167 | 0 | 23185.7509
2017-07-04 | 12:15 | 1.7811 | 0 | 0 | 1.5 | 78.8812 | 0 | 23146.0055
2017-07-04 | 12:30 | 1.7756 | 0 | 0 | 1.5 | 78.6088 | 0 | 23066.0597
2017-07-04 | 12:45 | 1.7374 | 0 | 0 | 1.5 | 78.5162 | 0 | 23038.9046
2017-07-04 | 13:00 | 1.7078 | 0 | 0 | 1.5 | 78.8276 | 0 | 23130.2583
2017-07-04 | 13:15 | 1.7702 | 0 | 0 | 1.5 | 79.0731 | 0 | 23202.3194
2017-07-04 | 13:30 | 1.7748 | 0 | 0 | 1.5 | 79.0101 | 0 | 23183.8123
2017-07-04 | 13:45 | 1.7062 | 0 | 0 | 1.5 | 79.1189 | 0 | 23215.7335
2017-07-04 | 14:00 | 1.714 | 0 | 0 | 1.5 | 79.3286 | 0 | 23277.2684
2017-07-04 | 14:15 | 1.7522 | 0 | 0 | 1.5 | 79.3903 | 0 | 23295.3902
2017-07-04 | 14:30 | 1.7819 | 0 | 0 | 1.5 | 79.1989 | 0 | 23239.2286
2017-07-04 | 14:45 | 1.7351 | 0 | 0 | 1.5 | 79.3034 | 0 | 23269.8919
2017-07-04 | 15:00 | 1.7078 | 0 | 0 | 1.5 | 79.4947 | 0 | 23326.011
2017-07-04 | 15:15 | 1.7351 | 0 | 0 | 1.5 | 79.6247 | 0 | 23364.1605
2017-07-04 | 15:30 | 1.7694 | 0 | 0 | 1.5 | 79.3048 | 0 | 23270.2836
2017-07-04 | 15:45 | 1.7772 | 0 | 0 | 1.5 | 78.9705 | 0 | 23172.2136
2017-07-04 | 16:00 | 1.7156 | 0 | 0 | 1.5 | 79.0178 | 0 | 23186.0667
2017-07-04 | 16:15 | 1.7312 | 0 | 0 | 1.5 | 79.0779 | 0 | 23203.7141
2017-07-04 | 16:30 | 1.7982 | 0 | 0 | 1.5 | 78.9492 | 0 | 23165.9586
2017-07-04 | 16:45 | 1.7725 | 0 | 0 | 1.5 | 78.8856 | 0 | 23147.2836
2017-07-04 | 17:00 | 1.7351 | 0 | 0 | 1.5 | 78.8563 | 0 | 23138.7029
2017-07-04 | 17:15 | 1.7218 | 0 | 0 | 1.5 | 78.9127 | 0 | 23155.2488
2017-07-04 | 17:30 | 1.7858 | 0 | 0 | 1.5 | 78.7219 | 0 | 23099.2415
2017-07-04 | 17:45 | 1.7709 | 0 | 0 | 1.5 | 78.5174 | 0 | 23039.2359
2017-07-04 | 18:00 | 1.7234 | 0 | 0 | 1.5 | 78.6277 | 0 | 23071.6207
2017-07-04 | 18:15 | 1.7616 | 0 | 0 | 1.5 | 78.3045 | 0 | 22976.7676
2017-07-04 | 18:30 | 1.7748 | 0 | 0 | 1.5 | 77.9696 | 0 | 22878.5051
2017-07-04 | 18:45 | 1.7468 | 0 | 0 | 1.5 | 77.8777 | 0 | 22851.556
2017-07-04 | 19:00 | 1.7585 | 0 | 0 | 1.5 | 77.8181 | 0 | 22834.0516
2017-07-04 | 19:15 | 1.753 | 0 | 0 | 1.5 | 77.8416 | 0 | 22840.9377
2017-07-04 | 19:30 | 1.76 | 0 | 0 | 1.5 | 77.816 | 0 | 22833.4406
2017-07-04 | 19:45 | 1.7452 | 0 | 0 | 1.5 | 77.7852 | 0 | 22824.4119
2017-07-04 | 20:00 | 1.7725 | 0 | 0 | 1.5 | 77.4906 | 0 | 22737.9496
2017-07-04 | 20:15 | 1.7717 | 0 | 0 | 1.5 | 77.0732 | 0 | 22615.469
2017-07-04 | 20:30 | 1.7561 | 0 | 0 | 1.5 | 76.6585 | 0 | 22493.7897
2017-07-04 | 20:45 | 1.7694 | 0 | 0 | 1.5 | 76.2447 | 0 | 22372.3681
2017-07-04 | 21:00 | 1.7124 | 0 | 0 | 1.5 | 76.4616 | 0 | 22436.0116
2017-07-04 | 21:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 21:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 21:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 22:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 22:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 22:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 23:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 23:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-04 | 23:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 0:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 0:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 0:15 |  |  |  | 0 |  |  | 0
2017-07-05 | 0:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 0:30 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 0:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 0:45 |  |  |  | 0 |  |  | 0
2017-07-05 | 1:00 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 1:00 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 1:15 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 1:15 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 1:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 1:30 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 1:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 1:45 |  |  |  | 0 |  |  | 0
2017-07-05 | 2:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 2:00 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 2:15 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 2:15 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 2:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 2:30 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 2:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 2:45 |  |  |  | 0 |  |  | 0
2017-07-05 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 3:00 |  |  |  | 0 |  |  | 0
2017-07-05 | 3:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 3:15 |  |  |  | 0 |  |  | 0
2017-07-05 | 3:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 3:30 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 3:45 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 3:45 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 4:00 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 4:00 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 4:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 4:15 |  |  |  | 0 |  |  | 0
2017-07-05 | 4:30 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 4:30 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 4:45 | 0.0292 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 4:45 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 5:00 | 0.0292 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 5:00 |  |  |  | 1.5 | 25 |  | 7335.7143
2017-07-05 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-05 | 5:15 | 2.1921 | 9.8172 | 1 |  | 90.9927 | 98.5432 | 26699.8442
2017-07-05 | 5:15 |  |  |  | 10 |  |  | 0
2017-07-05 | 5:30 | 1.9285 | 8.1431 | 1 | 10 |  | 82.3518 | 0
2017-07-05 | 5:30 |  |  |  | 10 | 84.6449 |  | 24837.2359
2017-07-05 | 5:45 | 1.8404 | 7.0025 | 1 |  | 81.834 | 71.3943 | 24012.4405
2017-07-05 | 5:45 |  |  |  | 10 |  |  | 0
2017-07-05 | 6:00 | 1.817 | 6.2364 | 1 | 10 | 80.4605 | 63.4877 | 23609.4105
2017-07-05 | 6:00 |  |  |  | 10 |  |  | 0
2017-07-05 | 6:15 | 1.7951 | 6.2115 | 1 |  | 79.2578 | 63.3059 | 23256.4887
2017-07-05 | 6:15 |  |  |  | 10 |  |  | 0
2017-07-05 | 6:30 | 1.7468 | 5.7673 | 1 | 10 | 78.5986 | 0 | 23063.0778
2017-07-05 | 6:30 |  |  |  | 10 |  |  | 0
2017-07-05 | 6:39 |  |  | 0 |  |  |  | 0
2017-07-05 | 6:45 | 1.7015 | 2.8693 | 0 |  | 78.5987 | 0 | 23063.0913
2017-07-05 | 6:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 7:00 | 1.7694 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 7:00 |  |  |  | 1.5 | 78.0786 |  | 22910.5026
2017-07-05 | 7:02 |  |  | 1 |  |  |  | 0
2017-07-05 | 7:15 | 1.7951 | 3.4254 | 1 |  | 77.6702 | 0 | 22790.6614
2017-07-05 | 7:15 |  |  |  | 10 |  |  | 0
2017-07-05 | 7:30 | 1.7241 | 3.71 | 1 | 10 |  | 0 | 0
2017-07-05 | 7:30 |  |  |  | 10 | 77.715 |  | 22803.8003
2017-07-05 | 7:45 | 1.7327 | 3.1407 | 1 |  | 77.7891 | 0 | 22825.5424
2017-07-05 | 7:45 |  |  |  | 10 |  |  | 0
2017-07-05 | 8:00 | 1.7031 | 2.4956 | 1 | 10 |  | 0 | 0
2017-07-05 | 8:00 |  |  |  | 10 | 78.6241 |  | 23070.5482
2017-07-05 | 8:15 | 1.7787 | 3.6535 | 1 |  | 78.8684 | 0 | 23142.2287
2017-07-05 | 8:15 |  |  |  | 10 |  |  | 0
2017-07-05 | 8:26 |  |  | 0 |  |  |  | 0
2017-07-05 | 8:30 | 1.6828 | 1.0134 | 0 | 1.5 | 79.1718 | 0 | 23231.2655
2017-07-05 | 8:30 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 8:45 | 1.6968 | 0 | 0 |  | 79.8915 | 0 | 23442.4361
2017-07-05 | 8:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 9:00 | 1.7273 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 9:00 |  |  |  | 1.5 | 80.531 |  | 23630.0957
2017-07-05 | 9:15 | 1.76 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 9:15 |  |  |  | 1.5 | 81.0842 |  | 23792.4092
2017-07-05 | 9:30 | 1.785 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 9:30 |  |  |  | 1.5 | 81.4585 |  | 23902.2413
2017-07-05 | 9:45 | 1.7507 | 0 | 0 |  | 81.487 | 0 | 23910.6049
2017-07-05 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 10:00 | 1.7117 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 10:00 |  |  |  | 1.5 | 82.3738 |  | 24170.8361
2017-07-05 | 10:15 | 1.7546 | 0 | 0 |  | 83.1994 | 0 | 24413.0682
2017-07-05 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 10:30 | 1.7405 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 10:30 |  |  |  | 1.5 | 83.4314 |  | 24481.1489
2017-07-05 | 10:45 | 1.6344 | 0 | 0 |  | 84.4456 | 0 | 24778.7436
2017-07-05 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 11:00 | 1.7429 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 11:00 |  |  |  | 1.5 | 85.7102 |  | 25149.8095
2017-07-05 | 11:15 | 1.6766 | 0 | 0 |  | 86.1487 | 0 | 25278.4867
2017-07-05 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 11:30 | 1.7054 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 11:30 |  |  |  | 1.5 | 86.5142 |  | 25385.7331
2017-07-05 | 11:45 | 1.8474 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 11:45 |  |  |  | 1.5 | 87.2075 |  | 25589.1645
2017-07-05 | 12:00 | 1.799 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 12:00 |  |  |  | 1.5 | 84.7043 |  | 24854.6573
2017-07-05 | 12:15 | 1.7405 | 0 | 0 |  | 85.0808 | 0 | 24965.1496
2017-07-05 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 12:30 | 1.6828 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 12:30 |  |  |  | 1.5 | 86.6448 |  | 25424.0593
2017-07-05 | 12:45 | 1.87 | 0 | 0 |  | 85.6636 | 0 | 25136.1513
2017-07-05 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 13:00 | 1.6844 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 13:00 |  |  |  | 1.5 | 85.479 |  | 25081.9709
2017-07-05 | 13:15 | 1.6828 | 0 | 0 |  | 87.9326 | 0 | 25801.9445
2017-07-05 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 13:30 | 1.948 | 0 | 0 | 1.5 | 86.3425 | 0 | 25335.3494
2017-07-05 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 13:45 | 1.7015 | 0 | 0 |  | 85.2803 | 0 | 25023.6622
2017-07-05 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 14:00 | 1.5713 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 14:00 |  |  |  | 1.5 | 87.359 |  | 25633.6181
2017-07-05 | 14:15 | 1.8762 | 0 | 0 |  | 88.422 | 0 | 25945.5315
2017-07-05 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 14:30 | 1.8224 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 14:30 |  |  |  | 1.5 | 85.3421 |  | 25041.8246
2017-07-05 | 14:45 | 1.6173 | 0 | 0 |  | 85.6949 | 0 | 25145.3435
2017-07-05 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 15:00 | 1.8255 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 15:00 |  |  |  | 1.5 | 87.1843 |  | 25582.3766
2017-07-05 | 15:15 | 1.9074 | 0 | 0 |  | 84.4413 | 0 | 24777.5012
2017-07-05 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 15:30 | 1.6641 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 15:30 |  |  |  | 1.5 | 85.0427 |  | 24953.963
2017-07-05 | 15:45 | 1.7639 | 0 | 0 |  | 86.5411 | 0 | 25393.6378
2017-07-05 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 16:00 | 1.8879 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 16:00 |  |  |  | 1.5 | 83.9567 |  | 24635.2998
2017-07-05 | 16:15 | 1.7124 | 0 | 0 |  | 84.6891 | 0 | 24850.1887
2017-07-05 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 16:30 | 1.721 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 16:30 |  |  |  | 1.5 | 87.2084 |  | 25589.4442
2017-07-05 | 16:45 | 1.8911 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 16:45 |  |  |  | 1.5 | 84.6381 |  | 24835.2388
2017-07-05 | 17:00 | 1.6617 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 17:00 |  |  |  | 1.5 | 84.8544 |  | 24898.6966
2017-07-05 | 17:15 | 1.9106 | 0 | 0 |  | 85.487 | 0 | 25084.3327
2017-07-05 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 17:30 | 1.8599 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 17:30 |  |  |  | 1.5 | 82.215 |  | 24124.2268
2017-07-05 | 17:45 | 1.7265 | 0 | 0 |  | 81.7629 | 0 | 23991.5736
2017-07-05 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 18:00 | 1.6875 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 18:00 |  |  |  | 1.5 | 83.1041 |  | 24385.1094
2017-07-05 | 18:15 | 1.8794 | 0 | 0 |  | 81.9261 | 0 | 24039.4702
2017-07-05 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 18:30 | 1.7475 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 18:30 |  |  |  | 1.5 | 81.531 |  | 23923.5175
2017-07-05 | 18:45 | 1.7 | 0 | 0 |  | 82.9819 | 0 | 24349.2545
2017-07-05 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 19:00 | 1.7195 | 0 | 0 | 1.5 | 84.5445 | 0 | 24807.7771
2017-07-05 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 19:15 | 1.7842 | 0 | 0 |  | 82.4443 | 0 | 24191.5058
2017-07-05 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 19:30 | 1.7023 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 19:30 |  |  |  | 1.5 | 82.3042 |  | 24150.4035
2017-07-05 | 19:45 | 1.6812 | 0 | 0 |  | 83.2627 | 0 | 24431.6448
2017-07-05 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 20:00 | 1.7702 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 20:00 |  |  |  | 1.5 | 83.1383 |  | 24395.1544
2017-07-05 | 20:15 | 1.7741 | 0 | 0 |  | 83.0218 | 0 | 24360.9629
2017-07-05 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 20:30 | 1.7717 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-05 | 20:30 |  |  |  | 1.5 | 82.3677 |  | 24169.0451
2017-07-05 | 20:45 | 1.8263 | 0 | 0 |  | 81.692 | 0 | 23970.7783
2017-07-05 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-07-05 | 21:00 | 1.8162 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 21:00 |  |  |  | 0 | 80.5678 |  | 23640.8997
2017-07-05 | 21:15 | 0.03232 | 0 | 0 |  |  | 0 | 0
2017-07-05 | 21:15 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 21:30 |  |  |  | 0 |  |  | 0
2017-07-05 | 21:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 21:45 |  |  |  | 0 |  |  | 0
2017-07-05 | 22:00 | 0.02998 | 0 | 0 | 0 |  | 0 | 0
2017-07-05 | 22:00 |  |  |  | 0 | 0 |  | 0
2017-07-05 | 22:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 22:15 |  |  |  | 0 |  |  | 0
2017-07-05 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 22:30 |  |  |  | 0 |  |  | 0
2017-07-05 | 22:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 22:45 |  |  |  | 0 |  |  | 0
2017-07-05 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 23:00 |  |  |  | 0 |  |  | 0
2017-07-05 | 23:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 23:15 |  |  |  | 0 |  |  | 0
2017-07-05 | 23:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-05 | 23:30 |  |  |  | 0 |  |  | 0
2017-07-05 | 23:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-05 | 23:45 |  |  |  | 0 |  |  | 0
2017-07-06 | 0:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-06 | 0:00 |  |  |  | 0 | 0 |  | 0
2017-07-06 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 1:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 3:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 4:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 4:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 4:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 5:00 | 0.02998 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-06 | 5:15 | 2.207 | 9.9972 | 1 | 10 | 91.2331 | 99.9793 | 26770.4029
2017-07-06 | 5:30 | 1.9074 | 8.6906 | 1 | 10 | 84.9233 | 87.6167 | 24918.9164
2017-07-06 | 5:45 | 1.8209 | 8.1029 | 1 | 10 | 83.2902 | 81.8426 | 24439.7353
2017-07-06 | 6:00 | 1.8224 | 7.4463 | 1 | 10 | 82.2848 | 75.3856 | 24144.7151
2017-07-06 | 6:15 | 1.7803 | 7.1891 | 1 | 10 | 81.1897 | 72.6612 | 23823.3792
2017-07-06 | 6:30 | 1.7967 | 6.1658 | 1 | 10 | 79.277 | 62.8837 | 23262.1281
2017-07-06 | 6:45 | 1.8528 | 6.1528 | 1 | 10 | 78.3236 | 0 | 22982.3912
2017-07-06 | 7:00 | 1.7327 | 5.2187 | 1 | 10 | 78.0835 | 0 | 22911.9398
2017-07-06 | 7:15 | 1.7257 | 5.4816 | 1 | 10 | 77.7266 | 0 | 22807.1943
2017-07-06 | 7:30 | 1.7273 | 4.9958 | 1 | 10 | 77.8496 | 0 | 22843.3019
2017-07-06 | 7:45 | 1.6976 | 4.609 | 1 | 10 | 78.2714 | 0 | 22967.0718
2017-07-06 | 8:00 | 1.6719 | 3.9454 | 1 | 10 | 79.058 | 0 | 23197.8889
2017-07-06 | 8:15 | 1.7327 | 5.0969 | 1 | 10 | 79.7289 | 0 | 23394.7229
2017-07-06 | 8:30 | 1.7585 | 5.28 | 1 | 10 | 79.7794 | 0 | 23409.5653
2017-07-06 | 8:45 | 1.7686 | 5.7418 | 1 | 10 | 79.8324 | 0 | 23425.113
2017-07-06 | 9:00 | 1.7553 | 5.3878 | 1 | 10 | 80.4898 | 0 | 23618.0067
2017-07-06 | 9:15 | 1.7397 | 5.7388 | 1 | 10 | 80.8034 | 0 | 23710.028
2017-07-06 | 9:30 | 1.7452 | 6.2073 | 1 | 10 | 82.2565 | 0 | 24136.4208
2017-07-06 | 9:42 |  |  | 0 |  |  |  | 0
2017-07-06 | 9:45 | 1.6103 | 4.9773 | 0 | 1.5 | 83.2042 | 0 | 24414.4851
2017-07-06 | 10:00 | 1.6836 | 0 | 0 | 1.5 | 85.0516 | 0 | 24956.5689
2017-07-06 | 10:15 | 1.7499 | 0 | 0 | 1.5 | 85.603 | 0 | 25118.3807
2017-07-06 | 10:30 | 1.7397 | 0 | 0 | 1.5 | 86.296 | 0 | 25321.7067
2017-07-06 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 87.4321 | 0 | 25655.0712
2017-07-06 | 11:00 | 1.8131 | 0 | 0 | 1.5 | 88.0227 | 0 | 25828.3833
2017-07-06 | 11:15 | 1.6929 | 0 | 0 | 1.5 | 89.2729 | 0 | 26195.2092
2017-07-06 | 11:30 | 1.6758 | 0 | 0 | 1.5 | 91.0049 | 0 | 26703.4507
2017-07-06 | 11:45 | 1.9145 | 0 | 0 | 1.5 | 90.7356 | 0 | 26624.4072
2017-07-06 | 12:00 | 1.7865 | 0 | 0 | 1.5 | 90.0334 | 0 | 26418.3702
2017-07-06 | 12:15 | 1.6656 | 0 | 0 | 1.5 | 91.1224 | 0 | 26737.9218
2017-07-06 | 12:30 | 1.8661 | 0 | 0 | 1.5 | 91.4964 | 0 | 26847.6621
2017-07-06 | 12:45 | 1.8279 | 0 | 0 | 1.5 | 87.9554 | 0 | 25808.6156
2017-07-06 | 13:00 | 1.7312 | 0 | 0 | 1.5 | 87.6406 | 0 | 25716.2499
2017-07-06 | 13:15 | 1.7327 | 0 | 0 | 1.5 | 89.5894 | 0 | 26288.099
2017-07-06 | 13:30 | 1.8887 | 0 | 0 | 1.5 | 87.1506 | 0 | 25572.4728
2017-07-06 | 13:45 | 1.636 | 0 | 0 | 1.5 | 87.591 | 0 | 25701.7076
2017-07-06 | 14:00 | 1.7483 | 0 | 0 | 1.5 | 89.7454 | 0 | 26333.8689
2017-07-06 | 14:15 | 1.9145 | 0 | 0 | 1.5 | 87.6838 | 0 | 25728.9231
2017-07-06 | 14:30 | 1.6383 | 0 | 0 | 1.5 | 86.8275 | 0 | 25477.669
2017-07-06 | 14:45 | 1.6633 | 0 | 0 | 1.5 | 89.3001 | 0 | 26203.2014
2017-07-06 | 15:00 | 1.9199 | 0 | 0 | 1.5 | 87.3881 | 0 | 25642.1674
2017-07-06 | 15:15 | 1.7187 | 0 | 0 | 1.5 | 86.734 | 0 | 25450.2252
2017-07-06 | 15:30 | 1.6243 | 0 | 0 | 1.5 | 89.1048 | 0 | 26145.8933
2017-07-06 | 15:45 | 1.8318 | 0 | 0 | 1.5 | 87.6723 | 0 | 25725.5495
2017-07-06 | 16:00 | 1.7546 | 0 | 0 | 1.5 | 86.0347 | 0 | 25245.0341
2017-07-06 | 16:15 | 1.6516 | 0 | 0 | 1.5 | 88.2351 | 0 | 25890.6902
2017-07-06 | 16:30 | 1.8677 | 0 | 0 | 1.5 | 88.1395 | 0 | 25862.6508
2017-07-06 | 16:45 | 1.8411 | 0 | 0 | 1.5 | 84.887 | 0 | 24908.267
2017-07-06 | 17:00 | 1.778 | 0 | 0 | 1.5 | 84.4497 | 0 | 24779.9434
2017-07-06 | 17:15 | 1.7748 | 0 | 0 | 1.5 | 85.6808 | 0 | 25141.1862
2017-07-06 | 17:30 | 1.8942 | 0 | 0 | 1.5 | 83.3152 | 0 | 24447.0739
2017-07-06 | 17:45 | 1.7647 | 0 | 0 | 1.5 | 82.0778 | 0 | 24083.9707
2017-07-06 | 18:00 | 1.6727 | 0 | 0 | 1.5 | 83.0146 | 0 | 24358.854
2017-07-06 | 18:15 | 1.8809 | 0 | 0 | 1.5 | 82.221 | 0 | 24125.9953
2017-07-06 | 18:30 | 1.7468 | 0 | 0 | 1.5 | 80.9482 | 0 | 23752.5071
2017-07-06 | 18:45 | 1.675 | 0 | 0 | 1.5 | 82.169 | 0 | 24110.7208
2017-07-06 | 19:00 | 1.7046 | 0 | 0 | 1.5 | 83.6688 | 0 | 24550.8144
2017-07-06 | 19:15 | 1.8411 | 0 | 0 | 1.5 | 83.9818 | 0 | 24642.6696
2017-07-06 | 19:30 | 1.7951 | 0 | 0 | 1.5 | 82.6052 | 0 | 24238.7197
2017-07-06 | 19:45 | 1.7304 | 0 | 0 | 1.5 | 82.7941 | 0 | 24294.1627
2017-07-06 | 20:00 | 1.714 | 0 | 0 | 1.5 | 82.955 | 0 | 24341.361
2017-07-06 | 20:15 | 1.76 | 0 | 0 | 1.5 | 82.7457 | 0 | 24279.9561
2017-07-06 | 20:30 | 1.7624 | 0 | 0 | 1.5 | 82.583 | 0 | 24232.2006
2017-07-06 | 20:45 | 1.7686 | 0 | 0 | 1.5 | 82.3721 | 0 | 24170.3144
2017-07-06 | 21:00 | 1.7709 | 0 | 0 | 1.5 | 81.6031 | 0 | 23944.6775
2017-07-06 | 21:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 21:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 21:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 22:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 22:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 22:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 22:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 23:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 23:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 23:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-06 | 23:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 0:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 0:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 0:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 0:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 1:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 1:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 4:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 5:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 5:00 |  |  | 1 |  |  |  | 0
2017-07-07 | 5:15 | 2.1063 | 10 | 1 | 10 | 93.873 | 100 | 27545.0182
2017-07-07 | 5:30 | 1.955 | 9.2041 | 1 | 10 | 86.9355 | 92.6199 | 25509.3643
2017-07-07 | 5:45 | 1.8357 | 8.2222 | 1 | 10 | 83.9029 | 83.0564 | 24619.5128
2017-07-07 | 6:00 | 1.8934 | 7.4297 | 1 | 10 | 81.9077 | 75.3962 | 24034.0503
2017-07-07 | 6:15 | 1.8014 | 7.1088 | 1 | 10 | 80.3313 | 72.0041 | 23571.5118
2017-07-07 | 6:30 | 1.7483 | 6.8787 | 1 | 10 | 79.5017 | 69.6288 | 23328.082
2017-07-07 | 6:45 | 1.7031 | 6.7289 | 1 | 10 | 79.7719 | 68.5437 | 23407.3403
2017-07-07 | 7:00 | 1.8068 | 6.0008 | 1 | 10 | 79.0156 | 0 | 23185.4241
2017-07-07 | 7:15 | 1.7865 | 5.7276 | 1 | 10 | 78.4842 | 0 | 23029.5067
2017-07-07 | 7:30 | 1.7538 | 5.9196 | 1 | 10 | 78.5414 | 0 | 23046.2923
2017-07-07 | 7:45 | 1.689 | 4.914 | 1 | 10 | 78.9806 | 0 | 23175.1596
2017-07-07 | 8:00 | 1.7351 | 4.8683 | 1 | 10 | 78.9752 | 0 | 23173.5701
2017-07-07 | 8:15 | 1.7312 | 5.1435 | 1 | 10 | 78.9015 | 0 | 23151.9468
2017-07-07 | 8:30 | 1.6719 | 4.5006 | 1 | 10 | 79.2859 | 0 | 23264.7495
2017-07-07 | 8:45 | 1.6625 | 4.3783 | 1 | 10 | 79.7733 | 0 | 23407.7634
2017-07-07 | 9:00 | 1.7156 | 4.8148 | 1 | 10 | 80.3174 | 0 | 23567.415
2017-07-07 | 9:15 | 1.831 | 5.9149 | 1 | 10 | 80.0928 | 0 | 23501.5215
2017-07-07 | 9:30 | 1.6454 | 5.3695 | 1 | 10 | 80.2315 | 0 | 23542.2118
2017-07-07 | 9:45 | 1.7748 | 5.4934 | 1 | 10 | 79.9697 | 0 | 23465.3802
2017-07-07 | 10:00 | 1.6617 | 4.9414 | 1 | 10 | 80.4942 | 0 | 23619.3119
2017-07-07 | 10:15 | 1.8458 | 4.6859 | 1 | 10 | 80.3419 | 0 | 23574.5966
2017-07-07 | 10:30 | 1.6961 | 5.3156 | 1 | 10 | 80.7022 | 0 | 23680.3318
2017-07-07 | 10:45 | 1.7226 | 4.7766 | 1 | 10 | 80.6501 | 0 | 23665.0328
2017-07-07 | 11:00 | 1.8287 | 4.457 | 1 | 10 | 81.2966 | 0 | 23854.7587
2017-07-07 | 11:15 | 1.8911 | 5.1414 | 1 | 10 | 80.8271 | 0 | 23716.9767
2017-07-07 | 11:30 | 1.7179 | 6.2683 | 1 | 10 | 82.048 | 0 | 24075.2398
2017-07-07 | 11:45 | 1.7039 | 6.0727 | 1 | 10 | 81.6943 | 0 | 23971.4456
2017-07-07 | 12:00 | 1.799 | 6.6587 | 1 | 10 | 82.2715 | 0 | 24140.7973
2017-07-07 | 12:15 | 1.8575 | 5.9331 | 1 | 10 | 81.4407 | 0 | 23897.0139
2017-07-07 | 12:30 | 1.8333 | 6.2414 | 1 | 10 | 79.9076 | 0 | 23447.1665
2017-07-07 | 12:45 | 1.7312 | 5.5914 | 1 | 10 | 80.5608 | 0 | 23638.8513
2017-07-07 | 13:00 | 1.6563 | 5.0809 | 1 | 10 | 80.8518 | 0 | 23724.2211
2017-07-07 | 13:15 | 1.8201 | 5.773 | 1 | 10 | 80.4016 | 0 | 23592.1366
2017-07-07 | 13:30 | 1.7483 | 6.1218 | 1 | 10 | 81.1454 | 0 | 23810.3882
2017-07-07 | 13:45 | 1.7624 | 6.6614 | 1 | 10 | 80.7561 | 0 | 23696.1368
2017-07-07 | 13:57 |  |  | 0 |  |  |  | 0
2017-07-07 | 14:00 | 1.6851 | 4.1107 | 0 | 1.5 | 80.7393 | 0 | 23691.2119
2017-07-07 | 14:15 | 1.7717 | 0 | 0 | 1.5 | 81.2793 | 0 | 23849.6569
2017-07-07 | 14:30 | 1.7928 | 0 | 0 | 1.5 | 81.5467 | 0 | 23928.1317
2017-07-07 | 14:45 | 1.7343 | 0 | 0 | 1.5 | 81.7329 | 0 | 23982.7666
2017-07-07 | 15:00 | 1.7023 | 0 | 0 | 1.5 | 82.2294 | 0 | 24128.4557
2017-07-07 | 15:15 | 1.7842 | 0 | 0 | 1.5 | 82.4385 | 0 | 24189.8045
2017-07-07 | 15:30 | 1.8045 | 0 | 0 | 1.5 | 82.813 | 0 | 24299.7103
2017-07-07 | 15:45 | 1.7327 | 0 | 0 | 1.5 | 83.3277 | 0 | 24450.7409
2017-07-07 | 16:00 | 1.6844 | 0 | 0 | 1.5 | 83.6259 | 0 | 24538.2307
2017-07-07 | 16:15 | 1.8365 | 0 | 0 | 1.5 | 83.5421 | 0 | 24513.632
2017-07-07 | 16:30 | 1.8154 | 0 | 0 | 1.5 | 82.8901 | 0 | 24322.3298
2017-07-07 | 16:45 | 1.7374 | 0 | 0 | 1.5 | 82.4893 | 0 | 24204.7298
2017-07-07 | 17:00 | 1.6836 | 0 | 0 | 1.5 | 82.8253 | 0 | 24303.2989
2017-07-07 | 17:15 | 1.7382 | 0 | 0 | 1.5 | 82.637 | 0 | 24248.0706
2017-07-07 | 17:30 | 1.8068 | 0 | 0 | 1.5 | 81.9722 | 0 | 24052.9897
2017-07-07 | 17:45 | 1.7514 | 0 | 0 | 1.5 | 81.2574 | 0 | 23843.234
2017-07-07 | 18:00 | 1.7296 | 0 | 0 | 1.5 | 80.7496 | 0 | 23694.2407
2017-07-07 | 18:15 | 1.7858 | 0 | 0 | 1.5 | 79.8157 | 0 | 23420.208
2017-07-07 | 18:30 | 1.7085 | 0 | 0 | 1.5 | 79.2555 | 0 | 23255.8261
2017-07-07 | 18:45 | 1.8341 | 0 | 0 | 1.5 | 78.3129 | 0 | 22979.2368
2017-07-07 | 19:00 | 1.792 | 0 | 0 | 1.5 | 78.0165 | 0 | 22892.2842
2017-07-07 | 19:15 | 1.7491 | 0 | 0 | 1.5 | 77.6286 | 0 | 22778.4495
2017-07-07 | 19:30 | 1.7507 | 0 | 0 | 1.5 | 77.1556 | 0 | 22639.6557
2017-07-07 | 19:45 | 1.7475 | 0 | 0 | 1.5 | 77.554 | 0 | 22756.5732
2017-07-07 | 20:00 | 1.7943 | 0 | 0 | 1.5 | 77.0149 | 0 | 22598.3633
2017-07-07 | 20:15 | 1.7858 | 0 | 0 | 1.5 | 77.107 | 0 | 22625.4021
2017-07-07 | 20:25 |  |  | 1 |  |  |  | 0
2017-07-07 | 20:30 | 1.7382 | 0 | 1 | 10 | 76.6705 | 0 | 22497.3135
2017-07-07 | 20:45 | 1.7374 | 0.073931 | 1 | 10 | 76.6364 | 0 | 22487.3135
2017-07-07 | 21:00 | 1.7491 | 0 | 1 | 10 | 76.6935 | 0 | 22504.0633
2017-07-07 | 21:00 |  |  | 0 |  |  |  | 0
2017-07-07 | 21:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 21:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 22:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 22:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 22:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 23:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 0:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 1:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 1:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 1:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 1:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 2:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 2:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 2:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 3:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-08 | 5:15 | 2.2343 | 8.1521 | 1 | 10 | 86.9023 | 85.2412 | 25499.6104
2017-07-08 | 5:30 | 1.8825 | 5.678 | 1 | 10 | 80.3186 | 0 | 23567.7709
2017-07-08 | 5:45 | 1.8622 | 4.9495 | 1 | 10 | 77.8503 | 0 | 22843.5055
2017-07-08 | 6:00 | 1.8037 | 4.2804 | 1 | 10 | 76.7392 | 0 | 22517.4639
2017-07-08 | 6:15 | 1.7288 | 5.2209 | 1 | 10 | 76.359 | 0 | 22405.9217
2017-07-08 | 6:30 | 1.728 | 5.5389 | 1 | 10 | 76.2335 | 0 | 22369.0976
2017-07-08 | 6:45 | 1.7889 | 5.3488 | 1 | 10 | 76.1363 | 0 | 22340.5789
2017-07-08 | 7:00 | 1.7897 | 5.1033 | 1 | 10 | 75.9758 | 0 | 22293.4769
2017-07-08 | 7:15 | 1.7171 | 5.358 | 1 | 10 | 76.1489 | 0 | 22344.2527
2017-07-08 | 7:30 | 1.6688 | 5.6686 | 1 | 10 | 76.6884 | 0 | 22502.5768
2017-07-08 | 7:45 | 1.7483 | 5.6509 | 1 | 10 | 76.9808 | 0 | 22588.3764
2017-07-08 | 8:00 | 1.792 | 5.6453 | 1 | 10 | 76.4856 | 0 | 22443.0592
2017-07-08 | 8:15 | 1.7834 | 5.5789 | 1 | 10 | 76.4386 | 0 | 22429.2777
2017-07-08 | 8:30 | 1.7413 | 5.5049 | 1 | 10 | 76.5649 | 0 | 22466.3257
2017-07-08 | 8:45 | 1.7592 | 5.493 | 1 | 10 | 76.939 | 0 | 22576.1017
2017-07-08 | 9:00 | 1.8037 | 5.6348 | 1 | 10 | 77.3873 | 0 | 22707.6534
2017-07-08 | 9:15 | 1.6859 | 5.6616 | 1 | 10 | 77.849 | 0 | 22843.1094
2017-07-08 | 9:30 | 1.714 | 6.0962 | 1 | 10 | 78.1144 | 0 | 22920.9842
2017-07-08 | 9:45 | 1.7655 | 5.7566 | 1 | 10 | 78.2023 | 0 | 22946.7939
2017-07-08 | 10:00 | 1.8076 | 3.4265 | 1 | 10 | 77.9935 | 0 | 22885.5122
2017-07-08 | 10:14 |  |  | 0 |  |  |  | 0
2017-07-08 | 10:15 | 1.6984 | 1.8475 | 0 | 1.5 | 78.1993 | 0 | 22945.9142
2017-07-08 | 10:30 | 1.7093 | 0 | 0 | 1.5 | 78.5603 | 0 | 23051.8328
2017-07-08 | 10:45 | 1.7499 | 0 | 0 | 1.5 | 78.6918 | 0 | 23090.4189
2017-07-08 | 11:00 | 1.7733 | 0 | 0 | 1.5 | 78.4166 | 0 | 23009.6809
2017-07-08 | 11:15 | 1.7647 | 0 | 0 | 1.5 | 78.3982 | 0 | 23004.263
2017-07-08 | 11:30 | 1.7109 | 0 | 0 | 1.5 | 78.5006 | 0 | 23034.3309
2017-07-08 | 11:45 | 1.7078 | 0 | 0 | 1.5 | 78.5735 | 0 | 23055.7192
2017-07-08 | 12:00 | 1.799 | 0 | 0 | 1.5 | 78.4151 | 0 | 23009.2443
2017-07-08 | 12:15 | 1.753 | 0 | 0 | 1.5 | 78.1906 | 0 | 22943.3687
2017-07-08 | 12:30 | 1.707 | 0 | 0 | 1.5 | 78.1591 | 0 | 22934.1163
2017-07-08 | 12:45 | 1.7335 | 0 | 0 | 1.5 | 78.1634 | 0 | 22935.3722
2017-07-08 | 13:00 | 1.8014 | 0 | 0 | 1.5 | 77.8454 | 0 | 22842.0639
2017-07-08 | 13:15 | 1.7592 | 0 | 0 | 1.5 | 77.6849 | 0 | 22794.9554
2017-07-08 | 13:30 | 1.7756 | 0 | 0 | 1.5 | 77.491 | 0 | 22738.0681
2017-07-08 | 13:45 | 1.7655 | 0 | 0 | 1.5 | 77.0748 | 0 | 22615.9482
2017-07-08 | 14:00 | 1.7304 | 0 | 0 | 1.5 | 76.9809 | 0 | 22588.4099
2017-07-08 | 14:15 | 1.7561 | 0 | 0 | 1.5 | 76.9828 | 0 | 22588.9519
2017-07-08 | 14:30 | 1.7507 | 0 | 0 | 1.5 | 77.0057 | 0 | 22595.6813
2017-07-08 | 14:45 | 1.7499 | 0 | 0 | 1.5 | 76.9779 | 0 | 22587.5234
2017-07-08 | 15:00 | 1.7483 | 0 | 0 | 1.5 | 76.9854 | 0 | 22589.7198
2017-07-08 | 15:15 | 1.7452 | 0 | 0 | 1.5 | 77.0479 | 0 | 22608.059
2017-07-08 | 15:30 | 1.7553 | 0 | 0 | 1.5 | 77.069 | 0 | 22614.2577
2017-07-08 | 15:45 | 1.7421 | 0 | 0 | 1.5 | 77.1016 | 0 | 22623.8258
2017-07-08 | 16:00 | 1.7436 | 0 | 0 | 1.5 | 77.0862 | 0 | 22619.3015
2017-07-08 | 16:15 | 1.7468 | 0 | 0 | 1.5 | 77.1036 | 0 | 22624.3878
2017-07-08 | 16:30 | 1.7343 | 0 | 0 | 1.5 | 77.1288 | 0 | 22631.8048
2017-07-08 | 16:45 | 1.7624 | 0 | 0 | 1.5 | 77.1826 | 0 | 22647.585
2017-07-08 | 17:00 | 1.76 | 0 | 0 | 1.5 | 77.1678 | 0 | 22643.2332
2017-07-08 | 17:15 | 1.7444 | 0 | 0 | 1.5 | 77.2149 | 0 | 22657.0549
2017-07-08 | 17:30 | 1.7429 | 0 | 0 | 1.5 | 77.191 | 0 | 22650.0454
2017-07-08 | 17:45 | 1.7639 | 0 | 0 | 1.5 | 77.7946 | 0 | 22827.1721
2017-07-08 | 18:00 | 1.7741 | 0 | 0 | 1.5 | 78.0394 | 0 | 22899.0002
2017-07-08 | 18:15 | 1.728 | 0 | 0 | 1.5 | 78.3105 | 0 | 22978.5519
2017-07-08 | 18:30 | 1.7842 | 0 | 0 | 1.5 | 78.0488 | 0 | 22901.7517
2017-07-08 | 18:45 | 1.7624 | 0 | 0 | 1.5 | 77.809 | 0 | 22831.3899
2017-07-08 | 19:00 | 1.7514 | 0 | 0 | 1.5 | 77.7787 | 0 | 22822.4911
2017-07-08 | 19:15 | 1.753 | 0 | 0 | 1.5 | 77.8103 | 0 | 22831.7681
2017-07-08 | 19:30 | 1.7397 | 0 | 0 | 1.5 | 77.8947 | 0 | 22856.5347
2017-07-08 | 19:45 | 1.7538 | 0 | 0 | 1.5 | 77.8811 | 0 | 22852.5296
2017-07-08 | 20:00 | 1.7709 | 0 | 0 | 1.5 | 77.6893 | 0 | 22796.265
2017-07-08 | 20:15 | 1.7694 | 0 | 0 | 1.5 | 77.3223 | 0 | 22688.5597
2017-07-08 | 20:30 | 1.76 | 0 | 0 | 1.5 | 76.9655 | 0 | 22583.8811
2017-07-08 | 20:45 | 1.7569 | 0 | 0 | 1.5 | 76.6695 | 0 | 22497.0136
2017-07-08 | 21:00 | 1.7538 | 0 | 0 | 1.5 | 76.4211 | 0 | 22424.1377
2017-07-08 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 21:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 21:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 22:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 22:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 22:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 23:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 3:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 4:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 4:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 4:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 5:00 | 0.03154 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-09 | 5:15 | 2.3006 | 8.367 | 1 | 10 | 87.8455 | 86.5186 | 25776.3831
2017-07-09 | 5:30 | 1.9636 | 6.0906 | 1 | 10 | 81.6544 | 64.0172 | 23959.7395
2017-07-09 | 5:45 | 1.7998 | 5.6993 | 1 | 10 | 79.4483 | 0 | 23312.4088
2017-07-09 | 6:00 | 1.7507 | 5.517 | 1 | 10 | 78.532 | 0 | 23043.5452
2017-07-09 | 6:15 | 1.7858 | 5.8906 | 1 | 10 | 77.9304 | 0 | 22867.0074
2017-07-09 | 6:30 | 1.806 | 5.664 | 1 | 10 | 77.4032 | 0 | 22712.321
2017-07-09 | 6:45 | 1.7858 | 5.5837 | 1 | 10 | 76.8777 | 0 | 22558.116
2017-07-09 | 7:00 | 1.7195 | 5.1022 | 1 | 10 | 76.6224 | 0 | 22483.192
2017-07-09 | 7:15 | 1.7226 | 4.9708 | 1 | 10 | 76.2875 | 0 | 22384.9363
2017-07-09 | 7:30 | 1.7483 | 4.4121 | 1 | 10 | 75.4359 | 0 | 22135.0478
2017-07-09 | 7:45 | 1.728 | 4.147 | 1 | 10 | 75.224 | 0 | 22072.8797
2017-07-09 | 8:00 | 1.7039 | 4.206 | 1 | 10 | 75.4193 | 0 | 22130.1695
2017-07-09 | 8:15 | 1.7748 | 4.4449 | 1 | 10 | 75.2914 | 0 | 22092.6538
2017-07-09 | 8:30 | 1.7054 | 4.4389 | 1 | 10 | 75.5574 | 0 | 22170.7123
2017-07-09 | 8:45 | 1.7631 | 4.4103 | 1 | 10 | 75.7166 | 0 | 22217.4111
2017-07-09 | 9:00 | 1.6851 | 2.7399 | 1 | 10 | 76.4892 | 0 | 22444.1293
2017-07-09 | 9:15 | 1.7405 | 0.00453 | 1 | 10 | 76.8484 | 0 | 22549.5083
2017-07-09 | 9:23 |  |  | 0 |  |  |  | 0
2017-07-09 | 9:30 | 1.7226 | 0 | 0 | 1.5 | 77.3852 | 0 | 22707.0222
2017-07-09 | 9:45 | 1.7577 | 0 | 0 | 1.5 | 77.8697 | 0 | 22849.2007
2017-07-09 | 10:00 | 1.7093 | 0 | 0 | 1.5 | 77.9187 | 0 | 22863.5643
2017-07-09 | 10:15 | 1.76 | 0 | 0 | 1.5 | 77.7712 | 0 | 22820.295
2017-07-09 | 10:30 | 1.753 | 0 | 0 | 1.5 | 77.5176 | 0 | 22745.8901
2017-07-09 | 10:45 | 1.7592 | 0 | 0 | 1.5 | 77.3421 | 0 | 22694.3781
2017-07-09 | 11:00 | 1.7304 | 0 | 0 | 1.5 | 77.3011 | 0 | 22682.3631
2017-07-09 | 11:15 | 1.7429 | 0 | 0 | 1.5 | 77.332 | 0 | 22691.4118
2017-07-09 | 11:30 | 1.7694 | 0 | 0 | 1.5 | 77.3265 | 0 | 22689.8132
2017-07-09 | 11:45 | 1.7491 | 0 | 0 | 1.5 | 77.4096 | 0 | 22714.1992
2017-07-09 | 12:00 | 1.7592 | 0 | 0 | 1.5 | 77.3259 | 0 | 22689.614
2017-07-09 | 12:15 | 1.76 | 0 | 0 | 1.5 | 77.2258 | 0 | 22660.2427
2017-07-09 | 12:30 | 1.7499 | 0 | 0 | 1.5 | 77.0612 | 0 | 22611.9631
2017-07-09 | 12:45 | 1.7413 | 0 | 0 | 1.5 | 76.9832 | 0 | 22589.0569
2017-07-09 | 13:00 | 1.7499 | 0 | 0 | 1.5 | 76.9251 | 0 | 22572.016
2017-07-09 | 13:15 | 1.7507 | 0 | 0 | 1.5 | 76.9088 | 0 | 22567.2252
2017-07-09 | 13:30 | 1.7436 | 0 | 0 | 1.5 | 76.9045 | 0 | 22565.9896
2017-07-09 | 13:45 | 1.728 | 0 | 0 | 1.5 | 77.0485 | 0 | 22608.2225
2017-07-09 | 14:00 | 1.7452 | 0 | 0 | 1.5 | 77.1108 | 0 | 22626.5213
2017-07-09 | 14:15 | 1.7397 | 0 | 0 | 1.5 | 77.2962 | 0 | 22680.9168
2017-07-09 | 14:30 | 1.767 | 0 | 0 | 1.5 | 77.2169 | 0 | 22657.6367
2017-07-09 | 14:45 | 1.7468 | 0 | 0 | 1.5 | 77.2171 | 0 | 22657.6904
2017-07-09 | 15:00 | 1.7429 | 0 | 0 | 1.5 | 77.3005 | 0 | 22682.1838
2017-07-09 | 15:15 | 1.7397 | 0 | 0 | 1.5 | 77.4436 | 0 | 22724.1546
2017-07-09 | 15:30 | 1.7405 | 0 | 0 | 1.5 | 77.4777 | 0 | 22734.1773
2017-07-09 | 15:45 | 1.7546 | 0 | 0 | 1.5 | 77.5077 | 0 | 22742.9619
2017-07-09 | 16:00 | 1.7507 | 0 | 0 | 1.5 | 77.4903 | 0 | 22737.8534
2017-07-09 | 16:15 | 1.7358 | 0 | 0 | 1.5 | 77.6289 | 0 | 22778.5346
2017-07-09 | 16:30 | 1.7639 | 0 | 0 | 1.5 | 77.7192 | 0 | 22805.025
2017-07-09 | 16:45 | 1.7304 | 0 | 0 | 1.5 | 77.809 | 0 | 22831.3855
2017-07-09 | 17:00 | 1.7507 | 0 | 0 | 1.5 | 77.9038 | 0 | 22859.2034
2017-07-09 | 17:15 | 1.7569 | 0 | 0 | 1.5 | 77.8107 | 0 | 22831.8957
2017-07-09 | 17:30 | 1.7483 | 0 | 0 | 1.5 | 77.7812 | 0 | 22823.2188
2017-07-09 | 17:45 | 1.7725 | 0 | 0 | 1.5 | 77.66 | 0 | 22787.6573
2017-07-09 | 18:00 | 1.7475 | 0 | 0 | 1.5 | 77.7156 | 0 | 22803.9907
2017-07-09 | 18:15 | 1.7546 | 0 | 0 | 1.5 | 77.7866 | 0 | 22824.8083
2017-07-09 | 18:30 | 1.7468 | 0 | 0 | 1.5 | 77.7472 | 0 | 22813.2566
2017-07-09 | 18:45 | 1.7413 | 0 | 0 | 1.5 | 77.7981 | 0 | 22828.193
2017-07-09 | 19:00 | 1.7483 | 0 | 0 | 1.5 | 77.6842 | 0 | 22794.7741
2017-07-09 | 19:15 | 1.7663 | 0 | 0 | 1.5 | 77.7049 | 0 | 22800.8252
2017-07-09 | 19:30 | 1.7429 | 0 | 0 | 1.5 | 77.8736 | 0 | 22850.3404
2017-07-09 | 19:45 | 1.739 | 0 | 0 | 1.5 | 77.9264 | 0 | 22865.8387
2017-07-09 | 20:00 | 1.7514 | 0 | 0 | 1.5 | 77.762 | 0 | 22817.6064
2017-07-09 | 20:15 | 1.7475 | 0 | 0 | 1.5 | 77.4786 | 0 | 22734.4326
2017-07-09 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 77.1687 | 0 | 22643.4949
2017-07-09 | 20:45 | 1.7507 | 0 | 0 | 1.5 | 76.8861 | 0 | 22560.5653
2017-07-09 | 21:00 | 1.7702 | 0 | 0 | 1.5 | 76.646 | 0 | 22490.1251
2017-07-09 | 21:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 21:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 21:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 22:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 22:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 22:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 22:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 23:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 23:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-09 | 23:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 0:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 2:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 4:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 5:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-10 | 5:15 | 2.3037 | 9.1549 | 1 | 10 | 89.6118 | 93.8304 | 26294.6672
2017-07-10 | 5:30 | 1.9152 | 6.5608 | 1 | 10 | 82.2768 | 68.388 | 24142.3557
2017-07-10 | 5:45 | 1.8567 | 5.4018 | 1 | 10 | 78.8903 | 0 | 23148.6648
2017-07-10 | 6:00 | 1.792 | 4.4462 | 1 | 10 | 77.3624 | 0 | 22700.3306
2017-07-10 | 6:15 | 1.7171 | 5.2527 | 1 | 10 | 76.8515 | 0 | 22550.4217
2017-07-10 | 6:30 | 1.7858 | 5.3883 | 1 | 10 | 76.7098 | 0 | 22508.8338
2017-07-10 | 6:45 | 1.863 | 5.1378 | 1 | 10 | 76.2592 | 0 | 22376.6375
2017-07-10 | 7:00 | 1.8419 | 3.27 | 1 | 10 | 75.8073 | 0 | 22244.0222
2017-07-10 | 7:15 | 1.7694 | 4.2272 | 1 | 10 | 75.885 | 0 | 22266.8257
2017-07-10 | 7:30 | 1.7678 | 4.5046 | 1 | 10 | 76.1294 | 0 | 22338.5484
2017-07-10 | 7:45 | 1.8271 | 3.992 | 1 | 10 | 76.216 | 0 | 22363.9529
2017-07-10 | 8:00 | 1.8232 | 2.135 | 1 | 10 | 76.2432 | 0 | 22371.9338
2017-07-10 | 8:15 | 1.6664 | 2.1573 | 1 | 10 | 76.616 | 0 | 22481.3225
2017-07-10 | 8:30 | 1.728 | 1.4715 | 1 | 10 | 76.8098 | 0 | 22538.1808
2017-07-10 | 8:45 | 1.7031 | 0.79277 | 1 | 10 | 77.2732 | 0 | 22674.1559
2017-07-10 | 9:00 | 1.8154 | 0.25569 | 1 | 10 | 77.2893 | 0 | 22678.893
2017-07-10 | 9:15 | 1.6485 | 1.0712 | 1 | 10 | 78.1838 | 0 | 22941.3675
2017-07-10 | 9:30 | 1.7078 | 2.7816 | 1 | 10 | 79.2045 | 0 | 23240.865
2017-07-10 | 9:45 | 1.7694 | 2.7145 | 1 | 10 | 79.8006 | 0 | 23415.7667
2017-07-10 | 10:00 | 1.8224 | 0 | 1 | 10 | 80.064 | 0 | 23493.0751
2017-07-10 | 10:15 | 1.7795 | 1.5218 | 1 | 10 | 79.7394 | 0 | 23397.8279
2017-07-10 | 10:30 | 1.739 | 0 | 1 | 10 | 80.1526 | 0 | 23519.0749
2017-07-10 | 10:35 |  |  | 0 |  |  |  | 0
2017-07-10 | 10:45 | 1.7078 | 0 | 0 | 1.5 | 80.4766 | 0 | 23614.1206
2017-07-10 | 10:48 |  |  | 1 |  |  |  | 0
2017-07-10 | 10:52 |  |  | 0 |  |  |  | 0
2017-07-10 | 11:00 | 1.7803 | 0 | 0 | 1.5 | 80.3421 | 0 | 23574.675
2017-07-10 | 11:15 | 1.7569 | 0 | 0 | 1.5 | 80.9181 | 0 | 23743.6886
2017-07-10 | 11:30 | 1.6578 | 0 | 0 | 1.5 | 81.1888 | 0 | 23823.106
2017-07-10 | 11:45 | 1.7397 | 0 | 0 | 1.5 | 81.313 | 0 | 23859.5428
2017-07-10 | 12:00 | 1.7936 | 0 | 0 | 1.5 | 81.4865 | 0 | 23910.4796
2017-07-10 | 12:15 | 1.7366 | 0 | 0 | 1.5 | 81.3869 | 0 | 23881.2356
2017-07-10 | 12:30 | 1.6906 | 0 | 0 | 1.5 | 81.6645 | 0 | 23962.6855
2017-07-10 | 12:45 | 1.7085 | 0 | 0 | 1.5 | 81.6763 | 0 | 23966.1512
2017-07-10 | 13:00 | 1.7522 | 0 | 0 | 1.5 | 81.5585 | 0 | 23931.6082
2017-07-10 | 13:15 | 1.7273 | 0 | 0 | 1.5 | 81.7117 | 0 | 23976.5497
2017-07-10 | 13:30 | 1.689 | 0 | 0 | 1.5 | 82.2615 | 0 | 24137.8782
2017-07-10 | 13:45 | 1.6883 | 0 | 0 | 1.5 | 82.7636 | 0 | 24285.197
2017-07-10 | 14:00 | 1.7694 | 0 | 0 | 1.5 | 83.0808 | 0 | 24378.2948
2017-07-10 | 14:15 | 1.7007 | 0 | 0 | 1.5 | 83.6819 | 0 | 24554.6492
2017-07-10 | 14:30 | 1.8084 | 0 | 0 | 1.5 | 83.911 | 0 | 24621.8813
2017-07-10 | 14:45 | 1.8076 | 0 | 0 | 1.5 | 83.3634 | 0 | 24461.2022
2017-07-10 | 15:00 | 1.7 | 0 | 0 | 1.5 | 83.3563 | 0 | 24459.12
2017-07-10 | 15:15 | 1.7031 | 0 | 0 | 1.5 | 83.907 | 0 | 24620.6971
2017-07-10 | 15:30 | 1.7585 | 0.047304 | 0 | 1.5 | 83.323 | 0 | 24449.3415
2017-07-10 | 15:45 | 1.7585 | 0 | 0 | 1.5 | 83.2044 | 0 | 24414.5614
2017-07-10 | 16:00 | 1.7975 | 0 | 0 | 1.5 | 83.004 | 0 | 24355.7534
2017-07-10 | 16:15 | 1.7772 | 0 | 0 | 1.5 | 82.9638 | 0 | 24343.9355
2017-07-10 | 16:30 | 1.728 | 0 | 0 | 1.5 | 83.7867 | 0 | 24585.4088
2017-07-10 | 16:45 | 1.7085 | 0 | 0 | 1.5 | 84.6496 | 0 | 24838.6194
2017-07-10 | 17:00 | 1.8037 | 0 | 0 | 1.5 | 84.8139 | 0 | 24886.8159
2017-07-10 | 17:15 | 1.799 | 0 | 0 | 1.5 | 84.3315 | 0 | 24745.2572
2017-07-10 | 17:30 | 1.7483 | 0 | 0 | 1.5 | 83.5207 | 0 | 24507.3526
2017-07-10 | 17:45 | 1.7507 | 0 | 0 | 1.5 | 82.9507 | 0 | 24340.1163
2017-07-10 | 18:00 | 1.7585 | 0 | 0 | 1.5 | 82.5256 | 0 | 24215.3633
2017-07-10 | 18:15 | 1.7912 | 0 | 0 | 1.5 | 81.7812 | 0 | 23996.9284
2017-07-10 | 18:30 | 1.7897 | 0 | 0 | 1.5 | 80.9177 | 0 | 23743.5724
2017-07-10 | 18:45 | 1.7819 | 0 | 0 | 1.5 | 80.5632 | 0 | 23639.5429
2017-07-10 | 19:00 | 1.7546 | 0 | 0 | 1.5 | 80.1265 | 0 | 23511.403
2017-07-10 | 19:15 | 1.792 | 0 | 0 | 1.5 | 79.4682 | 0 | 23318.2295
2017-07-10 | 19:30 | 1.7608 | 0 | 0 | 1.5 | 79.0968 | 0 | 23209.2549
2017-07-10 | 19:45 | 1.7803 | 0 | 0 | 1.5 | 78.5499 | 0 | 23048.7861
2017-07-10 | 20:00 | 1.7959 | 0 | 0 | 1.5 | 77.9913 | 0 | 22884.8787
2017-07-10 | 20:15 | 1.7413 | 0 | 0 | 1.5 | 77.9229 | 0 | 22864.8043
2017-07-10 | 20:30 | 1.7819 | 0 | 0 | 1.5 | 77.5131 | 0 | 22744.5515
2017-07-10 | 20:43 |  |  | 1 |  |  |  | 0
2017-07-10 | 20:45 | 1.8271 | 0.48018 | 1 | 10 | 77.2037 | 0 | 22653.7661
2017-07-10 | 21:00 | 1.7062 | 0.46393 | 0 | 10 | 77.3219 | 0 | 22688.4523
2017-07-10 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 21:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 22:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 0:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 0:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 1:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 1:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 1:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 2:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 2:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 4:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-11 | 5:15 | 2.2148 | 8.3817 | 1 | 10 | 87.739 | 86.3966 | 25745.1288
2017-07-11 | 5:30 | 1.8786 | 6.447 | 1 | 10 | 81.6821 | 67.1155 | 23967.8481
2017-07-11 | 5:45 | 1.8053 | 5.9795 | 1 | 10 | 79.4551 | 0 | 23314.3833
2017-07-11 | 6:00 | 1.824 | 5.4532 | 1 | 10 | 78.2731 | 0 | 22967.5601
2017-07-11 | 6:15 | 1.7639 | 5.5794 | 1 | 10 | 77.6297 | 0 | 22778.7787
2017-07-11 | 6:30 | 1.7335 | 5.7609 | 1 | 10 | 77.314 | 0 | 22686.1442
2017-07-11 | 6:45 | 1.7405 | 5.5997 | 1 | 10 | 77.1656 | 0 | 22642.6017
2017-07-11 | 7:00 | 1.7912 | 4.7288 | 1 | 10 | 76.8748 | 0 | 22557.2542
2017-07-11 | 7:15 | 1.7897 | 4.9062 | 1 | 10 | 76.9721 | 0 | 22585.8265
2017-07-11 | 7:30 | 1.728 | 3.9344 | 1 | 10 | 76.8453 | 0 | 22548.5996
2017-07-11 | 7:45 | 1.7187 | 4.2475 | 1 | 10 | 77.2467 | 0 | 22666.3991
2017-07-11 | 8:00 | 1.7358 | 2.9994 | 1 | 10 | 76.8007 | 0 | 22535.5056
2017-07-11 | 8:15 | 1.7 | 3.1974 | 1 | 10 | 76.8635 | 0 | 22553.9411
2017-07-11 | 8:30 | 1.6976 | 3.1345 | 1 | 10 | 77.3384 | 0 | 22693.2989
2017-07-11 | 8:45 | 1.7756 | 4.2911 | 1 | 10 | 77.5187 | 0 | 22746.2146
2017-07-11 | 9:00 | 1.6867 | 4.2889 | 1 | 10 | 77.9432 | 0 | 22870.7571
2017-07-11 | 9:15 | 1.7374 | 5.5091 | 1 | 10 | 78.5397 | 0 | 23045.8043
2017-07-11 | 9:30 | 1.6875 | 5.7186 | 1 | 10 | 79.3852 | 0 | 23293.8747
2017-07-11 | 9:45 | 1.7429 | 5.5183 | 1 | 10 | 80.029 | 0 | 23482.7972
2017-07-11 | 10:00 | 1.6797 | 4.5929 | 1 | 10 | 80.5951 | 0 | 23648.9098
2017-07-11 | 10:15 | 1.7101 | 4.822 | 1 | 10 | 81.4052 | 0 | 23886.6174
2017-07-11 | 10:30 | 1.8138 | 4.9326 | 1 | 10 | 82.1262 | 0 | 24098.1595
2017-07-11 | 10:45 | 1.767 | 4.8069 | 1 | 10 | 81.5114 | 0 | 23917.7778
2017-07-11 | 11:00 | 1.7592 | 4.2492 | 1 | 10 | 81.1051 | 0 | 23798.5545
2017-07-11 | 11:15 | 1.7538 | 4.0955 | 1 | 10 | 81.614 | 0 | 23947.8768
2017-07-11 | 11:30 | 1.728 | 0.86948 | 1 | 10 | 80.9623 | 0 | 23756.6418
2017-07-11 | 11:41 |  |  | 0 |  |  |  | 0
2017-07-11 | 11:45 | 1.707 | 0 | 0 | 1.5 | 81.5312 | 0 | 23923.5959
2017-07-11 | 12:00 | 1.7023 | 0 | 0 | 1.5 | 82.4337 | 0 | 24188.4143
2017-07-11 | 12:15 | 1.8318 | 0 | 0 | 1.5 | 82.7813 | 0 | 24290.3974
2017-07-11 | 12:30 | 1.8053 | 0 | 0 | 1.5 | 82.2808 | 0 | 24143.5285
2017-07-11 | 12:45 | 1.7101 | 0 | 0 | 1.5 | 81.7283 | 0 | 23981.4212
2017-07-11 | 13:00 | 1.6844 | 0 | 0 | 1.5 | 82.4356 | 0 | 24188.9715
2017-07-11 | 13:15 | 1.7429 | 0 | 0 | 1.5 | 82.8957 | 0 | 24323.9574
2017-07-11 | 13:30 | 1.7257 | 0 | 0 | 1.5 | 83.0245 | 0 | 24361.7531
2017-07-11 | 13:45 | 1.6781 | 0 | 0 | 1.5 | 83.8771 | 0 | 24611.9347
2017-07-11 | 14:00 | 1.6758 | 0 | 0 | 1.5 | 85.0175 | 0 | 24946.5642
2017-07-11 | 14:15 | 1.7444 | 0 | 0 | 1.5 | 85.7375 | 0 | 25157.8398
2017-07-11 | 14:30 | 1.7226 | 0 | 0 | 1.5 | 86.2392 | 0 | 25305.0555
2017-07-11 | 14:45 | 1.6859 | 0 | 0 | 1.5 | 87.5745 | 0 | 25696.8698
2017-07-11 | 15:00 | 1.6461 | 0 | 0 | 1.5 | 89.2781 | 0 | 26196.7383
2017-07-11 | 15:15 | 1.9191 | 0 | 0 | 1.5 | 89.159 | 0 | 26161.7857
2017-07-11 | 15:30 | 1.8255 | 0 | 0 | 1.5 | 85.6374 | 0 | 25128.4705
2017-07-11 | 15:45 | 1.6383 | 0 | 0 | 1.5 | 86.0606 | 0 | 25252.6369
2017-07-11 | 16:00 | 1.6305 | 0 | 0 | 1.5 | 87.9216 | 0 | 25798.7074
2017-07-11 | 16:15 | 1.9184 | 0 | 0 | 1.5 | 89.0274 | 0 | 26123.1954
2017-07-11 | 16:30 | 1.8427 | 0 | 0 | 1.5 | 85.8786 | 0 | 25199.2285
2017-07-11 | 16:45 | 1.675 | 0 | 0 | 1.5 | 86.2529 | 0 | 25309.0649
2017-07-11 | 17:00 | 1.668 | 0 | 0 | 1.5 | 87.9115 | 0 | 25795.7432
2017-07-11 | 17:15 | 2.0096 | 0 | 0 | 1.5 | 87.7039 | 0 | 25734.8175
2017-07-11 | 17:30 | 1.8677 | 0 | 0 | 1.5 | 83.2453 | 0 | 24426.5495
2017-07-11 | 17:45 | 1.7343 | 0 | 0 | 1.5 | 82.3295 | 0 | 24157.8226
2017-07-11 | 18:00 | 1.6883 | 0 | 0 | 1.5 | 82.2154 | 0 | 24124.3453
2017-07-11 | 18:15 | 1.7741 | 0 | 0 | 1.5 | 82.0652 | 0 | 24080.2767
2017-07-11 | 18:30 | 1.7592 | 0 | 0 | 1.5 | 81.705 | 0 | 23974.5729
2017-07-11 | 18:45 | 1.7109 | 0 | 0 | 1.5 | 81.374 | 0 | 23877.4633
2017-07-11 | 19:00 | 1.6867 | 0 | 0 | 1.5 | 81.5121 | 0 | 23917.9835
2017-07-11 | 19:15 | 1.7577 | 0 | 0 | 1.5 | 81.2637 | 0 | 23845.0987
2017-07-11 | 19:30 | 1.8084 | 0 | 0 | 1.5 | 80.9108 | 0 | 23741.5372
2017-07-11 | 19:45 | 1.7624 | 0 | 0 | 1.5 | 80.8473 | 0 | 23722.9204
2017-07-11 | 20:00 | 1.7655 | 0 | 0 | 1.5 | 80.4356 | 0 | 23602.1032
2017-07-11 | 20:15 | 1.7865 | 0 | 0 | 1.5 | 79.9395 | 0 | 23456.5262
2017-07-11 | 20:30 | 1.7538 | 0 | 0 | 1.5 | 79.2668 | 0 | 23259.155
2017-07-11 | 20:45 | 1.7842 | 0 | 0 | 1.5 | 78.5054 | 0 | 23035.7145
2017-07-11 | 21:00 | 1.7514 | 0 | 0 | 1.5 | 77.9908 | 0 | 22884.7176
2017-07-11 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 21:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 22:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 4:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 4:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 4:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 5:00 | 0.03076 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-12 | 5:15 | 2.2631 | 9.5795 | 1 | 10 | 90.326 | 97.8133 | 26504.2394
2017-07-12 | 5:30 | 1.9207 | 7.8281 | 1 | 10 | 83.7618 | 80.612 | 24578.1173
2017-07-12 | 5:45 | 1.8622 | 6.6697 | 1 | 10 | 81.0288 | 69.3882 | 23776.1542
2017-07-12 | 6:00 | 1.7889 | 6.0408 | 1 | 10 | 79.652 | 0 | 23372.1594
2017-07-12 | 6:15 | 1.7234 | 7.0415 | 1 | 10 | 79.087 | 0 | 23206.3939
2017-07-12 | 6:30 | 1.7647 | 6.8886 | 1 | 10 | 78.844 | 0 | 23135.0761
2017-07-12 | 6:45 | 1.8622 | 6.6099 | 1 | 10 | 78.2081 | 0 | 22948.4999
2017-07-12 | 7:00 | 1.7756 | 5.8094 | 1 | 10 | 77.5549 | 0 | 22756.8194
2017-07-12 | 7:15 | 1.7148 | 5.869 | 1 | 10 | 77.3298 | 0 | 22690.7625
2017-07-12 | 7:30 | 1.7257 | 5.4808 | 1 | 10 | 77.3387 | 0 | 22693.3708
2017-07-12 | 7:45 | 1.746 | 4.9412 | 1 | 10 | 77.1239 | 0 | 22630.3473
2017-07-12 | 8:00 | 1.7296 | 4.8304 | 1 | 10 | 77.4063 | 0 | 22713.2344
2017-07-12 | 8:15 | 1.6742 | 5.9935 | 1 | 10 | 78.7224 | 0 | 23099.3961
2017-07-12 | 8:30 | 1.7312 | 4.9077 | 1 | 10 | 79.2374 | 0 | 23250.5092
2017-07-12 | 8:45 | 1.739 | 5.2155 | 1 | 10 | 79.9276 | 0 | 23453.045
2017-07-12 | 9:00 | 1.7686 | 5.6799 | 1 | 10 | 80.5961 | 0 | 23649.2005
2017-07-12 | 9:15 | 1.7312 | 5.505 | 1 | 10 | 81.0041 | 0 | 23768.9232
2017-07-12 | 9:30 | 1.7499 | 5.4585 | 1 | 10 | 80.7836 | 0 | 23704.2298
2017-07-12 | 9:45 | 1.8177 | 4.9206 | 1 | 10 | 80.8102 | 0 | 23712.0113
2017-07-12 | 10:00 | 1.7717 | 3.1991 | 1 | 10 | 80.6689 | 0 | 23670.5466
2017-07-12 | 10:09 |  |  | 0 |  |  |  | 0
2017-07-12 | 10:15 | 1.6305 | 0 | 0 | 1.5 | 81.1849 | 0 | 23821.9754
2017-07-12 | 10:30 | 1.6695 | 0 | 0 | 1.5 | 82.2574 | 0 | 24136.6761
2017-07-12 | 10:45 | 1.7546 | 0 | 0 | 1.5 | 82.5954 | 0 | 24235.8564
2017-07-12 | 11:00 | 1.7577 | 0 | 0 | 1.5 | 82.2898 | 0 | 24146.1746
2017-07-12 | 11:15 | 1.6656 | 0 | 0 | 1.5 | 83.0396 | 0 | 24366.1789
2017-07-12 | 11:30 | 1.6578 | 0 | 0 | 1.5 | 83.9207 | 0 | 24624.7423
2017-07-12 | 11:45 | 1.7319 | 0 | 0 | 1.5 | 84.7895 | 0 | 24879.6677
2017-07-12 | 12:00 | 1.7585 | 0 | 0 | 1.5 | 85.2482 | 0 | 25014.2663
2017-07-12 | 12:15 | 1.6727 | 0 | 0 | 1.5 | 85.9845 | 0 | 25230.3014
2017-07-12 | 12:30 | 1.6976 | 0 | 0 | 1.5 | 86.3083 | 0 | 25325.3311
2017-07-12 | 12:45 | 1.7764 | 0 | 0 | 1.5 | 86.8893 | 0 | 25495.8002
2017-07-12 | 13:00 | 1.7608 | 0 | 0 | 1.5 | 87.2704 | 0 | 25607.6179
2017-07-12 | 13:15 | 1.6961 | 0 | 0 | 1.5 | 87.9527 | 0 | 25807.8366
2017-07-12 | 13:30 | 1.6664 | 0 | 0 | 1.5 | 88.5784 | 0 | 25991.4243
2017-07-12 | 13:45 | 1.7741 | 0 | 0 | 1.5 | 87.3088 | 0 | 25618.8853
2017-07-12 | 14:00 | 1.7397 | 0 | 0 | 1.5 | 87.5402 | 0 | 25686.8067
2017-07-12 | 14:15 | 1.8404 | 0 | 0 | 1.5 | 88.4826 | 0 | 25963.3355
2017-07-12 | 14:30 | 1.7374 | 0 | 0 | 1.5 | 86.058 | 0 | 25251.869
2017-07-12 | 14:45 | 1.6625 | 0 | 0 | 1.5 | 87.1375 | 0 | 25568.6222
2017-07-12 | 15:00 | 1.753 | 0 | 0 | 1.5 | 88.7597 | 0 | 26044.6422
2017-07-12 | 15:15 | 1.8942 | 0 | 0 | 1.5 | 86.5698 | 0 | 25402.0463
2017-07-12 | 15:30 | 1.6586 | 0 | 0 | 1.5 | 86.2967 | 0 | 25321.9286
2017-07-12 | 15:45 | 1.6188 | 0 | 0 | 1.5 | 88.2055 | 0 | 25882.0021
2017-07-12 | 16:00 | 1.9176 | 0 | 0 | 1.5 | 87.4821 | 0 | 25669.7503
2017-07-12 | 16:15 | 1.7335 | 0 | 0 | 1.5 | 85.8887 | 0 | 25202.2106
2017-07-12 | 16:30 | 1.689 | 0 | 0 | 1.5 | 87.1324 | 0 | 25567.1424
2017-07-12 | 16:45 | 1.8232 | 0 | 0 | 1.5 | 84.695 | 0 | 24851.9373
2017-07-12 | 17:00 | 1.7561 | 0 | 0 | 1.5 | 84.4804 | 0 | 24788.9698
2017-07-12 | 17:15 | 1.7046 | 0 | 0 | 1.5 | 85.7678 | 0 | 25166.7139
2017-07-12 | 17:30 | 1.9472 | 0 | 0 | 1.5 | 83.9146 | 0 | 24622.9468
2017-07-12 | 17:45 | 1.8014 | 0 | 0 | 1.5 | 81.4218 | 0 | 23891.491
2017-07-12 | 18:00 | 1.6797 | 0 | 0 | 1.5 | 81.6671 | 0 | 23963.4625
2017-07-12 | 18:15 | 1.7179 | 0 | 0 | 1.5 | 82.8066 | 0 | 24297.8364
2017-07-12 | 18:30 | 1.8029 | 0 | 0 | 1.5 | 82.8581 | 0 | 24312.9298
2017-07-12 | 18:45 | 1.7975 | 0 | 0 | 1.5 | 82.826 | 0 | 24303.5116
2017-07-12 | 19:00 | 1.7897 | 0 | 0 | 1.5 | 82.9289 | 0 | 24333.7136
2017-07-12 | 19:15 | 1.7936 | 0 | 0 | 1.5 | 82.493 | 0 | 24205.7976
2017-07-12 | 19:30 | 1.8138 | 0 | 0 | 1.5 | 81.8111 | 0 | 24005.711
2017-07-12 | 19:45 | 1.8138 | 0 | 0 | 1.5 | 81.0471 | 0 | 23781.5248
2017-07-12 | 20:00 | 1.7936 | 0 | 0 | 1.5 | 80.2536 | 0 | 23548.686
2017-07-12 | 20:15 | 1.7639 | 0 | 0 | 1.5 | 79.4269 | 0 | 23306.1203
2017-07-12 | 20:30 | 1.7967 | 0 | 0 | 1.5 | 78.9419 | 0 | 23163.796
2017-07-12 | 20:45 | 1.7951 | 0 | 0 | 1.5 | 78.4064 | 0 | 23006.6876
2017-07-12 | 21:00 | 1.7709 | 0 | 0 | 1.5 | 77.674 | 0 | 22791.7852
2017-07-12 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 22:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 22:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 22:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 23:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 23:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 23:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 0:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 0:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 0:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 1:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 2:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 4:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 5:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-13 | 5:15 | 2.189 | 9.8969 | 1 | 10 | 92.2507 | 99.182 | 27068.9873
2017-07-13 | 5:30 | 2.0268 | 8.3913 | 1 | 10 | 84.9745 | 84.8535 | 24933.9514
2017-07-13 | 5:45 | 1.9472 | 7.0177 | 1 | 10 | 81.6459 | 71.3537 | 23957.2477
2017-07-13 | 6:00 | 1.8474 | 6.4395 | 1 | 10 | 79.8737 | 65.6035 | 23437.2198
2017-07-13 | 6:15 | 1.7865 | 6.5317 | 1 | 10 | 78.966 | 66.2296 | 23170.8815
2017-07-13 | 6:30 | 1.8029 | 6.2368 | 1 | 10 | 78.2681 | 0 | 22966.1047
2017-07-13 | 6:45 | 1.7943 | 6.3091 | 1 | 10 | 77.8687 | 0 | 22848.9032
2017-07-13 | 7:00 | 1.7444 | 5.3839 | 1 | 10 | 77.4363 | 0 | 22722.0279
2017-07-13 | 7:15 | 1.7171 | 5.8962 | 1 | 10 | 77.5519 | 0 | 22755.9441
2017-07-13 | 7:30 | 1.7647 | 5.0513 | 1 | 10 | 77.6418 | 0 | 22782.3113
2017-07-13 | 7:45 | 1.824 | 4.2649 | 1 | 10 | 77.369 | 0 | 22702.2693
2017-07-13 | 8:00 | 1.7249 | 3.5113 | 1 | 10 | 78.0956 | 0 | 22915.4927
2017-07-13 | 8:15 | 1.6906 | 4.1981 | 1 | 10 | 79.8471 | 0 | 23429.4337
2017-07-13 | 8:30 | 1.7062 | 4.2837 | 1 | 10 | 81.1383 | 0 | 23808.2925
2017-07-13 | 8:45 | 1.7951 | 4.6729 | 1 | 10 | 81.115 | 0 | 23801.4489
2017-07-13 | 9:00 | 1.7764 | 4.2096 | 1 | 10 | 80.4527 | 0 | 23607.1135
2017-07-13 | 9:15 | 1.6875 | 4.5966 | 1 | 10 | 80.6098 | 0 | 23653.2281
2017-07-13 | 9:30 | 1.7117 | 5.1359 | 1 | 10 | 81.0428 | 0 | 23780.2622
2017-07-13 | 9:45 | 1.7039 | 5.0334 | 1 | 10 | 81.096 | 0 | 23795.8925
2017-07-13 | 10:00 | 1.8209 | 4.123 | 1 | 10 | 81.5325 | 0 | 23923.9764
2017-07-13 | 10:15 | 1.7046 | 1.7893 | 1 | 10 | 81.9534 | 0 | 24047.4779
2017-07-13 | 10:19 |  |  | 0 |  |  |  | 0
2017-07-13 | 10:25 |  |  | 1 |  |  |  | 0
2017-07-13 | 10:30 | 1.7561 | 0 | 1 | 10 | 81.6832 | 0 | 23968.1882
2017-07-13 | 10:38 |  |  | 0 |  |  |  | 0
2017-07-13 | 10:45 | 1.7889 | 0 | 0 | 1.5 | 80.9423 | 0 | 23750.7788
2017-07-13 | 11:00 | 1.7483 | 0 | 0 | 1.5 | 81.0225 | 0 | 23774.3296
2017-07-13 | 11:15 | 1.7062 | 0 | 0 | 1.5 | 81.2722 | 0 | 23847.5861
2017-07-13 | 11:30 | 1.6337 | 0 | 0 | 1.5 | 82.0339 | 0 | 24071.0848
2017-07-13 | 11:45 | 1.668 | 0 | 0 | 1.5 | 82.7348 | 0 | 24276.7659
2017-07-13 | 12:00 | 1.7436 | 0 | 0 | 1.5 | 83.1502 | 0 | 24398.6579
2017-07-13 | 12:15 | 1.7101 | 0 | 0 | 1.5 | 83.8967 | 0 | 24617.6791
2017-07-13 | 12:30 | 1.728 | 0 | 0 | 1.5 | 84.2794 | 0 | 24729.9804
2017-07-13 | 12:45 | 1.7772 | 0 | 0 | 1.5 | 84.1653 | 0 | 24696.49
2017-07-13 | 13:00 | 1.8185 | 0 | 0 | 1.5 | 83.279 | 0 | 24436.4489
2017-07-13 | 13:15 | 1.7452 | 0 | 0 | 1.5 | 83.1076 | 0 | 24386.1502
2017-07-13 | 13:30 | 1.6633 | 0 | 0 | 1.5 | 83.4327 | 0 | 24481.5248
2017-07-13 | 13:45 | 1.6968 | 0 | 0 | 1.5 | 83.9092 | 0 | 24621.362
2017-07-13 | 14:00 | 1.785 | 0 | 0 | 1.5 | 83.7275 | 0 | 24568.0319
2017-07-13 | 14:15 | 1.7538 | 0 | 0 | 1.5 | 84.1347 | 0 | 24687.5195
2017-07-13 | 14:30 | 1.7234 | 0 | 0 | 1.5 | 85.0195 | 0 | 24947.1551
2017-07-13 | 14:45 | 1.6898 | 0 | 0 | 1.5 | 85.7948 | 0 | 25174.6344
2017-07-13 | 15:00 | 1.7982 | 0 | 0 | 1.5 | 85.9575 | 0 | 25222.3765
2017-07-13 | 15:15 | 1.7468 | 0 | 0 | 1.5 | 86.436 | 0 | 25362.8046
2017-07-13 | 15:30 | 1.6664 | 0 | 0 | 1.5 | 87.0657 | 0 | 25547.5719
2017-07-13 | 15:45 | 1.7163 | 0 | 0 | 1.5 | 87.1149 | 0 | 25562.0136
2017-07-13 | 16:00 | 1.8185 | 0 | 0 | 1.5 | 86.3143 | 0 | 25327.0706
2017-07-13 | 16:15 | 1.8162 | 0 | 0 | 1.5 | 85.748 | 0 | 25160.9202
2017-07-13 | 16:30 | 1.7078 | 0 | 0 | 1.5 | 85.7569 | 0 | 25163.5305
2017-07-13 | 16:45 | 1.6867 | 0 | 0 | 1.5 | 86.167 | 0 | 25283.8574
2017-07-13 | 17:00 | 1.7826 | 0 | 0 | 1.5 | 86.2747 | 0 | 25315.4608
2017-07-13 | 17:15 | 1.8536 | 0 | 0 | 1.5 | 85.7608 | 0 | 25164.6743
2017-07-13 | 17:30 | 1.7468 | 0 | 0 | 1.5 | 84.9578 | 0 | 24929.06
2017-07-13 | 17:45 | 1.7694 | 0 | 0 | 1.5 | 84.0297 | 0 | 24656.7107
2017-07-13 | 18:00 | 1.8162 | 0 | 0 | 1.5 | 82.5867 | 0 | 24233.2997
2017-07-13 | 18:15 | 1.7538 | 0 | 0 | 1.5 | 81.6455 | 0 | 23957.1224
2017-07-13 | 18:30 | 1.7655 | 0 | 0 | 1.5 | 80.823 | 0 | 23715.7903
2017-07-13 | 18:45 | 1.7351 | 0 | 0 | 1.5 | 80.1084 | 0 | 23506.0863
2017-07-13 | 19:00 | 1.7273 | 0 | 0 | 1.5 | 79.832 | 0 | 23424.9809
2017-07-13 | 19:15 | 1.7943 | 0 | 0 | 1.5 | 79.6248 | 0 | 23364.1852
2017-07-13 | 19:30 | 1.8138 | 0 | 0 | 1.5 | 79.1997 | 0 | 23239.4569
2017-07-13 | 19:45 | 1.7585 | 0 | 0 | 1.5 | 78.3649 | 0 | 22994.5048
2017-07-13 | 20:00 | 1.7795 | 0 | 0 | 1.5 | 77.7606 | 0 | 22817.1674
2017-07-13 | 20:15 | 1.7881 | 0 | 0 | 1.5 | 77.2847 | 0 | 22677.5432
2017-07-13 | 20:30 | 1.7444 | 0 | 0 | 1.5 | 77.2703 | 0 | 22673.3278
2017-07-13 | 20:45 | 1.7249 | 0 | 0 | 1.5 | 77.4114 | 0 | 22714.7098
2017-07-13 | 21:00 | 1.7148 | 0 | 0 | 1.5 | 77.087 | 0 | 22619.5344
2017-07-13 | 21:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 21:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 22:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 22:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 22:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 23:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 23:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 1:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 2:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 3:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 3:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 3:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 4:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 4:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 4:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 5:00 | 0.03154 | 0 | 1 | 0 | 25 | 0 | 7335.7143
2017-07-14 | 5:15 | 2.2686 | 9.3076 | 1 | 10 | 89.6563 | 95.2045 | 26307.7145
2017-07-14 | 5:30 | 1.994 | 7.5144 | 1 | 10 | 82.86 | 77.6792 | 24313.5029
2017-07-14 | 5:45 | 1.7873 | 6.4417 | 1 | 10 | 80.2481 | 66.9914 | 23547.0944
2017-07-14 | 6:00 | 1.7429 | 6.0771 | 1 | 10 | 79.1924 | 63.6038 | 23237.319
2017-07-14 | 6:15 | 1.7881 | 6.575 | 1 | 10 | 78.6057 | 68.1407 | 23065.153
2017-07-14 | 6:30 | 1.7982 | 6.2392 | 1 | 10 | 78.0262 | 65.0343 | 22895.1185
2017-07-14 | 6:45 | 1.7631 | 6.2968 | 1 | 10 | 77.8845 | 0 | 22853.5258
2017-07-14 | 7:00 | 1.7397 | 6.3624 | 1 | 10 | 77.4047 | 0 | 22712.762
2017-07-14 | 7:15 | 1.7928 | 5.5405 | 1 | 10 | 76.9979 | 0 | 22593.382
2017-07-14 | 7:30 | 1.7889 | 4.7986 | 1 | 10 | 76.6925 | 0 | 22503.7563
2017-07-14 | 7:45 | 1.7327 | 4.4792 | 1 | 10 | 76.486 | 0 | 22443.1666
2017-07-14 | 8:00 | 1.6797 | 4.7181 | 1 | 10 | 76.7654 | 0 | 22525.1716
2017-07-14 | 8:15 | 1.6734 | 4.8365 | 1 | 10 | 77.4937 | 0 | 22738.8695
2017-07-14 | 8:30 | 1.8076 | 4.5049 | 1 | 10 | 77.8777 | 0 | 22851.5314
2017-07-14 | 8:45 | 1.7234 | 4.7032 | 1 | 10 | 78.1595 | 0 | 22934.2395
2017-07-14 | 9:00 | 1.7304 | 4.0689 | 1 | 10 | 78.7019 | 0 | 23093.3805
2017-07-14 | 9:15 | 1.7639 | 4.9413 | 1 | 10 | 79.192 | 0 | 23237.1981
2017-07-14 | 9:30 | 1.6937 | 5.3538 | 1 | 10 | 79.5844 | 0 | 23352.3424
2017-07-14 | 9:45 | 1.7764 | 4.6572 | 1 | 10 | 79.4349 | 0 | 23308.4821
2017-07-14 | 10:00 |  |  | 0 |  |  |  | 0
2017-07-14 | 10:00 | 1.753 | 2.7873 | 0 | 1.5 | 79.6316 | 0 | 23366.1863
2017-07-14 | 10:15 | 1.7553 | 0 | 0 | 1.5 | 80.66 | 0 | 23667.943
2017-07-14 | 10:30 | 1.767 | 0 | 0 | 1.5 | 80.9085 | 0 | 23740.8659
2017-07-14 | 10:45 | 1.7717 | 0 | 0 | 1.5 | 80.8304 | 0 | 23717.9394
2017-07-14 | 11:00 | 1.7202 | 0 | 0 | 1.5 | 80.9966 | 0 | 23766.7113
2017-07-14 | 11:15 | 1.7202 | 0 | 0 | 1.5 | 81.5812 | 0 | 23938.255
2017-07-14 | 11:30 | 1.7179 | 0 | 0 | 1.5 | 81.6436 | 0 | 23956.574
2017-07-14 | 11:45 | 1.7288 | 0 | 0 | 1.5 | 81.7865 | 0 | 23998.5067
2017-07-14 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 82.0367 | 0 | 24071.9132
2017-07-14 | 12:15 | 1.7078 | 0 | 0 | 1.5 | 82.5149 | 0 | 24212.2316
2017-07-14 | 12:30 | 1.7686 | 0 | 0 | 1.5 | 82.8379 | 0 | 24306.9993
2017-07-14 | 12:45 | 1.7382 | 0 | 0 | 1.5 | 83.0418 | 0 | 24366.8394
2017-07-14 | 13:00 | 1.7304 | 0 | 0 | 1.5 | 83.5206 | 0 | 24507.33
2017-07-14 | 13:15 | 1.7015 | 0 | 0 | 1.5 | 84.0469 | 0 | 24661.77
2017-07-14 | 13:30 | 1.728 | 0 | 0 | 1.5 | 84.7078 | 0 | 24855.6937
2017-07-14 | 13:45 | 1.7117 | 0 | 0 | 1.5 | 85.6665 | 0 | 25136.9975
2017-07-14 | 14:00 | 1.8092 | 0 | 0 | 1.5 | 86.3621 | 0 | 25341.1185
2017-07-14 | 14:15 | 1.8279 | 0 | 0 | 1.5 | 83.8654 | 0 | 24608.5051
2017-07-14 | 14:30 | 1.7514 | 0 | 0 | 1.5 | 84.4428 | 0 | 24777.9176
2017-07-14 | 14:45 | 1.7413 | 0 | 0 | 1.5 | 85.1015 | 0 | 24971.2098
2017-07-14 | 15:00 | 1.9028 | 0 | 0 | 1.5 | 83.85 | 0 | 24603.9986
2017-07-14 | 15:15 | 1.7241 | 0 | 0 | 1.5 | 82.3603 | 0 | 24166.8646
2017-07-14 | 15:30 | 1.6547 | 0 | 0 | 1.5 | 83.8524 | 0 | 24604.6882
2017-07-14 | 15:45 | 1.8224 | 0 | 0 | 1.5 | 85.0774 | 0 | 24964.1355
2017-07-14 | 16:00 | 1.7748 | 0 | 0 | 1.5 | 82.9891 | 0 | 24351.3657
2017-07-14 | 16:15 | 1.6945 | 0 | 0 | 1.5 | 83.5794 | 0 | 24524.5927
2017-07-14 | 16:30 | 1.7007 | 0 | 0 | 1.5 | 85.1236 | 0 | 24977.7063
2017-07-14 | 16:45 | 1.8848 | 0 | 0 | 1.5 | 82.8195 | 0 | 24301.602
2017-07-14 | 17:00 | 1.7351 | 0 | 0 | 1.5 | 82.5336 | 0 | 24217.7096
2017-07-14 | 17:15 | 1.6945 | 0 | 0 | 1.5 | 83.3381 | 0 | 24453.7808
2017-07-14 | 17:30 | 1.7343 | 0 | 0 | 1.5 | 83.4357 | 0 | 24482.4271
2017-07-14 | 17:45 | 1.824 | 0 | 0 | 1.5 | 82.4962 | 0 | 24206.7424
2017-07-14 | 18:00 | 1.7062 | 0 | 0 | 1.5 | 81.7524 | 0 | 23988.4888
2017-07-14 | 18:15 | 1.7226 | 0 | 0 | 1.5 | 81.8966 | 0 | 24030.7909
2017-07-14 | 18:30 | 1.7491 | 0 | 0 | 1.5 | 81.8964 | 0 | 24030.7572
2017-07-14 | 18:45 | 1.7842 | 0 | 0 | 1.5 | 82.107 | 0 | 24092.545
2017-07-14 | 19:00 | 1.7569 | 0 | 0 | 1.5 | 82.28 | 0 | 24143.3026
2017-07-14 | 19:15 | 1.739 | 0 | 0 | 1.5 | 82.4929 | 0 | 24205.7641
2017-07-14 | 19:30 | 1.7312 | 0 | 0 | 1.5 | 82.4072 | 0 | 24180.6349
2017-07-14 | 19:45 | 1.7959 | 0 | 0 | 1.5 | 81.8387 | 0 | 24013.8058
2017-07-14 | 20:00 | 1.7873 | 0 | 0 | 1.5 | 81.3458 | 0 | 23869.1892
2017-07-14 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 80.6626 | 0 | 23668.7042
2017-07-14 | 20:30 | 1.7756 | 0 | 0 | 1.5 | 79.7983 | 0 | 23415.1018
2017-07-14 | 20:45 | 1.7694 | 0 | 0 | 1.5 | 79.0388 | 0 | 23192.2498
2017-07-14 | 21:00 | 1.7468 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 22:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 22:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 23:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 23:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-14 | 23:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-15 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-15 | 0:15 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 0:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 0:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 0:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 0:45 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 0:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 1:00 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 1:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 1:15 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 1:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 1:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 1:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 1:45 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 1:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 2:00 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 2:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 2:15 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 2:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 2:30 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 2:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 2:45 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 2:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 3:00 | 0.02686 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 3:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 3:15 | 0.02686 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 3:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 3:30 | 0.02608 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 3:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 3:45 | 0.02608 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 3:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 4:00 | 0.02608 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 4:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 4:15 | 0.02608 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 4:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 4:30 | 0.02608 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 4:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 4:45 | 0.02608 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 4:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 5:00 | 0.02608 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 5:00 |  |  |  | 1.5 | 25 |  | 7335.7143
2017-07-15 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-15 | 5:15 | 2.2538 | 10 | 1 |  |  | 100 | 0
2017-07-15 | 5:15 |  |  |  | 10 | 91.8101 |  | 26939.7009
2017-07-15 | 5:30 | 1.9753 | 9.0743 | 1 | 10 |  | 91.2621 | 0
2017-07-15 | 5:30 |  |  |  | 10 | 85.0562 |  | 24957.9075
2017-07-15 | 5:45 | 1.8599 | 7.5149 | 1 |  |  | 76.2243 | 0
2017-07-15 | 5:45 |  |  |  | 10 | 81.3586 |  | 23872.9278
2017-07-15 | 6:00 | 1.7819 | 6.922 | 1 | 10 |  | 70.2639 | 0
2017-07-15 | 6:00 |  |  |  | 10 | 80.2326 |  | 23542.5363
2017-07-15 | 6:15 | 1.7366 | 7.4087 | 1 |  |  | 74.7687 | 0
2017-07-15 | 6:15 |  |  |  | 10 | 79.8563 |  | 23432.1133
2017-07-15 | 6:30 | 1.7608 | 6.9489 | 1 | 10 |  | 70.4725 | 0
2017-07-15 | 6:30 |  |  |  | 10 | 78.5419 |  | 23046.449
2017-07-15 | 6:45 | 1.8271 | 6.5129 | 1 |  |  | 66.3443 | 0
2017-07-15 | 6:45 |  |  |  | 10 | 77.4254 |  | 22718.8333
2017-07-15 | 7:00 | 1.7873 | 6.0311 | 1 | 10 |  | 61.752 | 0
2017-07-15 | 7:00 |  |  |  | 10 | 76.5913 |  | 22474.0737
2017-07-15 | 7:15 | 1.7007 | 6.3926 | 1 |  |  | 0 | 0
2017-07-15 | 7:15 |  |  |  | 10 | 76.2324 |  | 22368.7616
2017-07-15 | 7:30 | 1.7179 | 6.4107 | 1 | 10 |  | 0 | 0
2017-07-15 | 7:30 |  |  |  | 10 | 76.0195 |  | 22306.3003
2017-07-15 | 7:45 | 1.7663 | 6.1953 | 1 |  |  | 0 | 0
2017-07-15 | 7:45 |  |  |  | 10 | 75.792 |  | 22239.545
2017-07-15 | 8:00 | 1.753 | 5.9928 | 1 | 10 |  | 0 | 0
2017-07-15 | 8:00 |  |  |  | 10 | 75.7606 |  | 22230.317
2017-07-15 | 8:15 | 1.7639 | 6.1669 | 1 |  |  | 0 | 0
2017-07-15 | 8:15 |  |  |  | 10 | 75.6433 |  | 22195.9131
2017-07-15 | 8:30 | 1.6625 | 6.3186 | 1 | 10 |  | 0 | 0
2017-07-15 | 8:30 |  |  |  | 10 | 76.0321 |  | 22309.9761
2017-07-15 | 8:45 | 1.7655 | 6.3133 | 1 |  |  | 0 | 0
2017-07-15 | 8:45 |  |  |  | 10 | 76.3506 |  | 22403.439
2017-07-15 | 9:00 | 1.7366 | 6.245 | 1 | 10 |  | 0 | 0
2017-07-15 | 9:00 |  |  |  | 10 | 76.6056 |  | 22478.2779
2017-07-15 | 9:15 | 1.7444 | 6.7635 | 1 |  |  | 0 | 0
2017-07-15 | 9:15 |  |  |  | 10 | 77.0568 |  | 22610.6559
2017-07-15 | 9:30 | 1.6758 | 4.9766 | 1 | 10 |  | 0 | 0
2017-07-15 | 9:30 |  |  |  | 10 | 77.5948 |  | 22768.521
2017-07-15 | 9:36 |  |  | 0 |  |  |  | 0
2017-07-15 | 9:45 | 1.7187 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 9:45 |  |  |  | 1.5 | 78.7376 |  | 23103.8621
2017-07-15 | 10:00 | 1.7936 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 10:00 |  |  |  | 1.5 | 79.0605 |  | 23198.6075
2017-07-15 | 10:15 | 1.7265 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 10:15 |  |  |  | 1.5 | 78.7402 |  | 23104.6256
2017-07-15 | 10:30 | 1.7553 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 10:30 |  |  |  | 1.5 | 78.7854 |  | 23117.8874
2017-07-15 | 10:45 | 1.7093 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 10:45 |  |  |  | 1.5 | 78.9092 |  | 23154.2124
2017-07-15 | 11:00 | 1.8209 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 11:00 |  |  |  | 1.5 | 78.3295 |  | 22984.1218
2017-07-15 | 11:15 | 1.8037 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 11:15 |  |  |  | 1.5 | 77.6521 |  | 22785.3468
2017-07-15 | 11:30 | 1.6649 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 11:30 |  |  |  | 1.5 | 77.8805 |  | 22852.3753
2017-07-15 | 11:45 | 1.7413 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 11:45 |  |  |  | 1.5 | 78.2638 |  | 22964.8377
2017-07-15 | 12:00 | 1.7881 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 12:00 |  |  |  | 1.5 | 77.7803 |  | 22822.9702
2017-07-15 | 12:15 | 1.7897 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 12:15 |  |  |  | 1.5 | 76.6589 |  | 22493.9221
2017-07-15 | 12:30 | 1.7109 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 12:30 |  |  |  | 1.5 | 76.4384 |  | 22429.2217
2017-07-15 | 12:45 | 1.7678 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 12:45 |  |  |  | 1.5 | 76.4861 |  | 22443.1956
2017-07-15 | 13:00 | 1.7592 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 13:00 |  |  |  | 1.5 | 76.182 |  | 22353.9707
2017-07-15 | 13:15 | 1.7522 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 13:15 |  |  |  | 1.5 | 75.9517 |  | 22286.3894
2017-07-15 | 13:30 | 1.753 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 13:30 |  |  |  | 1.5 | 75.8127 |  | 22245.6164
2017-07-15 | 13:45 | 1.7686 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 13:45 |  |  |  | 1.5 | 75.646 |  | 22196.6989
2017-07-15 | 14:00 | 1.746 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 14:00 |  |  |  | 1.5 | 76.3461 |  | 22402.1271
2017-07-15 | 14:15 | 1.7039 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 14:15 |  |  |  | 1.5 | 76.8729 |  | 22556.7082
2017-07-15 | 14:30 | 1.7054 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 14:30 |  |  |  | 1.5 | 77.2395 |  | 22664.2811
2017-07-15 | 14:45 | 1.7741 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 14:45 |  |  |  | 1.5 | 77.5279 |  | 22748.8965
2017-07-15 | 15:00 | 1.7741 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 15:00 |  |  |  | 1.5 | 77.6068 |  | 22772.058
2017-07-15 | 15:15 | 1.7452 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 15:15 |  |  |  | 1.5 | 77.7379 |  | 22810.5142
2017-07-15 | 15:30 | 1.6875 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 15:30 |  |  |  | 1.5 | 77.7861 |  | 22824.6739
2017-07-15 | 15:45 | 1.7561 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 15:45 |  |  |  | 1.5 | 77.995 |  | 22885.9488
2017-07-15 | 16:00 | 1.7928 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 16:00 |  |  |  | 1.5 | 77.829 |  | 22837.2552
2017-07-15 | 16:15 | 1.7655 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 16:15 |  |  |  | 1.5 | 77.7336 |  | 22809.2651
2017-07-15 | 16:30 | 1.728 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 16:30 |  |  |  | 1.5 | 77.6339 |  | 22780.0076
2017-07-15 | 16:45 | 1.7288 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 16:45 |  |  |  | 1.5 | 77.5951 |  | 22768.6129
2017-07-15 | 17:00 | 1.7897 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 17:00 |  |  |  | 1.5 | 77.3794 |  | 22705.3365
2017-07-15 | 17:15 | 1.753 | 0 | 0 |  | 77.2049 | 0 | 22654.1288
2017-07-15 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-07-15 | 17:30 | 1.707 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 17:30 |  |  |  | 1.5 | 77.2716 |  | 22673.6905
2017-07-15 | 17:45 | 1.7257 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 17:45 |  |  |  | 1.5 | 77.4177 |  | 22716.5789
2017-07-15 | 18:00 | 1.7834 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 18:00 |  |  |  | 1.5 | 77.3037 |  | 22683.1198
2017-07-15 | 18:15 | 1.7655 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 18:15 |  |  |  | 1.5 | 77.2349 |  | 22662.9334
2017-07-15 | 18:30 | 1.7202 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 18:30 |  |  |  | 1.5 | 77.3484 |  | 22696.2384
2017-07-15 | 18:45 | 1.7312 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 18:45 |  |  |  | 1.5 | 77.5668 |  | 22760.3162
2017-07-15 | 19:00 | 1.785 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 19:00 |  |  |  | 1.5 | 77.4617 |  | 22729.4827
2017-07-15 | 19:15 | 1.8068 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 19:15 |  |  |  | 1.5 | 77.2021 |  | 22653.296
2017-07-15 | 19:30 | 1.7756 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 19:30 |  |  |  | 1.5 | 76.6042 |  | 22477.8481
2017-07-15 | 19:45 | 1.7522 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 19:45 |  |  |  | 1.5 | 76.3447 |  | 22401.7107
2017-07-15 | 20:00 | 1.7569 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 20:00 |  |  |  | 1.5 | 76.3668 |  | 22408.1916
2017-07-15 | 20:15 | 1.7249 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 20:15 |  |  |  | 1.5 | 76.2965 |  | 22387.5621
2017-07-15 | 20:30 | 1.7335 | 0 | 0 | 1.5 |  | 0 | 0
2017-07-15 | 20:30 |  |  |  | 1.5 | 76.32 |  | 22394.4818
2017-07-15 | 20:45 | 1.7327 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 20:45 |  |  |  | 1.5 | 75.8936 |  | 22269.3486
2017-07-15 | 21:00 | 1.8053 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 21:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 21:15 | 0.03544 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 21:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 21:30 | 0.03388 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 21:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 21:45 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 21:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 22:00 | 0.03232 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 22:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 22:15 | 0.02998 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 22:15 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 22:30 | 0.03076 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 22:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 22:45 | 0.03076 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 22:45 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 23:00 | 0.02998 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 23:00 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 23:15 |  | 0 |  |  |  | 0 | 0
2017-07-15 | 23:15 | 0.0292 |  | 0 | 0 | 0 |  | 0
2017-07-15 | 23:30 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-07-15 | 23:30 |  |  |  | 0 | 0 |  | 0
2017-07-15 | 23:45 | 0.0292 | 0 | 0 |  |  | 0 | 0
2017-07-15 | 23:45 |  |  |  | 0 | 0 |  | 0
2017-07-16 | 0:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-07-16 | 0:00 |  |  |  | 0 | 0 |  | 0
2017-07-16 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 2:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 2:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 3:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 3:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 3:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 3:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 4:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 4:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 4:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 4:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 5:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-16 | 5:15 | 2.2054 | 9.352 | 1 | 10 | 89.1669 | 96.0194 | 26164.1184
2017-07-16 | 5:30 | 1.9535 | 8.0026 | 1 | 10 | 82.4211 | 82.9174 | 24184.698
2017-07-16 | 5:45 | 1.9028 | 6.4684 | 1 | 10 | 78.822 | 68.0858 | 23128.6175
2017-07-16 | 6:00 | 1.7748 | 5.9099 | 1 | 10 | 77.4031 | 0 | 22712.2919
2017-07-16 | 6:15 | 1.7491 | 6.5057 | 1 | 10 | 76.819 | 0 | 22540.8874
2017-07-16 | 6:30 | 1.8037 | 6.7551 | 1 | 10 | 76.448 | 0 | 22432.0292
2017-07-16 | 6:45 | 1.7663 | 6.3967 | 1 | 10 | 76.0628 | 0 | 22319.0046
2017-07-16 | 7:00 | 1.7733 | 6.1078 | 1 | 10 | 75.6265 | 0 | 22190.9612
2017-07-16 | 7:15 | 1.7663 | 6.0703 | 1 | 10 | 75.5968 | 0 | 22182.2704
2017-07-16 | 7:30 | 1.7702 | 5.8134 | 1 | 10 | 75.3926 | 0 | 22122.3567
2017-07-16 | 7:45 | 1.817 | 5.8559 | 1 | 10 | 75.2393 | 0 | 22077.348
2017-07-16 | 8:00 | 1.8123 | 5.6647 | 1 | 10 | 75.063 | 0 | 22025.6142
2017-07-16 | 8:15 | 1.7631 | 5.6298 | 1 | 10 | 75.3102 | 0 | 22098.1588
2017-07-16 | 8:30 | 1.7405 | 5.7071 | 1 | 10 | 75.8027 | 0 | 22242.6812
2017-07-16 | 8:45 | 1.7304 | 5.793 | 1 | 10 | 76.0887 | 0 | 22326.605
2017-07-16 | 9:00 | 1.8099 | 6.0154 | 1 | 10 | 76.0456 | 0 | 22313.9409
2017-07-16 | 9:15 | 1.6766 | 5.8647 | 1 | 10 | 76.2094 | 0 | 22362.0256
2017-07-16 | 9:30 | 1.7319 | 6.591 | 1 | 10 | 76.6654 | 0 | 22495.8068
2017-07-16 | 9:45 | 1.7241 | 4.1187 | 1 | 10 | 77.0714 | 0 | 22614.9652
2017-07-16 | 9:51 |  |  | 0 |  |  |  | 0
2017-07-16 | 10:00 | 1.7819 | 0 | 0 | 1.5 | 77.7682 | 0 | 22819.4198
2017-07-16 | 10:15 | 1.714 | 0 | 0 | 1.5 | 78.2846 | 0 | 22970.9336
2017-07-16 | 10:22 |  |  | 1 |  |  |  | 0
2017-07-16 | 10:29 |  |  | 0 |  |  |  | 0
2017-07-16 | 10:30 | 1.7358 | 0 | 0 | 1.5 | 77.9964 | 0 | 22886.3696
2017-07-16 | 10:45 | 1.7436 | 0 | 0 | 1.5 | 78.1135 | 0 | 22920.7245
2017-07-16 | 11:00 | 1.8123 | 0 | 0 | 1.5 | 78.0173 | 0 | 22892.4926
2017-07-16 | 11:15 | 1.7787 | 0 | 0 | 1.5 | 78.0506 | 0 | 22902.289
2017-07-16 | 11:30 | 1.7273 | 0 | 0 | 1.5 | 78.129 | 0 | 22925.2914
2017-07-16 | 11:45 | 1.7397 | 0 | 0 | 1.5 | 78.246 | 0 | 22959.6237
2017-07-16 | 12:00 | 1.7585 | 0 | 0 | 1.5 | 77.7878 | 0 | 22825.1575
2017-07-16 | 12:15 | 1.7405 | 0 | 0 | 1.5 | 77.6857 | 0 | 22795.2172
2017-07-16 | 12:30 | 1.7475 | 0 | 0 | 1.5 | 77.7193 | 0 | 22805.0676
2017-07-16 | 12:45 | 1.7452 | 0 | 0 | 1.5 | 77.5702 | 0 | 22761.3191
2017-07-16 | 13:00 | 1.7709 | 0 | 0 | 1.5 | 77.6322 | 0 | 22779.4973
2017-07-16 | 13:15 | 1.7842 | 0 | 0 | 1.5 | 77.0884 | 0 | 22619.9532
2017-07-16 | 13:30 | 1.7436 | 0 | 0 | 1.5 | 77.1414 | 0 | 22635.4917
2017-07-16 | 13:45 | 1.7101 | 0 | 0 | 1.5 | 77.4268 | 0 | 22719.2409
2017-07-16 | 14:00 | 1.8138 | 0 | 0 | 1.5 | 76.9695 | 0 | 22585.0498
2017-07-16 | 14:15 | 1.8185 | 0 | 0 | 1.5 | 76.908 | 0 | 22567.0104
2017-07-16 | 14:30 | 1.7421 | 0 | 0 | 1.5 | 76.5629 | 0 | 22465.755
2017-07-16 | 14:45 | 1.7234 | 0 | 0 | 1.5 | 76.3963 | 0 | 22416.8463
2017-07-16 | 15:00 | 1.7709 | 0 | 0 | 1.5 | 76.6649 | 0 | 22495.6659
2017-07-16 | 15:15 | 1.8014 | 0 | 0 | 1.5 | 76.3098 | 0 | 22391.4753
2017-07-16 | 15:30 | 1.6906 | 0 | 0 | 1.5 | 76.3209 | 0 | 22394.7303
2017-07-16 | 15:45 | 1.7491 | 0 | 0 | 1.5 | 76.4102 | 0 | 22420.9388
2017-07-16 | 16:00 | 1.753 | 0 | 0 | 1.5 | 76.6992 | 0 | 22505.7511
2017-07-16 | 16:15 | 1.8216 | 0 | 0 | 1.5 | 76.3035 | 0 | 22389.6194
2017-07-16 | 16:30 | 1.7101 | 0 | 0 | 1.5 | 76.156 | 0 | 22346.3436
2017-07-16 | 16:45 | 1.7101 | 0 | 0 | 1.5 | 76.3582 | 0 | 22405.691
2017-07-16 | 17:00 | 1.7475 | 0 | 0 | 1.5 | 76.7067 | 0 | 22507.9474
2017-07-16 | 17:15 | 1.8107 | 0 | 0 | 1.5 | 76.3334 | 0 | 22398.3996
2017-07-16 | 17:30 | 1.7647 | 0 | 0 | 1.5 | 76.4015 | 0 | 22418.3909
2017-07-16 | 17:45 | 1.6586 | 0 | 0 | 1.5 | 76.4926 | 0 | 22445.114
2017-07-16 | 18:00 | 1.7421 | 0 | 0 | 1.5 | 76.669 | 0 | 22496.8881
2017-07-16 | 18:15 | 1.7951 | 0 | 0 | 1.5 | 76.7375 | 0 | 22516.9826
2017-07-16 | 18:30 | 1.7156 | 0 | 0 | 1.5 | 76.6457 | 0 | 22490.0289
2017-07-16 | 18:45 | 1.7234 | 0 | 0 | 1.5 | 76.8757 | 0 | 22557.5207
2017-07-16 | 19:00 | 1.7366 | 0 | 0 | 1.5 | 77.0993 | 0 | 22623.1298
2017-07-16 | 19:15 | 1.785 | 0 | 0 | 1.5 | 77.3291 | 0 | 22690.5656
2017-07-16 | 19:30 | 1.7366 | 0 | 0 | 1.5 | 77.1788 | 0 | 22646.4592
2017-07-16 | 19:45 | 1.6922 | 0 | 0 | 1.5 | 77.4611 | 0 | 22729.2946
2017-07-16 | 20:00 | 1.6859 | 0 | 0 | 1.5 | 77.7139 | 0 | 22803.4734
2017-07-16 | 20:15 | 1.7078 | 0 | 0 | 1.5 | 77.6669 | 0 | 22789.6743
2017-07-16 | 20:30 | 1.7553 | 0 | 0 | 1.5 | 77.2826 | 0 | 22676.932
2017-07-16 | 20:45 | 1.7257 | 0 | 0 | 1.5 | 76.9586 | 0 | 22581.8664
2017-07-16 | 21:00 | 1.6922 | 0 | 0 | 1.5 | 76.671 | 0 | 22497.4658
2017-07-16 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 3:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 3:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 3:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 3:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 4:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 4:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 4:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 4:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 5:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-17 | 5:15 | 2.2623 | 8.0053 | 1 | 10 | 86.3985 | 83.9227 | 25351.7858
2017-07-17 | 5:30 | 1.8989 | 5.5905 | 1 | 10 | 79.7253 | 0 | 23393.6932
2017-07-17 | 5:45 | 1.8099 | 5.0186 | 1 | 10 | 77.2433 | 0 | 22665.405
2017-07-17 | 6:00 | 1.8053 | 4.7687 | 1 | 10 | 76.1555 | 0 | 22346.1934
2017-07-17 | 6:15 | 1.767 | 5.245 | 1 | 10 | 75.6741 | 0 | 22204.9574
2017-07-17 | 6:30 | 1.7117 | 5.3578 | 1 | 10 | 75.6312 | 0 | 22192.3626
2017-07-17 | 6:45 | 1.7351 | 5.3079 | 1 | 10 | 75.6553 | 0 | 22199.4345
2017-07-17 | 7:00 | 1.7686 | 4.8428 | 1 | 10 | 75.7362 | 0 | 22223.1691
2017-07-17 | 7:15 | 1.7514 | 4.4807 | 1 | 10 | 75.8575 | 0 | 22258.7461
2017-07-17 | 7:30 | 1.7085 | 4.0396 | 1 | 10 | 76.2897 | 0 | 22385.5654
2017-07-17 | 7:45 | 1.7156 | 3.98 | 1 | 10 | 76.1191 | 0 | 22335.5194
2017-07-17 | 8:00 | 1.7436 | 3.0398 | 1 | 10 | 76.0051 | 0 | 22302.0714
2017-07-17 | 8:15 | 1.6719 | 4.0906 | 1 | 10 | 76.707 | 0 | 22508.0278
2017-07-17 | 8:30 | 1.7241 | 5.1696 | 1 | 10 | 77.6463 | 0 | 22783.632
2017-07-17 | 8:45 | 1.661 | 5.8014 | 1 | 10 | 78.5441 | 0 | 23047.0825
2017-07-17 | 9:00 | 1.7811 | 5.2647 | 1 | 10 | 79.2049 | 0 | 23240.9903
2017-07-17 | 9:15 | 1.7358 | 6.028 | 1 | 10 | 80.0243 | 0 | 23481.4025
2017-07-17 | 9:30 | 1.7663 | 5.5133 | 1 | 10 | 80.2067 | 0 | 23534.9474
2017-07-17 | 9:45 | 1.7826 | 6.0456 | 1 | 10 | 80.2559 | 0 | 23549.3823
2017-07-17 | 10:00 | 1.7842 | 5.0145 | 1 | 10 | 80.0746 | 0 | 23496.1846
2017-07-17 | 10:15 | 1.7436 | 2.3981 | 1 | 10 | 80.5931 | 0 | 23648.3276
2017-07-17 | 10:22 |  |  | 0 |  |  |  | 0
2017-07-17 | 10:30 | 1.6937 | 0 | 0 | 1.5 | 80.8665 | 0 | 23728.5463
2017-07-17 | 10:45 | 1.7647 | 0 | 0 | 1.5 | 81.0242 | 0 | 23774.8244
2017-07-17 | 11:00 | 1.7904 | 0 | 0 | 1.5 | 80.7101 | 0 | 23682.64
2017-07-17 | 11:15 | 1.7444 | 0 | 0 | 1.5 | 80.4085 | 0 | 23594.1448
2017-07-17 | 11:30 | 1.7163 | 0 | 0 | 1.5 | 80.6918 | 0 | 23677.267
2017-07-17 | 11:45 | 1.7218 | 0 | 0 | 1.5 | 80.6503 | 0 | 23665.0885
2017-07-17 | 12:00 | 1.746 | 0 | 0 | 1.5 | 80.8885 | 0 | 23734.9826
2017-07-17 | 12:15 | 1.7546 | 0 | 0 | 1.5 | 81.1046 | 0 | 23798.3931
2017-07-17 | 12:30 | 1.7694 | 0 | 0 | 1.5 | 81.0013 | 0 | 23768.104
2017-07-17 | 12:45 | 1.7842 | 0 | 0 | 1.5 | 80.6634 | 0 | 23668.9412
2017-07-17 | 13:00 | 1.7436 | 0 | 0 | 1.5 | 80.5509 | 0 | 23635.9387
2017-07-17 | 13:15 | 1.7241 | 0 | 0 | 1.5 | 80.8451 | 0 | 23722.2534
2017-07-17 | 13:30 | 1.7273 | 0 | 0 | 1.5 | 80.8429 | 0 | 23721.631
2017-07-17 | 13:45 | 1.746 | 0 | 0 | 1.5 | 80.6253 | 0 | 23657.7637
2017-07-17 | 14:00 | 1.7452 | 0 | 0 | 1.5 | 80.3116 | 0 | 23565.7113
2017-07-17 | 14:15 | 1.7429 | 0 | 0 | 1.5 | 80.7113 | 0 | 23682.9935
2017-07-17 | 14:30 | 1.7421 | 0 | 0 | 1.5 | 80.8242 | 0 | 23716.124
2017-07-17 | 14:45 | 1.7522 | 0 | 0 | 1.5 | 81.0466 | 0 | 23781.3992
2017-07-17 | 15:00 | 1.7241 | 0 | 0 | 1.5 | 81.4131 | 0 | 23888.939
2017-07-17 | 15:15 | 1.7218 | 0 | 0 | 1.5 | 82.2373 | 0 | 24130.7793
2017-07-17 | 15:30 | 1.7335 | 0 | 0 | 1.5 | 82.9192 | 0 | 24330.8727
2017-07-17 | 15:45 | 1.767 | 0 | 0 | 1.5 | 82.9586 | 0 | 24342.4132
2017-07-17 | 16:00 | 1.7319 | 0 | 0 | 1.5 | 83.5883 | 0 | 24527.194
2017-07-17 | 16:15 | 1.7514 | 0 | 0 | 1.5 | 84.0308 | 0 | 24657.0241
2017-07-17 | 16:30 | 1.8177 | 0 | 0 | 1.5 | 83.7334 | 0 | 24569.7805
2017-07-17 | 16:45 | 1.8029 | 0 | 0 | 1.5 | 83.2175 | 0 | 24418.4007
2017-07-17 | 17:00 | 1.7912 | 0 | 0 | 1.5 | 82.8374 | 0 | 24306.8473
2017-07-17 | 17:15 | 1.8201 | 0 | 0 | 1.5 | 81.9786 | 0 | 24054.852
2017-07-17 | 17:30 | 1.8193 | 0 | 0 | 1.5 | 80.9786 | 0 | 23761.4302
2017-07-17 | 17:45 | 1.8099 | 0 | 0 | 1.5 | 80.064 | 0 | 23493.0549
2017-07-17 | 18:00 | 1.7967 | 0 | 0 | 1.5 | 79.4556 | 0 | 23314.5535
2017-07-17 | 18:15 | 1.7561 | 0 | 0 | 1.5 | 79.0838 | 0 | 23205.4423
2017-07-17 | 18:30 | 1.7374 | 0 | 0 | 1.5 | 78.576 | 0 | 23056.4558
2017-07-17 | 18:45 | 1.7725 | 0 | 0 | 1.5 | 78.3751 | 0 | 22997.4933
2017-07-17 | 19:00 | 1.7405 | 0 | 0 | 1.5 | 78.1897 | 0 | 22943.0799
2017-07-17 | 19:15 | 1.7624 | 0 | 0 | 1.5 | 77.7596 | 0 | 22816.9013
2017-07-17 | 19:30 | 1.7748 | 0 | 0 | 1.5 | 77.622 | 0 | 22776.5152
2017-07-17 | 19:45 | 1.7507 | 0 | 0 | 1.5 | 77.2755 | 0 | 22674.8343
2017-07-17 | 20:00 | 1.7397 | 0 | 0 | 1.5 | 76.9879 | 0 | 22590.4516
2017-07-17 | 20:15 | 1.7514 | 0 | 0 | 1.5 | 76.5821 | 0 | 22471.3739
2017-07-17 | 20:30 | 1.753 | 0 | 0 | 1.5 | 76.6383 | 0 | 22487.8575
2017-07-17 | 20:45 | 1.7483 | 0 | 0 | 1.5 | 76.5703 | 0 | 22467.9061
2017-07-17 | 21:00 | 1.7858 | 0 | 0 | 1.5 | 76.3134 | 0 | 22392.5275
2017-07-17 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 2:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 2:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 2:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 3:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 3:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 3:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 3:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 4:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 4:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 4:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 4:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 5:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-18 | 5:15 | 2.2787 | 9.0931 | 1 | 10 | 89.9084 | 93.2544 | 26381.6825
2017-07-18 | 5:30 | 1.916 | 7.369 | 1 | 10 | 82.9806 | 76.2755 | 24348.8851
2017-07-18 | 5:45 | 1.8505 | 6.362 | 1 | 10 | 80.0321 | 66.4609 | 23483.7106
2017-07-18 | 6:00 | 1.8099 | 6.0893 | 1 | 10 | 78.5356 | 0 | 23044.5775
2017-07-18 | 6:15 | 1.7803 | 6.6687 | 1 | 10 | 77.8043 | 0 | 22830.0108
2017-07-18 | 6:30 | 1.7647 | 6.8151 | 1 | 10 | 77.3731 | 0 | 22703.4849
2017-07-18 | 6:45 | 1.7436 | 6.2365 | 1 | 10 | 77.2075 | 0 | 22654.8721
2017-07-18 | 7:00 | 1.8131 | 5.6073 | 1 | 10 | 76.9465 | 0 | 22578.3157
2017-07-18 | 7:15 | 1.7351 | 5.7479 | 1 | 10 | 76.4979 | 0 | 22446.6634
2017-07-18 | 7:30 | 1.7405 | 4.6827 | 1 | 10 | 76.214 | 0 | 22363.3531
2017-07-18 | 7:45 | 1.7109 | 4.1294 | 1 | 10 | 76.1321 | 0 | 22339.3342
2017-07-18 | 8:00 | 1.6953 | 3.6396 | 1 | 10 | 76.7862 | 0 | 22531.2609
2017-07-18 | 8:15 | 1.7561 | 4.7264 | 1 | 10 | 77.5788 | 0 | 22763.8467
2017-07-18 | 8:30 | 1.6844 | 5.9489 | 1 | 10 | 78.3881 | 0 | 23001.3194
2017-07-18 | 8:45 | 1.7327 | 6.0899 | 1 | 10 | 78.995 | 0 | 23179.3997
2017-07-18 | 9:00 | 1.7265 | 6.3143 | 1 | 10 | 79.1709 | 0 | 23230.9923
2017-07-18 | 9:15 | 1.7273 | 6.3979 | 1 | 10 | 79.9664 | 0 | 23464.413
2017-07-18 | 9:30 | 1.7218 | 5.7368 | 1 | 10 | 79.9069 | 0 | 23446.9737
2017-07-18 | 9:45 | 1.6805 | 2.4089 | 1 | 10 | 80.2302 | 0 | 23541.8336
2017-07-18 | 9:49 |  |  | 0 |  |  |  | 0
2017-07-18 | 10:00 | 1.6906 | 0 | 0 | 1.5 | 81.1256 | 0 | 23804.5698
2017-07-18 | 10:15 | 1.7819 | 0 | 0 | 1.5 | 81.4938 | 0 | 23912.6196
2017-07-18 | 10:30 | 1.7257 | 0 | 0 | 1.5 | 81.756 | 0 | 23989.5363
2017-07-18 | 10:45 | 1.6867 | 0 | 0 | 1.5 | 81.9602 | 0 | 24049.4591
2017-07-18 | 11:00 | 1.6968 | 0 | 0 | 1.5 | 82.4012 | 0 | 24178.8573
2017-07-18 | 11:15 | 1.7351 | 0 | 0 | 1.5 | 83.0065 | 0 | 24356.4767
2017-07-18 | 11:30 | 1.7195 | 0 | 0 | 1.5 | 83.7984 | 0 | 24588.8495
2017-07-18 | 11:45 | 1.6571 | 0 | 0 | 1.5 | 84.6088 | 0 | 24826.6446
2017-07-18 | 12:00 | 1.6703 | 0 | 0 | 1.5 | 85.3116 | 0 | 25032.863
2017-07-18 | 12:15 | 1.7936 | 0 | 0 | 1.5 | 86.0943 | 0 | 25262.5339
2017-07-18 | 12:30 | 1.8162 | 0 | 0 | 1.5 | 86.1171 | 0 | 25269.2074
2017-07-18 | 12:45 | 1.6672 | 0 | 0 | 1.5 | 86.8683 | 0 | 25489.655
2017-07-18 | 13:00 | 1.7834 | 0 | 0 | 1.5 | 87.1841 | 0 | 25582.2962
2017-07-18 | 13:15 | 1.8154 | 0 | 0 | 1.5 | 85.7246 | 0 | 25154.0364
2017-07-18 | 13:30 | 1.7577 | 0 | 0 | 1.5 | 86.5034 | 0 | 25382.5565
2017-07-18 | 13:45 | 1.7678 | 0 | 0 | 1.5 | 87.5124 | 0 | 25678.6268
2017-07-18 | 14:00 | 1.785 | 0 | 0 | 1.5 | 84.5133 | 0 | 24798.6119
2017-07-18 | 14:15 | 1.6391 | 0 | 0 | 1.5 | 85.6972 | 0 | 25146.0196
2017-07-18 | 14:30 | 1.6773 | 0 | 0 | 1.5 | 87.9061 | 0 | 25794.1517
2017-07-18 | 14:45 | 1.8887 | 0 | 0 | 1.5 | 85.7969 | 0 | 25175.27
2017-07-18 | 15:00 | 1.5853 | 0 | 0 | 1.5 | 86.262 | 0 | 25311.7222
2017-07-18 | 15:15 | 1.7826 | 0 | 0 | 1.5 | 88.344 | 0 | 25922.6476
2017-07-18 | 15:30 | 1.877 | 0 | 0 | 1.5 | 85.2558 | 0 | 25016.485
2017-07-18 | 15:45 | 1.604 | 0 | 0 | 1.5 | 86.6665 | 0 | 25430.4396
2017-07-18 | 16:00 | 1.8458 | 0 | 0 | 1.5 | 86.6279 | 0 | 25419.1141
2017-07-18 | 16:15 | 1.7156 | 0 | 0 | 1.5 | 84.9492 | 0 | 24926.53
2017-07-18 | 16:30 | 1.7039 | 0 | 0 | 1.5 | 86.5334 | 0 | 25391.3678
2017-07-18 | 16:45 | 1.9316 | 0 | 0 | 1.5 | 83.7469 | 0 | 24573.725
2017-07-18 | 17:00 | 1.689 | 0 | 0 | 1.5 | 83.192 | 0 | 24410.9124
2017-07-18 | 17:15 | 1.6875 | 0 | 0 | 1.5 | 84.7137 | 0 | 24857.4264
2017-07-18 | 17:30 | 1.98 | 0 | 0 | 1.5 | 82.7707 | 0 | 24287.2833
2017-07-18 | 17:45 | 1.8396 | 0 | 0 | 1.5 | 79.8596 | 0 | 23433.0828
2017-07-18 | 18:00 | 1.767 | 0 | 0 | 1.5 | 79.5595 | 0 | 23345.0263
2017-07-18 | 18:15 | 1.7436 | 0 | 0 | 1.5 | 79.8912 | 0 | 23442.3487
2017-07-18 | 18:30 | 1.7553 | 0 | 0 | 1.5 | 79.9698 | 0 | 23465.4385
2017-07-18 | 18:45 | 1.7585 | 0 | 0 | 1.5 | 80.0656 | 0 | 23493.5317
2017-07-18 | 19:00 | 1.746 | 0 | 0 | 1.5 | 80.1604 | 0 | 23521.3517
2017-07-18 | 19:15 | 1.767 | 0 | 0 | 1.5 | 80.1585 | 0 | 23520.7988
2017-07-18 | 19:30 | 1.7748 | 0 | 0 | 1.5 | 80.1486 | 0 | 23517.8751
2017-07-18 | 19:45 | 1.7475 | 0 | 0 | 1.5 | 79.8908 | 0 | 23442.2433
2017-07-18 | 20:00 | 1.8053 | 0 | 0 | 1.5 | 78.906 | 0 | 23153.2743
2017-07-18 | 20:15 | 1.7873 | 0 | 0 | 1.5 | 78.2113 | 0 | 22949.4265
2017-07-18 | 20:30 | 1.7811 | 0 | 0 | 1.5 | 77.498 | 0 | 22740.1368
2017-07-18 | 20:45 | 1.7998 | 0 | 0 | 1.5 | 76.8233 | 0 | 22542.1565
2017-07-18 | 21:00 | 1.7546 | 0 | 0 | 1.5 | 76.7366 | 0 | 22516.7027
2017-07-18 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 22:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 22:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 23:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 23:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 0:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 0:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 0:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 0:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 0:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 1:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 1:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 1:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 1:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 1:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 1:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 2:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 2:15 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 2:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 2:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 2:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 2:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 3:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 3:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 3:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 3:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 3:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 3:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 3:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 4:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 4:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 4:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 4:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 4:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 4:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 4:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 5:00 | 0.02842 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-07-19 | 5:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-19 | 5:15 | 2.2608 | 9.6757 | 1 |  | 89.6148 | 98.205 | 26295.5448
2017-07-19 | 5:15 |  |  |  | 10 |  |  | 0
2017-07-19 | 5:30 | 1.973 | 8.1413 | 1 | 10 | 82.6145 | 83.2109 | 24241.4553
2017-07-19 | 5:30 |  |  |  | 10 |  |  | 0
2017-07-19 | 5:45 | 1.7897 | 7.191 | 1 |  | 79.9502 | 73.6636 | 23459.6648
2017-07-19 | 5:45 |  |  |  | 10 |  |  | 0
2017-07-19 | 6:00 | 1.7655 | 6.639 | 1 | 10 | 78.5853 | 68.2906 | 23059.1623
2017-07-19 | 6:00 |  |  |  | 10 |  |  | 0
2017-07-19 | 6:15 | 1.8068 | 7.5854 | 1 |  | 77.7627 | 76.8065 | 22817.8012
2017-07-19 | 6:15 |  |  |  | 10 |  |  | 0
2017-07-19 | 6:30 | 1.8014 | 9.785 | 1 | 10 | 77.1524 | 98.4834 | 22638.7065
2017-07-19 | 6:30 |  |  |  | 10 |  |  | 0
2017-07-19 | 6:45 | 1.7249 | 9.3551 | 1 |  | 76.9598 | 94.0638 | 22582.2089
2017-07-19 | 6:45 |  |  |  | 10 |  |  | 0
2017-07-19 | 7:00 | 1.6851 | 6.9276 | 1 | 10 | 77.1137 | 70.7982 | 22627.3766
2017-07-19 | 7:00 |  |  |  | 10 |  |  | 0
2017-07-19 | 7:15 | 1.8224 | 6.5605 | 1 |  | 77.1756 | 66.536 | 22645.5299
2017-07-19 | 7:15 |  |  |  | 10 |  |  | 0
2017-07-19 | 7:30 | 1.7491 | 6.2406 | 1 | 10 | 76.7506 | 0 | 22520.833
2017-07-19 | 7:30 |  |  |  | 10 |  |  | 0
2017-07-19 | 7:45 | 1.7179 | 5.9991 | 1 |  | 76.8061 | 0 | 22537.0972
2017-07-19 | 7:45 |  |  |  | 10 |  |  | 0
2017-07-19 | 8:00 | 1.7358 | 6.5268 | 1 | 10 | 76.698 | 0 | 22505.3728
2017-07-19 | 8:00 |  |  |  | 10 |  |  | 0
2017-07-19 | 8:15 | 1.7351 | 9.2743 | 1 |  | 76.9848 | 93.7281 | 22589.5516
2017-07-19 | 8:15 |  |  |  | 10 |  |  | 0
2017-07-19 | 8:30 | 1.7374 | 5.5929 | 1 | 10 | 77.4898 | 0 | 22737.7345
2017-07-19 | 8:30 |  |  |  | 10 |  |  | 0
2017-07-19 | 8:45 | 1.7452 | 3.4259 | 1 |  | 77.8615 | 0 | 22846.8031
2017-07-19 | 8:45 |  |  |  | 10 |  |  | 0
2017-07-19 | 9:00 | 0.037 | 0 | 1 | 10 | 89.7137 | 0 | 26324.5558
2017-07-19 | 9:00 |  |  |  | 10 |  |  | 0
2017-07-19 | 9:15 | 2.4363 | 8.6521 | 1 |  | 91.0209 | 0 | 26708.1406
2017-07-19 | 9:15 |  |  |  | 10 |  |  | 0
2017-07-19 | 9:30 | 1.994 | 6.4772 | 1 | 10 | 82.9155 | 70.1038 | 24329.7714
2017-07-19 | 9:30 |  |  |  | 10 |  |  | 0
2017-07-19 | 9:45 | 1.8879 | 5.2147 | 1 |  | 80.4169 | 0 | 23596.6117
2017-07-19 | 9:45 |  |  |  | 10 |  |  | 0
2017-07-19 | 10:00 | 1.714 | 4.2709 | 1 | 10 | 80.2292 | 0 | 23541.5536
2017-07-19 | 10:00 |  |  |  | 10 |  |  | 0
2017-07-19 | 10:15 | 1.6836 | 2.6501 | 1 |  | 81.1876 | 0 | 23822.7612
2017-07-19 | 10:15 |  |  |  | 10 |  |  | 0
2017-07-19 | 10:16 |  |  | 0 |  |  |  | 0
2017-07-19 | 10:19 |  |  | 1 |  |  |  | 0
2017-07-19 | 10:28 |  |  | 0 |  |  |  | 0
2017-07-19 | 10:30 | 1.767 | 0 | 0 | 1.5 | 81.1654 | 0 | 23816.2444
2017-07-19 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 10:45 | 1.7842 | 0 | 0 |  | 81.5553 | 0 | 23930.6455
2017-07-19 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 11:00 | 1.6992 | 0 | 0 | 1.5 | 82.1466 | 0 | 24104.1636
2017-07-19 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 11:15 | 1.6828 | 0 | 0 |  | 82.5143 | 0 | 24212.0614
2017-07-19 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 11:30 | 1.778 | 0 | 0 | 1.5 | 82.6413 | 0 | 24249.3265
2017-07-19 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 11:45 | 1.7663 | 0 | 0 |  | 82.6461 | 0 | 24250.7303
2017-07-19 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 12:00 | 1.6945 | 0 | 0 | 1.5 | 83.0866 | 0 | 24379.9759
2017-07-19 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 12:15 | 1.6742 | 0 | 0 |  | 83.816 | 0 | 24594.0097
2017-07-19 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 12:30 | 1.7639 | 0 | 0 | 1.5 | 83.995 | 0 | 24646.5246
2017-07-19 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 12:45 | 1.7647 | 0 | 0 |  | 83.8218 | 0 | 24595.6975
2017-07-19 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 13:00 | 1.6976 | 0 | 0 | 1.5 | 83.9913 | 0 | 24645.4413
2017-07-19 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 13:15 | 1.6508 | 0 | 0 |  | 84.8439 | 0 | 24895.6185
2017-07-19 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 13:30 | 1.739 | 0 | 0 | 1.5 | 85.2676 | 0 | 25019.9548
2017-07-19 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 13:45 | 1.7148 | 0 | 0 |  | 86.513 | 0 | 25385.3816
2017-07-19 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 14:00 | 1.7007 | 0 | 0 | 1.5 | 88.255 | 0 | 25896.5424
2017-07-19 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 14:15 | 1.6672 | 0 | 0 |  | 88.3458 | 0 | 25923.1804
2017-07-19 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 14:30 | 1.9004 | 0 | 0 | 1.5 | 88.3343 | 0 | 25919.811
2017-07-19 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 14:45 | 1.8747 | 0 | 0 |  | 85.272 | 0 | 25021.2332
2017-07-19 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 15:00 | 1.661 | 0 | 0 | 1.5 | 86.8147 | 0 | 25473.9172
2017-07-19 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 15:15 | 1.7967 | 0 | 0 |  | 88.1176 | 0 | 25856.2168
2017-07-19 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 15:30 | 1.7413 | 0 | 0 | 1.5 | 86.484 | 0 | 25376.8634
2017-07-19 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 15:45 | 1.7452 | 0 | 0 |  | 87.5747 | 0 | 25696.9124
2017-07-19 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 16:00 | 1.8942 | 0 | 0 | 1.5 | 86.2767 | 0 | 25316.043
2017-07-19 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 16:15 | 1.6368 | 0 | 0 |  | 86.4684 | 0 | 25372.3032
2017-07-19 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 16:30 | 1.8692 | 0 | 0 | 1.5 | 87.1928 | 0 | 25584.8461
2017-07-19 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 16:45 | 1.7897 | 0 | 0 |  | 84.955 | 0 | 24928.2269
2017-07-19 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 17:00 | 1.7171 | 0 | 0 | 1.5 | 85.9334 | 0 | 25215.3022
2017-07-19 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 17:15 | 1.8021 | 0 | 0 |  | 86.018 | 0 | 25240.1427
2017-07-19 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 17:30 | 1.8084 | 0 | 0 | 1.5 | 82.9179 | 0 | 24330.4698
2017-07-19 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 17:45 | 1.8029 | 0 | 0 |  | 82.0681 | 0 | 24081.1142
2017-07-19 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 18:00 | 1.7858 | 0 | 0 | 1.5 | 82.1026 | 0 | 24091.2419
2017-07-19 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 18:15 | 1.7795 | 0 | 0 |  | 81.9436 | 0 | 24044.5788
2017-07-19 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 18:30 | 1.7631 | 0 | 0 | 1.5 | 81.8271 | 0 | 24010.4008
2017-07-19 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 18:45 | 1.8037 | 0 | 0 |  | 81.158 | 0 | 23814.0886
2017-07-19 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 19:00 | 1.7787 | 0 | 0 | 1.5 | 80.5961 | 0 | 23649.1917
2017-07-19 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 19:15 | 1.7756 | 0 | 0 |  | 80.1337 | 0 | 23513.5074
2017-07-19 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 19:30 | 1.7686 | 0 | 0 | 1.5 | 79.5582 | 0 | 23344.6346
2017-07-19 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 19:45 | 1.7795 | 0 | 0 |  | 79.1923 | 0 | 23237.2764
2017-07-19 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 20:00 | 1.7826 | 0 | 0 | 1.5 | 78.6388 | 0 | 23074.8713
2017-07-19 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 20:15 | 1.7522 | 0 | 0 |  | 77.9573 | 0 | 22874.8898
2017-07-19 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 20:30 | 1.7865 | 0 | 0 | 1.5 | 77.2792 | 0 | 22675.9335
2017-07-19 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 20:45 | 1.7374 | 0 | 0 |  | 76.8139 | 0 | 22539.3941
2017-07-19 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-07-19 | 21:00 | 1.7959 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 21:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 21:15 | 0.03778 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 21:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 21:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 21:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 21:45 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 21:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 22:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 22:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 22:15 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 22:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 22:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 22:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 22:45 |  |  |  | 0 |  |  | 0
2017-07-19 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 23:00 |  |  |  | 0 |  |  | 0
2017-07-19 | 23:15 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 23:15 |  |  |  | 0 |  |  | 0
2017-07-19 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 23:30 |  |  |  | 0 |  |  | 0
2017-07-19 | 23:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-19 | 23:45 |  |  |  | 0 |  |  | 0
2017-07-20 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 0:00 |  |  |  | 0 |  |  | 0
2017-07-20 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 3:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 4:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 4:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 4:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 5:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-20 | 5:15 | 2.2413 | 9.9622 | 1 | 10 | 92.3846 | 99.7776 | 27108.2739
2017-07-20 | 5:30 | 1.9948 | 8.7499 | 1 | 10 | 85.3065 | 88.2573 | 25031.3633
2017-07-20 | 5:45 | 1.8365 | 7.2977 | 1 | 10 | 81.7144 | 74.0969 | 23977.3265
2017-07-20 | 6:00 | 1.817 | 6.5321 | 1 | 10 | 79.8133 | 66.5006 | 23419.514
2017-07-20 | 6:15 | 1.8482 | 6.6773 | 1 | 10 | 78.6351 | 67.971 | 23073.7742
2017-07-20 | 6:30 | 1.8092 | 6.2551 | 1 | 10 | 78.0932 | 63.5851 | 22914.7629
2017-07-20 | 6:45 | 1.6929 | 6.2295 | 1 | 10 | 77.8217 | 0 | 22835.0994
2017-07-20 | 7:00 | 1.7195 | 5.99 | 1 | 10 | 77.61 | 0 | 22772.9961
2017-07-20 | 7:15 | 1.7982 | 6.4502 | 1 | 10 | 77.5862 | 0 | 22766.0181
2017-07-20 | 7:30 | 1.7655 | 5.5595 | 1 | 10 | 77.2614 | 0 | 22670.6996
2017-07-20 | 7:45 | 1.6906 | 5.1286 | 1 | 10 | 77.6056 | 0 | 22771.6886
2017-07-20 | 8:00 | 1.7397 | 4.5084 | 1 | 10 | 78.0338 | 0 | 22897.3503
2017-07-20 | 8:15 | 1.7725 | 4.7115 | 1 | 10 | 78.554 | 0 | 23049.9903
2017-07-20 | 8:30 | 1.8076 | 4.417 | 1 | 10 | 78.5179 | 0 | 23039.4037
2017-07-20 | 8:45 | 1.6922 | 5.7513 | 1 | 10 | 78.8733 | 0 | 23143.6815
2017-07-20 | 9:00 | 1.7234 | 4.8112 | 1 | 10 | 79.2619 | 0 | 23257.7134
2017-07-20 | 9:15 | 1.8084 | 6.1279 | 1 | 10 | 79.8427 | 0 | 23428.1353
2017-07-20 | 9:30 | 1.7351 | 5.4848 | 1 | 10 | 80.4614 | 0 | 23609.6654
2017-07-20 | 9:45 | 1.7475 | 4.5129 | 1 | 10 | 80.4483 | 0 | 23605.835
2017-07-20 | 9:46 |  |  | 0 |  |  |  | 0
2017-07-20 | 10:00 | 1.7358 | 0 | 0 | 1.5 | 81.0693 | 0 | 23788.0439
2017-07-20 | 10:01 |  |  | 1 |  |  |  | 0
2017-07-20 | 10:04 |  |  | 0 |  |  |  | 0
2017-07-20 | 10:06 |  |  | 1 |  |  |  | 0
2017-07-20 | 10:13 |  |  | 0 |  |  |  | 0
2017-07-20 | 10:15 | 1.7187 | 0 | 0 | 1.5 | 80.7706 | 0 | 23700.3971
2017-07-20 | 10:25 |  |  | 1 |  |  |  | 0
2017-07-20 | 10:30 | 1.7764 | 0 | 1 | 10 | 80.5984 | 0 | 23649.888
2017-07-20 | 10:30 |  |  | 0 |  |  |  | 0
2017-07-20 | 10:42 |  |  | 1 |  |  |  | 0
2017-07-20 | 10:45 | 1.7592 | 0 | 1 | 10 | 80.6099 | 0 | 23653.2349
2017-07-20 | 10:48 |  |  | 0 |  |  |  | 0
2017-07-20 | 10:53 |  |  | 1 |  |  |  | 0
2017-07-20 | 11:00 | 1.7897 | 0.58238 | 1 | 10 | 80.1344 | 0 | 23513.7158
2017-07-20 | 11:12 |  |  | 0 |  |  |  | 0
2017-07-20 | 11:15 | 1.7514 | 0 | 0 | 1.5 | 80.3862 | 0 | 23587.6122
2017-07-20 | 11:30 | 1.7733 | 0 | 0 | 1.5 | 80.6819 | 0 | 23674.3838
2017-07-20 | 11:45 | 1.6961 | 0 | 0 | 1.5 | 80.992 | 0 | 23765.3795
2017-07-20 | 12:00 | 1.7522 | 0 | 0 | 1.5 | 81.2364 | 0 | 23837.0867
2017-07-20 | 12:15 | 1.7234 | 0 | 0 | 1.5 | 81.166 | 0 | 23816.4146
2017-07-20 | 12:30 | 1.7959 | 0 | 0 | 1.5 | 80.9703 | 0 | 23758.988
2017-07-20 | 12:45 | 1.6836 | 0 | 0 | 1.5 | 81.3834 | 0 | 23880.2148
2017-07-20 | 13:00 | 1.6461 | 0 | 0 | 1.5 | 82.3337 | 0 | 24159.065
2017-07-20 | 13:15 | 1.6859 | 0 | 0 | 1.5 | 83.3578 | 0 | 24459.5522
2017-07-20 | 13:30 | 1.7787 | 0 | 0 | 1.5 | 83.4484 | 0 | 24486.1545
2017-07-20 | 13:45 | 1.7358 | 0 | 0 | 1.5 | 83.9465 | 0 | 24632.2934
2017-07-20 | 14:00 | 1.6812 | 0 | 0 | 1.5 | 84.4217 | 0 | 24771.7388
2017-07-20 | 14:15 | 1.721 | 0 | 0 | 1.5 | 85.0249 | 0 | 24948.7335
2017-07-20 | 14:30 | 1.7405 | 0 | 0 | 1.5 | 85.4953 | 0 | 25086.7549
2017-07-20 | 14:45 | 1.7101 | 0 | 0 | 1.5 | 86.1566 | 0 | 25280.8172
2017-07-20 | 15:00 | 1.6781 | 0 | 0 | 1.5 | 86.6021 | 0 | 25411.5182
2017-07-20 | 15:15 | 1.707 | 0 | 0 | 1.5 | 87.109 | 0 | 25560.2721
2017-07-20 | 15:30 | 1.7257 | 0 | 0 | 1.5 | 87.1706 | 0 | 25578.3314
2017-07-20 | 15:45 | 1.7655 | 0 | 0 | 1.5 | 87.6478 | 0 | 25718.3544
2017-07-20 | 16:00 | 1.7592 | 0 | 0 | 1.5 | 87.7021 | 0 | 25734.3116
2017-07-20 | 16:15 | 1.682 | 0 | 0 | 1.5 | 89.1082 | 0 | 26146.8942
2017-07-20 | 16:30 | 1.8076 | 0 | 0 | 1.5 | 88.8885 | 0 | 26082.4335
2017-07-20 | 16:45 | 1.8224 | 0 | 0 | 1.5 | 88.0443 | 0 | 25834.7099
2017-07-20 | 17:00 | 1.746 | 0 | 0 | 1.5 | 87.3251 | 0 | 25623.6849
2017-07-20 | 17:15 | 1.7499 | 0 | 0 | 1.5 | 86.6102 | 0 | 25413.8958
2017-07-20 | 17:30 | 1.8271 | 0 | 0 | 1.5 | 84.795 | 0 | 24881.2751
2017-07-20 | 17:45 | 1.8232 | 0 | 0 | 1.5 | 82.998 | 0 | 24353.9737
2017-07-20 | 18:00 | 1.7975 | 0 | 0 | 1.5 | 81.497 | 0 | 23913.5556
2017-07-20 | 18:15 | 1.76 | 0 | 0 | 1.5 | 80.7929 | 0 | 23706.9341
2017-07-20 | 18:30 | 1.7741 | 0 | 0 | 1.5 | 80.0641 | 0 | 23493.0974
2017-07-20 | 18:45 | 1.7795 | 0 | 0 | 1.5 | 79.5497 | 0 | 23342.1431
2017-07-20 | 19:00 | 1.7936 | 0 | 0 | 1.5 | 79.1226 | 0 | 23216.8259
2017-07-20 | 19:15 | 1.7678 | 0 | 0 | 1.5 | 78.6455 | 0 | 23076.8347
2017-07-20 | 19:30 | 1.7982 | 0 | 0 | 1.5 | 77.8431 | 0 | 22841.399
2017-07-20 | 19:45 | 1.7834 | 0 | 0 | 1.5 | 77.2651 | 0 | 22671.7829
2017-07-20 | 20:00 | 1.7561 | 0 | 0 | 1.5 | 76.7832 | 0 | 22530.3832
2017-07-20 | 20:15 | 1.7538 | 0 | 0 | 1.5 | 76.7561 | 0 | 22522.436
2017-07-20 | 20:30 | 1.7132 | 0 | 0 | 1.5 | 76.5865 | 0 | 22472.6567
2017-07-20 | 20:45 | 1.7694 | 0 | 0 | 1.5 | 76.6866 | 0 | 22502.0462
2017-07-20 | 21:00 | 1.7858 | 0 | 0 | 1.5 | 76.5463 | 0 | 22460.8835
2017-07-20 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 21:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 23:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 0:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 0:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 0:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 1:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 1:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 1:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 2:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 2:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 3:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 5:00 | 0.03232 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-21 | 5:15 | 2.1656 | 9.3496 | 1 | 10 | 89.6505 | 95.2526 | 26306.0196
2017-07-21 | 5:30 | 1.9035 | 7.8678 | 1 | 10 | 83.4399 | 80.8847 | 24483.6583
2017-07-21 | 5:45 | 1.8708 | 6.7373 | 1 | 10 | 80.5636 | 69.9381 | 23639.6706
2017-07-21 | 6:00 | 1.8107 | 6.0905 | 1 | 10 | 79.1622 | 63.5165 | 23228.4471
2017-07-21 | 6:15 | 1.7421 | 6.4745 | 1 | 10 | 78.702 | 66.9546 | 23093.4099
2017-07-21 | 6:30 | 1.7421 | 6.2744 | 1 | 10 | 78.5076 | 65.3682 | 23036.3861
2017-07-21 | 6:45 | 1.7733 | 6.4099 | 1 | 10 | 78.2565 | 0 | 22962.693
2017-07-21 | 7:00 | 1.8123 | 6.5463 | 1 | 10 | 77.4743 | 0 | 22733.1655
2017-07-21 | 7:15 | 1.7132 | 6.061 | 1 | 10 | 77.354 | 0 | 22697.8725
2017-07-21 | 7:30 | 1.7655 | 5.648 | 1 | 10 | 77.2734 | 0 | 22674.2099
2017-07-21 | 7:45 | 1.7975 | 4.9942 | 1 | 10 | 77.4134 | 0 | 22715.3098
2017-07-21 | 8:00 | 1.7897 | 4.1 | 1 | 10 | 77.4141 | 0 | 22715.5158
2017-07-21 | 8:15 | 1.682 | 3.8233 | 1 | 10 | 78.1735 | 0 | 22938.3428
2017-07-21 | 8:30 | 1.7405 | 4.9183 | 1 | 10 | 78.8684 | 0 | 23142.2554
2017-07-21 | 8:45 | 1.7343 | 5.4293 | 1 | 10 | 79.9034 | 0 | 23445.9282
2017-07-21 | 9:00 | 1.7975 | 5.7085 | 1 | 10 | 79.8508 | 0 | 23430.5015
2017-07-21 | 9:15 | 1.6781 | 5.7642 | 1 | 10 | 80.3179 | 0 | 23567.5784
2017-07-21 | 9:30 | 1.7062 | 6.7136 | 1 | 10 | 81.3406 | 0 | 23867.6423
2017-07-21 | 9:45 | 1.7725 | 5.8598 | 1 | 10 | 80.8939 | 0 | 23736.5742
2017-07-21 | 10:00 | 1.7787 | 3.5659 | 1 | 10 | 80.3724 | 0 | 23583.5714
2017-07-21 | 10:04 |  |  | 0 |  |  |  | 0
2017-07-21 | 10:15 | 1.6937 | 0 | 0 | 1.5 | 81.1607 | 0 | 23814.8633
2017-07-21 | 10:30 | 1.7982 | 0 | 0 | 1.5 | 80.9813 | 0 | 23762.2184
2017-07-21 | 10:45 | 1.7491 | 0 | 0 | 1.5 | 80.7315 | 0 | 23688.9237
2017-07-21 | 11:00 | 1.7616 | 0 | 0 | 1.5 | 80.7036 | 0 | 23680.7391
2017-07-21 | 11:15 | 1.7546 | 0 | 0 | 1.5 | 81.2108 | 0 | 23829.5714
2017-07-21 | 11:30 | 1.7686 | 0 | 0 | 1.5 | 81.1065 | 0 | 23798.9753
2017-07-21 | 11:45 | 1.7444 | 0 | 0 | 1.5 | 81.9296 | 0 | 24040.4911
2017-07-21 | 12:00 | 1.6859 | 0 | 0 | 1.5 | 82.3479 | 0 | 24163.2334
2017-07-21 | 12:15 | 1.7741 | 0 | 0 | 1.5 | 82.0312 | 0 | 24070.2855
2017-07-21 | 12:30 | 1.7483 | 0 | 0 | 1.5 | 81.9251 | 0 | 24039.1656
2017-07-21 | 12:45 | 1.7031 | 0 | 0 | 1.5 | 81.9513 | 0 | 24046.8467
2017-07-21 | 13:00 | 1.6976 | 0 | 0 | 1.5 | 82.2277 | 0 | 24127.9518
2017-07-21 | 13:15 | 1.7218 | 0 | 0 | 1.5 | 82.7333 | 0 | 24276.3117
2017-07-21 | 13:30 | 1.76 | 0 | 0 | 1.5 | 83.0228 | 0 | 24361.2607
2017-07-21 | 13:45 | 1.6773 | 0 | 0 | 1.5 | 83.5238 | 0 | 24508.2793
2017-07-21 | 14:00 | 1.7101 | 0 | 0 | 1.5 | 84.2312 | 0 | 24715.8545
2017-07-21 | 14:15 | 1.6875 | 0 | 0 | 1.5 | 84.8722 | 0 | 24903.9351
2017-07-21 | 14:30 | 1.7312 | 0 | 0 | 1.5 | 85.9629 | 0 | 25223.9704
2017-07-21 | 14:45 | 1.8435 | 0 | 0 | 1.5 | 83.8906 | 0 | 24615.8951
2017-07-21 | 15:00 | 1.7304 | 0 | 0 | 1.5 | 83.8865 | 0 | 24614.7017
2017-07-21 | 15:15 | 1.6789 | 0 | 0 | 1.5 | 85.7569 | 0 | 25163.5147
2017-07-21 | 15:30 | 1.9207 | 0 | 0 | 1.5 | 84.9748 | 0 | 24934.0298
2017-07-21 | 15:45 | 1.7366 | 0 | 0 | 1.5 | 82.4443 | 0 | 24191.5058
2017-07-21 | 16:00 | 1.7429 | 0 | 0 | 1.5 | 83.4494 | 0 | 24486.4523
2017-07-21 | 16:15 | 1.7031 | 0 | 0 | 1.5 | 85.204 | 0 | 25001.2798
2017-07-21 | 16:30 | 1.7897 | 0 | 0 | 1.5 | 85.1618 | 0 | 24988.9021
2017-07-21 | 16:45 | 1.7998 | 0 | 0 | 1.5 | 82.1763 | 0 | 24112.8632
2017-07-21 | 17:00 | 1.6672 | 0 | 0 | 1.5 | 82.582 | 0 | 24231.9095
2017-07-21 | 17:15 | 1.6797 | 0 | 0 | 1.5 | 83.725 | 0 | 24567.3133
2017-07-21 | 17:30 | 1.7959 | 0 | 0 | 1.5 | 83.2467 | 0 | 24426.9459
2017-07-21 | 17:45 | 1.7936 | 0 | 0 | 1.5 | 82.5274 | 0 | 24215.9097
2017-07-21 | 18:00 | 1.7569 | 0 | 0 | 1.5 | 82.1569 | 0 | 24107.1859
2017-07-21 | 18:15 | 1.7764 | 0 | 0 | 1.5 | 81.2683 | 0 | 23846.4286
2017-07-21 | 18:30 | 1.7865 | 0 | 0 | 1.5 | 80.9168 | 0 | 23743.2925
2017-07-21 | 18:45 | 1.739 | 0 | 0 | 1.5 | 80.6681 | 0 | 23670.3136
2017-07-21 | 19:00 | 1.7678 | 0 | 0 | 1.5 | 80.1349 | 0 | 23513.8836
2017-07-21 | 19:15 | 1.7421 | 0 | 0 | 1.5 | 80.0068 | 0 | 23476.2892
2017-07-21 | 19:30 | 1.7858 | 0 | 0 | 1.5 | 79.635 | 0 | 23367.196
2017-07-21 | 19:45 | 1.778 | 0 | 0 | 1.5 | 79.2425 | 0 | 23252.0183
2017-07-21 | 20:00 | 1.7678 | 0 | 0 | 1.5 | 78.8683 | 0 | 23142.2243
2017-07-21 | 20:15 | 1.7608 | 0 | 0 | 1.5 | 78.1906 | 0 | 22943.3643
2017-07-21 | 20:30 | 1.7624 | 0 | 0 | 1.5 | 77.6243 | 0 | 22777.1801
2017-07-21 | 20:45 | 1.7951 | 0 | 0 | 1.5 | 77.2684 | 0 | 22672.748
2017-07-21 | 21:00 | 1.7803 | 0 | 0 | 1.5 | 76.6489 | 0 | 22490.967
2017-07-21 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 21:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 21:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 1:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 3:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 4:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 5:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-22 | 5:15 | 2.1266 | 10 | 1 | 10 | 94.4196 | 100 | 27705.4133
2017-07-22 | 5:30 | 2.0775 | 9.2731 | 1 | 10 | 87.1041 | 93.428 | 25558.8369
2017-07-22 | 5:45 | 1.9394 | 7.6753 | 1 | 10 | 82.4222 | 77.8242 | 24185.0158
2017-07-22 | 6:00 | 1.7834 | 6.8594 | 1 | 10 | 80.4734 | 69.6204 | 23613.2071
2017-07-22 | 6:15 | 1.7483 | 7.005 | 1 | 10 | 79.6016 | 70.7761 | 23357.3841
2017-07-22 | 6:30 | 1.7842 | 6.5362 | 1 | 10 | 78.5841 | 66.4892 | 23058.8132
2017-07-22 | 6:45 | 1.7998 | 6.1828 | 1 | 10 | 77.7596 | 63.1938 | 22816.9013
2017-07-22 | 6:55 |  |  | 0 |  |  |  | 0
2017-07-22 | 7:00 | 1.7218 | 1.9324 | 0 | 1.5 | 78.0144 | 0 | 22891.6575
2017-07-22 | 7:01 |  |  | 1 |  |  |  | 0
2017-07-22 | 7:15 | 1.7577 | 5.2514 | 1 | 10 | 77.1633 | 0 | 22641.9034
2017-07-22 | 7:30 | 1.7772 | 5.9846 | 1 | 10 | 77.1933 | 0 | 22650.7124
2017-07-22 | 7:45 | 1.7928 | 5.6681 | 1 | 10 | 76.5308 | 0 | 22456.3142
2017-07-22 | 8:00 | 1.7429 | 5.8772 | 1 | 10 | 77.0567 | 0 | 22610.6312
2017-07-22 | 8:05 |  |  | 0 |  |  |  | 0
2017-07-22 | 8:15 | 1.7171 | 1.239 | 0 | 1.5 | 77.2471 | 0 | 22666.5085
2017-07-22 | 8:30 | 1.7592 | 0 | 0 | 1.5 | 77.361 | 0 | 22699.921
2017-07-22 | 8:45 | 1.7842 | 0 | 0 | 1.5 | 77.3975 | 0 | 22710.6288
2017-07-22 | 9:00 | 1.7319 | 0 | 0 | 1.5 | 77.4605 | 0 | 22729.12
2017-07-22 | 9:15 | 1.6976 | 0 | 0 | 1.5 | 77.9882 | 0 | 22883.9585
2017-07-22 | 9:30 | 1.7226 | 0 | 0 | 1.5 | 78.3979 | 0 | 23004.1759
2017-07-22 | 9:45 | 1.8014 | 0 | 0 | 1.5 | 78.3765 | 0 | 22997.8942
2017-07-22 | 10:00 | 1.721 | 0 | 0 | 1.5 | 78.5685 | 0 | 23054.255
2017-07-22 | 10:15 | 1.7109 | 0 | 0 | 1.5 | 78.5995 | 0 | 23063.351
2017-07-22 | 10:30 | 1.7085 | 0 | 0 | 1.5 | 78.8199 | 0 | 23128.0174
2017-07-22 | 10:45 | 1.7959 | 0 | 0 | 1.5 | 78.743 | 0 | 23105.4516
2017-07-22 | 11:00 | 1.7507 | 0 | 0 | 1.5 | 78.8674 | 0 | 23141.9488
2017-07-22 | 11:15 | 1.6992 | 0 | 0 | 1.5 | 79.3152 | 0 | 23273.3596
2017-07-22 | 11:30 | 1.7179 | 0 | 0 | 1.5 | 79.9024 | 0 | 23445.6418
2017-07-22 | 11:45 | 1.7889 | 0 | 0 | 1.5 | 80.129 | 0 | 23512.133
2017-07-22 | 12:00 | 1.7343 | 0 | 0 | 1.5 | 80.3718 | 0 | 23583.3968
2017-07-22 | 12:15 | 1.7062 | 0 | 0 | 1.5 | 80.8347 | 0 | 23719.2064
2017-07-22 | 12:30 | 1.7007 | 0 | 0 | 1.5 | 81.2113 | 0 | 23829.7078
2017-07-22 | 12:45 | 1.7717 | 0 | 0 | 1.5 | 81.4636 | 0 | 23903.7434
2017-07-22 | 13:00 | 1.7631 | 0 | 0 | 1.5 | 81.782 | 0 | 23997.1725
2017-07-22 | 13:15 | 1.7592 | 0 | 0 | 1.5 | 80.904 | 0 | 23739.5583
2017-07-22 | 13:30 | 1.714 | 0 | 0 | 1.5 | 80.9311 | 0 | 23747.4991
2017-07-22 | 13:45 | 1.7491 | 0 | 0 | 1.5 | 81.3457 | 0 | 23869.1399
2017-07-22 | 14:00 | 1.8326 | 0 | 0 | 1.5 | 80.9525 | 0 | 23753.7697
2017-07-22 | 14:15 | 1.7093 | 0 | 0 | 1.5 | 80.5193 | 0 | 23626.6729
2017-07-22 | 14:30 | 1.689 | 0 | 0 | 1.5 | 81.2321 | 0 | 23835.824
2017-07-22 | 14:45 | 1.8365 | 0 | 0 | 1.5 | 80.5955 | 0 | 23649.035
2017-07-22 | 15:00 | 1.7592 | 0 | 0 | 1.5 | 80.0417 | 0 | 23486.5246
2017-07-22 | 15:15 | 1.728 | 0 | 0 | 1.5 | 80.6925 | 0 | 23677.4888
2017-07-22 | 15:30 | 1.7265 | 0 | 0 | 1.5 | 80.0299 | 0 | 23483.0592
2017-07-22 | 15:45 | 1.7772 | 0 | 0 | 1.5 | 79.8378 | 0 | 23426.6957
2017-07-22 | 16:00 | 1.767 | 0.010001 | 0 | 1.5 | 80.2588 | 0 | 23550.2174
2017-07-22 | 16:15 | 1.7273 | 0 | 0 | 1.5 | 79.8156 | 0 | 23420.1857
2017-07-22 | 16:30 | 1.6734 | 0 | 0 | 1.5 | 80.2513 | 0 | 23548.0099
2017-07-22 | 16:45 | 1.8302 | 0 | 0 | 1.5 | 80.4149 | 0 | 23596.0319
2017-07-22 | 17:00 | 1.7787 | 0 | 0 | 1.5 | 79.6861 | 0 | 23382.1797
2017-07-22 | 17:15 | 1.6922 | 0 | 0 | 1.5 | 80.2254 | 0 | 23540.4163
2017-07-22 | 17:30 | 1.7592 | 0 | 0 | 1.5 | 80.5479 | 0 | 23635.0411
2017-07-22 | 17:45 | 1.8014 | 0 | 0 | 1.5 | 79.7439 | 0 | 23399.151
2017-07-22 | 18:00 | 1.7663 | 0 | 0 | 1.5 | 79.8865 | 0 | 23440.9719
2017-07-22 | 18:15 | 1.7507 | 0 | 0 | 1.5 | 80.089 | 0 | 23500.3888
2017-07-22 | 18:30 | 1.7202 | 0 | 0 | 1.5 | 79.5796 | 0 | 23350.9143
2017-07-22 | 18:45 | 1.7616 | 0 | 0 | 1.5 | 79.7863 | 0 | 23411.5824
2017-07-22 | 19:00 | 1.7553 | 0 | 0 | 1.5 | 80.2459 | 0 | 23546.4316
2017-07-22 | 19:15 | 1.6968 | 0 | 0 | 1.5 | 80.8657 | 0 | 23728.3112
2017-07-22 | 19:30 | 1.6883 | 0 | 0 | 1.5 | 81.33 | 0 | 23864.5551
2017-07-22 | 19:45 | 1.7904 | 0 | 0 | 1.5 | 81.3209 | 0 | 23861.8755
2017-07-22 | 20:00 | 1.7951 | 0 | 0 | 1.5 | 81.0597 | 0 | 23785.2296
2017-07-22 | 20:15 | 1.7904 | 0 | 0 | 1.5 | 80.6186 | 0 | 23655.7912
2017-07-22 | 20:30 | 1.7819 | 0 | 0 | 1.5 | 79.7061 | 0 | 23388.0538
2017-07-22 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 79.2459 | 0 | 23253.0121
2017-07-22 | 21:00 | 1.7553 | 0 | 0 | 1.5 | 78.7396 | 0 | 23104.4486
2017-07-22 | 21:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 21:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 22:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 22:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 22:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 22:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 23:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 23:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 23:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-22 | 23:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 0:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 0:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 0:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 1:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 1:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 1:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 1:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 2:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 2:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 2:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 2:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 3:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 3:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 3:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 3:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 4:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 4:15 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 4:30 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 4:45 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 5:00 | 0.02608 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-23 | 5:15 | 2.0081 | 10 | 1 | 10 | 94.0223 | 100 | 27588.8271
2017-07-23 | 5:30 | 1.8747 | 10 | 1 | 10 | 89.9687 | 100 | 26399.3727
2017-07-23 | 5:45 | 1.8942 | 9.3883 | 1 | 10 | 86.9014 | 94.3028 | 25499.3663
2017-07-23 | 6:00 | 1.8645 | 8.3025 | 1 | 10 | 84.2005 | 83.866 | 24706.8371
2017-07-23 | 6:15 | 1.8318 | 7.6846 | 1 | 10 | 81.9204 | 77.6689 | 24037.7777
2017-07-23 | 6:30 | 1.7756 | 7.4849 | 1 | 10 | 80.908 | 75.2838 | 23740.7271
2017-07-23 | 6:45 | 1.785 | 7.6539 | 1 | 10 | 79.8537 | 77.4734 | 23431.3433
2017-07-23 | 7:00 | 1.8216 | 6.5816 | 1 | 10 | 78.7196 | 67.0389 | 23098.5877
2017-07-23 | 7:15 | 1.7858 | 7.2925 | 1 | 10 | 77.9213 | 73.7372 | 22864.3501
2017-07-23 | 7:30 | 1.7304 | 6.4837 | 1 | 10 | 77.5774 | 65.5948 | 22763.4348
2017-07-23 | 7:45 | 1.7538 | 6.8658 | 1 | 10 | 77.4043 | 68.8608 | 22712.6232
2017-07-23 | 8:00 | 1.799 | 6.4667 | 1 | 10 | 76.9805 | 65.8867 | 22588.269
2017-07-23 | 8:09 |  |  | 0 |  |  |  | 0
2017-07-23 | 8:15 | 1.7748 | 2.0146 | 0 | 1.5 | 76.8088 | 0 | 22537.8918
2017-07-23 | 8:30 | 1.7179 | 0 | 0 | 1.5 | 76.8713 | 0 | 22556.2357
2017-07-23 | 8:45 | 1.7561 | 0 | 0 | 1.5 | 76.8508 | 0 | 22550.2205
2017-07-23 | 9:00 | 1.7741 | 0 | 0 | 1.5 | 75.9839 | 0 | 22295.8411
2017-07-23 | 9:15 | 1.76 | 0 | 0 | 1.5 | 75.878 | 0 | 22264.7594
2017-07-23 | 9:30 | 1.7569 | 0 | 0 | 1.5 | 75.6674 | 0 | 22202.9648
2017-07-23 | 9:45 | 1.7444 | 0 | 0 | 1.5 | 75.8359 | 0 | 22252.4219
2017-07-23 | 10:00 | 1.7358 | 0 | 0 | 1.5 | 75.7366 | 0 | 22223.2721
2017-07-23 | 10:15 | 1.739 | 0 | 0 | 1.5 | 75.7357 | 0 | 22223.0235
2017-07-23 | 10:30 | 1.7436 | 0 | 0 | 1.5 | 75.7299 | 0 | 22221.3175
2017-07-23 | 10:45 | 1.7655 | 0 | 0 | 1.5 | 75.7169 | 0 | 22217.4939
2017-07-23 | 11:00 | 1.7491 | 0 | 0 | 1.5 | 75.8799 | 0 | 22265.3277
2017-07-23 | 11:15 | 1.721 | 0 | 0 | 1.5 | 76.5926 | 0 | 22474.4522
2017-07-23 | 11:30 | 1.7655 | 0 | 0 | 1.5 | 76.986 | 0 | 22589.9032
2017-07-23 | 11:45 | 1.707 | 0 | 0 | 1.5 | 77.4442 | 0 | 22724.336
2017-07-23 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 77.6188 | 0 | 22775.5818
2017-07-23 | 12:15 | 1.7608 | 0 | 0 | 1.5 | 77.9627 | 0 | 22876.4793
2017-07-23 | 12:30 | 1.7772 | 0 | 0 | 1.5 | 78.1379 | 0 | 22927.8974
2017-07-23 | 12:45 | 1.7007 | 0 | 0 | 1.5 | 78.3319 | 0 | 22984.8114
2017-07-23 | 13:00 | 1.7148 | 0 | 0 | 1.5 | 78.6833 | 0 | 23087.9339
2017-07-23 | 13:15 | 1.7507 | 0 | 0 | 1.5 | 78.9315 | 0 | 23160.7605
2017-07-23 | 13:30 | 1.8045 | 0 | 0 | 1.5 | 78.9888 | 0 | 23177.5596
2017-07-23 | 13:45 | 1.7327 | 0 | 0 | 1.5 | 79.1039 | 0 | 23211.3479
2017-07-23 | 14:00 | 1.7031 | 0 | 0 | 1.5 | 79.4635 | 0 | 23316.8616
2017-07-23 | 14:15 | 1.7358 | 0 | 0 | 1.5 | 79.6966 | 0 | 23385.2489
2017-07-23 | 14:30 | 1.7959 | 0 | 0 | 1.5 | 79.6612 | 0 | 23374.8815
2017-07-23 | 14:45 | 1.7507 | 0 | 0 | 1.5 | 79.697 | 0 | 23385.381
2017-07-23 | 15:00 | 1.7062 | 0 | 0 | 1.5 | 80.0528 | 0 | 23489.7641
2017-07-23 | 15:15 | 1.721 | 0 | 0 | 1.5 | 80.3135 | 0 | 23566.2888
2017-07-23 | 15:30 | 1.7795 | 0 | 0 | 1.5 | 80.2426 | 0 | 23545.46
2017-07-23 | 15:45 | 1.7725 | 0 | 0 | 1.5 | 80.0863 | 0 | 23499.6165
2017-07-23 | 16:00 | 1.7156 | 0 | 0 | 1.5 | 80.2227 | 0 | 23539.6352
2017-07-23 | 16:15 | 1.7343 | 0 | 0 | 1.5 | 80.2504 | 0 | 23547.7682
2017-07-23 | 16:30 | 1.7826 | 0 | 0 | 1.5 | 80.1439 | 0 | 23516.5095
2017-07-23 | 16:45 | 1.778 | 0 | 0 | 1.5 | 79.918 | 0 | 23450.2131
2017-07-23 | 17:00 | 1.7031 | 0 | 0 | 1.5 | 79.9603 | 0 | 23462.6378
2017-07-23 | 17:15 | 1.7319 | 0 | 0 | 1.5 | 79.922 | 0 | 23451.3951
2017-07-23 | 17:30 | 1.7881 | 0 | 0 | 1.5 | 79.5789 | 0 | 23350.7083
2017-07-23 | 17:45 | 1.8021 | 0 | 0 | 1.5 | 79.1609 | 0 | 23228.0598
2017-07-23 | 18:00 | 1.7202 | 0 | 0 | 1.5 | 79.0334 | 0 | 23190.6468
2017-07-23 | 18:15 | 1.7343 | 0 | 0 | 1.5 | 79.0664 | 0 | 23200.3537
2017-07-23 | 18:30 | 1.7873 | 0 | 0 | 1.5 | 78.9811 | 0 | 23175.3231
2017-07-23 | 18:45 | 1.7733 | 0 | 0 | 1.5 | 78.7172 | 0 | 23097.8647
2017-07-23 | 19:00 | 1.7179 | 0 | 0 | 1.5 | 78.6946 | 0 | 23091.2493
2017-07-23 | 19:15 | 1.7117 | 0 | 0 | 1.5 | 78.6723 | 0 | 23084.6924
2017-07-23 | 19:30 | 1.7702 | 0 | 0 | 1.5 | 78.4939 | 0 | 23032.3585
2017-07-23 | 19:45 | 1.7951 | 0.013443 | 0 | 1.5 | 78.0931 | 0 | 22914.7427
2017-07-23 | 20:00 | 1.7538 | 0 | 0 | 1.5 | 77.819 | 0 | 22834.3045
2017-07-23 | 20:15 | 1.7413 | 0 | 0 | 1.5 | 77.7323 | 0 | 22808.871
2017-07-23 | 20:30 | 1.778 | 0 | 0 | 1.5 | 77.4864 | 0 | 22736.7204
2017-07-23 | 20:45 | 1.7951 | 0 | 0 | 1.5 | 76.9368 | 0 | 22575.4459
2017-07-23 | 21:00 | 1.7195 | 0 | 0 | 1.5 | 76.7142 | 0 | 22510.1366
2017-07-23 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 21:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 23:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-23 | 23:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 0:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 0:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 1:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 1:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 2:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 4:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 4:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 5:00 |  |  | 1 |  |  |  | 0
2017-07-24 | 5:15 | 2.2928 | 8.6295 | 1 | 10 | 87.5042 | 89.1504 | 25676.2424
2017-07-24 | 5:30 | 1.9769 | 6.401 | 1 | 10 | 80.8125 | 67.1484 | 23712.6964
2017-07-24 | 5:45 | 1.7998 | 5.9015 | 1 | 10 | 78.4556 | 0 | 23021.1272
2017-07-24 | 6:00 | 1.7631 | 5.6013 | 1 | 10 | 77.5644 | 0 | 22759.6178
2017-07-24 | 6:15 | 1.7865 | 6.0315 | 1 | 10 | 77.1006 | 0 | 22623.5125
2017-07-24 | 6:30 | 1.7811 | 6.1857 | 1 | 10 | 76.7541 | 0 | 22521.8474
2017-07-24 | 6:45 | 1.746 | 5.5399 | 1 | 10 | 76.7563 | 0 | 22522.5032
2017-07-24 | 7:00 | 1.7834 | 4.838 | 1 | 10 | 76.8048 | 0 | 22536.721
2017-07-24 | 7:15 | 1.7663 | 4.9298 | 1 | 10 | 76.3812 | 0 | 22412.4205
2017-07-24 | 7:30 | 1.7702 | 4.8602 | 1 | 10 | 76.0321 | 0 | 22309.9896
2017-07-24 | 7:45 | 1.7171 | 4.2516 | 1 | 10 | 76.0933 | 0 | 22327.9348
2017-07-24 | 8:00 | 1.6875 | 3.5395 | 1 | 10 | 76.6727 | 0 | 22497.9717
2017-07-24 | 8:15 | 1.7819 | 4.3897 | 1 | 10 | 77.4916 | 0 | 22738.2471
2017-07-24 | 8:30 | 1.8014 | 4.1147 | 1 | 10 | 77.4868 | 0 | 22736.8504
2017-07-24 | 8:45 | 1.7304 | 5.2784 | 1 | 10 | 78.1229 | 0 | 22923.4959
2017-07-24 | 9:00 | 1.7093 | 5.0355 | 1 | 10 | 78.5504 | 0 | 23048.9317
2017-07-24 | 9:07 |  |  | 0 |  |  |  | 0
2017-07-24 | 9:15 | 1.7187 | 1.0478 | 0 | 1.5 | 79.3772 | 0 | 23291.5466
2017-07-24 | 9:30 | 1.7725 | 0 | 0 | 1.5 | 80.0195 | 0 | 23479.9988
2017-07-24 | 9:45 | 1.7452 | 0 | 0 | 1.5 | 80.0583 | 0 | 23491.3826
2017-07-24 | 10:00 | 1.7015 | 0 | 0 | 1.5 | 80.2984 | 0 | 23561.8407
2017-07-24 | 10:15 | 1.7054 | 0 | 0 | 1.5 | 80.9944 | 0 | 23766.0623
2017-07-24 | 10:30 | 1.7522 | 0 | 0 | 1.5 | 81.4931 | 0 | 23912.396
2017-07-24 | 10:45 | 1.6617 | 0 | 0 | 1.5 | 82.4313 | 0 | 24187.7001
2017-07-24 | 11:00 | 1.6165 | 0 | 0 | 1.5 | 83.8179 | 0 | 24594.5737
2017-07-24 | 11:15 | 1.7187 | 0 | 0 | 1.5 | 85.3739 | 0 | 25051.1509
2017-07-24 | 11:30 | 1.7858 | 0 | 0 | 1.5 | 86.3436 | 0 | 25335.6874
2017-07-24 | 11:45 | 1.7382 | 0 | 0 | 1.5 | 87.0151 | 0 | 25532.7138
2017-07-24 | 12:00 | 1.6649 | 0 | 0 | 1.5 | 87.8312 | 0 | 25772.1879
2017-07-24 | 12:15 | 1.6797 | 0 | 0 | 1.5 | 88.0824 | 0 | 25845.8875
2017-07-24 | 12:30 | 1.7764 | 0 | 0 | 1.5 | 88.386 | 0 | 25934.9895
2017-07-24 | 12:45 | 1.7577 | 0 | 0 | 1.5 | 88.2296 | 0 | 25889.0987
2017-07-24 | 13:00 | 1.7273 | 0 | 0 | 1.5 | 87.0905 | 0 | 25554.8454
2017-07-24 | 13:15 | 1.7124 | 0 | 0 | 1.5 | 87.48 | 0 | 25669.1303
2017-07-24 | 13:30 | 1.863 | 0 | 0 | 1.5 | 87.5966 | 0 | 25703.3396
2017-07-24 | 13:45 | 1.8279 | 0 | 0 | 1.5 | 85.0921 | 0 | 24968.4516
2017-07-24 | 14:00 | 1.6727 | 0 | 0 | 1.5 | 86.2052 | 0 | 25295.0552
2017-07-24 | 14:15 | 1.6851 | 0 | 0 | 1.5 | 88.2028 | 0 | 25881.2072
2017-07-24 | 14:30 | 1.9269 | 0 | 0 | 1.5 | 85.2568 | 0 | 25016.7669
2017-07-24 | 14:45 | 1.7343 | 0 | 0 | 1.5 | 84.9541 | 0 | 24927.9719
2017-07-24 | 15:00 | 1.622 | 0 | 0 | 1.5 | 87.3577 | 0 | 25633.253
2017-07-24 | 15:15 | 1.8302 | 0 | 0 | 1.5 | 86.878 | 0 | 25492.4936
2017-07-24 | 15:30 | 1.7842 | 0 | 0 | 1.5 | 84.7927 | 0 | 24880.5947
2017-07-24 | 15:45 | 1.6563 | 0 | 0 | 1.5 | 86.3803 | 0 | 25346.4577
2017-07-24 | 16:00 | 1.838 | 0 | 0 | 1.5 | 87.3735 | 0 | 25637.8693
2017-07-24 | 16:15 | 1.7741 | 0 | 0 | 1.5 | 84.7428 | 0 | 24865.9602
2017-07-24 | 16:30 | 1.6656 | 0 | 0 | 1.5 | 85.2258 | 0 | 25007.6959
2017-07-24 | 16:45 | 1.8388 | 0 | 0 | 1.5 | 86.5275 | 0 | 25389.6463
2017-07-24 | 17:00 | 1.7717 | 0 | 0 | 1.5 | 84.2873 | 0 | 24732.3064
2017-07-24 | 17:15 | 1.6719 | 0 | 0 | 1.5 | 85.6742 | 0 | 25139.2631
2017-07-24 | 17:30 | 1.948 | 0 | 0 | 1.5 | 84.6645 | 0 | 24842.9871
2017-07-24 | 17:45 | 1.8388 | 0 | 0 | 1.5 | 82.1144 | 0 | 24094.7164
2017-07-24 | 18:00 | 1.7273 | 0 | 0 | 1.5 | 82.0709 | 0 | 24081.9358
2017-07-24 | 18:15 | 1.7226 | 0 | 0 | 1.5 | 82.6204 | 0 | 24243.1971
2017-07-24 | 18:30 | 1.7257 | 0 | 0 | 1.5 | 83.3163 | 0 | 24447.3782
2017-07-24 | 18:45 | 1.7694 | 0 | 0 | 1.5 | 83.0229 | 0 | 24361.2965
2017-07-24 | 19:00 | 1.7951 | 0 | 0 | 1.5 | 82.6542 | 0 | 24253.1076
2017-07-24 | 19:15 | 1.792 | 0 | 0 | 1.5 | 82.6282 | 0 | 24245.4691
2017-07-24 | 19:30 | 1.753 | 0 | 0 | 1.5 | 82.3769 | 0 | 24171.7293
2017-07-24 | 19:45 | 1.7733 | 0 | 0 | 1.5 | 81.5657 | 0 | 23933.7171
2017-07-24 | 20:00 | 1.7982 | 0 | 0 | 1.5 | 81.0055 | 0 | 23769.324
2017-07-24 | 20:15 | 1.7717 | 0 | 0 | 1.5 | 80.0491 | 0 | 23488.6828
2017-07-24 | 20:30 | 1.8092 | 0 | 0 | 1.5 | 79.3413 | 0 | 23281.0023
2017-07-24 | 20:45 | 1.7631 | 0 | 0 | 1.5 | 78.5217 | 0 | 23040.5232
2017-07-24 | 21:00 | 1.7663 | 0 | 0 | 1.5 | 77.9229 | 0 | 22864.8155
2017-07-24 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 21:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 3:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 3:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 4:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 4:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 4:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 5:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-25 | 5:15 | 2.1196 | 10 | 1 | 10 | 92.984 | 100 | 27284.1649
2017-07-25 | 5:30 | 1.9683 | 9.2055 | 1 | 10 | 86.3703 | 92.534 | 25343.5049
2017-07-25 | 5:45 | 1.8419 | 8.3056 | 1 | 10 | 83.316 | 83.5721 | 24447.3066
2017-07-25 | 6:00 | 1.8489 | 7.3186 | 1 | 10 | 81.1526 | 74.2507 | 23812.4991
2017-07-25 | 6:15 | 1.7998 | 7.2741 | 1 | 10 | 79.6267 | 73.6038 | 23364.7424
2017-07-25 | 6:30 | 1.7577 | 7.2533 | 1 | 10 | 79.0028 | 73.2819 | 23181.6764
2017-07-25 | 6:45 | 1.7468 | 6.9449 | 1 | 10 | 78.825 | 70.6905 | 23129.5039
2017-07-25 | 7:00 | 1.824 | 6.6474 | 1 | 10 | 78.2134 | 0 | 22950.0603
2017-07-25 | 7:15 | 1.7608 | 6.7673 | 1 | 10 | 77.9817 | 0 | 22882.0579
2017-07-25 | 7:30 | 1.6906 | 5.8524 | 1 | 10 | 77.6267 | 0 | 22777.8852
2017-07-25 | 7:45 | 1.7553 | 6.0634 | 1 | 10 | 77.6027 | 0 | 22770.8403
2017-07-25 | 8:00 | 1.7678 | 5.7778 | 1 | 10 | 77.9166 | 0 | 22862.9487
2017-07-25 | 8:15 | 1.7803 | 6.1972 | 1 | 10 | 77.9376 | 0 | 22869.1183
2017-07-25 | 8:30 | 1.7982 | 5.3786 | 1 | 10 | 77.8945 | 0 | 22856.4833
2017-07-25 | 8:44 |  |  | 0 |  |  |  | 0
2017-07-25 | 8:45 | 1.7304 | 4.1188 | 0 | 1.5 | 77.6547 | 0 | 22786.108
2017-07-25 | 9:00 | 1.7405 | 0 | 0 | 1.5 | 78.4782 | 0 | 23027.7558
2017-07-25 | 9:15 | 1.7249 | 0 | 0 | 1.5 | 79.0703 | 0 | 23201.4775
2017-07-25 | 9:30 | 1.7265 | 0 | 0 | 1.5 | 79.5137 | 0 | 23331.5943
2017-07-25 | 9:45 | 1.7312 | 0 | 0 | 1.5 | 79.949 | 0 | 23459.3267
2017-07-25 | 10:00 | 1.7296 | 0 | 0 | 1.5 | 80.5967 | 0 | 23649.3842
2017-07-25 | 10:15 | 1.7 | 0 | 0 | 1.5 | 81.1446 | 0 | 23810.1417
2017-07-25 | 10:30 | 1.7226 | 0 | 0 | 1.5 | 81.3968 | 0 | 23884.1459
2017-07-25 | 10:45 | 1.6883 | 0 | 0 | 1.5 | 82.4441 | 0 | 24191.4656
2017-07-25 | 11:00 | 1.7015 | 0 | 0 | 1.5 | 83.6056 | 0 | 24532.2847
2017-07-25 | 11:15 | 1.714 | 0 | 0 | 1.5 | 84.2646 | 0 | 24725.6553
2017-07-25 | 11:30 | 1.6906 | 0 | 0 | 1.5 | 85.2565 | 0 | 25016.7042
2017-07-25 | 11:45 | 1.746 | 0 | 0 | 1.5 | 85.9583 | 0 | 25222.6206
2017-07-25 | 12:00 | 1.6734 | 0 | 0 | 1.5 | 87.574 | 0 | 25696.7084
2017-07-25 | 12:15 | 1.941 | 0 | 0 | 1.5 | 86.9754 | 0 | 25521.0727
2017-07-25 | 12:30 | 1.7842 | 0 | 0 | 1.5 | 84.4983 | 0 | 24794.224
2017-07-25 | 12:45 | 1.6578 | 0 | 0 | 1.5 | 84.8243 | 0 | 24889.8741
2017-07-25 | 13:00 | 1.6485 | 0 | 0 | 1.5 | 86.8042 | 0 | 25470.8412
2017-07-25 | 13:15 | 1.8427 | 0 | 0 | 1.5 | 85.3592 | 0 | 25046.8369
2017-07-25 | 13:30 | 1.6664 | 0 | 0 | 1.5 | 85.7184 | 0 | 25152.2318
2017-07-25 | 13:45 | 1.7117 | 0 | 0 | 1.5 | 87.8852 | 0 | 25788.0378
2017-07-25 | 14:00 | 1.9168 | 0 | 0 | 1.5 | 85.4617 | 0 | 25076.918
2017-07-25 | 14:15 | 1.6594 | 0 | 0 | 1.5 | 84.4207 | 0 | 24771.4589
2017-07-25 | 14:30 | 1.668 | 0 | 0 | 1.5 | 86.1842 | 0 | 25288.8991
2017-07-25 | 14:45 | 1.8513 | 0 | 0 | 1.5 | 85.8779 | 0 | 25199.0427
2017-07-25 | 15:00 | 1.7249 | 0 | 0 | 1.5 | 84.7086 | 0 | 24855.9355
2017-07-25 | 15:15 | 1.6064 | 0 | 0 | 1.5 | 87.2128 | 0 | 25590.7203
2017-07-25 | 15:30 | 1.8848 | 0 | 0 | 1.5 | 85.7757 | 0 | 25169.0288
2017-07-25 | 15:45 | 1.7569 | 0 | 0 | 1.5 | 83.6673 | 0 | 24550.3622
2017-07-25 | 16:00 | 1.6298 | 0 | 0 | 1.5 | 86.0928 | 0 | 25262.0817
2017-07-25 | 16:15 | 1.8872 | 0 | 0 | 1.5 | 85.3203 | 0 | 25035.3994
2017-07-25 | 16:30 | 1.6812 | 0 | 0 | 1.5 | 84.0863 | 0 | 24673.3194
2017-07-25 | 16:45 | 1.6727 | 0 | 0 | 1.5 | 86.0334 | 0 | 25244.6603
2017-07-25 | 17:00 | 1.8357 | 0 | 0 | 1.5 | 84.45 | 0 | 24780.0396
2017-07-25 | 17:15 | 1.7709 | 0 | 0 | 1.5 | 84.091 | 0 | 24674.6985
2017-07-25 | 17:30 | 1.8934 | 0 | 0 | 1.5 | 83.3916 | 0 | 24469.4672
2017-07-25 | 17:45 | 1.8224 | 0 | 0 | 1.5 | 80.6776 | 0 | 23673.1255
2017-07-25 | 18:00 | 1.7078 | 0 | 0 | 1.5 | 80.6253 | 0 | 23657.7681
2017-07-25 | 18:15 | 1.6953 | 0 | 0 | 1.5 | 81.2399 | 0 | 23838.1119
2017-07-25 | 18:30 | 1.7366 | 0 | 0 | 1.5 | 82.2991 | 0 | 24148.9217
2017-07-25 | 18:45 | 1.8622 | 0 | 0 | 1.5 | 82.3931 | 0 | 24176.4887
2017-07-25 | 19:00 | 1.7608 | 0 | 0 | 1.5 | 80.7762 | 0 | 23702.0514
2017-07-25 | 19:15 | 1.7546 | 0 | 0 | 1.5 | 80.467 | 0 | 23611.3265
2017-07-25 | 19:30 | 1.7561 | 0 | 0 | 1.5 | 80.7186 | 0 | 23685.1361
2017-07-25 | 19:45 | 1.76 | 0 | 0 | 1.5 | 80.9397 | 0 | 23750.022
2017-07-25 | 20:00 | 1.7343 | 0 | 0 | 1.5 | 80.6705 | 0 | 23671.0167
2017-07-25 | 20:15 | 1.7842 | 0 | 0 | 1.5 | 80.3803 | 0 | 23585.8728
2017-07-25 | 20:30 | 1.7397 | 0 | 0 | 1.5 | 80.0007 | 0 | 23474.4984
2017-07-25 | 20:45 | 1.7733 | 0 | 0 | 1.5 | 79.4254 | 0 | 23305.6749
2017-07-25 | 21:00 | 1.7608 | 0 | 0 | 1.5 | 78.9185 | 0 | 23156.9301
2017-07-25 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 22:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 0:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 0:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 0:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 0:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 0:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 1:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 1:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 1:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 1:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 1:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 1:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 2:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 2:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 2:15 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 2:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 2:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 2:45 | 0.02764 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 2:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 3:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 3:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 3:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 3:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 3:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 3:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 4:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 4:15 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 4:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 4:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 4:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 4:45 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 4:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 5:00 | 0.02998 | 0 | 0 | 0 | 25 | 0 | 7335.7143
2017-07-26 | 5:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 5:00 |  |  | 1 |  |  |  | 0
2017-07-26 | 5:15 | 2.0299 | 10 | 1 |  | 94.9662 | 100 | 27865.7926
2017-07-26 | 5:15 |  |  |  | 10 |  |  | 0
2017-07-26 | 5:30 | 2.0564 | 9.8292 | 1 | 10 | 88.1376 | 98.6187 | 25862.0889
2017-07-26 | 5:30 |  |  |  | 10 |  |  | 0
2017-07-26 | 5:45 | 1.9051 | 8.0508 | 1 |  | 83.2417 | 81.6926 | 24425.484
2017-07-26 | 5:45 |  |  |  | 10 |  |  | 0
2017-07-26 | 6:00 | 1.8021 | 7.1838 | 1 | 10 | 81.0952 | 72.8066 | 23795.6507
2017-07-26 | 6:00 |  |  |  | 10 |  |  | 0
2017-07-26 | 6:15 | 1.8131 | 7.7179 | 1 |  | 80.4902 | 77.9925 | 23618.1144
2017-07-26 | 6:15 |  |  |  | 10 |  |  | 0
2017-07-26 | 6:30 | 1.7234 | 7.399 | 1 | 10 | 79.8522 | 74.9726 | 23430.9313
2017-07-26 | 6:30 |  |  |  | 10 |  |  | 0
2017-07-26 | 6:45 | 1.7234 | 7.1059 | 1 |  | 80.1225 | 72.497 | 23510.221
2017-07-26 | 6:45 |  |  |  | 10 |  |  | 0
2017-07-26 | 7:00 | 1.8427 | 6.8132 | 1 | 10 | 79.3655 | 69.1962 | 23288.0968
2017-07-26 | 7:00 |  |  |  | 10 |  |  | 0
2017-07-26 | 7:15 | 1.7881 | 7.0363 | 1 |  | 79.1045 | 0 | 23211.5272
2017-07-26 | 7:15 |  |  |  | 10 |  |  | 0
2017-07-26 | 7:30 | 1.7553 | 7.1703 | 1 | 10 | 78.6497 | 0 | 23078.0726
2017-07-26 | 7:30 |  |  |  | 10 |  |  | 0
2017-07-26 | 7:45 | 1.753 | 5.9572 | 1 |  | 79.0818 | 0 | 23204.8514
2017-07-26 | 7:45 |  |  |  | 10 |  |  | 0
2017-07-26 | 8:00 | 1.7179 | 4.84 | 1 | 10 | 78.9382 | 0 | 23162.7282
2017-07-26 | 8:00 |  |  |  | 10 |  |  | 0
2017-07-26 | 8:15 | 1.7421 | 5.689 | 1 |  | 80.0853 | 0 | 23499.3028
2017-07-26 | 8:15 |  |  |  | 10 |  |  | 0
2017-07-26 | 8:30 | 1.7304 | 5.1412 | 1 | 10 | 80.4423 | 0 | 23604.0777
2017-07-26 | 8:30 |  |  |  | 10 |  |  | 0
2017-07-26 | 8:45 | 1.7304 | 6.029 | 1 |  | 80.889 | 0 | 23735.1461
2017-07-26 | 8:45 |  |  |  | 10 |  |  | 0
2017-07-26 | 9:00 | 1.7413 | 5.4989 | 1 | 10 | 80.9345 | 0 | 23748.4886
2017-07-26 | 9:00 |  |  |  | 10 |  |  | 0
2017-07-26 | 9:15 | 1.7577 | 6.9955 | 1 |  | 81.3154 | 0 | 23860.2614
2017-07-26 | 9:15 |  |  |  | 10 |  |  | 0
2017-07-26 | 9:30 | 1.7023 | 7.311 | 1 | 10 | 82.1218 | 0 | 24096.8722
2017-07-26 | 9:30 |  |  |  | 10 |  |  | 0
2017-07-26 | 9:42 |  |  | 0 |  |  |  | 0
2017-07-26 | 9:45 | 1.622 | 5.6153 | 0 |  | 83.2998 | 0 | 24442.536
2017-07-26 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 9:48 |  |  | 1 |  |  |  | 0
2017-07-26 | 9:51 |  |  | 0 |  |  |  | 0
2017-07-26 | 10:00 |  |  | 1 |  |  |  | 0
2017-07-26 | 10:00 | 1.7491 | 0 | 1 | 10 | 83.8868 | 0 | 24614.7848
2017-07-26 | 10:00 |  |  |  | 10 |  |  | 0
2017-07-26 | 10:03 |  |  | 0 |  |  |  | 0
2017-07-26 | 10:15 | 1.6953 | 0 | 0 |  | 84.7082 | 0 | 24855.8035
2017-07-26 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 10:30 | 1.6953 | 0 | 0 | 1.5 | 85.9593 | 0 | 25222.9137
2017-07-26 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 10:45 | 1.6992 | 0 | 0 |  | 86.8767 | 0 | 25492.1042
2017-07-26 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 11:00 | 1.6945 | 0 | 0 | 1.5 | 87.9609 | 0 | 25810.2298
2017-07-26 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 11:15 | 1.6656 | 0 | 0 |  | 89.3608 | 0 | 26221.0213
2017-07-26 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 11:30 | 1.7109 | 0 | 0 | 1.5 | 90.2195 | 0 | 26472.9673
2017-07-26 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 11:45 | 1.6812 | 0 | 0 |  | 91.1346 | 0 | 26741.4837
2017-07-26 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 12:00 | 1.7421 | 0 | 0 | 1.5 | 91.8008 | 0 | 26936.9832
2017-07-26 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 12:15 | 1.9379 | 0 | 0 |  | 88.6176 | 0 | 26002.9223
2017-07-26 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 12:30 | 1.8076 | 0 | 0 | 1.5 | 87.4858 | 0 | 25670.8228
2017-07-26 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 12:45 | 1.7148 | 0 | 0 |  | 88.6754 | 0 | 26019.8892
2017-07-26 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 13:00 | 1.9043 | 0 | 0 | 1.5 | 88.6041 | 0 | 25998.9798
2017-07-26 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 13:15 | 1.7678 | 0 | 0 |  | 87.1638 | 0 | 25576.3546
2017-07-26 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 13:30 | 1.6064 | 0 | 0 | 1.5 | 88.588 | 0 | 25994.2383
2017-07-26 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 13:45 | 1.7624 | 0 | 0 |  | 89.8183 | 0 | 26355.2549
2017-07-26 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 14:00 | 1.8599 | 0 | 0 | 1.5 | 86.658 | 0 | 25427.9346
2017-07-26 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 14:15 | 1.611 | 0 | 0 |  | 87.2513 | 0 | 25602.0258
2017-07-26 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 14:30 | 1.6836 | 0 | 0 | 1.5 | 90.0666 | 0 | 26428.0994
2017-07-26 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 14:45 | 1.955 | 0 | 0 |  | 87.8615 | 0 | 25781.0689
2017-07-26 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 15:00 | 1.6563 | 0 | 0 | 1.5 | 86.89 | 0 | 25496.0197
2017-07-26 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 15:15 | 1.746 | 0 | 0 |  | 89.1503 | 0 | 26159.2361
2017-07-26 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 15:30 | 1.9652 | 0 | 0 | 1.5 | 86.7906 | 0 | 25466.8517
2017-07-26 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 15:45 | 1.6524 | 0 | 0 |  | 85.9309 | 0 | 25214.5859
2017-07-26 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 16:00 | 1.7499 | 0 | 0 | 1.5 | 88.0385 | 0 | 25833.0063
2017-07-26 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 16:15 | 1.9776 | 0 | 0 |  | 85.6379 | 0 | 25128.6049
2017-07-26 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 16:30 | 1.7156 | 0 | 0 | 1.5 | 83.3791 | 0 | 24465.8093
2017-07-26 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 16:45 | 1.6469 | 0 | 0 |  | 85.0743 | 0 | 24963.2288
2017-07-26 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 17:00 | 1.806 | 0 | 0 | 1.5 | 85.2386 | 0 | 25011.4301
2017-07-26 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 17:15 | 1.8138 | 0 | 0 |  | 82.7497 | 0 | 24281.1403
2017-07-26 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 17:30 | 1.7335 | 0 | 0 | 1.5 | 82.9536 | 0 | 24340.9602
2017-07-26 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 17:45 | 1.7179 | 0 | 0 |  | 83.5576 | 0 | 24518.2013
2017-07-26 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 18:00 | 1.8614 | 0 | 0 | 1.5 | 83.2613 | 0 | 24431.2396
2017-07-26 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 18:15 | 1.7592 | 0 | 0 |  | 81.688 | 0 | 23969.5829
2017-07-26 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 18:30 | 1.7 | 0 | 0 | 1.5 | 82.1181 | 0 | 24095.7865
2017-07-26 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 18:45 | 1.7273 | 0 | 0 |  | 82.7758 | 0 | 24288.7765
2017-07-26 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 19:00 | 1.7881 | 0 | 0 | 1.5 | 82.7652 | 0 | 24285.6738
2017-07-26 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 19:15 | 1.7608 | 0 | 0 |  | 82.9178 | 0 | 24330.4563
2017-07-26 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 19:30 | 1.7639 | 0 | 0 | 1.5 | 82.9435 | 0 | 24337.9851
2017-07-26 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 19:45 | 1.7865 | 0 | 0 |  | 82.7059 | 0 | 24268.277
2017-07-26 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 20:00 | 1.7881 | 0 | 0 | 1.5 | 82.1761 | 0 | 24112.823
2017-07-26 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 20:15 | 1.7538 | 0 | 0 |  | 81.4323 | 0 | 23894.5535
2017-07-26 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 20:30 | 1.7897 | 0 | 0 | 1.5 | 80.557 | 0 | 23637.7184
2017-07-26 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 20:45 | 1.8045 | 0 | 0 |  | 79.863 | 0 | 23434.079
2017-07-26 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-07-26 | 21:00 | 1.7975 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 21:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 21:15 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 21:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 21:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 21:45 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 21:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 22:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 22:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 22:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 22:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 22:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 22:45 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 22:45 |  |  |  | 0 |  |  | 0
2017-07-26 | 23:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 23:00 |  |  |  | 0 |  |  | 0
2017-07-26 | 23:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 23:15 |  |  |  | 0 |  |  | 0
2017-07-26 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 23:30 |  |  |  | 0 |  |  | 0
2017-07-26 | 23:45 | 0.02842 | 0 | 0 |  | 0 | 0 | 0
2017-07-26 | 23:45 |  |  |  | 0 |  |  | 0
2017-07-27 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 0:00 |  |  |  | 0 |  |  | 0
2017-07-27 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 0:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 1:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 2:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 3:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 3:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 3:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 5:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-27 | 5:15 | 1.9722 | 10 | 1 | 10 | 95.6125 | 100 | 28055.4513
2017-07-27 | 5:30 | 1.9995 | 9.998 | 1 | 10 | 89.6858 | 100 | 26316.3759
2017-07-27 | 5:45 | 1.9613 | 8.8346 | 1 | 10 | 83.6894 | 88.9662 | 24556.8499
2017-07-27 | 6:00 | 1.7772 | 8.0436 | 1 | 10 | 81.7722 | 81.0269 | 23994.2981
2017-07-27 | 6:15 | 1.7382 | 8.1481 | 1 | 10 | 80.9474 | 82.4786 | 23752.2785
2017-07-27 | 6:30 | 1.7741 | 7.7318 | 1 | 10 | 79.9897 | 78.515 | 23471.2546
2017-07-27 | 6:45 | 1.7943 | 6.9945 | 1 | 10 | 79.1961 | 71.0576 | 23238.3847
2017-07-27 | 7:00 | 1.7826 | 6.5156 | 1 | 10 | 78.7905 | 66.104 | 23119.3806
2017-07-27 | 7:15 | 1.7296 | 6.6293 | 1 | 10 | 78.7924 | 67.0298 | 23119.9358
2017-07-27 | 7:30 | 1.721 | 6.3866 | 1 | 10 | 78.9062 | 0 | 23153.3438
2017-07-27 | 7:45 | 1.7795 | 6.6236 | 1 | 10 | 79.017 | 0 | 23185.8472
2017-07-27 | 8:00 | 1.7491 | 5.8255 | 1 | 10 | 79.1392 | 0 | 23221.7042
2017-07-27 | 8:15 | 1.7007 | 5.554 | 1 | 10 | 79.4904 | 0 | 23324.7663
2017-07-27 | 8:30 | 1.6914 | 5.4908 | 1 | 10 | 80.8147 | 0 | 23713.3458
2017-07-27 | 8:45 | 1.7366 | 6.0637 | 1 | 10 | 81.0988 | 0 | 23796.7185
2017-07-27 | 9:00 | 1.7148 | 6.7878 | 1 | 10 | 81.5153 | 0 | 23918.9195
2017-07-27 | 9:15 | 1.7304 | 7.1411 | 1 | 10 | 82.2865 | 0 | 24145.221
2017-07-27 | 9:30 | 1.6844 | 7.7691 | 1 | 10 | 83.1322 | 0 | 24393.3521
2017-07-27 | 9:45 | 1.7702 | 7.0855 | 1 | 10 | 82.26 | 0 | 24137.4261
2017-07-27 | 10:00 | 1.8458 | 6.5705 | 1 | 10 | 82.5459 | 0 | 24221.3273
2017-07-27 | 10:15 | 1.6719 | 6.2795 | 1 | 10 | 81.9932 | 0 | 24059.1481
2017-07-27 | 10:30 | 1.76 | 6.9692 | 1 | 10 | 82.8449 | 0 | 24309.0636
2017-07-27 | 10:45 | 1.767 | 7.7171 | 1 | 10 | 82.4973 | 0 | 24207.0757
2017-07-27 | 11:00 | 1.7163 | 7.4235 | 1 | 10 | 82.9629 | 0 | 24343.6826
2017-07-27 | 11:15 | 1.746 | 8.1158 | 1 | 10 | 83.1375 | 0 | 24394.9258
2017-07-27 | 11:30 | 1.7226 | 7.4161 | 1 | 10 | 82.1508 | 0 | 24105.3837
2017-07-27 | 11:45 | 1.7257 | 7.3215 | 1 | 10 | 81.4211 | 0 | 23891.2762
2017-07-27 | 12:00 | 1.7756 | 6.3691 | 1 | 10 | 80.6903 | 0 | 23676.8439
2017-07-27 | 12:15 | 1.7436 | 6.7652 | 1 | 10 | 80.4686 | 0 | 23611.7723
2017-07-27 | 12:18 |  |  | 0 |  |  |  | 0
2017-07-27 | 12:24 |  |  | 1 |  |  |  | 0
2017-07-27 | 12:30 | 1.7257 | 4.1833 | 1 | 10 | 80.0734 | 0 | 23495.8128
2017-07-27 | 12:36 |  |  | 0 |  |  |  | 0
2017-07-27 | 12:45 | 1.7015 | 0 | 0 | 1.5 | 80.7369 | 0 | 23690.5065
2017-07-27 | 13:00 | 1.7717 | 0 | 0 | 1.5 | 81.0108 | 0 | 23770.873
2017-07-27 | 13:15 | 1.7413 | 0 | 0 | 1.5 | 81.4168 | 0 | 23890.0291
2017-07-27 | 13:30 | 1.6477 | 0 | 0 | 1.5 | 82.0427 | 0 | 24073.6796
2017-07-27 | 13:45 | 1.6797 | 0 | 0 | 1.5 | 83.1623 | 0 | 24402.206
2017-07-27 | 14:00 | 1.7491 | 0 | 0 | 1.5 | 83.8052 | 0 | 24590.8263
2017-07-27 | 14:15 | 1.746 | 0 | 0 | 1.5 | 84.1813 | 0 | 24701.2112
2017-07-27 | 14:30 | 1.7811 | 0 | 0 | 1.5 | 84.0628 | 0 | 24666.4244
2017-07-27 | 14:45 | 1.767 | 0 | 0 | 1.5 | 84.0074 | 0 | 24650.1781
2017-07-27 | 15:00 | 1.7335 | 0 | 0 | 1.5 | 84.5129 | 0 | 24798.491
2017-07-27 | 15:15 | 1.7639 | 0 | 0 | 1.5 | 84.7169 | 0 | 24858.3733
2017-07-27 | 15:30 | 1.7288 | 0 | 0 | 1.5 | 84.8287 | 0 | 24891.1769
2017-07-27 | 15:45 | 1.7639 | 0 | 0 | 1.5 | 85.1982 | 0 | 24999.5829
2017-07-27 | 16:00 | 1.7366 | 0 | 0 | 1.5 | 85.8858 | 0 | 25201.3464
2017-07-27 | 16:15 | 1.714 | 0 | 0 | 1.5 | 86.3805 | 0 | 25346.507
2017-07-27 | 16:30 | 1.7733 | 0 | 0 | 1.5 | 86.4676 | 0 | 25372.0773
2017-07-27 | 16:45 | 1.7335 | 0 | 0 | 1.5 | 86.5285 | 0 | 25389.933
2017-07-27 | 17:00 | 1.7936 | 0 | 0 | 1.5 | 86.02 | 0 | 25240.736
2017-07-27 | 17:15 | 1.767 | 0 | 0 | 1.5 | 85.3551 | 0 | 25045.6168
2017-07-27 | 17:30 | 1.8021 | 0 | 0 | 1.5 | 84.5335 | 0 | 24804.5421
2017-07-27 | 17:45 | 1.7772 | 0 | 0 | 1.5 | 83.2385 | 0 | 24424.5682
2017-07-27 | 18:00 | 1.7865 | 0 | 0 | 1.5 | 82.1827 | 0 | 24114.7616
2017-07-27 | 18:15 | 1.7694 | 0 | 0 | 1.5 | 81.4123 | 0 | 23888.6814
2017-07-27 | 18:30 | 1.7655 | 0 | 0 | 1.5 | 80.8009 | 0 | 23709.2803
2017-07-27 | 18:45 | 1.7819 | 0 | 0 | 1.5 | 80.0662 | 0 | 23493.7198
2017-07-27 | 19:00 | 1.778 | 0 | 0 | 1.5 | 79.2395 | 0 | 23251.1383
2017-07-27 | 19:15 | 1.7873 | 0 | 0 | 1.5 | 78.8659 | 0 | 23141.499
2017-07-27 | 19:30 | 1.7811 | 0 | 0 | 1.5 | 78.7043 | 0 | 23094.0947
2017-07-27 | 19:45 | 1.7858 | 0 | 0 | 1.5 | 77.9937 | 0 | 22885.577
2017-07-27 | 20:00 | 1.7702 | 0 | 0 | 1.5 | 77.6086 | 0 | 22772.573
2017-07-27 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 77.0011 | 0 | 22594.3201
2017-07-27 | 20:30 | 1.7748 | 0 | 0 | 1.5 | 76.7056 | 0 | 22507.6205
2017-07-27 | 20:45 | 1.7569 | 0 | 0 | 1.5 | 76.1919 | 0 | 22356.881
2017-07-27 | 21:00 | 1.7764 | 0 | 0 | 1.5 | 76.1362 | 0 | 22340.532
2017-07-27 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 21:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 22:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 23:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-27 | 23:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 0:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 0:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 0:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 0:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 0:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 0:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 1:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 1:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 1:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 1:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 1:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 1:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 1:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 2:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 2:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 2:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 2:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 2:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 2:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 3:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 3:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 3:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 3:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 3:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 3:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 4:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 4:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 4:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 4:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 4:45 | 0.03232 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 4:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 5:00 | 0.0331 | 0 | 1 | 0 | 25 | 0 | 7335.7143
2017-07-28 | 5:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 5:15 | 2.1984 | 9.2029 | 1 |  | 89.8581 | 93.6573 | 26366.9366
2017-07-28 | 5:15 |  |  |  | 10 |  |  | 0
2017-07-28 | 5:30 | 1.9145 | 7.7997 | 1 | 10 | 83.2925 | 80.0254 | 24440.4093
2017-07-28 | 5:30 |  |  |  | 10 |  |  | 0
2017-07-28 | 5:45 | 1.8684 | 6.8277 | 1 |  | 80.3817 | 70.5941 | 23586.3003
2017-07-28 | 5:45 |  |  |  | 10 |  |  | 0
2017-07-28 | 6:00 | 1.8482 | 6.0326 | 1 | 10 | 78.748 | 62.8801 | 23106.9111
2017-07-28 | 6:00 |  |  |  | 10 |  |  | 0
2017-07-28 | 6:15 | 1.7694 | 6.755 | 1 |  | 77.8767 | 0 | 22851.2515
2017-07-28 | 6:15 |  |  |  | 10 |  |  | 0
2017-07-28 | 6:30 | 1.7421 | 6.7624 | 1 | 10 | 77.502 | 0 | 22741.2918
2017-07-28 | 6:30 |  |  |  | 10 |  |  | 0
2017-07-28 | 6:45 | 1.7709 | 6.7079 | 1 |  | 77.2262 | 0 | 22660.3747
2017-07-28 | 6:45 |  |  |  | 10 |  |  | 0
2017-07-28 | 7:00 | 1.7811 | 6.0577 | 1 | 10 | 77.0122 | 0 | 22597.591
2017-07-28 | 7:00 |  |  |  | 10 |  |  | 0
2017-07-28 | 7:15 | 1.7764 | 5.9017 | 1 |  | 77.0695 | 0 | 22614.3921
2017-07-28 | 7:15 |  |  |  | 10 |  |  | 0
2017-07-28 | 7:30 | 1.7842 | 5.1412 | 1 | 10 | 75.9475 | 0 | 22285.1603
2017-07-28 | 7:30 |  |  |  | 10 |  |  | 0
2017-07-28 | 7:45 | 1.7881 | 4.3564 | 1 |  | 75.4945 | 0 | 22152.243
2017-07-28 | 7:45 |  |  |  | 10 |  |  | 0
2017-07-28 | 8:00 | 1.6875 | 3.269 | 1 | 10 | 76.1156 | 0 | 22334.483
2017-07-28 | 8:00 |  |  |  | 10 |  |  | 0
2017-07-28 | 8:15 | 1.6992 | 5.0748 | 1 |  | 76.867 | 0 | 22554.9775
2017-07-28 | 8:15 |  |  |  | 10 |  |  | 0
2017-07-28 | 8:30 | 1.6922 | 5.1327 | 1 | 10 | 77.5826 | 0 | 22764.9412
2017-07-28 | 8:30 |  |  |  | 10 |  |  | 0
2017-07-28 | 8:45 | 1.7413 | 5.8155 | 1 |  | 77.7492 | 0 | 22813.8408
2017-07-28 | 8:45 |  |  |  | 10 |  |  | 0
2017-07-28 | 9:00 | 1.6929 | 6.2911 | 1 | 10 | 78.1717 | 0 | 22937.8214
2017-07-28 | 9:00 |  |  |  | 10 |  |  | 0
2017-07-28 | 9:15 | 1.728 | 6.4934 | 1 |  | 78.642 | 0 | 23075.8159
2017-07-28 | 9:15 |  |  |  | 10 |  |  | 0
2017-07-28 | 9:30 | 1.7507 | 6.5801 | 1 | 10 | 79.3881 | 0 | 23294.73
2017-07-28 | 9:30 |  |  |  | 10 |  |  | 0
2017-07-28 | 9:45 | 1.7592 | 6.4352 | 1 |  | 80.0383 | 0 | 23485.5217
2017-07-28 | 9:45 |  |  |  | 10 |  |  | 0
2017-07-28 | 10:00 | 1.6984 | 6.2634 | 1 | 10 | 80.6014 | 0 | 23650.7542
2017-07-28 | 10:00 |  |  |  | 10 |  |  | 0
2017-07-28 | 10:15 | 1.7101 | 6.3845 | 1 |  | 81.4233 | 0 | 23891.9276
2017-07-28 | 10:15 |  |  |  | 10 |  |  | 0
2017-07-28 | 10:30 | 1.7561 | 7.1225 | 1 | 10 | 80.916 | 0 | 23743.0686
2017-07-28 | 10:30 |  |  |  | 10 |  |  | 0
2017-07-28 | 10:36 |  |  | 0 |  |  |  | 0
2017-07-28 | 10:40 |  |  | 1 |  |  |  | 0
2017-07-28 | 10:45 | 1.6586 | 4.0419 | 1 |  | 81.3083 | 0 | 23858.1906
2017-07-28 | 10:45 |  |  |  | 10 |  |  | 0
2017-07-28 | 10:50 |  |  | 0 |  |  |  | 0
2017-07-28 | 11:00 | 1.675 | 0 | 0 | 1.5 | 83.028 | 0 | 24362.7962
2017-07-28 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 11:15 | 1.8045 | 0 | 0 |  | 84.1779 | 0 | 24700.2106
2017-07-28 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 11:30 | 1.7179 | 0 | 0 | 1.5 | 85.212 | 0 | 25003.6392
2017-07-28 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 11:45 | 1.6992 | 0 | 0 |  | 86.0668 | 0 | 25254.4567
2017-07-28 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 12:00 | 1.7343 | 0 | 0 | 1.5 | 86.753 | 0 | 25455.7951
2017-07-28 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 12:15 | 1.8287 | 0 | 0 |  | 87.1429 | 0 | 25570.2117
2017-07-28 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 12:30 | 1.7507 | 0 | 0 | 1.5 | 87.4223 | 0 | 25652.2012
2017-07-28 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 12:45 | 1.6703 | 0 | 0 |  | 88.096 | 0 | 25849.879
2017-07-28 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 13:00 | 1.6633 | 0 | 0 | 1.5 | 89.0576 | 0 | 26132.0561
2017-07-28 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 13:15 | 1.7928 | 0 | 0 |  | 89.5151 | 0 | 26266.2853
2017-07-28 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 13:30 | 1.7093 | 0 | 0 | 1.5 | 90.1542 | 0 | 26453.8243
2017-07-28 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 13:45 | 1.7046 | 0 | 0 |  | 90.8248 | 0 | 26650.5819
2017-07-28 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 14:00 | 1.8279 | 0 | 0 | 1.5 | 88.398 | 0 | 25938.495
2017-07-28 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 14:15 | 1.7897 | 0 | 0 |  | 88.3735 | 0 | 25931.3066
2017-07-28 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 14:30 | 1.6789 | 0 | 0 | 1.5 | 89.3471 | 0 | 26216.9872
2017-07-28 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 14:45 | 1.8107 | 0 | 0 |  | 87.9433 | 0 | 25805.0742
2017-07-28 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 15:00 | 1.6797 | 0 | 0 | 1.5 | 87.8794 | 0 | 25786.3297
2017-07-28 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 15:15 | 1.7187 | 0 | 0 |  | 88.9272 | 0 | 26093.7924
2017-07-28 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 15:30 | 1.9121 | 0 | 0 | 1.5 | 86.9256 | 0 | 25506.4608
2017-07-28 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 15:45 | 1.7249 | 0 | 0 |  | 86.1424 | 0 | 25276.6443
2017-07-28 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 16:00 | 1.6344 | 0 | 0 | 1.5 | 87.8561 | 0 | 25779.4794
2017-07-28 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 16:15 | 1.8505 | 0 | 0 |  | 88.0753 | 0 | 25843.81
2017-07-28 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 16:30 | 1.7686 | 0 | 0 | 1.5 | 85.6016 | 0 | 25117.9622
2017-07-28 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 16:45 | 1.6711 | 0 | 0 |  | 86.8876 | 0 | 25495.2897
2017-07-28 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 17:00 | 1.9152 | 0 | 0 | 1.5 | 86.871 | 0 | 25490.432
2017-07-28 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 17:15 | 1.87 | 0 | 0 |  | 83.2135 | 0 | 24417.2076
2017-07-28 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 17:30 | 1.785 | 0 | 0 | 1.5 | 82.5089 | 0 | 24210.4631
2017-07-28 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 17:45 | 1.7085 | 0 | 0 |  | 82.7177 | 0 | 24271.7468
2017-07-28 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 18:00 | 1.7382 | 0 | 0 | 1.5 | 82.9351 | 0 | 24335.5358
2017-07-28 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 18:15 | 1.7663 | 0 | 0 |  | 82.6156 | 0 | 24241.7798
2017-07-28 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 18:30 | 1.7858 | 0 | 0 | 1.5 | 81.9325 | 0 | 24041.3238
2017-07-28 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 18:45 | 1.7413 | 0 | 0 |  | 81.6335 | 0 | 23953.5989
2017-07-28 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 19:00 | 1.7897 | 0 | 0 | 1.5 | 80.8428 | 0 | 23721.5729
2017-07-28 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 19:15 | 1.7865 | 0 | 0 |  | 80.4399 | 0 | 23603.3614
2017-07-28 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 19:30 | 1.8084 | 0 | 0 | 1.5 | 79.9205 | 0 | 23450.9476
2017-07-28 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 19:45 | 1.7733 | 0 | 0 |  | 79.135 | 0 | 23220.4841
2017-07-28 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 20:00 | 1.7951 | 0 | 0 | 1.5 | 78.509 | 0 | 23036.7978
2017-07-28 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 20:15 | 1.7413 | 0 | 0 |  | 78.0296 | 0 | 22896.1102
2017-07-28 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 20:30 | 1.7928 | 0 | 0 | 1.5 | 77.4132 | 0 | 22715.2514
2017-07-28 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 20:45 | 1.7475 | 0 | 0 |  | 77.0814 | 0 | 22617.8868
2017-07-28 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-07-28 | 21:00 | 1.7616 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 21:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 21:15 | 0.037 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 21:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 21:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 21:45 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 21:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 22:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 22:15 | 0.03232 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 22:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 22:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 22:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 22:45 |  |  |  | 0 |  |  | 0
2017-07-28 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 23:00 |  |  |  | 0 |  |  | 0
2017-07-28 | 23:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 23:15 |  |  |  | 0 |  |  | 0
2017-07-28 | 23:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 23:30 |  |  |  | 0 |  |  | 0
2017-07-28 | 23:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-07-28 | 23:45 |  |  |  | 0 |  |  | 0
2017-07-29 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 0:00 |  |  |  | 0 |  |  | 0
2017-07-29 | 0:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 0:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 0:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 1:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 1:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 1:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 2:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 2:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 2:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 2:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 3:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 3:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 5:00 |  |  | 1 |  |  |  | 0
2017-07-29 | 5:15 | 2.1586 | 10 | 1 | 10 | 91.643 | 100 | 26890.676
2017-07-29 | 5:30 | 1.9457 | 8.7887 | 1 | 10 | 84.5332 | 88.4459 | 24804.4661
2017-07-29 | 5:45 | 1.8146 | 8.0133 | 1 | 10 | 81.8999 | 80.8625 | 24031.778
2017-07-29 | 6:00 | 1.7663 | 7.4452 | 1 | 10 | 80.435 | 75.1553 | 23601.9151
2017-07-29 | 6:15 | 1.8209 | 7.4713 | 1 | 10 | 79.3994 | 75.6308 | 23298.0387
2017-07-29 | 6:30 | 1.817 | 6.8282 | 1 | 10 | 78.3955 | 69.472 | 23003.4775
2017-07-29 | 6:45 | 1.7522 | 6.5614 | 1 | 10 | 77.8733 | 66.6201 | 22850.2641
2017-07-29 | 7:00 | 1.7 | 6.5794 | 1 | 10 | 77.8663 | 66.6679 | 22848.1934
2017-07-29 | 7:15 | 1.7491 | 6.5705 | 1 | 10 | 77.9102 | 66.6599 | 22861.0928
2017-07-29 | 7:30 | 1.8684 | 6.4539 | 1 | 10 | 77.3074 | 65.8907 | 22684.2123
2017-07-29 | 7:45 | 1.7234 | 6.063 | 1 | 10 | 76.9735 | 61.7549 | 22586.2362
2017-07-29 | 8:00 | 1.6797 | 6.3337 | 1 | 10 | 76.832 | 0 | 22544.6931
2017-07-29 | 8:15 | 1.6828 | 7.0414 | 1 | 10 | 77.1412 | 0 | 22635.4447
2017-07-29 | 8:30 | 1.8326 | 7.2766 | 1 | 10 | 76.6229 | 0 | 22483.3443
2017-07-29 | 8:45 | 1.7234 | 7.2252 | 1 | 10 | 76.7447 | 0 | 22519.0915
2017-07-29 | 9:00 | 1.7382 | 7.0987 | 1 | 10 | 76.8084 | 0 | 22537.7688
2017-07-29 | 9:15 | 1.6789 | 7.5474 | 1 | 10 | 77.5141 | 0 | 22744.8581
2017-07-29 | 9:30 | 1.792 | 7.4378 | 1 | 10 | 77.6218 | 0 | 22776.4595
2017-07-29 | 9:45 | 1.8037 | 7.606 | 1 | 10 | 77.6833 | 0 | 22794.5121
2017-07-29 | 9:53 |  |  | 0 |  |  |  | 0
2017-07-29 | 10:00 | 1.7858 | 1.8491 | 0 | 1.5 | 77.8694 | 0 | 22849.1159
2017-07-29 | 10:15 | 1.7943 | 0 | 0 | 1.5 | 78.0045 | 0 | 22888.7472
2017-07-29 | 10:30 | 1.7686 | 0 | 0 | 1.5 | 77.5758 | 0 | 22762.9667
2017-07-29 | 10:45 | 1.7608 | 0 | 0 | 1.5 | 77.9421 | 0 | 22870.4394
2017-07-29 | 11:00 | 1.7686 | 0 | 0 | 1.5 | 77.6933 | 0 | 22797.4267
2017-07-29 | 11:15 | 1.7616 | 0 | 0 | 1.5 | 77.4982 | 0 | 22740.1882
2017-07-29 | 11:30 | 1.7499 | 0 | 0 | 1.5 | 77.3037 | 0 | 22683.104
2017-07-29 | 11:45 | 1.7577 | 0 | 0 | 1.5 | 77.1908 | 0 | 22649.9961
2017-07-29 | 12:00 | 1.7382 | 0 | 0 | 1.5 | 77.1528 | 0 | 22638.8409
2017-07-29 | 12:15 | 1.7553 | 0 | 0 | 1.5 | 77.0219 | 0 | 22600.4117
2017-07-29 | 12:30 | 1.7452 | 0 | 0 | 1.5 | 76.8911 | 0 | 22562.0562
2017-07-29 | 12:45 | 1.7624 | 0 | 0 | 1.5 | 76.8205 | 0 | 22541.3193
2017-07-29 | 13:00 | 1.7491 | 0 | 0 | 1.5 | 76.8272 | 0 | 22543.2961
2017-07-29 | 13:15 | 1.7522 | 0 | 0 | 1.5 | 76.8499 | 0 | 22549.9493
2017-07-29 | 13:30 | 1.7647 | 0 | 0 | 1.5 | 76.8978 | 0 | 22564.0107
2017-07-29 | 13:45 | 1.7405 | 0 | 0 | 1.5 | 77.058 | 0 | 22611.0297
2017-07-29 | 14:00 | 1.7296 | 0 | 0 | 1.5 | 77.2291 | 0 | 22661.2119
2017-07-29 | 14:15 | 1.7366 | 0 | 0 | 1.5 | 77.3583 | 0 | 22699.1419
2017-07-29 | 14:30 | 1.7288 | 0 | 0 | 1.5 | 77.5225 | 0 | 22747.3117
2017-07-29 | 14:45 | 1.753 | 0 | 0 | 1.5 | 77.6944 | 0 | 22797.7468
2017-07-29 | 15:00 | 1.739 | 0 | 0 | 1.5 | 77.8067 | 0 | 22830.7182
2017-07-29 | 15:15 | 1.7468 | 0 | 0 | 1.5 | 77.877 | 0 | 22851.3275
2017-07-29 | 15:30 | 1.7436 | 0 | 0 | 1.5 | 77.9283 | 0 | 22866.3871
2017-07-29 | 15:45 | 1.7468 | 0 | 0 | 1.5 | 78.0217 | 0 | 22893.7842
2017-07-29 | 16:00 | 1.7702 | 0 | 0 | 1.5 | 78.0637 | 0 | 22906.1126
2017-07-29 | 16:15 | 1.7546 | 0 | 0 | 1.5 | 78.1178 | 0 | 22921.9871
2017-07-29 | 16:30 | 1.7475 | 0 | 0 | 1.5 | 78.1509 | 0 | 22931.721
2017-07-29 | 16:45 | 1.7585 | 0 | 0 | 1.5 | 78.2453 | 0 | 22959.3999
2017-07-29 | 17:00 | 1.7538 | 0 | 0 | 1.5 | 78.1205 | 0 | 22922.7729
2017-07-29 | 17:15 | 1.7585 | 0 | 0 | 1.5 | 78.0048 | 0 | 22888.8232
2017-07-29 | 17:30 | 1.746 | 0 | 0 | 1.5 | 77.8017 | 0 | 22829.2341
2017-07-29 | 17:45 | 1.7577 | 0 | 0 | 1.5 | 77.6291 | 0 | 22778.5883
2017-07-29 | 18:00 | 1.7702 | 0 | 0 | 1.5 | 77.4986 | 0 | 22740.2912
2017-07-29 | 18:15 | 1.7475 | 0 | 0 | 1.5 | 77.3754 | 0 | 22704.1499
2017-07-29 | 18:30 | 1.7358 | 0 | 0 | 1.5 | 77.1716 | 0 | 22644.3523
2017-07-29 | 18:45 | 1.7343 | 0 | 0 | 1.5 | 77.0883 | 0 | 22619.8992
2017-07-29 | 19:00 | 1.7421 | 0 | 0 | 1.5 | 76.9896 | 0 | 22590.9419
2017-07-29 | 19:15 | 1.7468 | 0 | 0 | 1.5 | 76.9725 | 0 | 22585.9251
2017-07-29 | 19:30 | 1.7616 | 0 | 0 | 1.5 | 76.9449 | 0 | 22577.8256
2017-07-29 | 19:45 | 1.753 | 0 | 0 | 1.5 | 76.8167 | 0 | 22540.2245
2017-07-29 | 20:00 | 1.7624 | 0 | 0 | 1.5 | 76.5818 | 0 | 22471.2979
2017-07-29 | 20:15 | 1.7928 | 0 | 0 | 1.5 | 76.2272 | 0 | 22367.2393
2017-07-29 | 20:30 | 1.7686 | 0 | 0 | 1.5 | 75.9482 | 0 | 22285.3774
2017-07-29 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 75.6587 | 0 | 22200.4331
2017-07-29 | 21:00 | 1.6875 | 0 | 0 | 1.5 | 75.7417 | 0 | 22224.7674
2017-07-29 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 21:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 21:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 22:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 22:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 22:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 22:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 23:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 23:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 23:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 23:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 0:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 0:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 0:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 1:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 1:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 1:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 2:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 2:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 5:01 |  |  | 1 |  |  |  | 0
2017-07-30 | 5:15 | 2.2382 | 9.999 | 1 | 10 | 90.1858 | 100 | 26463.0969
2017-07-30 | 5:30 | 1.8747 | 8.5956 | 1 | 10 | 83.4811 | 86.6072 | 24495.754
2017-07-30 | 5:45 | 1.8365 | 8.0511 | 1 | 10 | 81.4591 | 81.2297 | 23902.4382
2017-07-30 | 6:00 | 1.778 | 7.3428 | 1 | 10 | 80.4926 | 74.3615 | 23618.8351
2017-07-30 | 6:15 | 1.8224 | 7.0022 | 1 | 10 | 79.0825 | 71.159 | 23205.055
2017-07-30 | 6:30 | 1.728 | 6.9031 | 1 | 10 | 79.0101 | 70.0312 | 23183.8278
2017-07-30 | 6:45 | 1.7288 | 6.5458 | 1 | 10 | 78.1973 | 66.5082 | 22945.3165
2017-07-30 | 7:00 | 1.7335 | 6.0836 | 1 | 10 | 77.5503 | 62.0072 | 22755.4828
2017-07-30 | 7:15 | 1.7655 | 6.3988 | 1 | 10 | 77.1017 | 0 | 22623.8505
2017-07-30 | 7:30 | 1.7374 | 6.3897 | 1 | 10 | 76.5319 | 0 | 22456.6455
2017-07-30 | 7:45 | 1.739 | 6.8909 | 1 | 10 | 76.5915 | 0 | 22474.1388
2017-07-30 | 8:00 | 1.6828 | 6.7623 | 1 | 10 | 76.892 | 0 | 22562.3159
2017-07-30 | 8:15 | 1.8092 | 7.0482 | 1 | 10 | 76.8169 | 0 | 22540.2603
2017-07-30 | 8:30 | 1.7483 | 7.1135 | 1 | 10 | 76.6665 | 0 | 22496.1495
2017-07-30 | 8:38 |  |  | 0 |  |  |  | 0
2017-07-30 | 8:45 | 1.6539 | 3.3958 | 0 | 1.5 | 77.2509 | 0 | 22667.6192
2017-07-30 | 9:00 | 1.7101 | 0 | 0 | 1.5 | 77.7827 | 0 | 22823.6709
2017-07-30 | 9:15 | 1.7975 | 0 | 0 | 1.5 | 77.7495 | 0 | 22813.9147
2017-07-30 | 9:30 | 1.7358 | 0 | 0 | 1.5 | 77.8094 | 0 | 22831.5064
2017-07-30 | 9:45 | 1.7109 | 0 | 0 | 1.5 | 78.0489 | 0 | 22901.774
2017-07-30 | 10:00 | 1.739 | 0 | 0 | 1.5 | 78.2279 | 0 | 22954.3071
2017-07-30 | 10:15 | 1.792 | 0 | 0 | 1.5 | 78.1833 | 0 | 22941.2196
2017-07-30 | 10:30 | 1.7546 | 0 | 0 | 1.5 | 78.2076 | 0 | 22948.332
2017-07-30 | 10:45 | 1.7046 | 0 | 0 | 1.5 | 78.5097 | 0 | 23036.9791
2017-07-30 | 11:00 | 1.7163 | 0 | 0 | 1.5 | 78.7685 | 0 | 23112.9422
2017-07-30 | 11:15 | 1.7889 | 0 | 0 | 1.5 | 78.853 | 0 | 23137.7334
2017-07-30 | 11:30 | 1.7616 | 0 | 0 | 1.5 | 78.8496 | 0 | 23136.7328
2017-07-30 | 11:45 | 1.714 | 0 | 0 | 1.5 | 79.0834 | 0 | 23205.3394
2017-07-30 | 12:00 | 1.7039 | 0 | 0 | 1.5 | 79.3006 | 0 | 23269.05
2017-07-30 | 12:15 | 1.7826 | 0 | 0 | 1.5 | 79.1439 | 0 | 23223.0833
2017-07-30 | 12:30 | 1.7772 | 0 | 0 | 1.5 | 78.9436 | 0 | 23164.3043
2017-07-30 | 12:45 | 1.7109 | 0 | 0 | 1.5 | 78.9896 | 0 | 23177.8037
2017-07-30 | 13:00 | 1.7156 | 0 | 0 | 1.5 | 79.0842 | 0 | 23205.5565
2017-07-30 | 13:15 | 1.7858 | 0 | 0 | 1.5 | 79.0613 | 0 | 23198.854
2017-07-30 | 13:30 | 1.7764 | 0 | 0 | 1.5 | 78.9999 | 0 | 23180.8146
2017-07-30 | 13:45 | 1.7257 | 0 | 0 | 1.5 | 79.2477 | 0 | 23253.5426
2017-07-30 | 14:00 | 1.6976 | 0 | 0 | 1.5 | 79.6194 | 0 | 23362.6001
2017-07-30 | 14:15 | 1.76 | 0 | 0 | 1.5 | 79.9063 | 0 | 23446.8038
2017-07-30 | 14:30 | 1.799 | 0 | 0 | 1.5 | 79.9975 | 0 | 23473.556
2017-07-30 | 14:45 | 1.7265 | 0 | 0 | 1.5 | 80.1955 | 0 | 23531.6563
2017-07-30 | 15:00 | 1.7054 | 0 | 0 | 1.5 | 80.5087 | 0 | 23623.5408
2017-07-30 | 15:15 | 1.7631 | 0 | 0 | 1.5 | 80.1787 | 0 | 23526.7246
2017-07-30 | 15:30 | 1.7842 | 0 | 0 | 1.5 | 79.7928 | 0 | 23413.4832
2017-07-30 | 15:45 | 1.7397 | 0 | 0 | 1.5 | 79.9261 | 0 | 23452.6151
2017-07-30 | 16:00 | 1.6984 | 0 | 0 | 1.5 | 80.3578 | 0 | 23579.2888
2017-07-30 | 16:15 | 1.8248 | 0 | 0 | 1.5 | 80.0913 | 0 | 23501.0625
2017-07-30 | 16:30 | 1.8006 | 0 | 0 | 1.5 | 79.3474 | 0 | 23282.8022
2017-07-30 | 16:45 | 1.7795 | 0 | 0 | 1.5 | 79.3327 | 0 | 23278.4861
2017-07-30 | 17:00 | 1.7062 | 0 | 0 | 1.5 | 79.7455 | 0 | 23399.6032
2017-07-30 | 17:15 | 1.7156 | 0 | 0 | 1.5 | 80.0054 | 0 | 23475.8617
2017-07-30 | 17:30 | 1.7865 | 0 | 0 | 1.5 | 79.8164 | 0 | 23420.4028
2017-07-30 | 17:45 | 1.7624 | 0 | 0 | 1.5 | 79.6758 | 0 | 23379.1529
2017-07-30 | 18:00 | 1.7218 | 0 | 0 | 1.5 | 79.7926 | 0 | 23413.436
2017-07-30 | 18:15 | 1.6992 | 0 | 0 | 1.5 | 79.9604 | 0 | 23462.6648
2017-07-30 | 18:30 | 1.7897 | 0 | 0 | 1.5 | 79.8362 | 0 | 23426.228
2017-07-30 | 18:45 | 1.7772 | 0 | 0 | 1.5 | 79.7405 | 0 | 23398.1392
2017-07-30 | 19:00 | 1.7117 | 0 | 0 | 1.5 | 79.9383 | 0 | 23456.1747
2017-07-30 | 19:15 | 1.7171 | 0 | 0 | 1.5 | 80.0882 | 0 | 23500.1605
2017-07-30 | 19:30 | 1.8006 | 0 | 0 | 1.5 | 80.009 | 0 | 23476.9295
2017-07-30 | 19:45 | 1.7951 | 0 | 0 | 1.5 | 79.672 | 0 | 23378.0335
2017-07-30 | 20:00 | 1.7569 | 0 | 0 | 1.5 | 79.3832 | 0 | 23293.306
2017-07-30 | 20:15 | 1.7413 | 0 | 0 | 1.5 | 79.2103 | 0 | 23242.5775
2017-07-30 | 20:30 | 1.7819 | 0 | 0 | 1.5 | 78.8398 | 0 | 23133.8604
2017-07-30 | 20:45 | 1.8177 | 0 | 0 | 1.5 | 78.264 | 0 | 22964.8961
2017-07-30 | 21:00 | 1.7514 | 0 | 0 | 1.5 | 77.8856 | 0 | 22853.8595
2017-07-30 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-30 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 1:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 1:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 1:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 2:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 2:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 5:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 5:00 |  |  | 1 |  |  |  | 0
2017-07-31 | 5:15 | 2.2499 | 10 | 1 | 10 | 90.9926 | 100 | 26699.8283
2017-07-31 | 5:30 | 1.9574 | 9.1851 | 1 | 10 | 84.1717 | 92.3598 | 24698.3928
2017-07-31 | 5:45 | 1.8154 | 8.0567 | 1 | 10 | 81.5238 | 81.3036 | 23921.3975
2017-07-31 | 6:00 | 1.8287 | 6.8114 | 1 | 10 | 79.3409 | 69.3888 | 23280.8837
2017-07-31 | 6:15 | 1.7717 | 6.6309 | 1 | 10 | 78.032 | 67.6706 | 22896.8265
2017-07-31 | 6:30 | 1.7842 | 6.2116 | 1 | 10 | 77.3454 | 63.5158 | 22695.3429
2017-07-31 | 6:45 | 1.8326 | 6.2747 | 1 | 10 | 76.6681 | 0 | 22496.6105
2017-07-31 | 7:00 | 1.8435 | 5.9838 | 1 | 10 | 76.2942 | 0 | 22386.9063
2017-07-31 | 7:15 | 1.7787 | 5.8631 | 1 | 10 | 76.2266 | 0 | 22367.0738
2017-07-31 | 7:30 | 1.714 | 4.7433 | 1 | 10 | 76.1826 | 0 | 22354.1409
2017-07-31 | 7:45 | 1.7304 | 5.6068 | 1 | 10 | 76.2555 | 0 | 22375.5383
2017-07-31 | 8:00 | 1.7093 | 5.1955 | 1 | 10 | 77.1002 | 0 | 22623.3983
2017-07-31 | 8:15 | 1.7039 | 6.2345 | 1 | 10 | 77.7407 | 0 | 22811.3402
2017-07-31 | 8:30 | 1.6719 | 7.4212 | 1 | 10 | 78.4223 | 0 | 23011.3531
2017-07-31 | 8:45 | 1.6953 | 7.9124 | 1 | 10 | 79.1684 | 0 | 23230.2784
2017-07-31 | 8:49 |  |  | 0 |  |  |  | 0
2017-07-31 | 9:00 | 1.7663 | 2.9989 | 0 | 1.5 | 79.6109 | 0 | 23360.1018
2017-07-31 | 9:15 | 1.7522 | 0 | 0 | 1.5 | 80.0253 | 0 | 23481.7227
2017-07-31 | 9:30 | 1.7117 | 0 | 0 | 1.5 | 80.7518 | 0 | 23694.8968
2017-07-31 | 9:45 | 1.6922 | 0 | 0 | 1.5 | 81.3734 | 0 | 23877.282
2017-07-31 | 10:00 | 1.7709 | 0 | 0 | 1.5 | 81.7481 | 0 | 23987.2194
2017-07-31 | 10:15 | 1.7577 | 0 | 0 | 1.5 | 82.1371 | 0 | 24101.3763
2017-07-31 | 10:30 | 1.7015 | 0 | 0 | 1.5 | 82.68 | 0 | 24260.6655
2017-07-31 | 10:45 | 1.7475 | 0 | 0 | 1.5 | 82.8156 | 0 | 24300.4491
2017-07-31 | 11:00 | 1.7171 | 0 | 0 | 1.5 | 82.8335 | 0 | 24305.7032
2017-07-31 | 11:15 | 1.7483 | 0 | 0 | 1.5 | 83.2556 | 0 | 24429.5627
2017-07-31 | 11:30 | 1.7639 | 0 | 0 | 1.5 | 84.115 | 0 | 24681.7393
2017-07-31 | 11:45 | 1.6953 | 0 | 0 | 1.5 | 85.3519 | 0 | 25044.6834
2017-07-31 | 12:00 | 1.721 | 0 | 0 | 1.5 | 86.4448 | 0 | 25365.3701
2017-07-31 | 12:15 | 1.7444 | 0 | 0 | 1.5 | 86.8681 | 0 | 25489.5746
2017-07-31 | 12:30 | 1.8263 | 0 | 0 | 1.5 | 83.7492 | 0 | 24574.4078
2017-07-31 | 12:45 | 1.7124 | 0 | 0 | 1.5 | 82.8196 | 0 | 24301.6422
2017-07-31 | 13:00 | 1.6937 | 0 | 0 | 1.5 | 83.5721 | 0 | 24522.4525
2017-07-31 | 13:15 | 1.728 | 0 | 0 | 1.5 | 85.5409 | 0 | 25100.1488
2017-07-31 | 13:30 | 1.7959 | 0 | 0 | 1.5 | 83.4867 | 0 | 24497.3949
2017-07-31 | 13:45 | 1.6734 | 0 | 0 | 1.5 | 84.1459 | 0 | 24690.8192
2017-07-31 | 14:00 | 1.689 | 0 | 0 | 1.5 | 85.8376 | 0 | 25187.2158
2017-07-31 | 14:15 | 1.8996 | 0 | 0 | 1.5 | 84.0144 | 0 | 24652.2221
2017-07-31 | 14:30 | 1.7015 | 0 | 0 | 1.5 | 83.9321 | 0 | 24628.078
2017-07-31 | 14:45 | 1.6649 | 0 | 0 | 1.5 | 85.515 | 0 | 25092.5352
2017-07-31 | 15:00 | 1.8669 | 0 | 0 | 1.5 | 84.194 | 0 | 24704.9116
2017-07-31 | 15:15 | 1.6828 | 0 | 0 | 1.5 | 84.7077 | 0 | 24855.6512
2017-07-31 | 15:30 | 1.7928 | 0 | 0 | 1.5 | 85.7553 | 0 | 25163.0558
2017-07-31 | 15:45 | 1.8045 | 0 | 0 | 1.5 | 83.8503 | 0 | 24604.0591
2017-07-31 | 16:00 | 1.668 | 0 | 0 | 1.5 | 85.0606 | 0 | 24959.2238
2017-07-31 | 16:15 | 1.8216 | 0 | 0 | 1.5 | 84.9034 | 0 | 24913.0845
2017-07-31 | 16:30 | 1.7382 | 0 | 0 | 1.5 | 83.3716 | 0 | 24463.611
2017-07-31 | 16:45 | 1.6454 | 0 | 0 | 1.5 | 84.7769 | 0 | 24875.9696
2017-07-31 | 17:00 | 1.8318 | 0 | 0 | 1.5 | 83.7224 | 0 | 24566.5501
2017-07-31 | 17:15 | 1.746 | 0 | 0 | 1.5 | 83.3487 | 0 | 24456.8903
2017-07-31 | 17:30 | 1.8053 | 0 | 0 | 1.5 | 83.8038 | 0 | 24590.4434
2017-07-31 | 17:45 | 1.8427 | 0 | 0 | 1.5 | 81.2584 | 0 | 23843.5295
2017-07-31 | 18:00 | 1.7382 | 0 | 0 | 1.5 | 80.9424 | 0 | 23750.8011
2017-07-31 | 18:15 | 1.7101 | 0 | 0 | 1.5 | 81.6092 | 0 | 23946.4686
2017-07-31 | 18:30 | 1.7249 | 0 | 0 | 1.5 | 81.7596 | 0 | 23990.5909
2017-07-31 | 18:45 | 1.7483 | 0 | 0 | 1.5 | 81.7243 | 0 | 23980.2346
2017-07-31 | 19:00 | 1.7702 | 0 | 0 | 1.5 | 81.918 | 0 | 24037.0861
2017-07-31 | 19:15 | 1.753 | 0 | 0 | 1.5 | 82.0623 | 0 | 24079.4105
2017-07-31 | 19:30 | 1.7717 | 0 | 0 | 1.5 | 81.4615 | 0 | 23903.1345
2017-07-31 | 19:45 | 1.7717 | 0.021182 | 0 | 1.5 | 81.1539 | 0 | 23812.8753
2017-07-31 | 20:00 | 1.778 | 0 | 0 | 1.5 | 80.3573 | 0 | 23579.1186
2017-07-31 | 20:15 | 1.7936 | 0 | 0 | 1.5 | 79.8227 | 0 | 23422.2723
2017-07-31 | 20:30 | 1.7897 | 0 | 0 | 1.5 | 79.0571 | 0 | 23197.6113
2017-07-31 | 20:45 | 1.7881 | 0 | 0 | 1.5 | 78.5454 | 0 | 23047.4654
2017-07-31 | 21:00 | 1.8006 | 0 | 0 | 1.5 | 77.6715 | 0 | 22791.0487
2017-07-31 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 21:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 21:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 1:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 2:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 4:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 4:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 4:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 5:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 5:01 |  |  | 1 |  |  |  | 0
2017-08-01 | 5:15 | 2.0837 | 10 | 1 | 10 | 94.9742 | 100 | 27868.152
2017-08-01 | 5:30 | 2.0034 | 9.5913 | 1 | 10 | 87.2199 | 96.2925 | 25592.8045
2017-08-01 | 5:45 | 1.8505 | 8.6043 | 1 | 10 | 83.3584 | 87.0376 | 24459.7245
2017-08-01 | 6:00 | 1.7943 | 7.8694 | 1 | 10 | 81.3534 | 79.5614 | 23871.4166
2017-08-01 | 6:15 | 1.7327 | 7.946 | 1 | 10 | 80.4035 | 79.9532 | 23592.6965
2017-08-01 | 6:30 | 1.7405 | 7.6084 | 1 | 10 | 80.2973 | 77.4047 | 23561.5294
2017-08-01 | 6:45 | 1.7982 | 7.2758 | 1 | 10 | 79.9321 | 73.6577 | 23454.3569
2017-08-01 | 6:49 |  |  | 0 |  |  |  | 0
2017-08-01 | 6:53 |  |  | 1 |  |  |  | 0
2017-08-01 | 7:00 | 1.7936 | 3.9654 | 1 | 10 | 78.5165 | 0 | 23038.9897
2017-08-01 | 7:15 | 1.767 | 6.7673 | 1 | 10 | 78.1979 | 0 | 22945.5066
2017-08-01 | 7:30 | 1.7709 | 6.2682 | 1 | 10 | 77.7881 | 0 | 22825.2469
2017-08-01 | 7:45 | 1.7483 | 5.7867 | 1 | 10 | 77.6824 | 0 | 22794.2254
2017-08-01 | 7:56 |  |  | 0 |  |  |  | 0
2017-08-01 | 8:00 | 1.7553 | 1.8687 | 0 | 1.5 | 77.4962 | 0 | 22739.5949
2017-08-01 | 8:15 | 1.7858 | 0 | 0 | 1.5 | 78.1339 | 0 | 22926.7175
2017-08-01 | 8:30 | 1.7218 | 0 | 0 | 1.5 | 78.5376 | 0 | 23045.1796
2017-08-01 | 8:45 | 1.7327 | 0 | 0 | 1.5 | 79.6757 | 0 | 23379.1371
2017-08-01 | 9:00 | 1.6937 | 0 | 0 | 1.5 | 80.9582 | 0 | 23755.4619
2017-08-01 | 9:15 | 1.6836 | 0 | 0 | 1.5 | 82.1975 | 0 | 24119.1023
2017-08-01 | 9:30 | 1.7873 | 0 | 0 | 1.5 | 82.894 | 0 | 24323.4715
2017-08-01 | 9:45 | 1.7195 | 0 | 0 | 1.5 | 83.6128 | 0 | 24534.398
2017-08-01 | 10:00 | 1.6781 | 0 | 0 | 1.5 | 84.7794 | 0 | 24876.7038
2017-08-01 | 10:15 | 1.6992 | 0 | 0 | 1.5 | 86.1483 | 0 | 25278.3682
2017-08-01 | 10:30 | 1.7694 | 0 | 0 | 1.5 | 86.3632 | 0 | 25341.4363
2017-08-01 | 10:45 | 1.7483 | 0 | 0 | 1.5 | 87.0695 | 0 | 25548.6822
2017-08-01 | 11:00 | 1.6719 | 0 | 0 | 1.5 | 88.1569 | 0 | 25867.7462
2017-08-01 | 11:15 | 1.8879 | 0 | 0 | 1.5 | 86.9872 | 0 | 25524.5316
2017-08-01 | 11:30 | 1.6758 | 0 | 0 | 1.5 | 86.028 | 0 | 25243.0755
2017-08-01 | 11:45 | 1.6337 | 0 | 0 | 1.5 | 87.7137 | 0 | 25737.7101
2017-08-01 | 12:00 | 1.8552 | 0 | 0 | 1.5 | 87.1096 | 0 | 25560.4511
2017-08-01 | 12:15 | 1.6883 | 0 | 0 | 1.5 | 86.313 | 0 | 25326.6924
2017-08-01 | 12:30 | 1.7748 | 0 | 0 | 1.5 | 87.0546 | 0 | 25544.3081
2017-08-01 | 12:45 | 1.8084 | 0 | 0 | 1.5 | 84.4564 | 0 | 24781.9091
2017-08-01 | 13:00 | 1.7007 | 0 | 0 | 1.5 | 85.5128 | 0 | 25091.8949
2017-08-01 | 13:15 | 1.831 | 0 | 0 | 1.5 | 86.0231 | 0 | 25241.6336
2017-08-01 | 13:30 | 1.7187 | 0 | 0 | 1.5 | 85.0079 | 0 | 24943.7434
2017-08-01 | 13:45 | 1.7007 | 0 | 0 | 1.5 | 86.834 | 0 | 25479.5898
2017-08-01 | 14:00 | 1.8755 | 0 | 0 | 1.5 | 85.5177 | 0 | 25093.3277
2017-08-01 | 14:15 | 1.6594 | 0 | 0 | 1.5 | 85.0899 | 0 | 24967.8137
2017-08-01 | 14:30 | 1.7943 | 0 | 0 | 1.5 | 86.8768 | 0 | 25492.1377
2017-08-01 | 14:45 | 1.7826 | 0 | 0 | 1.5 | 85.4098 | 0 | 25061.6771
2017-08-01 | 15:00 | 1.643 | 0 | 0 | 1.5 | 85.5051 | 0 | 25089.6317
2017-08-01 | 15:15 | 1.707 | 0 | 0 | 1.5 | 88.6295 | 0 | 26006.4191
2017-08-01 | 15:30 | 1.8801 | 0 | 0 | 1.5 | 86.6071 | 0 | 25413.0114
2017-08-01 | 15:45 | 1.8045 | 0 | 0 | 1.5 | 84.592 | 0 | 24821.7015
2017-08-01 | 16:00 | 1.6547 | 0 | 0 | 1.5 | 84.4046 | 0 | 24766.7218
2017-08-01 | 16:15 | 1.7241 | 0 | 0 | 1.5 | 87.0772 | 0 | 25550.9478
2017-08-01 | 16:30 | 1.8778 | 0 | 0 | 1.5 | 85.1266 | 0 | 24978.5705
2017-08-01 | 16:45 | 1.7436 | 0 | 0 | 1.5 | 83.4585 | 0 | 24489.1184
2017-08-01 | 17:00 | 1.6578 | 0 | 0 | 1.5 | 85.489 | 0 | 25084.9014
2017-08-01 | 17:15 | 1.8794 | 0 | 0 | 1.5 | 84.5398 | 0 | 24806.3913
2017-08-01 | 17:30 | 1.7156 | 0 | 0 | 1.5 | 82.8883 | 0 | 24321.7905
2017-08-01 | 17:45 | 1.7444 | 0 | 0 | 1.5 | 84.2653 | 0 | 24725.8501
2017-08-01 | 18:00 | 1.8131 | 0 | 0 | 1.5 | 82.3227 | 0 | 24155.8258
2017-08-01 | 18:15 | 1.6719 | 0 | 0 | 1.5 | 82.9662 | 0 | 24344.6676
2017-08-01 | 18:30 | 1.8755 | 0 | 0 | 1.5 | 82.3543 | 0 | 24165.1184
2017-08-01 | 18:45 | 1.7163 | 0 | 0 | 1.5 | 81.5675 | 0 | 23934.2409
2017-08-01 | 19:00 | 1.7702 | 0 | 0 | 1.5 | 82.413 | 0 | 24182.3385
2017-08-01 | 19:15 | 1.8294 | 0 | 0 | 1.5 | 80.6811 | 0 | 23674.1329
2017-08-01 | 19:30 | 1.7085 | 0 | 0 | 1.5 | 80.7439 | 0 | 23692.5752
2017-08-01 | 19:45 | 1.7062 | 0 | 0 | 1.5 | 81.1016 | 0 | 23797.5158
2017-08-01 | 20:00 | 1.7507 | 0 | 0 | 1.5 | 81.541 | 0 | 23926.4682
2017-08-01 | 20:15 | 1.7639 | 0 | 0 | 1.5 | 81.9975 | 0 | 24060.4087
2017-08-01 | 20:30 | 1.7553 | 0 | 0 | 1.5 | 81.5346 | 0 | 23924.5809
2017-08-01 | 20:45 | 1.8045 | 0 | 0 | 1.5 | 80.9957 | 0 | 23766.4449
2017-08-01 | 21:00 | 1.7858 | 0 | 0 | 1.5 | 80.0786 | 0 | 23497.3463
2017-08-01 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-01 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-02 | 0:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-02 | 0:15 | 0.0292 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 0:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 0:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 0:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 0:45 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 0:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 1:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 1:00 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 1:15 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 1:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 1:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 1:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 1:45 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 1:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 2:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 2:00 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 2:15 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 2:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 2:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 2:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 2:45 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 2:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 3:00 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 3:00 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 3:15 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 3:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 3:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 3:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 3:45 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 3:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 4:00 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 4:00 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 4:15 | 0.02842 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 4:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 4:30 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 4:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 4:45 | 0.0292 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 4:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 5:00 | 0.02842 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 5:00 |  |  |  | 1.5 | 25 |  | 7335.7143
2017-08-02 | 5:01 |  |  | 1 |  |  |  | 0
2017-08-02 | 5:15 | 1.8918 | 10 | 1 |  |  | 100 | 0
2017-08-02 | 5:15 |  |  |  | 10 | 97.6529 |  | 28654.1533
2017-08-02 | 5:30 | 2.0205 | 10 | 1 | 10 |  | 100 | 0
2017-08-02 | 5:30 |  |  |  | 10 | 92.5738 |  | 27163.7908
2017-08-02 | 5:45 | 1.8801 | 10 | 1 |  |  | 100 | 0
2017-08-02 | 5:45 |  |  |  | 10 | 88.1222 |  | 25857.5736
2017-08-02 | 6:00 | 1.8833 | 9.2436 | 1 | 10 |  | 92.913 | 0
2017-08-02 | 6:00 |  |  |  | 10 | 84.8494 |  | 24897.2303
2017-08-02 | 6:15 | 1.8614 | 8.2034 | 1 |  |  | 82.8439 | 0
2017-08-02 | 6:15 |  |  |  | 10 | 82.3232 |  | 24155.9892
2017-08-02 | 6:30 | 1.8209 | 7.0991 | 1 | 10 |  | 71.8695 | 0
2017-08-02 | 6:30 |  |  |  | 10 | 80.5415 |  | 23633.1694
2017-08-02 | 6:36 |  |  | 0 |  |  |  | 0
2017-08-02 | 6:45 | 1.7764 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 6:45 |  |  |  | 1.5 | 79.8884 |  | 23441.5517
2017-08-02 | 7:00 | 1.7819 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 7:00 |  |  |  | 1.5 | 79.1301 |  | 23219.029
2017-08-02 | 7:15 | 1.7725 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 7:15 |  |  |  | 1.5 | 78.5989 |  | 23063.1562
2017-08-02 | 7:30 | 1.7429 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 7:30 |  |  |  | 1.5 | 78.2434 |  | 22958.8494
2017-08-02 | 7:45 | 1.7475 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 7:45 |  |  |  | 1.5 | 78.1484 |  | 22930.9798
2017-08-02 | 8:00 | 1.7093 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 8:00 |  |  |  | 1.5 | 78.6611 |  | 23081.4195
2017-08-02 | 8:15 | 1.7148 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 8:15 |  |  |  | 1.5 | 79.5113 |  | 23330.8869
2017-08-02 | 8:30 | 1.6945 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 8:30 |  |  |  | 1.5 | 80.2755 |  | 23555.1179
2017-08-02 | 8:45 | 1.7187 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 8:45 |  |  |  | 1.5 | 81.1634 |  | 23815.6646
2017-08-02 | 9:00 | 1.7132 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 9:00 |  |  |  | 1.5 | 81.9137 |  | 24035.81
2017-08-02 | 9:15 | 1.7273 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 9:15 |  |  |  | 1.5 | 83.0122 |  | 24358.1445
2017-08-02 | 9:30 | 1.7015 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 9:30 |  |  |  | 1.5 | 84.0276 |  | 24656.1019
2017-08-02 | 9:45 | 1.6415 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 9:45 |  |  |  | 1.5 | 85.2399 |  | 25011.835
2017-08-02 | 10:00 | 1.6727 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 10:00 |  |  |  | 1.5 | 86.5262 |  | 25389.2701
2017-08-02 | 10:15 | 1.7132 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 10:15 |  |  |  | 1.5 | 88.3318 |  | 25919.0633
2017-08-02 | 10:30 | 1.8981 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 10:30 |  |  |  | 1.5 | 86.5922 |  | 25408.617
2017-08-02 | 10:45 | 1.7335 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 10:45 |  |  |  | 1.5 | 86.0846 |  | 25259.6953
2017-08-02 | 11:00 | 1.6625 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 11:00 |  |  |  | 1.5 | 88.3842 |  | 25934.4498
2017-08-02 | 11:15 | 1.8419 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 11:15 |  |  |  | 1.5 | 87.1612 |  | 25575.5867
2017-08-02 | 11:30 | 1.7803 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 11:30 |  |  |  | 1.5 | 85.0117 |  | 24944.874
2017-08-02 | 11:45 | 1.6032 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 11:45 |  |  |  | 1.5 | 86.788 |  | 25466.0727
2017-08-02 | 12:00 | 1.7787 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 12:00 |  |  |  | 1.5 | 87.7278 |  | 25741.8292
2017-08-02 | 12:15 | 1.8216 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 12:15 |  |  |  | 1.5 | 85.8779 |  | 25199.0225
2017-08-02 | 12:30 | 1.6953 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 12:30 |  |  |  | 1.5 | 84.5427 |  | 24807.2396
2017-08-02 | 12:45 | 1.604 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 12:45 |  |  |  | 1.5 | 86.6057 |  | 25412.5974
2017-08-02 | 13:00 | 1.7959 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 13:00 |  |  |  | 1.5 | 86.9612 |  | 25516.8998
2017-08-02 | 13:15 | 1.8458 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 13:15 |  |  |  | 1.5 | 85.1264 |  | 24978.5033
2017-08-02 | 13:30 | 1.8162 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 13:30 |  |  |  | 1.5 | 83.9765 |  | 24641.1071
2017-08-02 | 13:45 | 1.7429 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 13:45 |  |  |  | 1.5 | 83.7425 |  | 24572.4401
2017-08-02 | 14:00 | 1.7062 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 14:00 |  |  |  | 1.5 | 83.746 |  | 24573.4653
2017-08-02 | 14:15 | 1.778 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 14:15 |  |  |  | 1.5 | 83.7419 |  | 24572.2699
2017-08-02 | 14:30 | 1.7764 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 14:30 |  |  |  | 1.5 | 83.4841 |  | 24496.6249
2017-08-02 | 14:45 | 1.7514 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 14:45 |  |  |  | 1.5 | 83.4364 |  | 24482.6263
2017-08-02 | 15:00 | 1.7491 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 15:00 |  |  |  | 1.5 | 83.4126 |  | 24475.6415
2017-08-02 | 15:15 | 1.7335 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 15:15 |  |  |  | 1.5 | 83.3199 |  | 24448.4281
2017-08-02 | 15:30 | 1.7725 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 15:30 |  |  |  | 1.5 | 83.2623 |  | 24431.5419
2017-08-02 | 15:40 |  |  | 0 |  |  |  | 0
2017-08-02 | 15:45 | 1.7577 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 15:45 |  |  |  | 1.5 | 83.2384 |  | 24424.5368
2017-08-02 | 16:00 | 1.583 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 16:00 |  |  |  | 1.5 | 84.4889 |  | 24791.4481
2017-08-02 | 16:15 | 1.6118 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 16:15 |  |  |  | 1.5 | 88.9096 |  | 26088.6166
2017-08-02 | 16:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-02 | 16:30 | 1.7928 |  | 0 | 1.5 | 88.4437 |  | 25951.8959
2017-08-02 | 16:45 | 1.8396 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 16:45 |  |  |  | 1.5 | 87.0417 |  | 25540.5314
2017-08-02 | 17:00 | 1.7335 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 17:00 |  |  |  | 1.5 | 86.15 |  | 25278.8741
2017-08-02 | 17:15 | 1.8326 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 17:15 |  |  |  | 1.5 | 85.4408 |  | 25070.764
2017-08-02 | 17:30 | 1.8068 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 17:30 |  |  |  | 1.5 | 84.6102 |  | 24827.0566
2017-08-02 | 17:45 | 1.6867 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 17:45 |  |  |  | 1.5 | 84.3196 |  | 24741.783
2017-08-02 | 18:00 | 1.5822 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 18:00 |  |  |  | 1.5 | 86.7498 |  | 25454.8772
2017-08-02 | 18:15 | 1.8279 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 18:15 |  |  |  | 1.5 | 86.7449 |  | 25453.4218
2017-08-02 | 18:30 | 1.8107 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 18:30 |  |  |  | 1.5 | 84.8334 |  | 24892.5313
2017-08-02 | 18:45 | 1.7249 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 18:45 |  |  |  | 1.5 | 83.1939 |  | 24411.4652
2017-08-02 | 19:00 | 1.6438 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 19:00 |  |  |  | 1.5 | 84.1788 |  | 24700.4703
2017-08-02 | 19:15 | 1.7811 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 19:15 |  |  |  | 1.5 | 84.9061 |  | 24913.8703
2017-08-02 | 19:30 | 1.7826 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 19:30 |  |  |  | 1.5 | 83.1176 |  | 24389.0783
2017-08-02 | 19:45 | 1.6766 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 19:45 |  |  |  | 1.5 | 83.2907 |  | 24439.8855
2017-08-02 | 20:00 | 1.7811 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 20:00 |  |  |  | 1.5 | 83.8992 |  | 24618.4247
2017-08-02 | 20:15 | 1.7959 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 20:15 |  |  |  | 1.5 | 82.2633 |  | 24138.3909
2017-08-02 | 20:30 | 1.7327 | 0 | 0 | 1.5 |  | 0 | 0
2017-08-02 | 20:30 |  |  |  | 1.5 | 82.395 |  | 24177.0348
2017-08-02 | 20:45 | 1.7124 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 20:45 |  |  |  | 1.5 | 82.8577 |  | 24312.8245
2017-08-02 | 21:00 | 1.7405 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 21:00 |  |  |  | 0 | 83.5506 |  | 24516.1394
2017-08-02 | 21:15 | 0.03544 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 21:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 21:30 | 0.03388 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 21:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 21:45 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 21:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 22:00 | 0.03232 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 22:00 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 22:15 | 0.03076 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 22:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 22:30 | 0.03076 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 22:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 22:45 | 0.02998 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 22:45 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 23:00 | 0.0292 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 23:00 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 23:15 | 0.0292 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 23:15 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 23:30 | 0.02842 | 0 | 0 | 0 |  | 0 | 0
2017-08-02 | 23:30 |  |  |  | 0 | 0 |  | 0
2017-08-02 | 23:45 | 0.02764 | 0 | 0 |  |  | 0 | 0
2017-08-02 | 23:45 |  |  |  | 0 | 0 |  | 0
2017-08-03 | 0:00 | 0.02764 | 0 | 0 | 0 |  | 0 | 0
2017-08-03 | 0:00 |  |  |  | 0 | 0 |  | 0
2017-08-03 | 0:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 0:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 0:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 1:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 1:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 1:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 1:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 2:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 2:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 2:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 2:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 3:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 3:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 3:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 3:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 4:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 4:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 4:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 4:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 5:00 | 0.02686 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-08-03 | 5:15 | 1.6259 | 0 | 0 | 1.5 | 100 | 0 | 29342.8571
2017-08-03 | 5:30 | 2.0112 | 0 | 0 | 1.5 | 98.4803 | 0 | 28896.9408
2017-08-03 | 5:45 | 1.9636 | 0 | 0 | 1.5 | 93.26 | 0 | 27365.1627
2017-08-03 | 6:00 | 1.8762 | 0 | 0 | 1.5 | 89.5507 | 0 | 26276.7287
2017-08-03 | 6:15 | 1.838 | 0 | 0 | 1.5 | 87.2709 | 0 | 25607.7881
2017-08-03 | 6:30 | 1.8162 | 0 | 0 | 1.5 | 85.5537 | 0 | 25103.9009
2017-08-03 | 6:45 | 1.7975 | 0 | 0 | 1.5 | 84.2664 | 0 | 24726.1659
2017-08-03 | 7:00 | 1.7787 | 0 | 0 | 1.5 | 83.1168 | 0 | 24388.8568
2017-08-03 | 7:15 | 1.7811 | 0 | 0 | 1.5 | 82.3649 | 0 | 24168.2167
2017-08-03 | 7:30 | 1.7826 | 0 | 0 | 1.5 | 81.7944 | 0 | 24000.8239
2017-08-03 | 7:45 | 1.7585 | 0 | 0 | 1.5 | 81.7562 | 0 | 23989.6079
2017-08-03 | 8:00 | 1.7366 | 0 | 0 | 1.5 | 82.0123 | 0 | 24064.7629
2017-08-03 | 8:15 | 1.6906 | 0 | 0 | 1.5 | 82.636 | 0 | 24247.7661
2017-08-03 | 8:30 | 1.7413 | 0 | 0 | 1.5 | 83.3766 | 0 | 24465.0684
2017-08-03 | 8:45 | 1.7288 | 0 | 0 | 1.5 | 83.8021 | 0 | 24589.9443
2017-08-03 | 9:00 | 1.707 | 0 | 0 | 1.5 | 84.7768 | 0 | 24875.9382
2017-08-03 | 9:15 | 1.7304 | 0 | 0 | 1.5 | 85.8835 | 0 | 25200.6589
2017-08-03 | 9:30 | 1.6266 | 0 | 0 | 1.5 | 86.9869 | 0 | 25524.433
2017-08-03 | 9:45 | 1.6797 | 0 | 0 | 1.5 | 88.5756 | 0 | 25990.6185
2017-08-03 | 10:00 | 1.6329 | 0 | 0 | 1.5 | 90.0716 | 0 | 26429.5927
2017-08-03 | 10:15 | 1.8185 | 0 | 0 | 1.5 | 89.7001 | 0 | 26320.5778
2017-08-03 | 10:30 | 1.7522 | 0 | 0 | 1.5 | 88.2986 | 0 | 25909.3274
2017-08-03 | 10:45 | 1.6399 | 0 | 0 | 1.5 | 89.4761 | 0 | 26254.8345
2017-08-03 | 11:00 | 1.7748 | 0 | 0 | 1.5 | 91.1634 | 0 | 26749.9571
2017-08-03 | 11:15 | 1.8864 | 0 | 0 | 1.5 | 89.4725 | 0 | 26253.789
2017-08-03 | 11:30 | 1.7865 | 0 | 0 | 1.5 | 87.4707 | 0 | 25666.4078
2017-08-03 | 11:45 | 1.5962 | 0 | 0 | 1.5 | 88.6605 | 0 | 26015.535
2017-08-03 | 12:00 | 1.8029 | 0 | 0 | 1.5 | 89.4069 | 0 | 26234.5363
2017-08-03 | 12:15 | 1.8177 | 0 | 0 | 1.5 | 87.8612 | 0 | 25780.9949
2017-08-03 | 12:30 | 1.8084 | 0 | 0 | 1.5 | 86.0539 | 0 | 25250.6668
2017-08-03 | 12:45 | 1.6664 | 0 | 0 | 1.5 | 86.969 | 0 | 25519.19
2017-08-03 | 13:00 | 1.728 | 0 | 0 | 1.5 | 89.318 | 0 | 26208.4423
2017-08-03 | 13:15 | 1.7912 | 0 | 0 | 1.5 | 88.2513 | 0 | 25895.4429
2017-08-03 | 13:30 | 1.7296 | 0 | 0 | 1.5 | 87.2981 | 0 | 25615.7421
2017-08-03 | 13:45 | 1.7889 | 0 | 0 | 1.5 | 86.6985 | 0 | 25439.8129
2017-08-03 | 14:00 | 1.7374 | 0 | 0 | 1.5 | 86.4729 | 0 | 25373.6286
2017-08-03 | 14:15 | 1.7608 | 0 | 0 | 1.5 | 86.4383 | 0 | 25363.4716
2017-08-03 | 14:30 | 1.7608 | 0 | 0 | 1.5 | 86.0399 | 0 | 25246.5676
2017-08-03 | 14:45 | 1.7616 | 0 | 0 | 1.5 | 85.6305 | 0 | 25126.4423
2017-08-03 | 15:00 | 1.7624 | 0 | 0 | 1.5 | 85.4167 | 0 | 25063.7076
2017-08-03 | 15:15 | 1.7148 | 0 | 0 | 1.5 | 85.479 | 0 | 25081.9665
2017-08-03 | 15:30 | 1.7171 | 0 | 0 | 1.5 | 85.5152 | 0 | 25092.6
2017-08-03 | 15:45 | 1.746 | 0 | 0 | 1.5 | 85.2866 | 0 | 25025.5314
2017-08-03 | 16:00 | 1.6976 | 0 | 0 | 1.5 | 85.3183 | 0 | 25034.8374
2017-08-03 | 16:15 | 1.5463 | 0 | 0 | 1.5 | 88.4872 | 0 | 25964.6809
2017-08-03 | 16:30 | 1.8411 | 0 | 0 | 1.5 | 89.0732 | 0 | 26136.6321
2017-08-03 | 16:45 | 1.8131 | 0 | 0 | 1.5 | 86.98 | 0 | 25522.4113
2017-08-03 | 17:00 | 1.8053 | 0 | 0 | 1.5 | 85.8212 | 0 | 25182.4027
2017-08-03 | 17:15 | 1.7772 | 0 | 0 | 1.5 | 84.5559 | 0 | 24811.1105
2017-08-03 | 17:30 | 1.6422 | 0 | 0 | 1.5 | 85.0895 | 0 | 24967.6904
2017-08-03 | 17:45 | 1.7499 | 0 | 0 | 1.5 | 87.4049 | 0 | 25647.0814
2017-08-03 | 18:00 | 1.8856 | 0 | 0 | 1.5 | 85.1024 | 0 | 24971.4762
2017-08-03 | 18:15 | 1.785 | 0 | 0 | 1.5 | 83.3418 | 0 | 24454.8644
2017-08-03 | 18:30 | 1.6758 | 0 | 0 | 1.5 | 84.0887 | 0 | 24674.0201
2017-08-03 | 18:45 | 1.7319 | 0 | 0 | 1.5 | 85.311 | 0 | 25032.6907
2017-08-03 | 19:00 | 1.845 | 0 | 0 | 1.5 | 83.4326 | 0 | 24481.4957
2017-08-03 | 19:15 | 1.7148 | 0 | 0 | 1.5 | 83.065 | 0 | 24373.6405
2017-08-03 | 19:30 | 1.6727 | 0 | 0 | 1.5 | 84.2651 | 0 | 24725.7741
2017-08-03 | 19:45 | 1.7975 | 0 | 0 | 1.5 | 84.7134 | 0 | 24857.3234
2017-08-03 | 20:00 | 1.8474 | 0 | 0 | 1.5 | 82.6786 | 0 | 24260.2579
2017-08-03 | 20:15 | 1.7507 | 0 | 0 | 1.5 | 82.3876 | 0 | 24174.8904
2017-08-03 | 20:30 | 1.7413 | 0 | 0 | 1.5 | 83.0523 | 0 | 24369.9042
2017-08-03 | 20:45 | 1.7046 | 0 | 0 | 1.5 | 83.4023 | 0 | 24472.6283
2017-08-03 | 21:00 | 1.7405 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 23:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 23:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 0:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 0:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 0:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 1:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 1:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 1:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 1:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 2:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 2:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 2:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 2:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 3:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 3:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 3:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 3:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 4:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 4:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 4:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 4:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 5:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 5:15 | 1.6469 | 0 | 0 | 1.5 | 100 | 0 | 29342.8571
2017-08-04 | 5:30 | 1.9893 | 0 | 0 | 1.5 | 98.6682 | 0 | 28952.0593
2017-08-04 | 5:45 | 2.0049 | 0 | 0 | 1.5 | 93.2702 | 0 | 27368.1556
2017-08-04 | 6:00 | 1.87 | 0 | 0 | 1.5 | 89.3123 | 0 | 26206.7944
2017-08-04 | 6:15 | 1.8357 | 0 | 0 | 1.5 | 87.0762 | 0 | 25550.6368
2017-08-04 | 6:30 | 1.7858 | 0 | 0 | 1.5 | 85.5432 | 0 | 25100.8228
2017-08-04 | 6:32 |  |  | 0 |  |  |  | 0
2017-08-04 | 6:45 | 1.8372 | 8.9572 | 1 | 10 | 82.6935 | 92.1258 | 24264.6479
2017-08-04 | 7:00 | 1.8014 | 7.116 | 1 | 10 | 81.3599 | 74.6591 | 23873.3263
2017-08-04 | 7:15 | 1.7577 | 6.9419 | 1 | 10 | 80.7522 | 72.4363 | 23695.0086
2017-08-04 | 7:30 | 1.7873 | 6.1712 | 1 | 10 | 80.2815 | 64.7371 | 23556.8885
2017-08-04 | 7:42 |  |  | 0 |  |  |  | 0
2017-08-04 | 7:45 | 1.7109 | 4.4426 | 0 | 1.5 | 80.4532 | 0 | 23607.2546
2017-08-04 | 8:00 | 1.6968 | 0 | 0 | 1.5 | 81.3995 | 0 | 23884.9452
2017-08-04 | 8:15 | 1.6937 | 0 | 0 | 1.5 | 82.597 | 0 | 24236.313
2017-08-04 | 8:30 | 1.7101 | 0 | 0 | 1.5 | 83.3782 | 0 | 24465.552
2017-08-04 | 8:45 | 1.7343 | 0 | 0 | 1.5 | 84.0563 | 0 | 24664.5282
2017-08-04 | 9:00 | 1.7195 | 0 | 0 | 1.5 | 84.8362 | 0 | 24893.3664
2017-08-04 | 9:15 | 1.7187 | 0 | 0 | 1.5 | 85.7424 | 0 | 25159.2726
2017-08-04 | 9:30 | 1.7483 | 0 | 0 | 1.5 | 86.8991 | 0 | 25498.6747
2017-08-04 | 9:45 | 1.7241 | 0 | 0 | 1.5 | 87.503 | 0 | 25675.8797
2017-08-04 | 10:00 | 1.6773 | 0 | 0 | 1.5 | 88.6818 | 0 | 26021.7607
2017-08-04 | 10:15 | 1.7078 | 0 | 0 | 1.5 | 90.3474 | 0 | 26510.4941
2017-08-04 | 10:30 | 1.6906 | 0 | 0 | 1.5 | 91.2376 | 0 | 26771.7236
2017-08-04 | 10:45 | 1.8989 | 0 | 0 | 1.5 | 90.0048 | 0 | 26409.9772
2017-08-04 | 11:00 | 1.7686 | 0 | 0 | 1.5 | 88.3849 | 0 | 25934.6447
2017-08-04 | 11:15 | 1.7312 | 0 | 0 | 1.5 | 89.6311 | 0 | 26300.3133
2017-08-04 | 11:30 | 1.8396 | 0 | 0 | 1.5 | 90.3176 | 0 | 26501.7611
2017-08-04 | 11:45 | 1.8318 | 0 | 0 | 1.5 | 88.1877 | 0 | 25876.8017
2017-08-04 | 12:00 | 1.6282 | 0 | 0 | 1.5 | 89.2222 | 0 | 26180.3356
2017-08-04 | 12:15 | 1.7585 | 0 | 0 | 1.5 | 90.1715 | 0 | 26458.8859
2017-08-04 | 12:30 | 1.817 | 0 | 0 | 1.5 | 88.1942 | 0 | 25878.6931
2017-08-04 | 12:45 | 1.6797 | 0 | 0 | 1.5 | 88.4154 | 0 | 25943.5925
2017-08-04 | 13:00 | 1.7873 | 0 | 0 | 1.5 | 89.8785 | 0 | 26372.9137
2017-08-04 | 13:15 | 1.8427 | 0 | 0 | 1.5 | 88.8303 | 0 | 26065.341
2017-08-04 | 13:30 | 1.806 | 0 | 0 | 1.5 | 87.1768 | 0 | 25580.1604
2017-08-04 | 13:45 | 1.668 | 0 | 0 | 1.5 | 86.8842 | 0 | 25494.3002
2017-08-04 | 14:00 | 1.6524 | 0 | 0 | 1.5 | 89.9567 | 0 | 26395.8534
2017-08-04 | 14:15 | 1.8497 | 0 | 0 | 1.5 | 89.0748 | 0 | 26137.0975
2017-08-04 | 14:30 | 1.8115 | 0 | 0 | 1.5 | 87.5564 | 0 | 25691.5617
2017-08-04 | 14:45 | 1.799 | 0 | 0 | 1.5 | 86.3987 | 0 | 25351.8418
2017-08-04 | 15:00 | 1.7288 | 0 | 0 | 1.5 | 86.1015 | 0 | 25264.6428
2017-08-04 | 15:15 | 1.6079 | 0 | 0 | 1.5 | 87.6745 | 0 | 25726.2033
2017-08-04 | 15:30 | 1.8404 | 0 | 0 | 1.5 | 88.6723 | 0 | 26018.9916
2017-08-04 | 15:45 | 1.8037 | 0 | 0 | 1.5 | 87.1848 | 0 | 25582.5154
2017-08-04 | 16:00 | 1.7943 | 0 | 0 | 1.5 | 86.1045 | 0 | 25265.516
2017-08-04 | 16:15 | 1.7429 | 0 | 0 | 1.5 | 85.4833 | 0 | 25083.2558
2017-08-04 | 16:30 | 1.597 | 0 | 0 | 1.5 | 87.8286 | 0 | 25771.4244
2017-08-04 | 16:45 | 1.8185 | 0 | 0 | 1.5 | 88.1306 | 0 | 25860.0249
2017-08-04 | 17:00 | 1.8404 | 0 | 0 | 1.5 | 86.5144 | 0 | 25385.7868
2017-08-04 | 17:15 | 1.8248 | 0 | 0 | 1.5 | 84.5894 | 0 | 24820.9494
2017-08-04 | 17:30 | 1.6875 | 0 | 0 | 1.5 | 84.6387 | 0 | 24835.4269
2017-08-04 | 17:45 | 1.7335 | 0 | 0 | 1.5 | 86.3006 | 0 | 25323.0679
2017-08-04 | 18:00 | 1.8482 | 0 | 0 | 1.5 | 84.4459 | 0 | 24778.851
2017-08-04 | 18:15 | 1.7156 | 0 | 0 | 1.5 | 83.9372 | 0 | 24629.5712
2017-08-04 | 18:30 | 1.7078 | 0 | 0 | 1.5 | 85.3979 | 0 | 25058.1961
2017-08-04 | 18:45 | 1.7967 | 0 | 0 | 1.5 | 84.0068 | 0 | 24650.0082
2017-08-04 | 19:00 | 1.7202 | 0 | 0 | 1.5 | 83.939 | 0 | 24630.095
2017-08-04 | 19:15 | 1.7421 | 0 | 0 | 1.5 | 84.5353 | 0 | 24805.0817
2017-08-04 | 19:30 | 1.8045 | 0 | 0 | 1.5 | 83.0792 | 0 | 24377.8066
2017-08-04 | 19:45 | 1.7491 | 0 | 0 | 1.5 | 83.0291 | 0 | 24363.1052
2017-08-04 | 20:00 | 1.7288 | 0 | 0 | 1.5 | 83.3747 | 0 | 24464.5065
2017-08-04 | 20:15 | 1.7592 | 0 | 0 | 1.5 | 83.1679 | 0 | 24403.8516
2017-08-04 | 20:30 | 1.7967 | 0 | 0 | 1.5 | 82.8503 | 0 | 24310.6551
2017-08-04 | 20:45 | 1.7218 | 0 | 0 | 1.5 | 82.6434 | 0 | 24249.9242
2017-08-04 | 21:00 | 1.7772 | 0 | 0 | 1.5 | 82.2896 | 0 | 24146.1074
2017-08-04 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 0:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 1:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 1:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 1:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 1:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 2:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 2:30 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 2:45 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 3:00 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 3:15 | 0.02764 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 3:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 3:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 4:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 4:15 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 4:30 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 4:45 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 5:00 | 0.02686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 5:01 |  |  | 1 |  |  |  | 0
2017-08-05 | 5:15 | 1.9355 | 10 | 1 | 10 | 97.1783 | 100 | 28514.8827
2017-08-05 | 5:30 | 2.0166 | 10 | 1 | 10 | 91.4153 | 100 | 26823.8717
2017-08-05 | 5:45 | 1.9051 | 9.5828 | 1 | 10 | 86.1986 | 96.1733 | 25293.1458
2017-08-05 | 6:00 | 1.778 | 9.0392 | 1 | 10 | 84.7495 | 90.7085 | 24867.9326
2017-08-05 | 6:15 | 1.7889 | 9.0656 | 1 | 10 | 83.3052 | 91.0715 | 24444.1164
2017-08-05 | 6:30 | 1.7608 | 8.9294 | 1 | 10 | 82.9938 | 89.6454 | 24352.7624
2017-08-05 | 6:45 | 1.7468 | 8.7984 | 1 | 10 | 82.4333 | 88.4163 | 24188.2843
2017-08-05 | 7:00 | 1.7787 | 8.5746 | 1 | 10 | 81.8243 | 86.2316 | 24009.5951
2017-08-05 | 7:15 | 1.7678 | 8.1993 | 1 | 10 | 80.8898 | 82.6698 | 23735.3811
2017-08-05 | 7:30 | 1.8037 | 8.1078 | 1 | 10 | 80.3211 | 81.6334 | 23568.5141
2017-08-05 | 7:45 | 1.7967 | 7.8953 | 1 | 10 | 80.1582 | 79.616 | 23520.7205
2017-08-05 | 8:00 | 1.7468 | 7.6128 | 1 | 10 | 79.5447 | 76.7822 | 23340.6789
2017-08-05 | 8:15 | 1.7616 | 7.8489 | 1 | 10 | 79.7456 | 79.0874 | 23399.6457
2017-08-05 | 8:30 | 1.7413 | 7.4412 | 1 | 10 | 79.3461 | 75.2 | 23282.4172
2017-08-05 | 8:45 | 1.7304 | 7.1191 | 1 | 10 | 79.7523 | 72.0705 | 23401.5935
2017-08-05 | 9:00 | 1.7561 | 6.9009 | 1 | 10 | 79.7468 | 69.9215 | 23399.9884
2017-08-05 | 9:15 | 1.7577 | 6.8075 | 1 | 10 | 79.6585 | 69.0303 | 23374.0778
2017-08-05 | 9:22 |  |  | 0 |  |  |  | 0
2017-08-05 | 9:30 | 1.7187 | 2.7147 | 0 | 1.5 | 80.1322 | 0 | 23513.0664
2017-08-05 | 9:45 | 1.7475 | 0 | 0 | 1.5 | 80.6692 | 0 | 23670.6361
2017-08-05 | 10:00 | 1.7663 | 0 | 0 | 1.5 | 80.7179 | 0 | 23684.9501
2017-08-05 | 10:15 | 1.7249 | 0 | 0 | 1.5 | 80.7702 | 0 | 23700.2873
2017-08-05 | 10:30 | 1.7655 | 0 | 0 | 1.5 | 80.7329 | 0 | 23689.3357
2017-08-05 | 10:45 | 1.7397 | 0 | 0 | 1.5 | 80.8359 | 0 | 23719.5603
2017-08-05 | 11:00 | 1.7468 | 0 | 0 | 1.5 | 80.8676 | 0 | 23728.862
2017-08-05 | 11:15 | 1.7616 | 0 | 0 | 1.5 | 80.9269 | 0 | 23746.2767
2017-08-05 | 11:30 | 1.7592 | 0 | 0 | 1.5 | 80.9305 | 0 | 23747.3178
2017-08-05 | 11:45 | 1.7436 | 0 | 0 | 1.5 | 80.9583 | 0 | 23755.4666
2017-08-05 | 12:00 | 1.753 | 0 | 0 | 1.5 | 80.9313 | 0 | 23747.5417
2017-08-05 | 12:15 | 1.7522 | 0 | 0 | 1.5 | 80.9552 | 0 | 23754.5643
2017-08-05 | 12:30 | 1.7452 | 0 | 0 | 1.5 | 80.9238 | 0 | 23745.343
2017-08-05 | 12:45 | 1.7499 | 0 | 0 | 1.5 | 80.8719 | 0 | 23730.1202
2017-08-05 | 13:00 | 1.7499 | 0 | 0 | 1.5 | 80.789 | 0 | 23705.7923
2017-08-05 | 13:15 | 1.7592 | 0 | 0 | 1.5 | 80.7431 | 0 | 23692.3425
2017-08-05 | 13:30 | 1.7312 | 0 | 0 | 1.5 | 80.7564 | 0 | 23696.2219
2017-08-05 | 13:45 | 1.7257 | 0 | 0 | 1.5 | 80.794 | 0 | 23707.2745
2017-08-05 | 14:00 | 1.7499 | 0 | 0 | 1.5 | 80.8506 | 0 | 23723.8898
2017-08-05 | 14:15 | 1.7522 | 0 | 0 | 1.5 | 80.8237 | 0 | 23715.9963
2017-08-05 | 14:30 | 1.7358 | 0 | 0 | 1.5 | 80.9166 | 0 | 23743.2567
2017-08-05 | 14:45 | 1.7452 | 0 | 0 | 1.5 | 81.014 | 0 | 23771.8246
2017-08-05 | 15:00 | 1.7452 | 0 | 0 | 1.5 | 81.2423 | 0 | 23838.8214
2017-08-05 | 15:15 | 1.7304 | 0 | 0 | 1.5 | 81.3153 | 0 | 23860.2414
2017-08-05 | 15:30 | 1.7397 | 0 | 0 | 1.5 | 81.473 | 0 | 23906.4946
2017-08-05 | 15:45 | 1.7592 | 0 | 0 | 1.5 | 81.6003 | 0 | 23943.8738
2017-08-05 | 16:00 | 1.739 | 0 | 0 | 1.5 | 81.6695 | 0 | 23964.1653
2017-08-05 | 16:15 | 1.7592 | 0 | 0 | 1.5 | 81.7702 | 0 | 23993.7183
2017-08-05 | 16:30 | 1.7327 | 0 | 0 | 1.5 | 81.8691 | 0 | 24022.7272
2017-08-05 | 16:45 | 1.739 | 0 | 0 | 1.5 | 81.8907 | 0 | 24029.0603
2017-08-05 | 17:00 | 1.7569 | 0 | 0 | 1.5 | 81.9192 | 0 | 24037.4306
2017-08-05 | 17:15 | 1.7452 | 0 | 0 | 1.5 | 82.0015 | 0 | 24061.5704
2017-08-05 | 17:30 | 1.7725 | 0 | 0 | 1.5 | 81.7457 | 0 | 23986.5119
2017-08-05 | 17:45 | 1.7756 | 0 | 0 | 1.5 | 81.4676 | 0 | 23904.9165
2017-08-05 | 18:00 | 1.7647 | 0 | 0 | 1.5 | 81.2304 | 0 | 23835.3179
2017-08-05 | 18:15 | 1.7624 | 0 | 0 | 1.5 | 81.0475 | 0 | 23781.6656
2017-08-05 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 80.8929 | 0 | 23736.2854
2017-08-05 | 18:45 | 1.7397 | 0 | 0 | 1.5 | 80.7134 | 0 | 23683.6159
2017-08-05 | 19:00 | 1.7382 | 0 | 0 | 1.5 | 80.5239 | 0 | 23628.0273
2017-08-05 | 19:15 | 1.7569 | 0 | 0 | 1.5 | 80.2666 | 0 | 23552.5208
2017-08-05 | 19:30 | 1.7507 | 0 | 0 | 1.5 | 79.9481 | 0 | 23459.0559
2017-08-05 | 19:45 | 1.7569 | 0 | 0 | 1.5 | 79.6459 | 0 | 23370.3906
2017-08-05 | 20:00 | 1.7787 | 0 | 0 | 1.5 | 79.2005 | 0 | 23239.6943
2017-08-05 | 20:15 | 1.7709 | 0 | 0 | 1.5 | 78.7445 | 0 | 23105.8993
2017-08-05 | 20:30 | 1.7639 | 0 | 0 | 1.5 | 78.3449 | 0 | 22988.6394
2017-08-05 | 20:45 | 1.7647 | 0 | 0 | 1.5 | 78.0014 | 0 | 22887.8493
2017-08-05 | 21:00 | 1.7639 | 0 | 0 | 1.5 | 77.6447 | 0 | 22783.1687
2017-08-05 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-05 | 23:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 1:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 1:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 1:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 2:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 2:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 2:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 2:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 5:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 5:01 |  |  | 1 |  |  |  | 0
2017-08-06 | 5:15 | 2.0923 | 10 | 1 | 10 | 92.0869 | 100 | 27020.9161
2017-08-06 | 5:30 | 1.9917 | 9.6199 | 1 | 10 | 85.8247 | 96.6852 | 25183.4235
2017-08-06 | 5:45 | 1.8232 | 8.5341 | 1 | 10 | 83.2789 | 85.9435 | 24436.3952
2017-08-06 | 6:00 | 1.8053 | 7.9402 | 1 | 10 | 81.6731 | 80.1388 | 23965.2175
2017-08-06 | 6:15 | 1.7499 | 8.2868 | 1 | 10 | 81.3367 | 83.3436 | 23866.5164
2017-08-06 | 6:30 | 1.7655 | 8.1386 | 1 | 10 | 80.6806 | 82.0904 | 23673.9829
2017-08-06 | 6:45 | 1.7616 | 7.9123 | 1 | 10 | 80.1216 | 79.9054 | 23509.9637
2017-08-06 | 7:00 | 1.7795 | 7.5278 | 1 | 10 | 79.4928 | 76.0705 | 23325.4693
2017-08-06 | 7:15 | 1.7647 | 7.323 | 1 | 10 | 79.098 | 74.0775 | 23209.6263
2017-08-06 | 7:30 | 1.7304 | 7.2269 | 1 | 10 | 78.8501 | 73.0053 | 23136.876
2017-08-06 | 7:45 | 1.6797 | 7.2202 | 1 | 10 | 79.1381 | 72.8928 | 23221.3705
2017-08-06 | 8:00 | 1.7616 | 7.3713 | 1 | 10 | 78.9374 | 74.5914 | 23162.4865
2017-08-06 | 8:15 | 1.8115 | 7.1095 | 1 | 10 | 78.5063 | 72.1676 | 23035.9829
2017-08-06 | 8:30 | 1.7288 | 6.6219 | 1 | 10 | 78.2886 | 67.2516 | 22972.1
2017-08-06 | 8:45 | 1.7351 | 6.6927 | 1 | 10 | 78.4211 | 67.7684 | 23010.977
2017-08-06 | 8:58 |  |  | 0 |  |  |  | 0
2017-08-06 | 9:00 | 1.7 | 4.9843 | 0 | 1.5 | 78.5458 | 0 | 23047.5927
2017-08-06 | 9:15 | 1.7795 | 0 | 0 | 1.5 | 78.6739 | 0 | 23085.1648
2017-08-06 | 9:30 | 1.7639 | 0 | 0 | 1.5 | 78.7219 | 0 | 23099.2438
2017-08-06 | 9:45 | 1.785 | 0 | 0 | 1.5 | 78.6822 | 0 | 23087.6161
2017-08-06 | 10:00 | 1.7608 | 0 | 0 | 1.5 | 78.4022 | 0 | 23005.4362
2017-08-06 | 10:15 | 1.7444 | 0 | 0 | 1.5 | 78.2839 | 0 | 22970.7256
2017-08-06 | 10:30 | 1.7374 | 0 | 0 | 1.5 | 78.5335 | 0 | 23043.973
2017-08-06 | 10:45 | 1.728 | 0 | 0 | 1.5 | 78.8975 | 0 | 23150.776
2017-08-06 | 11:00 | 1.7585 | 0 | 0 | 1.5 | 79.1007 | 0 | 23210.3987
2017-08-06 | 11:15 | 1.7304 | 0 | 0 | 1.5 | 79.2625 | 0 | 23257.8722
2017-08-06 | 11:30 | 1.7015 | 0 | 0 | 1.5 | 79.5553 | 0 | 23343.7907
2017-08-06 | 11:45 | 1.7351 | 0 | 0 | 1.5 | 79.7497 | 0 | 23400.8502
2017-08-06 | 12:00 | 1.7405 | 0 | 0 | 1.5 | 79.7938 | 0 | 23413.7719
2017-08-06 | 12:15 | 1.7296 | 0 | 0 | 1.5 | 80.0537 | 0 | 23490.0349
2017-08-06 | 12:30 | 1.7421 | 0 | 0 | 1.5 | 80.292 | 0 | 23559.9689
2017-08-06 | 12:45 | 1.7327 | 0 | 0 | 1.5 | 80.4789 | 0 | 23614.799
2017-08-06 | 13:00 | 1.7444 | 0 | 0 | 1.5 | 80.6267 | 0 | 23658.18
2017-08-06 | 13:15 | 1.7358 | 0 | 0 | 1.5 | 80.8226 | 0 | 23715.6536
2017-08-06 | 13:30 | 1.7374 | 0 | 0 | 1.5 | 81.1538 | 0 | 23812.8574
2017-08-06 | 13:45 | 1.7296 | 0 | 0 | 1.5 | 81.3853 | 0 | 23880.7656
2017-08-06 | 14:00 | 1.739 | 0 | 0 | 1.5 | 81.5984 | 0 | 23943.3166
2017-08-06 | 14:15 | 1.7538 | 0 | 0 | 1.5 | 81.7469 | 0 | 23986.8902
2017-08-06 | 14:30 | 1.7421 | 0 | 0 | 1.5 | 81.8785 | 0 | 24025.4807
2017-08-06 | 14:45 | 1.7624 | 0 | 0 | 1.5 | 81.9779 | 0 | 24054.6707
2017-08-06 | 15:00 | 1.7241 | 0 | 0 | 1.5 | 82.2072 | 0 | 24121.9386
2017-08-06 | 15:15 | 1.7358 | 0 | 0 | 1.5 | 82.4456 | 0 | 24191.8932
2017-08-06 | 15:30 | 1.8029 | 0 | 0 | 1.5 | 82.3042 | 0 | 24150.3924
2017-08-06 | 15:45 | 1.7889 | 0 | 0 | 1.5 | 80.9693 | 0 | 23758.7125
2017-08-06 | 16:00 | 1.7468 | 0 | 0 | 1.5 | 80.7507 | 0 | 23694.5608
2017-08-06 | 16:15 | 1.7327 | 0 | 0 | 1.5 | 81.0975 | 0 | 23796.3359
2017-08-06 | 16:30 | 1.7522 | 0 | 0 | 1.5 | 81.3881 | 0 | 23881.5892
2017-08-06 | 16:45 | 1.7553 | 0 | 0 | 1.5 | 81.6655 | 0 | 23962.9834
2017-08-06 | 17:00 | 1.7312 | 0 | 0 | 1.5 | 81.9885 | 0 | 24057.7758
2017-08-06 | 17:15 | 1.7858 | 0 | 0 | 1.5 | 81.4354 | 0 | 23895.4602
2017-08-06 | 17:30 | 1.7546 | 0 | 0 | 1.5 | 80.9424 | 0 | 23750.7987
2017-08-06 | 17:45 | 1.7265 | 0 | 0 | 1.5 | 81.1965 | 0 | 23825.3759
2017-08-06 | 18:00 | 1.7382 | 0 | 0 | 1.5 | 81.5653 | 0 | 23933.5804
2017-08-06 | 18:15 | 1.7865 | 0 | 0 | 1.5 | 80.8144 | 0 | 23713.2651
2017-08-06 | 18:30 | 1.7444 | 0 | 0 | 1.5 | 80.457 | 0 | 23608.3964
2017-08-06 | 18:45 | 1.7366 | 0 | 0 | 1.5 | 80.6449 | 0 | 23663.5169
2017-08-06 | 19:00 | 1.7257 | 0 | 0 | 1.5 | 81.0307 | 0 | 23776.7137
2017-08-06 | 19:15 | 1.7421 | 0 | 0 | 1.5 | 81.3773 | 0 | 23878.4237
2017-08-06 | 19:30 | 1.7413 | 0 | 0 | 1.5 | 81.541 | 0 | 23926.4524
2017-08-06 | 19:45 | 1.7709 | 0 | 0 | 1.5 | 81.5389 | 0 | 23925.8368
2017-08-06 | 20:00 | 1.7553 | 0 | 0 | 1.5 | 81.3974 | 0 | 23884.3137
2017-08-06 | 20:15 | 1.7702 | 0 | 0 | 1.5 | 81.034 | 0 | 23777.6785
2017-08-06 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 80.7036 | 0 | 23680.7347
2017-08-06 | 20:45 | 1.7647 | 0 | 0 | 1.5 | 80.2932 | 0 | 23560.3228
2017-08-06 | 21:00 | 1.7787 | 0 | 0 | 1.5 | 79.8274 | 0 | 23423.6423
2017-08-06 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 21:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 22:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 23:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 23:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 23:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-06 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 0:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 0:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 0:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 2:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 2:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 2:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 3:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 3:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 3:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 4:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 4:15 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 4:30 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 4:45 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 5:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 5:02 |  |  | 1 |  |  |  | 0
2017-08-07 | 5:15 | 1.9698 | 10 | 1 | 10 | 94.8385 | 100 | 27828.3235
2017-08-07 | 5:30 | 1.9269 | 10 | 1 | 10 | 91.0379 | 100 | 26713.1107
2017-08-07 | 5:45 | 1.8895 | 9.8786 | 1 | 10 | 87.2317 | 98.8972 | 25596.2766
2017-08-07 | 6:00 | 1.824 | 8.8539 | 1 | 10 | 84.699 | 89.0418 | 24853.1148
2017-08-07 | 6:15 | 1.8115 | 8.6877 | 1 | 10 | 83.0852 | 87.1483 | 24379.5774
2017-08-07 | 6:30 | 1.7967 | 8.1574 | 1 | 10 | 81.8048 | 82.0393 | 24003.8571
2017-08-07 | 6:45 | 1.7764 | 7.5759 | 1 | 10 | 80.8614 | 76.8359 | 23727.053
2017-08-07 | 7:00 | 1.8162 | 6.7323 | 1 | 10 | 79.8552 | 68.5019 | 23431.8046
2017-08-07 | 7:15 | 1.7772 | 6.3681 | 1 | 10 | 79.2329 | 0 | 23249.1861
2017-08-07 | 7:30 | 1.7257 | 6.0823 | 1 | 10 | 79.0551 | 0 | 23197.0136
2017-08-07 | 7:45 | 1.7951 | 6.1362 | 1 | 10 | 79.4515 | 0 | 23313.3469
2017-08-07 | 8:00 | 1.7585 | 4.8986 | 1 | 10 | 79.3004 | 0 | 23269.0142
2017-08-07 | 8:15 | 1.7335 | 5.1161 | 1 | 10 | 80.1594 | 0 | 23521.0541
2017-08-07 | 8:30 | 1.6773 | 5.3386 | 1 | 10 | 81.3006 | 0 | 23855.9072
2017-08-07 | 8:41 |  |  | 0 |  |  |  | 0
2017-08-07 | 8:45 | 1.6883 | 3.0345 | 0 | 1.5 | 82.513 | 0 | 24211.6764
2017-08-07 | 9:00 | 1.7405 | 0 | 0 | 1.5 | 82.8852 | 0 | 24320.8882
2017-08-07 | 9:15 | 1.7171 | 0 | 0 | 1.5 | 83.4534 | 0 | 24487.6231
2017-08-07 | 9:30 | 1.7078 | 0 | 0 | 1.5 | 84.0664 | 0 | 24667.4878
2017-08-07 | 9:45 | 1.689 | 0 | 0 | 1.5 | 84.9423 | 0 | 24924.4974
2017-08-07 | 10:00 | 1.7218 | 0 | 0 | 1.5 | 85.7024 | 0 | 25147.5261
2017-08-07 | 10:15 | 1.7039 | 0 | 0 | 1.5 | 86.6741 | 0 | 25432.665
2017-08-07 | 10:30 | 1.7117 | 0 | 0 | 1.5 | 87.5295 | 0 | 25683.6479
2017-08-07 | 10:45 | 1.7413 | 0 | 0 | 1.5 | 88.0396 | 0 | 25833.3197
2017-08-07 | 11:00 | 1.7483 | 0 | 0 | 1.5 | 88.8548 | 0 | 26072.5229
2017-08-07 | 11:15 | 1.7124 | 0 | 0 | 1.5 | 89.5967 | 0 | 26290.237
2017-08-07 | 11:30 | 1.9035 | 0 | 0 | 1.5 | 88.8913 | 0 | 26083.2348
2017-08-07 | 11:45 | 1.8216 | 0 | 0 | 1.5 | 86.66 | 0 | 25428.5344
2017-08-07 | 12:00 | 1.6617 | 0 | 0 | 1.5 | 87.6271 | 0 | 25712.283
2017-08-07 | 12:15 | 1.8443 | 0 | 0 | 1.5 | 88.0898 | 0 | 25848.0592
2017-08-07 | 12:30 | 1.8482 | 0 | 0 | 1.5 | 85.7974 | 0 | 25175.4135
2017-08-07 | 12:45 | 1.7 | 0 | 0 | 1.5 | 86.1391 | 0 | 25275.6772
2017-08-07 | 13:00 | 1.7335 | 0 | 0 | 1.5 | 87.755 | 0 | 25749.819
2017-08-07 | 13:15 | 1.8458 | 0 | 0 | 1.5 | 86.5247 | 0 | 25388.8091
2017-08-07 | 13:30 | 1.8232 | 0 | 0 | 1.5 | 85.1925 | 0 | 24997.9127
2017-08-07 | 13:45 | 1.6703 | 0 | 0 | 1.5 | 85.9038 | 0 | 25206.6252
2017-08-07 | 14:00 | 1.7616 | 0 | 0 | 1.5 | 86.8924 | 0 | 25496.7069
2017-08-07 | 14:15 | 1.7436 | 0 | 0 | 1.5 | 86.2797 | 0 | 25316.9318
2017-08-07 | 14:30 | 1.8084 | 0 | 0 | 1.5 | 85.5146 | 0 | 25092.4143
2017-08-07 | 14:45 | 1.7842 | 0 | 0 | 1.5 | 84.7633 | 0 | 24871.9758
2017-08-07 | 15:00 | 1.7257 | 0 | 0 | 1.5 | 85.139 | 0 | 24982.2016
2017-08-07 | 15:15 | 1.7686 | 0 | 0 | 1.5 | 85.0754 | 0 | 24963.5625
2017-08-07 | 15:30 | 1.8123 | 0 | 0 | 1.5 | 84.6891 | 0 | 24850.1934
2017-08-07 | 15:45 | 1.7265 | 0 | 0 | 1.5 | 84.5378 | 0 | 24805.798
2017-08-07 | 16:00 | 1.7772 | 0 | 0 | 1.5 | 84.6106 | 0 | 24827.1819
2017-08-07 | 16:15 | 1.76 | 0 | 0 | 1.5 | 84.0901 | 0 | 24674.4455
2017-08-07 | 16:30 | 1.7335 | 0 | 0 | 1.5 | 83.9619 | 0 | 24636.8245
2017-08-07 | 16:45 | 1.792 | 0 | 0 | 1.5 | 84.0904 | 0 | 24674.535
2017-08-07 | 17:00 | 1.7366 | 0 | 0 | 1.5 | 83.9305 | 0 | 24627.5988
2017-08-07 | 17:15 | 1.6461 | 0 | 0 | 1.5 | 86.0363 | 0 | 25245.4954
2017-08-07 | 17:30 | 1.8131 | 0 | 0 | 1.5 | 85.6062 | 0 | 25119.3076
2017-08-07 | 17:45 | 1.8435 | 0 | 0 | 1.5 | 83.92 | 0 | 24624.5319
2017-08-07 | 18:00 | 1.7124 | 0 | 0 | 1.5 | 83.3096 | 0 | 24445.4216
2017-08-07 | 18:15 | 1.6539 | 0 | 0 | 1.5 | 84.7306 | 0 | 24862.3783
2017-08-07 | 18:30 | 1.817 | 0 | 0 | 1.5 | 84.0438 | 0 | 24660.8454
2017-08-07 | 18:45 | 1.7756 | 0 | 0 | 1.5 | 82.6157 | 0 | 24241.8089
2017-08-07 | 19:00 | 1.6758 | 0 | 0 | 1.5 | 83.4044 | 0 | 24473.226
2017-08-07 | 19:15 | 1.7826 | 0 | 0 | 1.5 | 83.8779 | 0 | 24612.1586
2017-08-07 | 19:30 | 1.8341 | 0 | 0 | 1.5 | 82.0039 | 0 | 24062.2981
2017-08-07 | 19:45 | 1.746 | 0 | 0 | 1.5 | 81.1658 | 0 | 23816.3542
2017-08-07 | 20:00 | 1.7358 | 0 | 0 | 1.5 | 81.7086 | 0 | 23975.641
2017-08-07 | 20:15 | 1.7358 | 0 | 0 | 1.5 | 82.0622 | 0 | 24079.4038
2017-08-07 | 20:30 | 1.7748 | 0 | 0 | 1.5 | 82.4031 | 0 | 24179.4348
2017-08-07 | 20:45 | 1.7546 | 0 | 0 | 1.5 | 82.2983 | 0 | 24148.6641
2017-08-07 | 21:00 | 1.7538 | 0 | 0 | 1.5 | 82.5622 | 0 | 24226.1113
2017-08-07 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 23:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 0:15 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 0:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 0:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 0:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 0:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 1:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 1:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 1:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 1:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 1:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 1:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 1:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 2:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 2:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 2:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 2:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 2:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 2:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 3:00 | 0.02842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 3:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 3:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 3:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 3:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 3:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 3:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 4:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 4:15 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 4:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 4:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 4:45 | 0.0292 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 4:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 5:00 | 0.02998 | 0 | 0 | 0 | 25 | 0 | 7335.7143
2017-08-08 | 5:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 5:01 |  |  | 1 |  |  |  | 0
2017-08-08 | 5:15 | 1.9223 | 10 | 1 |  | 97.5062 | 100 | 28611.0924
2017-08-08 | 5:15 |  |  |  | 10 |  |  | 0
2017-08-08 | 5:30 | 1.923 | 10 | 1 | 10 | 94.0417 | 100 | 27594.529
2017-08-08 | 5:30 |  |  |  | 10 |  |  | 0
2017-08-08 | 5:45 | 1.9542 | 9.9793 | 1 |  | 90.0009 | 99.922 | 26408.8379
2017-08-08 | 5:45 |  |  |  | 10 |  |  | 0
2017-08-08 | 6:00 | 1.8918 | 9.4722 | 1 | 10 | 86.4875 | 95.1944 | 25377.9179
2017-08-08 | 6:00 |  |  |  | 10 |  |  | 0
2017-08-08 | 6:15 | 1.8372 | 9.3503 | 1 |  | 84.2146 | 93.9148 | 24710.9742
2017-08-08 | 6:15 |  |  |  | 10 |  |  | 0
2017-08-08 | 6:30 | 1.7951 | 8.6801 | 1 | 10 | 82.6139 | 87.3068 | 24241.2828
2017-08-08 | 6:30 |  |  |  | 10 |  |  | 0
2017-08-08 | 6:45 | 1.8084 | 7.9079 | 1 |  | 81.3059 | 80.2646 | 23857.4832
2017-08-08 | 6:45 |  |  |  | 10 |  |  | 0
2017-08-08 | 7:00 | 1.7982 | 6.493 | 1 | 10 | 80.0936 | 66.9056 | 23501.7365
2017-08-08 | 7:00 |  |  |  | 10 |  |  | 0
2017-08-08 | 7:15 | 1.7725 | 6.8904 | 1 |  | 79.338 | 69.7741 | 23280.0398
2017-08-08 | 7:15 |  |  |  | 10 |  |  | 0
2017-08-08 | 7:30 | 1.7702 | 5.9329 | 1 | 10 | 78.7714 | 0 | 23113.7885
2017-08-08 | 7:30 |  |  |  | 10 |  |  | 0
2017-08-08 | 7:45 | 1.7475 | 5.6577 | 1 |  | 78.7295 | 0 | 23101.4712
2017-08-08 | 7:45 |  |  |  | 10 |  |  | 0
2017-08-08 | 8:00 | 1.7397 | 4.9005 | 1 | 10 | 78.8715 | 0 | 23143.1442
2017-08-08 | 8:00 |  |  |  | 10 |  |  | 0
2017-08-08 | 8:15 | 1.7273 | 4.2373 | 1 |  | 79.1 | 0 | 23210.2018
2017-08-08 | 8:15 |  |  |  | 10 |  |  | 0
2017-08-08 | 8:25 |  |  | 0 |  |  |  | 0
2017-08-08 | 8:30 | 1.7335 | 2.0919 | 0 | 1.5 | 79.7151 | 0 | 23390.6911
2017-08-08 | 8:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 8:45 | 1.7226 | 0 | 0 |  | 79.9022 | 0 | 23445.5746
2017-08-08 | 8:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 9:00 | 1.7507 | 0 | 0 | 1.5 | 80.5923 | 0 | 23648.0747
2017-08-08 | 9:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 9:15 | 1.7569 | 0 | 0 |  | 80.7863 | 0 | 23705.0133
2017-08-08 | 9:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 9:30 | 1.7421 | 0 | 0 | 1.5 | 81.1384 | 0 | 23808.3219
2017-08-08 | 9:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 9:45 | 1.7093 | 0 | 0 |  | 81.8809 | 0 | 24026.1993
2017-08-08 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 10:00 | 1.7249 | 0 | 0 | 1.5 | 83.1506 | 0 | 24398.7697
2017-08-08 | 10:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 10:15 | 1.6898 | 0 | 0 |  | 84.3016 | 0 | 24736.5086
2017-08-08 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 10:30 | 1.7031 | 0 | 0 | 1.5 | 85.1299 | 0 | 24979.5467
2017-08-08 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 10:45 | 1.6734 | 0 | 0 |  | 85.9699 | 0 | 25226.0279
2017-08-08 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 11:00 | 1.6937 | 0 | 0 | 1.5 | 87.0997 | 0 | 25557.5476
2017-08-08 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 11:15 | 1.7124 | 0 | 0 |  | 88.0059 | 0 | 25823.4402
2017-08-08 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 11:30 | 1.7163 | 0 | 0 | 1.5 | 89.6205 | 0 | 26297.217
2017-08-08 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 11:45 | 1.8466 | 0 | 0 |  | 86.9939 | 0 | 25526.5081
2017-08-08 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 12:00 | 1.6688 | 0 | 0 | 1.5 | 86.1082 | 0 | 25266.6196
2017-08-08 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 12:15 | 1.7257 | 0 | 0 |  | 87.9335 | 0 | 25802.2063
2017-08-08 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 12:30 | 1.8833 | 0 | 0 | 1.5 | 86.249 | 0 | 25307.9344
2017-08-08 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 12:45 | 1.7444 | 0 | 0 |  | 84.5667 | 0 | 24814.278
2017-08-08 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 13:00 | 1.6142 | 0 | 0 | 1.5 | 86.2366 | 0 | 25304.2697
2017-08-08 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 13:15 | 1.7858 | 0 | 0 |  | 87.0182 | 0 | 25533.6249
2017-08-08 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 13:30 | 1.8193 | 0 | 0 | 1.5 | 84.9532 | 0 | 24927.7099
2017-08-08 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 13:45 | 1.7631 | 0 | 0 |  | 83.4132 | 0 | 24475.8208
2017-08-08 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 14:00 | 1.6274 | 0 | 0 | 1.5 | 85.079 | 0 | 24964.608
2017-08-08 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 14:15 | 1.7436 | 0 | 0 |  | 85.9009 | 0 | 25205.7834
2017-08-08 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 14:30 | 1.7975 | 0 | 0 | 1.5 | 84.3617 | 0 | 24754.1381
2017-08-08 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 14:45 | 1.8185 | 0 | 0 |  | 83.2374 | 0 | 24424.2369
2017-08-08 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 15:00 | 1.65 | 0 | 0 | 1.5 | 83.4924 | 0 | 24499.065
2017-08-08 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 15:15 | 1.7397 | 0 | 0 |  | 86.6541 | 0 | 25426.7794
2017-08-08 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 15:30 | 1.8037 | 0 | 0 | 1.5 | 85.363 | 0 | 25047.954
2017-08-08 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 15:45 | 1.7912 | 0 | 0 |  | 83.6964 | 0 | 24558.9116
2017-08-08 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 16:00 | 1.5752 | 0 | 0 | 1.5 | 85.195 | 0 | 24998.6424
2017-08-08 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 16:15 | 1.7499 | 0 | 0 |  | 87.0465 | 0 | 25541.9395
2017-08-08 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 16:30 | 1.8357 | 0 | 0 | 1.5 | 85.5117 | 0 | 25091.5613
2017-08-08 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 16:45 | 1.7928 | 0 | 0 |  | 83.5116 | 0 | 24504.6819
2017-08-08 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 17:00 | 1.6477 | 0 | 0 | 1.5 | 85.4766 | 0 | 25081.2722
2017-08-08 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 17:15 | 1.8333 | 0 | 0 |  | 85.3351 | 0 | 25039.7559
2017-08-08 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 17:30 | 1.8185 | 0 | 0 | 1.5 | 82.9555 | 0 | 24341.5268
2017-08-08 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 17:45 | 1.6664 | 0 | 0 |  | 83.4123 | 0 | 24475.5632
2017-08-08 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 18:00 | 1.7124 | 0 | 0 | 1.5 | 85.0209 | 0 | 24947.5647
2017-08-08 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 18:15 | 1.8427 | 0 | 0 |  | 82.7114 | 0 | 24269.9023
2017-08-08 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 18:30 | 1.7553 | 0 | 0 | 1.5 | 81.5982 | 0 | 23943.2562
2017-08-08 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 18:45 | 1.7436 | 0 | 0 |  | 82.1782 | 0 | 24113.4207
2017-08-08 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 19:00 | 1.707 | 0 | 0 | 1.5 | 83.2998 | 0 | 24442.5428
2017-08-08 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 19:15 | 1.8427 | 0 | 0 |  | 82.4027 | 0 | 24179.2983
2017-08-08 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 19:30 | 1.7881 | 0 | 0 | 1.5 | 81.201 | 0 | 23826.6923
2017-08-08 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 19:45 | 1.7234 | 0 | 0 |  | 81.0234 | 0 | 23774.5782
2017-08-08 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 20:00 | 1.7312 | 0 | 0 | 1.5 | 81.1836 | 0 | 23821.586
2017-08-08 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 20:15 | 1.7358 | 0 | 0 |  | 81.2916 | 0 | 23853.2901
2017-08-08 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 20:30 | 1.7475 | 0 | 0 | 1.5 | 80.9741 | 0 | 23760.125
2017-08-08 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 20:45 | 1.7226 | 0 | 0 |  | 81.1972 | 0 | 23825.5819
2017-08-08 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 20:53 |  |  | 0 |  |  |  | 0
2017-08-08 | 21:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 0 | 0
2017-08-08 | 21:00 |  |  |  | 1.5 |  |  | 0
2017-08-08 | 21:15 | 0.03622 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 21:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 21:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 21:45 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 21:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 22:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 22:15 | 0.03232 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 22:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 22:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 22:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 22:45 |  |  |  | 0 |  |  | 0
2017-08-08 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 23:00 |  |  |  | 0 |  |  | 0
2017-08-08 | 23:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 23:15 |  |  |  | 0 |  |  | 0
2017-08-08 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 23:30 |  |  |  | 0 |  |  | 0
2017-08-08 | 23:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-08-08 | 23:45 |  |  |  | 0 |  |  | 0
2017-08-09 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 0:00 |  |  |  | 0 |  |  | 0
2017-08-09 | 0:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 0:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 1:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 1:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 3:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 4:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 4:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 4:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 5:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 5:15 | 1.8294 | 0 | 0 | 1.5 | 99.0859 | 0 | 29074.6452
2017-08-09 | 5:30 | 1.9433 | 0 | 0 | 1.5 | 96.5115 | 0 | 28319.2286
2017-08-09 | 5:45 | 1.9925 | 0 | 0 | 1.5 | 90.0488 | 0 | 26422.8767
2017-08-09 | 6:00 | 1.8591 | 0 | 0 | 1.5 | 86.0031 | 0 | 25235.7547
2017-08-09 | 6:15 | 1.8411 | 0 | 0 | 1.5 | 83.7444 | 0 | 24572.9953
2017-08-09 | 6:30 | 1.8029 | 0 | 0 | 1.5 | 82.1415 | 0 | 24102.6615
2017-08-09 | 6:45 | 1.8053 | 0 | 0 | 1.5 | 80.6886 | 0 | 23676.3535
2017-08-09 | 7:00 | 1.7975 | 0 | 0 | 1.5 | 79.5457 | 0 | 23340.97
2017-08-09 | 7:15 | 1.7678 | 0 | 0 | 1.5 | 79.0328 | 0 | 23190.4678
2017-08-09 | 7:30 | 1.7717 | 0 | 0 | 1.5 | 78.7228 | 0 | 23099.5123
2017-08-09 | 7:45 | 1.753 | 0 | 0 | 1.5 | 78.8397 | 0 | 23133.8112
2017-08-09 | 8:00 | 1.6961 | 0 | 0 | 1.5 | 79.5795 | 0 | 23350.9096
2017-08-09 | 8:15 | 1.7265 | 0 | 0 | 1.5 | 80.6405 | 0 | 23662.2299
2017-08-09 | 8:30 | 1.7499 | 0 | 0 | 1.5 | 80.9421 | 0 | 23750.7271
2017-08-09 | 8:45 | 1.7 | 0 | 0 | 1.5 | 81.5397 | 0 | 23926.0718
2017-08-09 | 9:00 | 1.6773 | 0 | 0 | 1.5 | 82.7194 | 0 | 24272.2462
2017-08-09 | 9:15 | 1.7452 | 0 | 0 | 1.5 | 83.4349 | 0 | 24482.1809
2017-08-09 | 9:30 | 1.7249 | 0 | 0 | 1.5 | 84.2812 | 0 | 24730.52
2017-08-09 | 9:45 | 1.6469 | 0 | 0 | 1.5 | 84.9554 | 0 | 24928.3323
2017-08-09 | 10:00 | 1.6883 | 0 | 0 | 1.5 | 85.8434 | 0 | 25188.9083
2017-08-09 | 10:15 | 1.6992 | 0 | 0 | 1.5 | 87.3289 | 0 | 25624.7932
2017-08-09 | 10:30 | 1.6477 | 0 | 0 | 1.5 | 89.0952 | 0 | 26143.0861
2017-08-09 | 10:45 | 1.675 | 0 | 0 | 1.5 | 91.0722 | 0 | 26723.1756
2017-08-09 | 11:00 | 1.8396 | 0 | 0 | 1.5 | 91.3223 | 0 | 26796.582
2017-08-09 | 11:15 | 1.8879 | 0 | 0 | 1.5 | 88.6173 | 0 | 26002.8372
2017-08-09 | 11:30 | 1.7124 | 0 | 0 | 1.5 | 87.3274 | 0 | 25624.3633
2017-08-09 | 11:45 | 1.6415 | 0 | 0 | 1.5 | 89.8156 | 0 | 26354.467
2017-08-09 | 12:00 | 1.8833 | 0 | 0 | 1.5 | 89.432 | 0 | 26241.9037
2017-08-09 | 12:15 | 1.8957 | 0 | 0 | 1.5 | 87.2493 | 0 | 25601.4301
2017-08-09 | 12:30 | 1.6929 | 0 | 0 | 1.5 | 86.5924 | 0 | 25408.6863
2017-08-09 | 12:45 | 1.7054 | 0 | 0 | 1.5 | 88.7105 | 0 | 26030.1871
2017-08-09 | 13:00 | 1.8388 | 0 | 0 | 1.5 | 87.5422 | 0 | 25687.3932
2017-08-09 | 13:15 | 1.7429 | 0 | 0 | 1.5 | 85.9999 | 0 | 25234.8392
2017-08-09 | 13:30 | 1.7616 | 0 | 0 | 1.5 | 85.2074 | 0 | 25002.2804
2017-08-09 | 13:45 | 1.604 | 0 | 0 | 1.5 | 87.5561 | 0 | 25691.4587
2017-08-09 | 14:00 | 1.7772 | 0 | 0 | 1.5 | 88.8391 | 0 | 26067.9425
2017-08-09 | 14:15 | 1.753 | 0 | 0 | 1.5 | 88.0446 | 0 | 25834.7971
2017-08-09 | 14:30 | 1.8045 | 0 | 0 | 1.5 | 86.7015 | 0 | 25440.7108
2017-08-09 | 14:45 | 1.7998 | 0 | 0 | 1.5 | 85.907 | 0 | 25207.5586
2017-08-09 | 15:00 | 1.7171 | 0 | 0 | 1.5 | 85.5663 | 0 | 25107.6016
2017-08-09 | 15:15 | 1.7928 | 0 | 0 | 1.5 | 85.6554 | 0 | 25133.756
2017-08-09 | 15:30 | 1.7795 | 0 | 0 | 1.5 | 85.3548 | 0 | 25045.5317
2017-08-09 | 15:45 | 1.7881 | 0 | 0 | 1.5 | 84.8949 | 0 | 24910.5795
2017-08-09 | 16:00 | 1.7709 | 0 | 0 | 1.5 | 84.1391 | 0 | 24688.82
2017-08-09 | 16:15 | 1.6259 | 0 | 0 | 1.5 | 85.1677 | 0 | 24990.6371
2017-08-09 | 16:30 | 1.6828 | 0 | 0 | 1.5 | 88.2686 | 0 | 25900.5315
2017-08-09 | 16:45 | 1.8599 | 0 | 0 | 1.5 | 87.3008 | 0 | 25616.5637
2017-08-09 | 17:00 | 1.7904 | 0 | 0 | 1.5 | 85.7093 | 0 | 25149.5454
2017-08-09 | 17:15 | 1.8107 | 0 | 0 | 1.5 | 84.7119 | 0 | 24856.9003
2017-08-09 | 17:30 | 1.7241 | 0 | 0 | 1.5 | 83.9238 | 0 | 24625.6446
2017-08-09 | 17:45 | 1.6282 | 0 | 0 | 1.5 | 86.5595 | 0 | 25399.0422
2017-08-09 | 18:00 | 1.817 | 0 | 0 | 1.5 | 86.5586 | 0 | 25398.7599
2017-08-09 | 18:15 | 1.8279 | 0 | 0 | 1.5 | 84.3664 | 0 | 24755.4993
2017-08-09 | 18:30 | 1.721 | 0 | 0 | 1.5 | 83.934 | 0 | 24628.6196
2017-08-09 | 18:45 | 1.6617 | 0 | 0 | 1.5 | 85.6455 | 0 | 25130.8256
2017-08-09 | 19:00 | 1.8497 | 0 | 0 | 1.5 | 84.0916 | 0 | 24674.8798
2017-08-09 | 19:15 | 1.7491 | 0 | 0 | 1.5 | 82.6087 | 0 | 24239.7628
2017-08-09 | 19:30 | 1.7319 | 0 | 0 | 1.5 | 83.2067 | 0 | 24415.2172
2017-08-09 | 19:45 | 1.7117 | 0 | 0 | 1.5 | 84.2122 | 0 | 24710.2576
2017-08-09 | 20:00 | 1.7288 | 0 | 0 | 1.5 | 84.5945 | 0 | 24822.4404
2017-08-09 | 20:15 | 1.87 | 0 | 0 | 1.5 | 82.2914 | 0 | 24146.6427
2017-08-09 | 20:30 | 1.7819 | 0 | 0 | 1.5 | 81.2018 | 0 | 23826.934
2017-08-09 | 20:45 | 1.7156 | 0 | 0 | 1.5 | 80.9255 | 0 | 23745.8401
2017-08-09 | 21:00 | 1.7741 | 0 | 0 | 1.5 | 81.005 | 0 | 23769.1717
2017-08-09 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 21:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 21:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 22:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 22:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 23:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 0:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 0:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 1:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 1:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 1:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 1:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 2:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 2:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 2:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 3:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 3:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 3:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 4:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 4:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 4:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 5:00 | 0.0292 | 0 | 0 | 1.5 | 25.375 | 0 | 7445.75
2017-08-10 | 5:15 | 1.831 | 0 | 0 | 1.5 | 98.8089 | 0 | 28993.3629
2017-08-10 | 5:30 | 1.9488 | 0 | 0 | 1.5 | 96.8293 | 0 | 28412.4943
2017-08-10 | 5:45 | 2.0003 | 0 | 0 | 1.5 | 91.4006 | 0 | 26819.5375
2017-08-10 | 6:00 | 1.87 | 0 | 0 | 1.5 | 87.5293 | 0 | 25683.5875
2017-08-10 | 6:15 | 1.8669 | 0 | 0 | 1.5 | 85.1077 | 0 | 24973.0232
2017-08-10 | 6:30 | 1.8458 | 0 | 0 | 1.5 | 83.2998 | 0 | 24442.536
2017-08-10 | 6:45 | 1.8068 | 0 | 0 | 1.5 | 81.8106 | 0 | 24005.5563
2017-08-10 | 7:00 | 1.7873 | 0 | 0 | 1.5 | 80.5881 | 0 | 23646.8367
2017-08-10 | 7:15 | 1.7631 | 0 | 0 | 1.5 | 80.0689 | 0 | 23494.5009
2017-08-10 | 7:30 | 1.7717 | 0 | 0 | 1.5 | 79.7135 | 0 | 23390.2211
2017-08-10 | 7:45 | 1.7717 | 0 | 0 | 1.5 | 79.5311 | 0 | 23336.7053
2017-08-10 | 8:00 | 1.7366 | 0 | 0 | 1.5 | 79.5423 | 0 | 23339.9758
2017-08-10 | 8:15 | 1.7226 | 0 | 0 | 1.5 | 80.2129 | 0 | 23536.7652
2017-08-10 | 8:30 | 1.7031 | 0 | 0 | 1.5 | 80.7663 | 0 | 23699.1435
2017-08-10 | 8:45 | 1.6992 | 0 | 0 | 1.5 | 81.778 | 0 | 23996.0017
2017-08-10 | 9:00 | 1.6953 | 0 | 0 | 1.5 | 82.8006 | 0 | 24296.0524
2017-08-10 | 9:15 | 1.6961 | 0 | 0 | 1.5 | 83.8856 | 0 | 24614.4197
2017-08-10 | 9:30 | 1.753 | 0 | 0 | 1.5 | 84.5144 | 0 | 24798.9543
2017-08-10 | 9:45 | 1.714 | 0 | 0 | 1.5 | 85.3039 | 0 | 25030.6042
2017-08-10 | 10:00 | 1.7358 | 0 | 0 | 1.5 | 86.2677 | 0 | 25313.4171
2017-08-10 | 10:15 | 1.6867 | 0 | 0 | 1.5 | 87.6957 | 0 | 25732.4178
2017-08-10 | 10:30 | 1.6805 | 0 | 0 | 1.5 | 88.3648 | 0 | 25928.7614
2017-08-10 | 10:45 | 1.7413 | 0 | 0 | 1.5 | 89.1094 | 0 | 26147.2343
2017-08-10 | 11:00 | 1.7226 | 0 | 0 | 1.5 | 90.7 | 0 | 26613.9794
2017-08-10 | 11:15 | 1.6922 | 0 | 0 | 1.5 | 92.0182 | 0 | 27000.7543
2017-08-10 | 11:30 | 1.8918 | 0 | 0 | 1.5 | 89.9507 | 0 | 26394.0916
2017-08-10 | 11:45 | 1.7249 | 0 | 0 | 1.5 | 88.4021 | 0 | 25939.7084
2017-08-10 | 12:00 | 1.6352 | 0 | 0 | 1.5 | 90.0349 | 0 | 26418.82
2017-08-10 | 12:15 | 1.7998 | 0 | 0 | 1.5 | 90.3921 | 0 | 26523.6353
2017-08-10 | 12:30 | 1.8263 | 0 | 0 | 1.5 | 88.0118 | 0 | 25825.1685
2017-08-10 | 12:45 | 1.6789 | 0 | 0 | 1.5 | 88.1388 | 0 | 25862.4293
2017-08-10 | 13:00 | 1.7592 | 0 | 0 | 1.5 | 89.5769 | 0 | 26284.4341
2017-08-10 | 13:15 | 1.8934 | 0 | 0 | 1.5 | 88.0549 | 0 | 25837.8103
2017-08-10 | 13:30 | 1.7124 | 0 | 0 | 1.5 | 86.6867 | 0 | 25436.3677
2017-08-10 | 13:45 | 1.6259 | 0 | 0 | 1.5 | 89.1501 | 0 | 26159.2
2017-08-10 | 14:00 | 1.7663 | 0 | 0 | 1.5 | 89.068 | 0 | 26135.103
2017-08-10 | 14:15 | 1.824 | 0 | 0 | 1.5 | 87.349 | 0 | 25630.7055
2017-08-10 | 14:30 | 1.7928 | 0 | 0 | 1.5 | 85.6829 | 0 | 25141.8221
2017-08-10 | 14:45 | 1.6633 | 0 | 0 | 1.5 | 86.1526 | 0 | 25279.6197
2017-08-10 | 15:00 | 1.7616 | 0 | 0 | 1.5 | 88.32 | 0 | 25915.5979
2017-08-10 | 15:15 | 1.7897 | 0 | 0 | 1.5 | 87.8946 | 0 | 25790.7825
2017-08-10 | 15:30 | 1.8497 | 0 | 0 | 1.5 | 86.0816 | 0 | 25258.7865
2017-08-10 | 15:45 | 1.7585 | 0 | 0 | 1.5 | 85.1118 | 0 | 24974.223
2017-08-10 | 16:00 | 1.6454 | 0 | 0 | 1.5 | 85.1386 | 0 | 24982.0943
2017-08-10 | 16:15 | 1.746 | 0 | 0 | 1.5 | 87.3158 | 0 | 25620.9425
2017-08-10 | 16:30 | 1.8294 | 0 | 0 | 1.5 | 85.874 | 0 | 25197.8919
2017-08-10 | 16:45 | 1.7054 | 0 | 0 | 1.5 | 84.904 | 0 | 24913.2703
2017-08-10 | 17:00 | 1.6812 | 0 | 0 | 1.5 | 86.9501 | 0 | 25513.656
2017-08-10 | 17:15 | 1.8489 | 0 | 0 | 1.5 | 85.8739 | 0 | 25197.8696
2017-08-10 | 17:30 | 1.8092 | 0 | 0 | 1.5 | 83.6784 | 0 | 24553.6419
2017-08-10 | 17:45 | 1.6695 | 0 | 0 | 1.5 | 83.6611 | 0 | 24548.5576
2017-08-10 | 18:00 | 1.6688 | 0 | 0 | 1.5 | 85.1077 | 0 | 24973.0232
2017-08-10 | 18:15 | 1.8614 | 0 | 0 | 1.5 | 83.8418 | 0 | 24601.5652
2017-08-10 | 18:30 | 1.7577 | 0 | 0 | 1.5 | 82.6309 | 0 | 24246.2728
2017-08-10 | 18:45 | 1.6945 | 0 | 0 | 1.5 | 83.2266 | 0 | 24421.0758
2017-08-10 | 19:00 | 1.7 | 0 | 0 | 1.5 | 84.0452 | 0 | 24661.2641
2017-08-10 | 19:15 | 1.7483 | 0 | 0 | 1.5 | 84.3996 | 0 | 24765.2623
2017-08-10 | 19:30 | 1.7616 | 0 | 0 | 1.5 | 84.8233 | 0 | 24889.5651
2017-08-10 | 19:45 | 1.7109 | 0 | 0 | 1.5 | 84.7652 | 0 | 24872.5242
2017-08-10 | 20:00 | 1.7382 | 0 | 0 | 1.5 | 84.4951 | 0 | 24793.2659
2017-08-10 | 20:15 | 1.778 | 0 | 0 | 1.5 | 84.1377 | 0 | 24688.4171
2017-08-10 | 20:30 | 1.7858 | 0 | 0 | 1.5 | 83.8577 | 0 | 24606.2328
2017-08-10 | 20:45 | 1.7444 | 0 | 0 | 1.5 | 83.2558 | 0 | 24429.6366
2017-08-10 | 21:00 | 1.7686 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 21:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 22:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-10 | 23:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 0:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 0:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 0:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 0:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 1:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 1:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 1:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 1:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 2:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 2:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 2:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 2:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 3:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 3:15 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 3:30 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 3:45 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 4:00 | 0.0292 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 4:15 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 4:30 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 4:45 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 5:00 | 0.02998 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 5:15 | 1.8404 | 0 | 0 | 1.5 | 98.9887 | 0 | 29046.1064
2017-08-11 | 5:30 | 1.9519 | 0 | 0 | 1.5 | 96.9717 | 0 | 28454.2592
2017-08-11 | 5:45 | 2.0603 | 0 | 0 | 1.5 | 90.6518 | 0 | 26599.8332
2017-08-11 | 6:00 | 1.8848 | 0 | 0 | 1.5 | 86.0099 | 0 | 25237.7741
2017-08-11 | 6:15 | 1.8224 | 0 | 0 | 1.5 | 83.9272 | 0 | 24626.6519
2017-08-11 | 6:30 | 1.7819 | 0 | 0 | 1.5 | 83.1373 | 0 | 24394.8565
2017-08-11 | 6:45 | 1.7819 | 0 | 0 | 1.5 | 82.2085 | 0 | 24122.3192
2017-08-11 | 7:00 | 1.7959 | 0 | 0 | 1.5 | 81.3196 | 0 | 23861.4993
2017-08-11 | 7:15 | 1.7811 | 0 | 0 | 1.5 | 80.5619 | 0 | 23639.1714
2017-08-11 | 7:30 | 1.7452 | 0 | 0 | 1.5 | 80.3732 | 0 | 23583.7886
2017-08-11 | 7:45 | 1.7397 | 0 | 0 | 1.5 | 80.4445 | 0 | 23604.7047
2017-08-11 | 8:00 | 1.7374 | 0 | 0 | 1.5 | 80.4542 | 0 | 23607.5633
2017-08-11 | 8:15 | 1.7249 | 0 | 0 | 1.5 | 80.6753 | 0 | 23672.4471
2017-08-11 | 8:30 | 1.7678 | 0 | 0 | 1.5 | 80.8608 | 0 | 23726.874
2017-08-11 | 8:45 | 1.7234 | 0 | 0 | 1.5 | 81.1298 | 0 | 23805.7899
2017-08-11 | 9:00 | 1.7031 | 0 | 0 | 1.5 | 81.6491 | 0 | 23958.1882
2017-08-11 | 9:15 | 1.7234 | 0 | 0 | 1.5 | 82.3653 | 0 | 24168.3355
2017-08-11 | 9:30 | 1.7382 | 0 | 0 | 1.5 | 83.3602 | 0 | 24460.2665
2017-08-11 | 9:45 | 1.6976 | 0 | 0 | 1.5 | 84.0095 | 0 | 24650.7826
2017-08-11 | 10:00 | 1.7241 | 0 | 0 | 1.5 | 84.5469 | 0 | 24808.4866
2017-08-11 | 10:15 | 1.7624 | 0 | 0 | 1.5 | 85.4103 | 0 | 25061.8138
2017-08-11 | 10:30 | 1.6875 | 0 | 0 | 1.5 | 86.1846 | 0 | 25289.0132
2017-08-11 | 10:45 | 1.6945 | 0 | 0 | 1.5 | 87.1767 | 0 | 25580.1492
2017-08-11 | 11:00 | 1.7101 | 0 | 0 | 1.5 | 88.16 | 0 | 25868.6661
2017-08-11 | 11:15 | 1.6961 | 0 | 0 | 1.5 | 89.3945 | 0 | 26230.9142
2017-08-11 | 11:30 | 1.7889 | 0 | 0 | 1.5 | 90.1095 | 0 | 26440.7145
2017-08-11 | 11:45 | 1.7709 | 0 | 0 | 1.5 | 90.5787 | 0 | 26578.3844
2017-08-11 | 12:00 | 1.6695 | 0 | 0 | 1.5 | 91.61 | 0 | 26881.0029
2017-08-11 | 12:15 | 1.8583 | 0 | 0 | 1.5 | 91.1731 | 0 | 26752.7981
2017-08-11 | 12:30 | 1.7577 | 0 | 0 | 1.5 | 88.2243 | 0 | 25887.5294
2017-08-11 | 12:45 | 1.6766 | 0 | 0 | 1.5 | 88.7107 | 0 | 26030.2499
2017-08-11 | 13:00 | 1.7296 | 0 | 0 | 1.5 | 89.7448 | 0 | 26333.7011
2017-08-11 | 13:15 | 1.8833 | 0 | 0 | 1.5 | 87.453 | 0 | 25661.2053
2017-08-11 | 13:30 | 1.7039 | 0 | 0 | 1.5 | 86.3236 | 0 | 25329.8109
2017-08-11 | 13:45 | 1.7078 | 0 | 0 | 1.5 | 87.6339 | 0 | 25714.2889
2017-08-11 | 14:00 | 1.7943 | 0 | 0 | 1.5 | 88.0576 | 0 | 25838.6029
2017-08-11 | 14:15 | 1.7452 | 0 | 0 | 1.5 | 86.2282 | 0 | 25301.8073
2017-08-11 | 14:30 | 1.7148 | 0 | 0 | 1.5 | 87.5209 | 0 | 25681.1274
2017-08-11 | 14:45 | 1.8528 | 0 | 0 | 1.5 | 87.8317 | 0 | 25772.3402
2017-08-11 | 15:00 | 1.799 | 0 | 0 | 1.5 | 85.9204 | 0 | 25211.4988
2017-08-11 | 15:15 | 1.6617 | 0 | 0 | 1.5 | 86.8022 | 0 | 25470.2546
2017-08-11 | 15:30 | 1.7624 | 0 | 0 | 1.5 | 88.499 | 0 | 25968.1486
2017-08-11 | 15:45 | 1.8825 | 0 | 0 | 1.5 | 86.4263 | 0 | 25359.9501
2017-08-11 | 16:00 | 1.7351 | 0 | 0 | 1.5 | 85.8208 | 0 | 25182.2794
2017-08-11 | 16:15 | 1.7624 | 0 | 0 | 1.5 | 87.4481 | 0 | 25659.7746
2017-08-11 | 16:30 | 1.8778 | 0 | 0 | 1.5 | 85.2578 | 0 | 25017.0783
2017-08-11 | 16:45 | 1.7062 | 0 | 0 | 1.5 | 84.4735 | 0 | 24786.9484
2017-08-11 | 17:00 | 1.6664 | 0 | 0 | 1.5 | 86.2465 | 0 | 25307.1732
2017-08-11 | 17:15 | 1.817 | 0 | 0 | 1.5 | 86.2498 | 0 | 25308.1606
2017-08-11 | 17:30 | 1.8131 | 0 | 0 | 1.5 | 84.0646 | 0 | 24666.9616
2017-08-11 | 17:45 | 1.7085 | 0 | 0 | 1.5 | 83.5614 | 0 | 24519.2937
2017-08-11 | 18:00 | 1.7187 | 0 | 0 | 1.5 | 84.2295 | 0 | 24715.3307
2017-08-11 | 18:15 | 1.7569 | 0 | 0 | 1.5 | 84.797 | 0 | 24881.8617
2017-08-11 | 18:30 | 1.792 | 0 | 0 | 1.5 | 85.2735 | 0 | 25021.6675
2017-08-11 | 18:45 | 1.7912 | 0 | 0 | 1.5 | 83.2717 | 0 | 24434.293
2017-08-11 | 19:00 | 1.7741 | 0 | 0 | 1.5 | 82.0984 | 0 | 24090.0083
2017-08-11 | 19:15 | 1.7483 | 0 | 0 | 1.5 | 82.4472 | 0 | 24192.3565
2017-08-11 | 19:30 | 1.7577 | 0 | 0 | 1.5 | 82.2726 | 0 | 24141.1241
2017-08-11 | 19:45 | 1.7741 | 0 | 0 | 1.5 | 82.1652 | 0 | 24109.6237
2017-08-11 | 20:00 | 1.7413 | 0 | 0 | 1.5 | 81.8853 | 0 | 24027.4843
2017-08-11 | 20:15 | 1.7655 | 0 | 0 | 1.5 | 81.4107 | 0 | 23888.236
2017-08-11 | 20:30 | 1.7444 | 0 | 0 | 1.5 | 80.979 | 0 | 23761.5579
2017-08-11 | 20:45 | 1.7959 | 0 | 0 | 1.5 | 80.4409 | 0 | 23603.6613
2017-08-11 | 21:00 | 1.7772 | 0 | 0 | 1.5 | 79.7871 | 0 | 23411.8154
2017-08-11 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 21:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 21:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 22:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 22:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 22:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 22:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 23:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 23:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 23:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 0:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 0:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 0:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 1:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 1:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 1:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 2:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 2:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 2:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 5:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 5:15 | 1.902 | 0 | 0 | 1.5 | 97.2646 | 0 | 28540.2068
2017-08-12 | 5:30 | 1.962 | 0 | 0 | 1.5 | 93.0269 | 0 | 27296.7618
2017-08-12 | 5:45 | 1.955 | 0 | 0 | 1.5 | 87.9613 | 0 | 25810.3507
2017-08-12 | 6:00 | 1.902 | 0 | 0 | 1.5 | 84.2461 | 0 | 24720.2222
2017-08-12 | 6:15 | 1.792 | 0 | 0 | 1.5 | 82.3983 | 0 | 24178.0111
2017-08-12 | 6:30 | 1.8076 | 0 | 0 | 1.5 | 81.0378 | 0 | 23778.798
2017-08-12 | 6:45 | 1.7631 | 0 | 0 | 1.5 | 79.9862 | 0 | 23470.2294
2017-08-12 | 7:00 | 1.7655 | 0 | 0 | 1.5 | 79.4897 | 0 | 23324.538
2017-08-12 | 7:15 | 1.7592 | 0 | 0 | 1.5 | 79.1784 | 0 | 23233.2042
2017-08-12 | 7:30 | 1.7725 | 0 | 0 | 1.5 | 79.0294 | 0 | 23189.474
2017-08-12 | 7:45 | 1.7319 | 0 | 0 | 1.5 | 78.683 | 0 | 23087.8532
2017-08-12 | 8:00 | 1.7756 | 0 | 0 | 1.5 | 78.3955 | 0 | 23003.4775
2017-08-12 | 8:15 | 1.7686 | 0 | 0 | 1.5 | 78.2811 | 0 | 22969.9219
2017-08-12 | 8:30 | 1.7764 | 0 | 0 | 1.5 | 78.2715 | 0 | 22967.0809
2017-08-12 | 8:45 | 1.7592 | 0 | 0 | 1.5 | 78.149 | 0 | 22931.1433
2017-08-12 | 9:00 | 1.7624 | 0 | 0 | 1.5 | 78.1011 | 0 | 22917.0822
2017-08-12 | 9:15 | 1.7577 | 0 | 0 | 1.5 | 78.0942 | 0 | 22915.0763
2017-08-12 | 9:30 | 1.7702 | 0 | 0 | 1.5 | 78.0656 | 0 | 22906.6901
2017-08-12 | 9:45 | 1.7413 | 0 | 0 | 1.5 | 77.8017 | 0 | 22829.2429
2017-08-12 | 10:00 | 1.7374 | 0 | 0 | 1.5 | 77.7391 | 0 | 22810.8857
2017-08-12 | 10:15 | 1.767 | 0 | 0 | 1.5 | 77.6674 | 0 | 22789.8445
2017-08-12 | 10:30 | 1.7717 | 0 | 0 | 1.5 | 77.6253 | 0 | 22777.4935
2017-08-12 | 10:45 | 1.7585 | 0 | 0 | 1.5 | 77.6881 | 0 | 22795.9023
2017-08-12 | 11:00 | 1.7647 | 0 | 0 | 1.5 | 77.6694 | 0 | 22790.4331
2017-08-12 | 11:15 | 1.7265 | 0 | 0 | 1.5 | 77.5716 | 0 | 22761.7379
2017-08-12 | 11:30 | 1.7561 | 0 | 0 | 1.5 | 77.6223 | 0 | 22776.5868
2017-08-12 | 11:45 | 1.7413 | 0 | 0 | 1.5 | 77.7213 | 0 | 22805.6585
2017-08-12 | 12:00 | 1.7577 | 0 | 0 | 1.5 | 77.6215 | 0 | 22776.3788
2017-08-12 | 12:15 | 1.7546 | 0 | 0 | 1.5 | 77.7704 | 0 | 22820.0688
2017-08-12 | 12:30 | 1.753 | 0 | 0 | 1.5 | 77.6501 | 0 | 22784.7603
2017-08-12 | 12:45 | 1.76 | 0 | 0 | 1.5 | 77.6973 | 0 | 22798.6177
2017-08-12 | 13:00 | 1.7538 | 0 | 0 | 1.5 | 77.5751 | 0 | 22762.7428
2017-08-12 | 13:15 | 1.767 | 0 | 0 | 1.5 | 77.4261 | 0 | 22719.0194
2017-08-12 | 13:30 | 1.753 | 0 | 0 | 1.5 | 77.7273 | 0 | 22807.4091
2017-08-12 | 13:45 | 1.746 | 0 | 0 | 1.5 | 77.8743 | 0 | 22850.5464
2017-08-12 | 14:00 | 1.7351 | 0 | 0 | 1.5 | 78.0059 | 0 | 22889.1545
2017-08-12 | 14:15 | 1.7452 | 0 | 0 | 1.5 | 78.0744 | 0 | 22909.269
2017-08-12 | 14:30 | 1.7436 | 0 | 0 | 1.5 | 78.1829 | 0 | 22941.0943
2017-08-12 | 14:45 | 1.7468 | 0 | 0 | 1.5 | 78.2335 | 0 | 22955.9568
2017-08-12 | 15:00 | 1.7444 | 0 | 0 | 1.5 | 78.257 | 0 | 22962.8341
2017-08-12 | 15:15 | 1.7351 | 0 | 0 | 1.5 | 78.3024 | 0 | 22976.1587
2017-08-12 | 15:30 | 1.7655 | 0 | 0 | 1.5 | 78.3396 | 0 | 22987.0901
2017-08-12 | 15:45 | 1.7608 | 0 | 0 | 1.5 | 78.3968 | 0 | 23003.8645
2017-08-12 | 16:00 | 1.7553 | 0 | 0 | 1.5 | 78.4022 | 0 | 23005.4541
2017-08-12 | 16:15 | 1.7468 | 0 | 0 | 1.5 | 78.3924 | 0 | 23002.5708
2017-08-12 | 16:30 | 1.7429 | 0 | 0 | 1.5 | 78.395 | 0 | 23003.332
2017-08-12 | 16:45 | 1.7655 | 0 | 0 | 1.5 | 78.3504 | 0 | 22990.2603
2017-08-12 | 17:00 | 1.7538 | 0 | 0 | 1.5 | 78.3694 | 0 | 22995.8187
2017-08-12 | 17:15 | 1.7468 | 0 | 0 | 1.5 | 78.3312 | 0 | 22984.6007
2017-08-12 | 17:30 | 1.7499 | 0 | 0 | 1.5 | 78.2697 | 0 | 22966.566
2017-08-12 | 17:45 | 1.7608 | 0 | 0 | 1.5 | 78.1672 | 0 | 22936.4804
2017-08-12 | 18:00 | 1.7616 | 0 | 0 | 1.5 | 78.1379 | 0 | 22927.895
2017-08-12 | 18:15 | 1.7444 | 0 | 0 | 1.5 | 78.1196 | 0 | 22922.522
2017-08-12 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 78.0241 | 0 | 22894.5052
2017-08-12 | 18:45 | 1.7507 | 0 | 0 | 1.5 | 77.8078 | 0 | 22831.0363
2017-08-12 | 19:00 | 1.76 | 0 | 0 | 1.5 | 77.5239 | 0 | 22747.7349
2017-08-12 | 19:15 | 1.7631 | 0 | 0 | 1.5 | 77.2608 | 0 | 22670.5361
2017-08-12 | 19:30 | 1.7616 | 0 | 0 | 1.5 | 77.044 | 0 | 22606.9082
2017-08-12 | 19:45 | 1.7522 | 0 | 0 | 1.5 | 76.8591 | 0 | 22552.6492
2017-08-12 | 20:00 | 1.7616 | 0 | 0 | 1.5 | 76.9583 | 0 | 22581.7543
2017-08-12 | 20:15 | 1.7569 | 0 | 0 | 1.5 | 77.0886 | 0 | 22620.0022
2017-08-12 | 20:30 | 1.7226 | 0 | 0 | 1.5 | 76.8945 | 0 | 22563.048
2017-08-12 | 20:45 | 1.7639 | 0 | 0 | 1.5 | 76.7468 | 0 | 22519.7183
2017-08-12 | 21:00 | 1.7624 | 0 | 0 | 1.5 | 76.7439 | 0 | 22518.8632
2017-08-12 | 21:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 23:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 1:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 1:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 2:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 2:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 3:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 3:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 5:15 | 2.1625 | 0 | 0 | 1.5 | 91.0295 | 0 | 26710.6705
2017-08-13 | 5:30 | 1.9355 | 0 | 0 | 1.5 | 85.622 | 0 | 25123.9326
2017-08-13 | 5:45 | 1.8606 | 0 | 0 | 1.5 | 82.2951 | 0 | 24147.7395
2017-08-13 | 6:00 | 1.806 | 0 | 0 | 1.5 | 80.4392 | 0 | 23603.1713
2017-08-13 | 6:15 | 1.7733 | 0 | 0 | 1.5 | 79.8097 | 0 | 23418.4486
2017-08-13 | 6:30 | 1.7881 | 0 | 0 | 1.5 | 78.9573 | 0 | 23168.3319
2017-08-13 | 6:45 | 1.7709 | 0 | 0 | 1.5 | 78.8368 | 0 | 23132.9561
2017-08-13 | 7:00 | 1.7569 | 0 | 0 | 1.5 | 78.2995 | 0 | 22975.3013
2017-08-13 | 7:15 | 1.7858 | 0 | 0 | 1.5 | 78.2666 | 0 | 22965.6505
2017-08-13 | 7:30 | 1.7397 | 0 | 0 | 1.5 | 78.008 | 0 | 22889.7725
2017-08-13 | 7:45 | 1.7608 | 0 | 0 | 1.5 | 77.7986 | 0 | 22828.3318
2017-08-13 | 8:00 | 1.753 | 0 | 0 | 1.5 | 77.9952 | 0 | 22886.0069
2017-08-13 | 8:15 | 1.7429 | 0 | 0 | 1.5 | 77.6976 | 0 | 22798.6961
2017-08-13 | 8:30 | 1.778 | 0 | 0 | 1.5 | 77.8041 | 0 | 22829.9348
2017-08-13 | 8:45 | 1.7093 | 0 | 0 | 1.5 | 77.7281 | 0 | 22807.6351
2017-08-13 | 9:00 | 1.7678 | 0 | 0 | 1.5 | 77.8292 | 0 | 22837.3133
2017-08-13 | 9:15 | 1.7663 | 0 | 0 | 1.5 | 77.7226 | 0 | 22806.0368
2017-08-13 | 9:30 | 1.7475 | 0 | 0 | 1.5 | 77.5273 | 0 | 22748.731
2017-08-13 | 9:45 | 1.721 | 0 | 0 | 1.5 | 77.4721 | 0 | 22732.5408
2017-08-13 | 10:00 | 1.7741 | 0 | 0 | 1.5 | 77.5823 | 0 | 22764.872
2017-08-13 | 10:15 | 1.7413 | 0 | 0 | 1.5 | 77.3547 | 0 | 22698.065
2017-08-13 | 10:30 | 1.7748 | 0 | 0 | 1.5 | 77.4612 | 0 | 22729.3351
2017-08-13 | 10:45 | 1.7709 | 0 | 0 | 1.5 | 76.9555 | 0 | 22580.9283
2017-08-13 | 11:00 | 1.7624 | 0 | 0 | 1.5 | 76.7846 | 0 | 22530.7908
2017-08-13 | 11:15 | 1.7452 | 0 | 0 | 1.5 | 76.5737 | 0 | 22468.8979
2017-08-13 | 11:30 | 1.7319 | 0 | 0 | 1.5 | 76.5919 | 0 | 22474.2597
2017-08-13 | 11:45 | 1.7491 | 0 | 0 | 1.5 | 76.6714 | 0 | 22497.5823
2017-08-13 | 12:00 | 1.7725 | 0 | 0 | 1.5 | 76.8041 | 0 | 22536.5241
2017-08-13 | 12:15 | 1.7249 | 0 | 0 | 1.5 | 76.7028 | 0 | 22506.8077
2017-08-13 | 12:30 | 1.7553 | 0 | 0 | 1.5 | 76.6149 | 0 | 22481.0004
2017-08-13 | 12:45 | 1.7624 | 0 | 0 | 1.5 | 76.6491 | 0 | 22491.0474
2017-08-13 | 13:00 | 1.767 | 0 | 0 | 1.5 | 76.5042 | 0 | 22448.5237
2017-08-13 | 13:15 | 1.739 | 0 | 0 | 1.5 | 76.7502 | 0 | 22520.6942
2017-08-13 | 13:30 | 1.767 | 0 | 0 | 1.5 | 76.6292 | 0 | 22485.1844
2017-08-13 | 13:45 | 1.753 | 0 | 0 | 1.5 | 76.6707 | 0 | 22497.3696
2017-08-13 | 14:00 | 1.7592 | 0 | 0 | 1.5 | 76.7691 | 0 | 22526.235
2017-08-13 | 14:15 | 1.7686 | 0 | 0 | 1.5 | 76.656 | 0 | 22493.0579
2017-08-13 | 14:30 | 1.7569 | 0 | 0 | 1.5 | 76.5384 | 0 | 22458.5484
2017-08-13 | 14:45 | 1.7483 | 0 | 0 | 1.5 | 76.436 | 0 | 22428.4943
2017-08-13 | 15:00 | 1.739 | 0 | 0 | 1.5 | 76.7249 | 0 | 22513.2664
2017-08-13 | 15:15 | 1.7655 | 0 | 0 | 1.5 | 76.7235 | 0 | 22512.8814
2017-08-13 | 15:30 | 1.7413 | 0 | 0 | 1.5 | 76.7519 | 0 | 22521.2071
2017-08-13 | 15:45 | 1.7234 | 0 | 0 | 1.5 | 76.8035 | 0 | 22536.3495
2017-08-13 | 16:00 | 1.7647 | 0 | 0 | 1.5 | 76.915 | 0 | 22569.0477
2017-08-13 | 16:15 | 1.7483 | 0 | 0 | 1.5 | 77.0634 | 0 | 22612.6145
2017-08-13 | 16:30 | 1.7491 | 0 | 0 | 1.5 | 76.9544 | 0 | 22580.6238
2017-08-13 | 16:45 | 1.7608 | 0 | 0 | 1.5 | 77.0519 | 0 | 22609.2231
2017-08-13 | 17:00 | 1.767 | 0 | 0 | 1.5 | 76.938 | 0 | 22575.8107
2017-08-13 | 17:15 | 1.753 | 0 | 0 | 1.5 | 77.0634 | 0 | 22612.5966
2017-08-13 | 17:30 | 1.7655 | 0 | 0 | 1.5 | 77.0896 | 0 | 22620.2821
2017-08-13 | 17:45 | 1.7234 | 0 | 0 | 1.5 | 76.9417 | 0 | 22576.8943
2017-08-13 | 18:00 | 1.7733 | 0 | 0 | 1.5 | 76.8746 | 0 | 22557.1982
2017-08-13 | 18:15 | 1.7717 | 0 | 0 | 1.5 | 76.8792 | 0 | 22558.5662
2017-08-13 | 18:30 | 1.7631 | 0 | 0 | 1.5 | 76.9029 | 0 | 22565.5172
2017-08-13 | 18:45 | 1.76 | 0 | 0 | 1.5 | 76.8826 | 0 | 22559.5488
2017-08-13 | 19:00 | 1.7631 | 0 | 0 | 1.5 | 76.9728 | 0 | 22586.0146
2017-08-13 | 19:15 | 1.7748 | 0 | 0 | 1.5 | 76.8172 | 0 | 22540.3589
2017-08-13 | 19:30 | 1.7748 | 0 | 0 | 1.5 | 76.5467 | 0 | 22460.9753
2017-08-13 | 19:45 | 1.7647 | 0 | 0 | 1.5 | 76.3299 | 0 | 22397.3876
2017-08-13 | 20:00 | 1.7265 | 0 | 0 | 1.5 | 76.2021 | 0 | 22359.8607
2017-08-13 | 20:15 | 1.7663 | 0 | 0 | 1.5 | 76.3055 | 0 | 22390.2218
2017-08-13 | 20:30 | 1.7655 | 0 | 0 | 1.5 | 76.0396 | 0 | 22312.1812
2017-08-13 | 20:45 | 1.7468 | 0 | 0 | 1.5 | 75.9364 | 0 | 22281.9164
2017-08-13 | 21:00 | 1.7834 | 0 | 0 | 1.5 | 76.0372 | 0 | 22311.4761
2017-08-13 | 21:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 21:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 22:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 22:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-13 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 0:15 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 0:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 0:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 0:45 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 0:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 1:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 1:15 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 1:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 1:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 1:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 1:45 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 1:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 2:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 2:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 2:15 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 2:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 2:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 2:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 2:45 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 2:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 3:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 3:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 3:15 | 0.03544 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 3:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 3:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 3:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 3:45 | 0.03622 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 3:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 4:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 4:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 4:15 | 0.03622 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 4:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 4:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 4:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 4:45 | 0.037 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 4:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 5:00 | 0.037 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-08-14 | 5:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 5:15 | 2.2904 | 0 | 0 |  | 87.3519 | 0 | 25631.5426
2017-08-14 | 5:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 5:30 | 1.8638 | 0 | 0 | 1.5 | 81.7388 | 0 | 23984.4993
2017-08-14 | 5:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 5:45 | 1.8076 | 0 | 0 |  | 80.0648 | 0 | 23493.2967
2017-08-14 | 5:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 6:00 | 1.7351 | 0 | 0 | 1.5 | 79.8494 | 0 | 23430.0963
2017-08-14 | 6:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 6:15 | 1.7772 | 0 | 0 |  | 79.7386 | 0 | 23397.5706
2017-08-14 | 6:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 6:30 | 1.7647 | 0 | 0 | 1.5 | 79.7059 | 0 | 23387.9913
2017-08-14 | 6:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 6:45 | 1.7327 | 0 | 0 |  | 80.3419 | 0 | 23574.6145
2017-08-14 | 6:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 7:00 | 1.7374 | 0 | 0 | 1.5 | 80.7277 | 0 | 23687.8022
2017-08-14 | 7:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 7:15 | 1.7663 | 0 | 0 |  | 80.6966 | 0 | 23678.6954
2017-08-14 | 7:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 7:30 | 1.6906 | 0 | 0 | 1.5 | 81.3371 | 0 | 23866.6305
2017-08-14 | 7:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 7:45 | 1.7046 | 0 | 0 |  | 82.1071 | 0 | 24092.5784
2017-08-14 | 7:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 8:00 | 1.8099 | 0 | 0 | 1.5 | 81.7239 | 0 | 23980.1181
2017-08-14 | 8:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 8:15 | 1.7904 | 0 | 0 |  | 80.7585 | 0 | 23696.8621
2017-08-14 | 8:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 8:30 | 1.785 | 0 | 0 | 1.5 | 80.3946 | 0 | 23590.0659
2017-08-14 | 8:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 8:45 | 1.7561 | 0 | 0 |  | 80.1729 | 0 | 23525.0277
2017-08-14 | 8:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 9:00 | 1.7826 | 0 | 0 | 1.5 | 80.312 | 0 | 23565.8478
2017-08-14 | 9:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 9:15 | 1.753 | 0 | 0 |  | 80.3268 | 0 | 23570.1773
2017-08-14 | 9:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 9:30 | 1.746 | 0 | 0 | 1.5 | 80.1753 | 0 | 23525.7261
2017-08-14 | 9:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 9:45 | 1.7592 | 0 | 0 |  | 80.4221 | 0 | 23598.1431
2017-08-14 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 10:00 | 1.7655 | 0 | 0 | 1.5 | 80.2263 | 0 | 23540.6783
2017-08-14 | 10:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 10:15 | 1.7421 | 0 | 0 |  | 80.634 | 0 | 23660.3156
2017-08-14 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 10:30 | 1.778 | 0 | 0 | 1.5 | 80.4784 | 0 | 23614.669
2017-08-14 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 10:45 | 1.7452 | 0 | 0 |  | 80.375 | 0 | 23584.3326
2017-08-14 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 11:00 | 1.7577 | 0 | 0 | 1.5 | 80.1034 | 0 | 23504.6289
2017-08-14 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 11:15 | 1.7319 | 0 | 0 |  | 79.832 | 0 | 23424.9809
2017-08-14 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 11:30 | 1.7288 | 0 | 0 | 1.5 | 80.0053 | 0 | 23475.8283
2017-08-14 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 11:45 | 1.7444 | 0 | 0 |  | 79.6558 | 0 | 23373.3011
2017-08-14 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 12:00 | 1.753 | 0 | 0 | 1.5 | 79.5451 | 0 | 23340.791
2017-08-14 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 12:15 | 1.728 | 0 | 0 |  | 79.9842 | 0 | 23469.6381
2017-08-14 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 12:30 | 1.7405 | 0 | 0 | 1.5 | 80.1487 | 0 | 23517.9312
2017-08-14 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 12:45 | 1.746 | 0 | 0 |  | 80.2551 | 0 | 23549.127
2017-08-14 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 13:00 | 1.7413 | 0 | 0 | 1.5 | 80.0115 | 0 | 23477.6505
2017-08-14 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 13:15 | 1.8271 | 0 | 0 |  | 79.8169 | 0 | 23420.5707
2017-08-14 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 13:30 | 1.7553 | 0 | 0 | 1.5 | 78.9675 | 0 | 23171.3181
2017-08-14 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 13:45 | 1.7522 | 0 | 0 |  | 78.9302 | 0 | 23160.3887
2017-08-14 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 14:00 | 1.7592 | 0 | 0 | 1.5 | 79.1486 | 0 | 23224.4509
2017-08-14 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 14:15 | 1.7468 | 0 | 0 |  | 79.3176 | 0 | 23274.0624
2017-08-14 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 14:30 | 1.7522 | 0 | 0 | 1.5 | 79.6713 | 0 | 23377.8387
2017-08-14 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 14:45 | 1.7585 | 0 | 0 |  | 80.0351 | 0 | 23484.588
2017-08-14 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 15:00 | 1.7296 | 0 | 0 | 1.5 | 80.5244 | 0 | 23628.1526
2017-08-14 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 15:15 | 1.7522 | 0 | 0 |  | 80.713 | 0 | 23683.4862
2017-08-14 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 15:30 | 1.7616 | 0 | 0 | 1.5 | 81.0392 | 0 | 23779.2123
2017-08-14 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 15:45 | 1.7218 | 0 | 0 |  | 81.4742 | 0 | 23906.8505
2017-08-14 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 16:00 | 1.76 | 0 | 0 | 1.5 | 82.0827 | 0 | 24085.4147
2017-08-14 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 16:15 | 1.7881 | 0 | 0 |  | 82.4369 | 0 | 24189.35
2017-08-14 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 16:30 | 1.7608 | 0 | 0 | 1.5 | 82.7237 | 0 | 24273.4998
2017-08-14 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 16:45 | 1.8318 | 0 | 0 |  | 82.1065 | 0 | 24092.3971
2017-08-14 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 17:00 | 1.8185 | 0 | 0 | 1.5 | 81.2789 | 0 | 23849.5539
2017-08-14 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 17:15 | 1.7624 | 0 | 0 |  | 80.7453 | 0 | 23692.9713
2017-08-14 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 17:30 | 1.785 | 0 | 0 | 1.5 | 79.9906 | 0 | 23471.5254
2017-08-14 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 17:45 | 1.7561 | 0 | 0 |  | 79.5451 | 0 | 23340.8089
2017-08-14 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 18:00 | 1.7803 | 0 | 0 | 1.5 | 79.2199 | 0 | 23245.385
2017-08-14 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 18:15 | 1.7639 | 0 | 0 |  | 78.9266 | 0 | 23159.3142
2017-08-14 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 18:30 | 1.7647 | 0 | 0 | 1.5 | 78.5337 | 0 | 23044.0446
2017-08-14 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 18:45 | 1.7429 | 0 | 0 |  | 78.0989 | 0 | 22916.4352
2017-08-14 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 19:00 | 1.7569 | 0 | 0 | 1.5 | 77.8817 | 0 | 22852.7133
2017-08-14 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 19:15 | 1.7577 | 0 | 0 |  | 77.7054 | 0 | 22800.9907
2017-08-14 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 19:30 | 1.778 | 0 | 0 | 1.5 | 77.5359 | 0 | 22751.2495
2017-08-14 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 19:45 | 1.7397 | 0 | 0 | 1.5 | 77.3065 | 0 | 22683.9414
2017-08-14 | 20:00 | 1.7678 | 0 | 0 | 1.5 | 77.049 | 0 | 22608.3633
2017-08-14 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 20:15 | 1.7483 | 0 | 0 |  | 76.9935 | 0 | 22592.0927
2017-08-14 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 20:30 | 1.7507 | 0 | 0 | 1.5 | 77.08 | 0 | 22617.4614
2017-08-14 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 20:45 | 1.7631 | 0 | 0 |  | 76.9621 | 0 | 22582.8714
2017-08-14 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-08-14 | 21:00 | 1.7647 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 21:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 21:15 | 0.03778 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 21:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 21:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 21:45 | 0.03622 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 21:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 22:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 22:15 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 22:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 22:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 22:45 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 22:45 |  |  |  | 0 |  |  | 0
2017-08-14 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 23:00 |  |  |  | 0 |  |  | 0
2017-08-14 | 23:15 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 23:15 |  |  |  | 0 |  |  | 0
2017-08-14 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 23:30 |  |  |  | 0 |  |  | 0
2017-08-14 | 23:45 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-14 | 23:45 |  |  |  | 0 |  |  | 0
2017-08-15 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 0:00 |  |  |  | 0 |  |  | 0
2017-08-15 | 0:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 0:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 1:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 1:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 2:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 2:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 2:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 2:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 3:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 3:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 3:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 3:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 4:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 4:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 4:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 4:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 5:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 5:15 | 2.2031 | 0 | 0 | 1.5 | 88.7509 | 0 | 26042.0454
2017-08-15 | 5:30 | 1.8271 | 0 | 0 | 1.5 | 83.5447 | 0 | 24514.4043
2017-08-15 | 5:45 | 1.7616 | 0 | 0 | 1.5 | 82.4495 | 0 | 24193.046
2017-08-15 | 6:00 | 1.7327 | 0 | 0 | 1.5 | 82.6371 | 0 | 24248.0841
2017-08-15 | 6:15 | 1.721 | 0 | 0 | 1.5 | 83.0257 | 0 | 24362.1046
2017-08-15 | 6:30 | 1.739 | 0 | 0 | 1.5 | 83.4552 | 0 | 24488.1266
2017-08-15 | 6:45 | 1.7366 | 0 | 0 | 1.5 | 83.8725 | 0 | 24610.5873
2017-08-15 | 7:00 | 1.7429 | 0 | 0 | 1.5 | 84.2165 | 0 | 24711.5293
2017-08-15 | 7:15 | 1.7468 | 0 | 0 | 1.5 | 84.4231 | 0 | 24772.1596
2017-08-15 | 7:30 | 1.799 | 0 | 0 | 1.5 | 84.5722 | 0 | 24815.9013
2017-08-15 | 7:45 | 1.8723 | 0 | 0 | 1.5 | 83.0394 | 0 | 24366.1299
2017-08-15 | 8:00 | 1.8287 | 0 | 0 | 1.5 | 81.1402 | 0 | 23808.8591
2017-08-15 | 8:15 | 1.7772 | 0 | 0 | 1.5 | 80.4003 | 0 | 23591.7337
2017-08-15 | 8:30 | 1.7694 | 0 | 0 | 1.5 | 80.2534 | 0 | 23548.6525
2017-08-15 | 8:45 | 1.7631 | 0 | 0 | 1.5 | 80.0048 | 0 | 23475.6962
2017-08-15 | 9:00 | 1.7273 | 0 | 0 | 1.5 | 80.0734 | 0 | 23495.8152
2017-08-15 | 9:15 | 1.7475 | 0 | 0 | 1.5 | 80.1205 | 0 | 23509.6412
2017-08-15 | 9:30 | 1.7507 | 0 | 0 | 1.5 | 80.1366 | 0 | 23514.3625
2017-08-15 | 9:45 | 1.7148 | 0 | 0 | 1.5 | 80.5804 | 0 | 23644.5779
2017-08-15 | 10:00 | 1.7327 | 0 | 0 | 1.5 | 80.8013 | 0 | 23709.4144
2017-08-15 | 10:15 | 1.7421 | 0 | 0 | 1.5 | 81.1088 | 0 | 23799.6378
2017-08-15 | 10:30 | 1.7452 | 0 | 0 | 1.5 | 81.1901 | 0 | 23823.4821
2017-08-15 | 10:45 | 1.7733 | 0 | 0 | 1.5 | 81.3583 | 0 | 23872.845
2017-08-15 | 11:00 | 1.7078 | 0 | 0 | 1.5 | 81.9923 | 0 | 24058.8952
2017-08-15 | 11:15 | 1.7335 | 0 | 0 | 1.5 | 81.8983 | 0 | 24031.3123
2017-08-15 | 11:30 | 1.7553 | 0 | 0 | 1.5 | 82.3958 | 0 | 24177.2834
2017-08-15 | 11:45 | 1.7678 | 0 | 0 | 1.5 | 82.8425 | 0 | 24308.3582
2017-08-15 | 12:00 | 1.7429 | 0 | 0 | 1.5 | 82.9315 | 0 | 24334.4859
2017-08-15 | 12:15 | 1.76 | 0 | 0 | 1.5 | 83.0279 | 0 | 24362.7584
2017-08-15 | 12:30 | 1.7764 | 0 | 0 | 1.5 | 82.7639 | 0 | 24285.2865
2017-08-15 | 12:45 | 1.7616 | 0 | 0 | 1.5 | 82.4287 | 0 | 24186.9413
2017-08-15 | 13:00 | 1.7483 | 0 | 0 | 1.5 | 82.4661 | 0 | 24197.9061
2017-08-15 | 13:15 | 1.7374 | 0 | 0 | 1.5 | 82.8471 | 0 | 24309.7059
2017-08-15 | 13:30 | 1.7187 | 0 | 0 | 1.5 | 83.3532 | 0 | 24458.2113
2017-08-15 | 13:45 | 1.7109 | 0 | 0 | 1.5 | 83.9295 | 0 | 24627.3168
2017-08-15 | 14:00 | 1.7273 | 0 | 0 | 1.5 | 84.0873 | 0 | 24673.6104
2017-08-15 | 14:15 | 1.7312 | 0 | 0 | 1.5 | 84.6982 | 0 | 24852.8595
2017-08-15 | 14:30 | 1.7429 | 0 | 0 | 1.5 | 84.7481 | 0 | 24867.5051
2017-08-15 | 14:45 | 1.7249 | 0 | 0 | 1.5 | 85.4236 | 0 | 25065.727
2017-08-15 | 15:00 | 1.7101 | 0 | 0 | 1.5 | 86.4487 | 0 | 25366.5253
2017-08-15 | 15:15 | 1.7078 | 0 | 0 | 1.5 | 86.9937 | 0 | 25526.4433
2017-08-15 | 15:30 | 1.7296 | 0 | 0 | 1.5 | 87.4387 | 0 | 25657.0055
2017-08-15 | 15:45 | 1.7366 | 0 | 0 | 1.5 | 87.7095 | 0 | 25736.4698
2017-08-15 | 16:00 | 1.9113 | 0 | 0 | 1.5 | 86.6377 | 0 | 25421.9751
2017-08-15 | 16:15 | 1.7943 | 0 | 0 | 1.5 | 84.5367 | 0 | 24805.489
2017-08-15 | 16:30 | 1.7132 | 0 | 0 | 1.5 | 84.1668 | 0 | 24696.9556
2017-08-15 | 16:45 | 1.7343 | 0 | 0 | 1.5 | 84.8233 | 0 | 24889.5695
2017-08-15 | 17:00 | 1.7413 | 0 | 0 | 1.5 | 85.6132 | 0 | 25121.3628
2017-08-15 | 17:15 | 1.8107 | 0 | 0 | 1.5 | 85.3164 | 0 | 25034.2711
2017-08-15 | 17:30 | 1.7733 | 0 | 0 | 1.5 | 84.4364 | 0 | 24776.0525
2017-08-15 | 17:45 | 1.778 | 0 | 0 | 1.5 | 83.4408 | 0 | 24483.9224
2017-08-15 | 18:00 | 1.7873 | 0 | 0 | 1.5 | 82.4098 | 0 | 24181.3802
2017-08-15 | 18:15 | 1.7647 | 0 | 0 | 1.5 | 81.5766 | 0 | 23936.8961
2017-08-15 | 18:30 | 1.7725 | 0 | 0 | 1.5 | 81.03 | 0 | 23776.5303
2017-08-15 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 80.4339 | 0 | 23601.5973
2017-08-15 | 19:00 | 1.7772 | 0 | 0 | 1.5 | 79.9385 | 0 | 23456.2463
2017-08-15 | 19:15 | 1.7842 | 0 | 0 | 1.5 | 79.5597 | 0 | 23345.0824
2017-08-15 | 19:30 | 1.7936 | 0 | 0 | 1.5 | 78.9841 | 0 | 23176.1849
2017-08-15 | 19:45 | 1.7889 | 0 | 0 | 1.5 | 78.6146 | 0 | 23067.7792
2017-08-15 | 20:00 | 1.7858 | 0 | 0 | 1.5 | 78.0668 | 0 | 22907.0349
2017-08-15 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 77.6919 | 0 | 22797.0262
2017-08-15 | 20:30 | 1.7655 | 0 | 0 | 1.5 | 77.2564 | 0 | 22669.2354
2017-08-15 | 20:45 | 1.7772 | 0 | 0 | 1.5 | 77.3272 | 0 | 22690.0104
2017-08-15 | 21:00 | 1.7686 | 0 | 0 | 1.5 | 77.1688 | 0 | 22643.5354
2017-08-15 | 21:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 21:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 21:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 23:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-15 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 3:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 3:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 3:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 3:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 4:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 4:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 5:15 | 2.182 | 0 | 0 | 1.5 | 91.2044 | 0 | 26761.9742
2017-08-16 | 5:30 | 1.9886 | 0 | 0 | 1.5 | 84.7486 | 0 | 24867.6551
2017-08-16 | 5:45 | 1.8372 | 0 | 0 | 1.5 | 81.1205 | 0 | 23803.0789
2017-08-16 | 6:00 | 1.7327 | 0 | 0 | 1.5 | 80.7558 | 0 | 23696.0631
2017-08-16 | 6:15 | 1.7928 | 0 | 0 | 1.5 | 80.2583 | 0 | 23550.0898
2017-08-16 | 6:30 | 1.7936 | 0 | 0 | 1.5 | 79.4779 | 0 | 23321.0746
2017-08-16 | 6:45 | 1.7998 | 0 | 0 | 1.5 | 78.8691 | 0 | 23142.4614
2017-08-16 | 7:00 | 1.8076 | 0 | 0 | 1.5 | 78.0423 | 0 | 22899.8512
2017-08-16 | 7:15 | 1.746 | 0 | 0 | 1.5 | 77.5744 | 0 | 22762.5504
2017-08-16 | 7:30 | 1.7546 | 0 | 0 | 1.5 | 77.6957 | 0 | 22798.1388
2017-08-16 | 7:45 | 1.7444 | 0 | 0 | 1.5 | 77.67 | 0 | 22790.5878
2017-08-16 | 8:00 | 1.7202 | 0 | 0 | 1.5 | 77.7578 | 0 | 22816.3481
2017-08-16 | 8:15 | 1.7132 | 0 | 0 | 1.5 | 78.2314 | 0 | 22955.3279
2017-08-16 | 8:30 | 1.7039 | 0 | 0 | 1.5 | 78.6705 | 0 | 23084.1707
2017-08-16 | 8:45 | 1.7288 | 0 | 0 | 1.5 | 79.1368 | 0 | 23220.9991
2017-08-16 | 9:00 | 1.7234 | 0 | 0 | 1.5 | 79.594 | 0 | 23355.1631
2017-08-16 | 9:15 | 1.7288 | 0 | 0 | 1.5 | 80.0466 | 0 | 23487.9662
2017-08-16 | 9:30 | 1.7663 | 0 | 0 | 1.5 | 80.0334 | 0 | 23484.0733
2017-08-16 | 9:45 | 1.7241 | 0 | 0 | 1.5 | 80.0978 | 0 | 23502.9901
2017-08-16 | 10:00 | 1.7468 | 0 | 0 | 1.5 | 80.2683 | 0 | 23553.0246
2017-08-16 | 10:15 | 1.7226 | 0 | 0 | 1.5 | 80.4134 | 0 | 23595.5864
2017-08-16 | 10:30 | 1.7546 | 0 | 0 | 1.5 | 80.3763 | 0 | 23584.6997
2017-08-16 | 10:45 | 1.728 | 0 | 0 | 1.5 | 80.56 | 0 | 23638.6028
2017-08-16 | 11:00 | 1.7397 | 0 | 0 | 1.5 | 81.103 | 0 | 23797.9254
2017-08-16 | 11:15 | 1.7202 | 0 | 0 | 1.5 | 81.6971 | 0 | 23972.2537
2017-08-16 | 11:30 | 1.707 | 0 | 0 | 1.5 | 81.9006 | 0 | 24031.9728
2017-08-16 | 11:45 | 1.707 | 0 | 0 | 1.5 | 82.1672 | 0 | 24110.2035
2017-08-16 | 12:00 | 1.7218 | 0 | 0 | 1.5 | 82.4945 | 0 | 24206.2318
2017-08-16 | 12:15 | 1.7304 | 0 | 0 | 1.5 | 83.0944 | 0 | 24382.2684
2017-08-16 | 12:30 | 1.7475 | 0 | 0 | 1.5 | 83.3312 | 0 | 24451.7682
2017-08-16 | 12:45 | 1.7374 | 0 | 0 | 1.5 | 83.1313 | 0 | 24393.0992
2017-08-16 | 13:00 | 1.7132 | 0 | 0 | 1.5 | 83.4611 | 0 | 24489.864
2017-08-16 | 13:15 | 1.7429 | 0 | 0 | 1.5 | 84.2192 | 0 | 24712.3195
2017-08-16 | 13:30 | 1.7312 | 0 | 0 | 1.5 | 84.965 | 0 | 24931.1442
2017-08-16 | 13:45 | 1.7803 | 0 | 0 | 1.5 | 85.4288 | 0 | 25067.2513
2017-08-16 | 14:00 | 1.6937 | 0 | 0 | 1.5 | 85.9033 | 0 | 25206.4706
2017-08-16 | 14:15 | 1.7218 | 0 | 0 | 1.5 | 87.1112 | 0 | 25560.9279
2017-08-16 | 14:30 | 1.8131 | 0 | 0 | 1.5 | 84.4981 | 0 | 24794.1524
2017-08-16 | 14:45 | 1.714 | 0 | 0 | 1.5 | 84.2236 | 0 | 24713.6136
2017-08-16 | 15:00 | 1.7179 | 0 | 0 | 1.5 | 85.3583 | 0 | 25046.5728
2017-08-16 | 15:15 | 1.6734 | 0 | 0 | 1.5 | 86.6528 | 0 | 25426.41
2017-08-16 | 15:30 | 1.9074 | 0 | 0 | 1.5 | 84.2394 | 0 | 24718.2386
2017-08-16 | 15:45 | 1.6812 | 0 | 0 | 1.5 | 83.6741 | 0 | 24552.3725
2017-08-16 | 16:00 | 1.6641 | 0 | 0 | 1.5 | 84.9003 | 0 | 24912.16
2017-08-16 | 16:15 | 1.6883 | 0 | 0 | 1.5 | 86.2176 | 0 | 25298.6999
2017-08-16 | 16:30 | 1.9262 | 0 | 0 | 1.5 | 84.1034 | 0 | 24678.3408
2017-08-16 | 16:45 | 1.7421 | 0 | 0 | 1.5 | 82.9773 | 0 | 24347.9024
2017-08-16 | 17:00 | 1.7007 | 0 | 0 | 1.5 | 83.9241 | 0 | 24625.7297
2017-08-16 | 17:15 | 1.7397 | 0 | 0 | 1.5 | 84.4198 | 0 | 24771.179
2017-08-16 | 17:30 | 1.7631 | 0 | 0 | 1.5 | 84.1411 | 0 | 24689.3978
2017-08-16 | 17:45 | 1.7405 | 0 | 0 | 1.5 | 84.1413 | 0 | 24689.4491
2017-08-16 | 18:00 | 1.7265 | 0 | 0 | 1.5 | 83.8513 | 0 | 24604.3725
2017-08-16 | 18:15 | 1.7803 | 0 | 0 | 1.5 | 83.3739 | 0 | 24464.2826
2017-08-16 | 18:30 | 1.7811 | 0 | 0 | 1.5 | 82.9954 | 0 | 24353.2082
2017-08-16 | 18:45 | 1.7959 | 0 | 0 | 1.5 | 82.6794 | 0 | 24260.4841
2017-08-16 | 19:00 | 1.7725 | 0 | 0 | 1.5 | 81.9867 | 0 | 24057.2297
2017-08-16 | 19:15 | 1.7499 | 0 | 0 | 1.5 | 81.4686 | 0 | 23905.2008
2017-08-16 | 19:30 | 1.7725 | 0 | 0 | 1.5 | 81.0488 | 0 | 23782.0263
2017-08-16 | 19:45 | 1.7865 | 0 | 0 | 1.5 | 80.7653 | 0 | 23698.8457
2017-08-16 | 20:00 | 1.7296 | 0 | 0 | 1.5 | 80.3889 | 0 | 23588.398
2017-08-16 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 80.0236 | 0 | 23481.2053
2017-08-16 | 20:30 | 1.7826 | 0 | 0 | 1.5 | 79.7993 | 0 | 23415.3905
2017-08-16 | 20:45 | 1.7616 | 0 | 0 | 1.5 | 79.371 | 0 | 23289.713
2017-08-16 | 21:00 | 1.7499 | 0 | 0 | 1.5 | 79.1646 | 0 | 23229.1455
2017-08-16 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 22:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 4:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 5:15 | 1.9121 | 0 | 0 | 1.5 | 97.2432 | 0 | 28533.9362
2017-08-17 | 5:30 | 2.0159 | 0 | 0 | 1.5 | 92.8073 | 0 | 27232.3261
2017-08-17 | 5:45 | 1.9886 | 0 | 0 | 1.5 | 86.2237 | 0 | 25300.493
2017-08-17 | 6:00 | 1.8591 | 0 | 0 | 1.5 | 82.4347 | 0 | 24188.7007
2017-08-17 | 6:15 | 1.817 | 0 | 0 | 1.5 | 80.4565 | 0 | 23608.2262
2017-08-17 | 6:30 | 1.7483 | 0 | 0 | 1.5 | 79.3812 | 0 | 23292.7262
2017-08-17 | 6:45 | 1.767 | 0 | 0 | 1.5 | 78.9776 | 0 | 23174.2978
2017-08-17 | 7:00 | 1.7413 | 0 | 0 | 1.5 | 78.7859 | 0 | 23118.0262
2017-08-17 | 7:15 | 1.7226 | 0 | 0 | 1.5 | 78.617 | 0 | 23068.4775
2017-08-17 | 7:30 | 1.778 | 0 | 0 | 1.5 | 78.7263 | 0 | 23100.5355
2017-08-17 | 7:45 | 1.7351 | 0 | 0 | 1.5 | 78.9854 | 0 | 23176.5746
2017-08-17 | 8:00 | 1.7312 | 0 | 0 | 1.5 | 78.7853 | 0 | 23117.8539
2017-08-17 | 8:15 | 1.7585 | 0 | 0 | 1.5 | 79.0689 | 0 | 23201.0723
2017-08-17 | 8:30 | 1.7452 | 0 | 0 | 1.5 | 78.9745 | 0 | 23173.3867
2017-08-17 | 8:45 | 1.7382 | 0 | 0 | 1.5 | 79.186 | 0 | 23235.4272
2017-08-17 | 9:00 | 1.7624 | 0 | 0 | 1.5 | 79.1304 | 0 | 23219.134
2017-08-17 | 9:15 | 1.7382 | 0 | 0 | 1.5 | 79.2768 | 0 | 23262.0899
2017-08-17 | 9:30 | 1.7234 | 0 | 0 | 1.5 | 79.5057 | 0 | 23329.2369
2017-08-17 | 9:45 | 1.7592 | 0 | 0 | 1.5 | 79.511 | 0 | 23330.7883
2017-08-17 | 10:00 | 1.7483 | 0 | 0 | 1.5 | 79.5273 | 0 | 23335.5902
2017-08-17 | 10:15 | 1.7335 | 0 | 0 | 1.5 | 79.9288 | 0 | 23453.4033
2017-08-17 | 10:30 | 1.7195 | 0 | 0 | 1.5 | 79.8094 | 0 | 23418.3588
2017-08-17 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 79.9376 | 0 | 23455.9846
2017-08-17 | 11:00 | 1.7538 | 0 | 0 | 1.5 | 80.255 | 0 | 23549.1115
2017-08-17 | 11:15 | 1.7483 | 0 | 0 | 1.5 | 81.1582 | 0 | 23814.1244
2017-08-17 | 11:30 | 1.7234 | 0 | 0 | 1.5 | 81.6267 | 0 | 23951.6198
2017-08-17 | 11:45 | 1.7296 | 0 | 0 | 1.5 | 82.2164 | 0 | 24124.632
2017-08-17 | 12:00 | 1.6898 | 0 | 0 | 1.5 | 82.8645 | 0 | 24314.8236
2017-08-17 | 12:15 | 1.7468 | 0 | 0 | 1.5 | 83.0115 | 0 | 24357.9429
2017-08-17 | 12:30 | 1.7195 | 0 | 0 | 1.5 | 83.0703 | 0 | 24375.1965
2017-08-17 | 12:45 | 1.7218 | 0 | 0 | 1.5 | 82.9454 | 0 | 24338.5605
2017-08-17 | 13:00 | 1.7343 | 0 | 0 | 1.5 | 83.001 | 0 | 24354.8581
2017-08-17 | 13:15 | 1.7491 | 0 | 0 | 1.5 | 83.2269 | 0 | 24421.1498
2017-08-17 | 13:30 | 1.7101 | 0 | 0 | 1.5 | 83.7763 | 0 | 24582.3483
2017-08-17 | 13:45 | 1.6602 | 0 | 0 | 1.5 | 84.5466 | 0 | 24808.3928
2017-08-17 | 14:00 | 1.721 | 0 | 0 | 1.5 | 85.1925 | 0 | 24997.8992
2017-08-17 | 14:15 | 1.7226 | 0 | 0 | 1.5 | 85.9733 | 0 | 25227.0308
2017-08-17 | 14:30 | 1.7553 | 0 | 0 | 1.5 | 86.4239 | 0 | 25359.2295
2017-08-17 | 14:45 | 1.6961 | 0 | 0 | 1.5 | 87.3478 | 0 | 25630.3516
2017-08-17 | 15:00 | 1.6953 | 0 | 0 | 1.5 | 88.0753 | 0 | 25843.8056
2017-08-17 | 15:15 | 1.884 | 0 | 0 | 1.5 | 87.4184 | 0 | 25651.0706
2017-08-17 | 15:30 | 1.7382 | 0 | 0 | 1.5 | 85.5654 | 0 | 25107.3351
2017-08-17 | 15:45 | 1.7109 | 0 | 0 | 1.5 | 86.2821 | 0 | 25317.619
2017-08-17 | 16:00 | 1.682 | 0 | 0 | 1.5 | 87.5162 | 0 | 25679.7483
2017-08-17 | 16:15 | 1.7397 | 0 | 0 | 1.5 | 88.37 | 0 | 25930.2905
2017-08-17 | 16:30 | 1.916 | 0 | 0 | 1.5 | 85.5466 | 0 | 25101.8055
2017-08-17 | 16:45 | 1.7413 | 0 | 0 | 1.5 | 84.4273 | 0 | 24773.3729
2017-08-17 | 17:00 | 1.6641 | 0 | 0 | 1.5 | 84.9794 | 0 | 24935.391
2017-08-17 | 17:15 | 1.7327 | 0 | 0 | 1.5 | 85.1786 | 0 | 24993.8472
2017-08-17 | 17:30 | 1.8107 | 0 | 0 | 1.5 | 84.7623 | 0 | 24871.6847
2017-08-17 | 17:45 | 1.8123 | 0 | 0 | 1.5 | 84.4052 | 0 | 24766.8852
2017-08-17 | 18:00 | 1.7538 | 0 | 0 | 1.5 | 84.3287 | 0 | 24744.4379
2017-08-17 | 18:15 | 1.7561 | 0 | 0 | 1.5 | 84.1873 | 0 | 24702.9665
2017-08-17 | 18:30 | 1.7842 | 0 | 0 | 1.5 | 83.2681 | 0 | 24433.2499
2017-08-17 | 18:45 | 1.7608 | 0 | 0 | 1.5 | 82.4152 | 0 | 24182.9853
2017-08-17 | 19:00 | 1.7538 | 0 | 0 | 1.5 | 81.8664 | 0 | 24021.9546
2017-08-17 | 19:15 | 1.7819 | 0 | 0 | 1.5 | 81.5172 | 0 | 23919.4635
2017-08-17 | 19:30 | 1.7858 | 0 | 0 | 1.5 | 81.0197 | 0 | 23773.4857
2017-08-17 | 19:45 | 1.7483 | 0 | 0 | 1.5 | 80.6141 | 0 | 23654.4705
2017-08-17 | 20:00 | 1.778 | 0 | 0 | 1.5 | 79.9902 | 0 | 23471.4022
2017-08-17 | 20:15 | 1.7709 | 0 | 0 | 1.5 | 79.7491 | 0 | 23400.6577
2017-08-17 | 20:30 | 1.7304 | 0 | 0 | 1.5 | 79.3021 | 0 | 23269.4955
2017-08-17 | 20:45 | 1.7694 | 0 | 0 | 1.5 | 78.7366 | 0 | 23103.5554
2017-08-17 | 21:00 | 1.7608 | 0 | 0 | 1.5 | 78.255 | 0 | 22962.2655
2017-08-17 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 3:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 3:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 3:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 4:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 4:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 5:15 | 2.0455 | 0 | 0 | 1.5 | 93.0492 | 0 | 27303.2877
2017-08-18 | 5:30 | 1.9925 | 0 | 0 | 1.5 | 86.925 | 0 | 25506.2929
2017-08-18 | 5:45 | 1.8903 | 0 | 0 | 1.5 | 82.2916 | 0 | 24146.7143
2017-08-18 | 6:00 | 1.8076 | 0 | 0 | 1.5 | 80.128 | 0 | 23511.8308
2017-08-18 | 6:15 | 1.7694 | 0 | 0 | 1.5 | 79.3821 | 0 | 23292.9659
2017-08-18 | 6:30 | 1.7561 | 0 | 0 | 1.5 | 78.5983 | 0 | 23062.9749
2017-08-18 | 6:45 | 1.7483 | 0 | 0 | 1.5 | 78.0021 | 0 | 22888.033
2017-08-18 | 7:00 | 1.7429 | 0 | 0 | 1.5 | 78.0303 | 0 | 22896.3294
2017-08-18 | 7:15 | 1.7725 | 0 | 0 | 1.5 | 77.8098 | 0 | 22831.607
2017-08-18 | 7:30 | 1.7514 | 0 | 0 | 1.5 | 77.489 | 0 | 22737.4974
2017-08-18 | 7:45 | 1.7561 | 0 | 0 | 1.5 | 77.3136 | 0 | 22686.0301
2017-08-18 | 8:00 | 1.7171 | 0 | 0 | 1.5 | 77.4676 | 0 | 22731.2043
2017-08-18 | 8:15 | 1.7319 | 0 | 0 | 1.5 | 78.2568 | 0 | 22962.7737
2017-08-18 | 8:30 | 1.7374 | 0 | 0 | 1.5 | 78.7796 | 0 | 23116.1928
2017-08-18 | 8:45 | 1.7171 | 0 | 0 | 1.5 | 79.2347 | 0 | 23249.7169
2017-08-18 | 9:00 | 1.739 | 0 | 0 | 1.5 | 79.4967 | 0 | 23326.6043
2017-08-18 | 9:15 | 1.7616 | 0 | 0 | 1.5 | 79.7594 | 0 | 23403.6821
2017-08-18 | 9:30 | 1.7421 | 0 | 0 | 1.5 | 79.8826 | 0 | 23439.8413
2017-08-18 | 9:45 | 1.7093 | 0 | 0 | 1.5 | 80.0769 | 0 | 23496.8471
2017-08-18 | 10:00 | 1.746 | 0 | 0 | 1.5 | 80.4052 | 0 | 23593.1844
2017-08-18 | 10:15 | 1.7421 | 0 | 0 | 1.5 | 80.7093 | 0 | 23682.407
2017-08-18 | 10:30 | 1.7257 | 0 | 0 | 1.5 | 81.1012 | 0 | 23797.3993
2017-08-18 | 10:45 | 1.7553 | 0 | 0 | 1.5 | 81.5944 | 0 | 23942.1367
2017-08-18 | 11:00 | 1.7273 | 0 | 0 | 1.5 | 81.9012 | 0 | 24032.1518
2017-08-18 | 11:15 | 1.7569 | 0 | 0 | 1.5 | 81.9981 | 0 | 24060.5833
2017-08-18 | 11:30 | 1.6984 | 0 | 0 | 1.5 | 82.3309 | 0 | 24158.2302
2017-08-18 | 11:45 | 1.7015 | 0 | 0 | 1.5 | 82.8077 | 0 | 24298.1522
2017-08-18 | 12:00 | 1.6914 | 0 | 0 | 1.5 | 83.5185 | 0 | 24506.7212
2017-08-18 | 12:15 | 1.7748 | 0 | 0 | 1.5 | 83.4529 | 0 | 24487.4732
2017-08-18 | 12:30 | 1.7631 | 0 | 0 | 1.5 | 83.4187 | 0 | 24477.4438
2017-08-18 | 12:45 | 1.7748 | 0 | 0 | 1.5 | 83.4602 | 0 | 24489.6111
2017-08-18 | 13:00 | 1.7608 | 0 | 0 | 1.5 | 83.6773 | 0 | 24553.3218
2017-08-18 | 13:15 | 1.7741 | 0 | 0 | 1.5 | 83.9261 | 0 | 24626.3071
2017-08-18 | 13:30 | 1.7366 | 0 | 0 | 1.5 | 84.4226 | 0 | 24772.0073
2017-08-18 | 13:45 | 1.7265 | 0 | 0 | 1.5 | 85.15 | 0 | 24985.4478
2017-08-18 | 14:00 | 1.7265 | 0 | 0 | 1.5 | 85.9456 | 0 | 25218.8976
2017-08-18 | 14:15 | 1.6844 | 0 | 0 | 1.5 | 86.7406 | 0 | 25452.1838
2017-08-18 | 14:30 | 1.7592 | 0 | 0 | 1.5 | 87.1555 | 0 | 25573.9235
2017-08-18 | 14:45 | 1.9176 | 0 | 0 | 1.5 | 85.2831 | 0 | 25024.5038
2017-08-18 | 15:00 | 1.7226 | 0 | 0 | 1.5 | 84.1671 | 0 | 24697.0384
2017-08-18 | 15:15 | 1.728 | 0 | 0 | 1.5 | 84.9023 | 0 | 24912.7644
2017-08-18 | 15:30 | 1.7358 | 0 | 0 | 1.5 | 85.9727 | 0 | 25226.8404
2017-08-18 | 15:45 | 1.7561 | 0 | 0 | 1.5 | 86.1859 | 0 | 25289.4049
2017-08-18 | 16:00 | 1.8006 | 0 | 0 | 1.5 | 83.8154 | 0 | 24593.824
2017-08-18 | 16:15 | 1.7039 | 0 | 0 | 1.5 | 84.0306 | 0 | 24656.9816
2017-08-18 | 16:30 | 1.7452 | 0 | 0 | 1.5 | 84.6338 | 0 | 24833.9785
2017-08-18 | 16:45 | 1.7296 | 0 | 0 | 1.5 | 84.8228 | 0 | 24889.4283
2017-08-18 | 17:00 | 1.7936 | 0 | 0 | 1.5 | 85.1977 | 0 | 24999.4461
2017-08-18 | 17:15 | 1.7553 | 0 | 0 | 1.5 | 85.3192 | 0 | 25035.0951
2017-08-18 | 17:30 | 1.7608 | 0 | 0 | 1.5 | 84.4983 | 0 | 24794.2172
2017-08-18 | 17:45 | 1.753 | 0 | 0 | 1.5 | 83.8709 | 0 | 24610.1169
2017-08-18 | 18:00 | 1.8006 | 0 | 0 | 1.5 | 83.0472 | 0 | 24368.4177
2017-08-18 | 18:15 | 1.7795 | 0 | 0 | 1.5 | 82.4765 | 0 | 24200.9666
2017-08-18 | 18:30 | 1.7795 | 0 | 0 | 1.5 | 81.7309 | 0 | 23982.1733
2017-08-18 | 18:45 | 1.7468 | 0 | 0 | 1.5 | 80.8147 | 0 | 23713.3522
2017-08-18 | 19:00 | 1.7787 | 0 | 0 | 1.5 | 80.2959 | 0 | 23561.113
2017-08-18 | 19:15 | 1.7538 | 0 | 0 | 1.5 | 80.104 | 0 | 23504.8079
2017-08-18 | 19:30 | 1.7819 | 0 | 0 | 1.5 | 79.5375 | 0 | 23338.568
2017-08-18 | 19:45 | 1.7709 | 0 | 0 | 1.5 | 79.32 | 0 | 23274.7563
2017-08-18 | 20:00 | 1.7819 | 0 | 0 | 1.5 | 78.7208 | 0 | 23098.9416
2017-08-18 | 20:15 | 1.7647 | 0 | 0 | 1.5 | 78.3761 | 0 | 22997.78
2017-08-18 | 20:30 | 1.7631 | 0 | 0 | 1.5 | 77.885 | 0 | 22853.6805
2017-08-18 | 20:45 | 1.7787 | 0 | 0 | 1.5 | 77.4514 | 0 | 22726.4472
2017-08-18 | 21:00 | 1.7819 | 0 | 0 | 1.5 | 77.1263 | 0 | 22631.0726
2017-08-18 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-18 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 2:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 3:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 3:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 3:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 3:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 4:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 4:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 5:15 | 2.0291 | 0 | 0 | 1.5 | 93.6117 | 0 | 27468.3524
2017-08-19 | 5:30 | 2.0393 | 0 | 0 | 1.5 | 87.213 | 0 | 25590.7831
2017-08-19 | 5:45 | 1.9246 | 0 | 0 | 1.5 | 82.4567 | 0 | 24195.1482
2017-08-19 | 6:00 | 1.8271 | 0 | 0 | 1.5 | 80.2004 | 0 | 23533.0759
2017-08-19 | 6:15 | 1.8107 | 0 | 0 | 1.5 | 78.907 | 0 | 23153.5565
2017-08-19 | 6:30 | 1.7538 | 0 | 0 | 1.5 | 78.2155 | 0 | 22950.6759
2017-08-19 | 6:45 | 1.7405 | 0 | 0 | 1.5 | 77.8882 | 0 | 22854.6162
2017-08-19 | 7:00 | 1.7803 | 0 | 0 | 1.5 | 77.643 | 0 | 22782.6672
2017-08-19 | 7:15 | 1.7756 | 0 | 0 | 1.5 | 77.0495 | 0 | 22608.5268
2017-08-19 | 7:30 | 1.7358 | 0 | 0 | 1.5 | 77.0978 | 0 | 22622.7111
2017-08-19 | 7:45 | 1.7725 | 0 | 0 | 1.5 | 76.7939 | 0 | 22533.5288
2017-08-19 | 8:00 | 1.7319 | 0 | 0 | 1.5 | 77.1046 | 0 | 22624.6879
2017-08-19 | 8:15 | 1.7569 | 0 | 0 | 1.5 | 77.366 | 0 | 22701.3872
2017-08-19 | 8:30 | 1.7514 | 0 | 0 | 1.5 | 77.1679 | 0 | 22643.2711
2017-08-19 | 8:45 | 1.7834 | 0 | 0 | 1.5 | 77.1444 | 0 | 22636.3761
2017-08-19 | 9:00 | 1.7694 | 0 | 0 | 1.5 | 77.2225 | 0 | 22659.3002
2017-08-19 | 9:15 | 1.7663 | 0 | 0 | 1.5 | 77.6211 | 0 | 22776.2376
2017-08-19 | 9:30 | 1.7499 | 0 | 0 | 1.5 | 77.965 | 0 | 22877.1462
2017-08-19 | 9:45 | 1.7522 | 0 | 0 | 1.5 | 78.2188 | 0 | 22951.6272
2017-08-19 | 10:00 | 1.7585 | 0 | 0 | 1.5 | 78.4473 | 0 | 23018.6668
2017-08-19 | 10:15 | 1.7678 | 0 | 0 | 1.5 | 78.4894 | 0 | 23031.0422
2017-08-19 | 10:30 | 1.6968 | 0 | 0 | 1.5 | 78.5163 | 0 | 23038.9202
2017-08-19 | 10:45 | 1.7507 | 0 | 0 | 1.5 | 78.1729 | 0 | 22938.1527
2017-08-19 | 11:00 | 1.7413 | 0 | 0 | 1.5 | 78.2335 | 0 | 22955.9321
2017-08-19 | 11:15 | 1.7865 | 0 | 0 | 1.5 | 77.9846 | 0 | 22882.9065
2017-08-19 | 11:30 | 1.6875 | 0 | 0 | 1.5 | 78.1432 | 0 | 22929.4575
2017-08-19 | 11:45 | 1.746 | 0 | 0 | 1.5 | 77.9918 | 0 | 22885.0107
2017-08-19 | 12:00 | 1.7475 | 0 | 0 | 1.5 | 77.7231 | 0 | 22806.18
2017-08-19 | 12:15 | 1.7522 | 0 | 0 | 1.5 | 77.5141 | 0 | 22744.8648
2017-08-19 | 12:30 | 1.7639 | 0 | 0 | 1.5 | 77.4641 | 0 | 22730.1881
2017-08-19 | 12:45 | 1.7382 | 0 | 0 | 1.5 | 77.6858 | 0 | 22795.2442
2017-08-19 | 13:00 | 1.7499 | 0 | 0 | 1.5 | 77.8037 | 0 | 22829.8274
2017-08-19 | 13:15 | 1.7421 | 0 | 0 | 1.5 | 77.8505 | 0 | 22843.5572
2017-08-19 | 13:30 | 1.746 | 0 | 0 | 1.5 | 77.8225 | 0 | 22835.3523
2017-08-19 | 13:45 | 1.7553 | 0 | 0 | 1.5 | 77.8374 | 0 | 22839.7177
2017-08-19 | 14:00 | 1.7483 | 0 | 0 | 1.5 | 77.8093 | 0 | 22831.475
2017-08-19 | 14:15 | 1.7358 | 0 | 0 | 1.5 | 77.8458 | 0 | 22842.1936
2017-08-19 | 14:30 | 1.7296 | 0 | 0 | 1.5 | 77.816 | 0 | 22833.4471
2017-08-19 | 14:45 | 1.7343 | 0 | 0 | 1.5 | 77.829 | 0 | 22837.262
2017-08-19 | 15:00 | 1.7514 | 0 | 0 | 1.5 | 77.7882 | 0 | 22825.276
2017-08-19 | 15:15 | 1.7491 | 0 | 0 | 1.5 | 77.8095 | 0 | 22831.5219
2017-08-19 | 15:30 | 1.7608 | 0 | 0 | 1.5 | 77.7254 | 0 | 22806.8584
2017-08-19 | 15:45 | 1.746 | 0 | 0 | 1.5 | 77.6923 | 0 | 22797.1515
2017-08-19 | 16:00 | 1.7507 | 0 | 0 | 1.5 | 77.6148 | 0 | 22774.3952
2017-08-19 | 16:15 | 1.76 | 0 | 0 | 1.5 | 77.5713 | 0 | 22761.646
2017-08-19 | 16:30 | 1.7374 | 0 | 0 | 1.5 | 77.4934 | 0 | 22738.7645
2017-08-19 | 16:45 | 1.7577 | 0 | 0 | 1.5 | 77.6178 | 0 | 22775.2884
2017-08-19 | 17:00 | 1.7553 | 0 | 0 | 1.5 | 77.5863 | 0 | 22766.0471
2017-08-19 | 17:15 | 1.7452 | 0 | 0 | 1.5 | 77.5085 | 0 | 22743.2125
2017-08-19 | 17:30 | 1.7655 | 0 | 0 | 1.5 | 77.382 | 0 | 22706.0885
2017-08-19 | 17:45 | 1.7616 | 0 | 0 | 1.5 | 77.039 | 0 | 22605.444
2017-08-19 | 18:00 | 1.7491 | 0 | 0 | 1.5 | 76.8649 | 0 | 22554.344
2017-08-19 | 18:15 | 1.7577 | 0 | 0 | 1.5 | 76.7445 | 0 | 22519.0331
2017-08-19 | 18:30 | 1.7405 | 0 | 0 | 1.5 | 77.1013 | 0 | 22623.7275
2017-08-19 | 18:45 | 1.7647 | 0 | 0 | 1.5 | 76.9817 | 0 | 22588.625
2017-08-19 | 19:00 | 1.7561 | 0 | 0 | 1.5 | 76.7534 | 0 | 22521.6346
2017-08-19 | 19:15 | 1.7312 | 0 | 0 | 1.5 | 76.9792 | 0 | 22587.9084
2017-08-19 | 19:30 | 1.7273 | 0 | 0 | 1.5 | 77.0073 | 0 | 22596.147
2017-08-19 | 19:45 | 1.7764 | 0 | 0 | 1.5 | 76.6568 | 0 | 22493.3041
2017-08-19 | 20:00 | 1.7842 | 0 | 0 | 1.5 | 76.6958 | 0 | 22504.7282
2017-08-19 | 20:15 | 1.7694 | 0 | 0 | 1.5 | 76.5134 | 0 | 22451.2235
2017-08-19 | 20:30 | 1.7592 | 0 | 0 | 1.5 | 76.3656 | 0 | 22407.8624
2017-08-19 | 20:45 | 1.7639 | 0 | 0 | 1.5 | 76.1575 | 0 | 22346.7935
2017-08-19 | 21:00 | 1.767 | 0 | 0 | 1.5 | 75.8822 | 0 | 22266.0129
2017-08-19 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 21:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 22:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 23:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 23:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-19 | 23:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 0:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 0:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 0:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 0:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 1:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 1:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 1:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 1:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 2:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 2:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 2:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 2:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 3:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 3:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 3:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 3:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 4:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 4:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 4:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 4:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 5:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 5:15 | 2.2109 | 0 | 0 | 1.5 | 87.7455 | 0 | 25747.0341
2017-08-20 | 5:30 | 1.8677 | 0 | 0 | 1.5 | 82.436 | 0 | 24189.0657
2017-08-20 | 5:45 | 1.7631 | 0 | 0 | 1.5 | 81.144 | 0 | 23809.9783
2017-08-20 | 6:00 | 1.7327 | 0 | 0 | 1.5 | 81.2165 | 0 | 23831.2301
2017-08-20 | 6:15 | 1.7195 | 0 | 0 | 1.5 | 81.8313 | 0 | 24011.6456
2017-08-20 | 6:30 | 1.7273 | 0 | 0 | 1.5 | 82.5222 | 0 | 24214.3695
2017-08-20 | 6:45 | 1.7179 | 0 | 0 | 1.5 | 83.1022 | 0 | 24384.5654
2017-08-20 | 7:00 | 1.7327 | 0 | 0 | 1.5 | 83.621 | 0 | 24536.78
2017-08-20 | 7:15 | 1.7397 | 0 | 0 | 1.5 | 83.8862 | 0 | 24614.6011
2017-08-20 | 7:30 | 1.7405 | 0 | 0 | 1.5 | 84.0264 | 0 | 24655.7503
2017-08-20 | 7:45 | 1.7429 | 0 | 0 | 1.5 | 84.1638 | 0 | 24696.0668
2017-08-20 | 8:00 | 1.8123 | 0 | 0 | 1.5 | 83.3572 | 0 | 24459.373
2017-08-20 | 8:15 | 1.8552 | 0 | 0 | 1.5 | 81.1542 | 0 | 23812.9671
2017-08-20 | 8:30 | 1.8006 | 0 | 0 | 1.5 | 79.7081 | 0 | 23388.6204
2017-08-20 | 8:45 | 1.8053 | 0 | 0 | 1.5 | 78.7491 | 0 | 23107.2471
2017-08-20 | 9:00 | 1.8154 | 0 | 0 | 1.5 | 78.4287 | 0 | 23013.2223
2017-08-20 | 9:15 | 1.778 | 0 | 0 | 1.5 | 78.2607 | 0 | 22963.9242
2017-08-20 | 9:30 | 1.7842 | 0 | 0 | 1.5 | 78.1157 | 0 | 22921.3648
2017-08-20 | 9:45 | 1.8138 | 0 | 0 | 1.5 | 77.7836 | 0 | 22823.9195
2017-08-20 | 10:00 | 1.785 | 0 | 0 | 1.5 | 77.4369 | 0 | 22722.2092
2017-08-20 | 10:15 | 1.7631 | 0 | 0 | 1.5 | 77.4195 | 0 | 22717.1074
2017-08-20 | 10:30 | 1.7491 | 0 | 0 | 1.5 | 77.5835 | 0 | 22765.2211
2017-08-20 | 10:45 | 1.7834 | 0 | 0 | 1.5 | 77.837 | 0 | 22839.588
2017-08-20 | 11:00 | 1.7819 | 0 | 0 | 1.5 | 77.8363 | 0 | 22839.4022
2017-08-20 | 11:15 | 1.7514 | 0 | 0 | 1.5 | 77.6602 | 0 | 22787.7177
2017-08-20 | 11:30 | 1.7569 | 0 | 0 | 1.5 | 77.5315 | 0 | 22749.9488
2017-08-20 | 11:45 | 1.6945 | 0 | 0 | 1.5 | 77.5068 | 0 | 22742.6999
2017-08-20 | 12:00 | 1.7616 | 0 | 0 | 1.5 | 77.207 | 0 | 22654.7377
2017-08-20 | 12:15 | 1.707 | 0 | 0 | 1.5 | 77.2246 | 0 | 22659.8911
2017-08-20 | 12:30 | 1.7639 | 0 | 0 | 1.5 | 77.1479 | 0 | 22637.3969
2017-08-20 | 12:45 | 1.7475 | 0 | 0 | 1.5 | 77.1067 | 0 | 22625.317
2017-08-20 | 13:00 | 1.7343 | 0 | 0 | 1.5 | 77.2712 | 0 | 22673.5696
2017-08-20 | 13:15 | 1.728 | 0 | 0 | 1.5 | 77.4355 | 0 | 22721.7996
2017-08-20 | 13:30 | 1.7514 | 0 | 0 | 1.5 | 77.5184 | 0 | 22746.1275
2017-08-20 | 13:45 | 1.753 | 0 | 0 | 1.5 | 77.488 | 0 | 22737.204
2017-08-20 | 14:00 | 1.7546 | 0 | 0 | 1.5 | 77.5 | 0 | 22740.7031
2017-08-20 | 14:15 | 1.7452 | 0 | 0 | 1.5 | 77.4872 | 0 | 22736.9666
2017-08-20 | 14:30 | 1.7452 | 0 | 0 | 1.5 | 77.5537 | 0 | 22756.4723
2017-08-20 | 14:45 | 1.7764 | 0 | 0 | 1.5 | 77.5684 | 0 | 22760.7707
2017-08-20 | 15:00 | 1.7546 | 0 | 0 | 1.5 | 77.6319 | 0 | 22779.421
2017-08-20 | 15:15 | 1.7475 | 0 | 0 | 1.5 | 77.6399 | 0 | 22781.7514
2017-08-20 | 15:30 | 1.7561 | 0 | 0 | 1.5 | 77.6647 | 0 | 22789.0496
2017-08-20 | 15:45 | 1.7382 | 0 | 0 | 1.5 | 77.6418 | 0 | 22782.3113
2017-08-20 | 16:00 | 1.7483 | 0 | 0 | 1.5 | 77.5721 | 0 | 22761.8743
2017-08-20 | 16:15 | 1.7663 | 0 | 0 | 1.5 | 77.4674 | 0 | 22731.1573
2017-08-20 | 16:30 | 1.7592 | 0 | 0 | 1.5 | 77.495 | 0 | 22739.2457
2017-08-20 | 16:45 | 1.7499 | 0 | 0 | 1.5 | 77.5239 | 0 | 22747.7146
2017-08-20 | 17:00 | 1.7499 | 0 | 0 | 1.5 | 77.524 | 0 | 22747.7548
2017-08-20 | 17:15 | 1.7577 | 0 | 0 | 1.5 | 77.4922 | 0 | 22738.4241
2017-08-20 | 17:30 | 1.778 | 0 | 0 | 1.5 | 77.3694 | 0 | 22702.3969
2017-08-20 | 17:45 | 1.7499 | 0 | 0 | 1.5 | 77.3181 | 0 | 22687.3464
2017-08-20 | 18:00 | 1.7725 | 0 | 0 | 1.5 | 77.1247 | 0 | 22630.5891
2017-08-20 | 18:15 | 1.7624 | 0 | 0 | 1.5 | 76.9475 | 0 | 22578.5888
2017-08-20 | 18:30 | 1.7397 | 0 | 0 | 1.5 | 77.1597 | 0 | 22640.86
2017-08-20 | 18:45 | 1.7694 | 0 | 0 | 1.5 | 76.9784 | 0 | 22587.6757
2017-08-20 | 19:00 | 1.7296 | 0 | 0 | 1.5 | 76.961 | 0 | 22582.556
2017-08-20 | 19:15 | 1.7639 | 0 | 0 | 1.5 | 76.7162 | 0 | 22510.7344
2017-08-20 | 19:30 | 1.7756 | 0 | 0 | 1.5 | 76.6433 | 0 | 22489.3238
2017-08-20 | 19:45 | 1.7319 | 0 | 0 | 1.5 | 76.5077 | 0 | 22449.5422
2017-08-20 | 20:00 | 1.7226 | 0 | 0 | 1.5 | 76.4329 | 0 | 22427.6078
2017-08-20 | 20:15 | 1.6992 | 0 | 0 | 1.5 | 76.3657 | 0 | 22407.8692
2017-08-20 | 20:30 | 1.7054 | 0 | 0 | 1.5 | 76.2081 | 0 | 22361.6383
2017-08-20 | 20:45 | 1.7179 | 0 | 0 | 1.5 | 76.048 | 0 | 22314.6551
2017-08-20 | 21:00 | 1.7132 | 0 | 0 | 1.5 | 75.9068 | 0 | 22273.2347
2017-08-20 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 21:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 21:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 22:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 22:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-20 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-21 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-21 | 0:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 0:15 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 0:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 0:30 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 0:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 0:45 | 0.03232 |  | 0 |  | 0 |  | 0
2017-08-21 | 1:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 1:00 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 1:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 1:15 | 0.03232 |  | 0 |  | 0 |  | 0
2017-08-21 | 1:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 1:30 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 1:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 1:45 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 2:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 2:00 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 2:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 2:15 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 2:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 2:30 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 2:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 2:45 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 3:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 3:00 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 3:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 3:15 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 3:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 3:30 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 3:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 3:45 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 4:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 4:00 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 4:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 4:15 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 4:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 4:30 | 0.03466 |  | 0 |  | 0 |  | 0
2017-08-21 | 4:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 4:45 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 5:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 5:00 | 0.03466 |  | 0 |  | 25 |  | 7335.7143
2017-08-21 | 5:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 5:15 | 2.1945 |  | 0 |  | 89.7674 |  | 26340.3097
2017-08-21 | 5:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 5:30 | 1.9847 |  | 0 |  | 82.4683 |  | 24198.5531
2017-08-21 | 5:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 5:45 | 1.8419 |  | 0 |  | 79.2973 |  | 23268.092
2017-08-21 | 6:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 6:00 | 1.7616 |  | 0 |  | 78.2396 |  | 22957.7367
2017-08-21 | 6:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 6:15 | 1.8021 |  | 0 |  | 77.462 |  | 22729.5634
2017-08-21 | 6:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 6:30 | 1.7514 |  | 0 |  | 77.223 |  | 22659.439
2017-08-21 | 6:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 6:45 | 1.7865 |  | 0 |  | 76.716 |  | 22510.6628
2017-08-21 | 7:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 7:00 | 1.7319 |  | 0 |  | 76.5721 |  | 22468.4413
2017-08-21 | 7:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 7:15 | 1.7702 |  | 0 |  | 76.1067 |  | 22331.8659
2017-08-21 | 7:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 7:30 | 1.7093 |  | 0 |  | 76.1264 |  | 22337.6576
2017-08-21 | 7:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 7:45 | 1.7709 |  | 0 |  | 75.8656 |  | 22261.1393
2017-08-21 | 8:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 8:00 | 1.7468 |  | 0 |  | 76.1069 |  | 22331.9375
2017-08-21 | 8:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 8:15 | 1.7085 |  | 0 |  | 76.8461 |  | 22548.8548
2017-08-21 | 8:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 8:30 | 1.7577 |  | 0 |  | 77.4974 |  | 22739.9555
2017-08-21 | 8:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 8:45 | 1.7351 |  | 0 |  | 78.016 |  | 22892.112
2017-08-21 | 9:00 |  | 0 |  | 1.5 |  |  | 0
2017-08-21 | 9:00 | 1.7382 |  | 0 |  | 78.0796 | 0 | 22910.7781
2017-08-21 | 9:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 9:15 | 1.7288 |  | 0 |  | 78.8038 |  | 23123.2894
2017-08-21 | 9:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 9:30 | 1.7709 |  | 0 |  | 78.9903 |  | 23178.003
2017-08-21 | 9:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 9:45 | 1.7553 |  | 0 |  | 79.0293 |  | 23189.4402
2017-08-21 | 10:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 10:00 | 1.7631 |  | 0 |  | 78.6151 |  | 23067.9156
2017-08-21 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-08-21 | 10:15 | 1.7733 | 0 | 0 |  | 78.5181 | 0 | 23039.4395
2017-08-21 | 10:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 10:30 | 1.7569 |  | 0 |  | 78.0996 |  | 22916.6435
2017-08-21 | 10:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 10:45 | 1.7296 |  | 0 |  | 77.9233 |  | 22864.9276
2017-08-21 | 11:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 11:00 | 1.7405 |  | 0 |  | 77.9143 |  | 22862.2747
2017-08-21 | 11:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 11:15 | 1.7374 |  | 0 |  | 77.92 |  | 22863.9516
2017-08-21 | 11:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 11:30 | 1.7343 |  | 0 |  | 78.103 |  | 22917.6417
2017-08-21 | 11:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 11:45 | 1.7148 |  | 0 |  | 78.3671 |  | 22995.1518
2017-08-21 | 12:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 12:00 | 1.7327 |  | 0 |  | 78.6149 |  | 23067.8464
2017-08-21 | 12:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 12:15 | 1.7405 |  | 0 |  | 78.8553 |  | 23138.4071
2017-08-21 | 12:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 12:30 | 1.7507 |  | 0 |  | 79.0881 |  | 23206.7229
2017-08-21 | 12:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 12:45 | 1.7163 |  | 0 |  | 79.6908 |  | 23383.5699
2017-08-21 | 13:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 13:00 | 1.7429 |  | 0 |  | 80.4863 |  | 23616.9727
2017-08-21 | 13:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 13:15 | 1.7592 |  | 0 |  | 80.6127 |  | 23654.0764
2017-08-21 | 13:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 13:30 | 1.7148 |  | 0 |  | 81.0711 |  | 23788.5856
2017-08-21 | 13:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 13:45 | 1.7491 |  | 0 |  | 81.5103 |  | 23917.4441
2017-08-21 | 14:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 14:00 | 1.7327 |  | 0 |  | 81.9319 |  | 24041.1695
2017-08-21 | 14:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 14:15 | 1.7101 |  | 0 |  | 82.2736 |  | 24141.4331
2017-08-21 | 14:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 14:30 | 1.7429 |  | 0 |  | 82.7918 |  | 24293.4799
2017-08-21 | 14:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 14:45 | 1.7179 |  | 0 |  | 83.4876 |  | 24497.6343
2017-08-21 | 15:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 15:00 | 1.7522 |  | 0 |  | 83.8062 |  | 24591.1441
2017-08-21 | 15:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 15:15 | 1.7475 |  | 0 |  | 84.3267 |  | 24743.8693
2017-08-21 | 15:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 15:30 | 1.7343 |  | 0 |  | 84.1574 |  | 24694.1886
2017-08-21 | 15:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 15:45 | 1.7865 |  | 0 |  | 84.4206 |  | 24771.4052
2017-08-21 | 16:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 16:00 | 1.7616 |  | 0 |  | 82.7057 |  | 24268.2166
2017-08-21 | 16:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 16:15 | 1.728 |  | 0 |  | 82.4495 |  | 24193.0258
2017-08-21 | 16:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 16:30 | 1.7312 |  | 0 |  | 83.2686 |  | 24433.3843
2017-08-21 | 16:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 16:45 | 1.753 |  | 0 |  | 83.2012 |  | 24413.6078
2017-08-21 | 17:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 17:00 | 1.7397 |  | 0 |  | 83.3286 |  | 24450.9847
2017-08-21 | 17:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 17:15 | 1.7756 |  | 0 |  | 83.3201 |  | 24448.5064
2017-08-21 | 17:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 17:30 | 1.7717 |  | 0 |  | 82.7162 |  | 24271.3014
2017-08-21 | 17:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 17:45 | 1.7842 |  | 0 |  | 82.5119 |  | 24211.3451
2017-08-21 | 18:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 18:00 | 1.7803 |  | 0 |  | 81.9677 |  | 24051.671
2017-08-21 | 18:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 18:15 | 1.7616 |  | 0 |  | 81.5373 |  | 23925.36
2017-08-21 | 18:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 18:30 | 1.7865 |  | 0 |  | 81.1969 |  | 23825.4836
2017-08-21 | 18:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 18:45 | 1.7865 |  | 0 |  | 81.0173 |  | 23772.7803
2017-08-21 | 19:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 19:00 | 1.7624 |  | 0 |  | 80.3586 |  | 23579.5239
2017-08-21 | 19:15 |  | 0 |  | 1.5 | 79.9525 | 0 | 23460.3611
2017-08-21 | 19:15 | 1.7787 |  | 0 |  |  |  | 0
2017-08-21 | 19:30 |  |  |  |  | 79.5687 |  | 23347.7241
2017-08-21 | 19:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 19:30 | 1.7741 |  | 0 |  |  |  | 0
2017-08-21 | 19:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 19:45 | 1.7561 |  | 0 |  | 79.2012 |  | 23239.9003
2017-08-21 | 20:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 20:00 | 1.7787 |  | 0 |  | 78.8106 |  | 23125.2774
2017-08-21 | 20:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 20:15 | 1.7577 |  | 0 |  | 78.4261 |  | 23012.4523
2017-08-21 | 20:30 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 20:30 | 1.7725 |  | 0 |  | 78.0545 |  | 22903.4128
2017-08-21 | 20:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 20:45 | 1.767 |  | 0 |  | 77.8405 |  | 22840.62
2017-08-21 | 21:00 |  | 0 |  | 1.5 |  | 0 | 0
2017-08-21 | 21:00 | 1.7639 |  | 0 |  | 0 |  | 0
2017-08-21 | 21:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 21:15 | 0.03934 |  | 0 |  | 0 |  | 0
2017-08-21 | 21:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 21:30 | 0.03778 |  | 0 |  | 0 |  | 0
2017-08-21 | 21:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 21:45 | 0.03622 |  | 0 |  | 0 |  | 0
2017-08-21 | 22:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 22:00 | 0.03544 |  | 0 |  | 0 |  | 0
2017-08-21 | 22:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 22:15 | 0.03466 |  | 0 |  | 0 |  | 0
2017-08-21 | 22:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 22:30 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 22:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 22:45 | 0.03388 |  | 0 |  | 0 |  | 0
2017-08-21 | 23:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 23:00 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 23:15 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 23:15 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-21 | 23:30 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 23:30 | 0.03232 |  | 0 |  | 0 |  | 0
2017-08-21 | 23:45 |  | 0 |  | 0 |  | 0 | 0
2017-08-21 | 23:45 | 0.0331 |  | 0 |  | 0 |  | 0
2017-08-22 | 0:00 |  | 0 |  | 0 |  | 0 | 0
2017-08-22 | 0:00 | 0.03232 |  | 0 |  | 0 |  | 0
2017-08-22 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 1:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 1:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 5:15 | 2.1204 | 0 | 0 | 1.5 | 92.3833 | 0 | 27107.8933
2017-08-22 | 5:30 | 1.9503 | 0 | 0 | 1.5 | 86.8678 | 0 | 25489.4804
2017-08-22 | 5:45 | 1.8965 | 0 | 0 | 1.5 | 83.0295 | 0 | 24363.2241
2017-08-22 | 6:00 | 1.8302 | 0 | 0 | 1.5 | 80.6221 | 0 | 23656.8367
2017-08-22 | 6:15 | 1.7936 | 0 | 0 | 1.5 | 79.4225 | 0 | 23304.8196
2017-08-22 | 6:30 | 1.7592 | 0 | 0 | 1.5 | 78.7268 | 0 | 23100.6831
2017-08-22 | 6:45 | 1.7312 | 0 | 0 | 1.5 | 78.3516 | 0 | 22990.6051
2017-08-22 | 7:00 | 1.7101 | 0 | 0 | 1.5 | 78.0498 | 0 | 22902.0269
2017-08-22 | 7:15 | 1.7265 | 0 | 0 | 1.5 | 77.8842 | 0 | 22853.4387
2017-08-22 | 7:30 | 1.7819 | 0 | 0 | 1.5 | 77.4846 | 0 | 22736.2011
2017-08-22 | 7:45 | 1.7421 | 0 | 0 | 1.5 | 77.4084 | 0 | 22713.8321
2017-08-22 | 8:00 | 1.7234 | 0 | 0 | 1.5 | 77.8612 | 0 | 22846.7068
2017-08-22 | 8:15 | 1.7624 | 0 | 0 | 1.5 | 78.3344 | 0 | 22985.5614
2017-08-22 | 8:30 | 1.7312 | 0 | 0 | 1.5 | 78.3429 | 0 | 22988.0417
2017-08-22 | 8:45 | 1.7413 | 0 | 0 | 1.5 | 78.0126 | 0 | 22891.1404
2017-08-22 | 9:00 | 1.7553 | 0 | 0 | 1.5 | 78.2122 | 0 | 22949.6862
2017-08-22 | 9:15 | 1.7124 | 0 | 0 | 1.5 | 78.7568 | 0 | 23109.5015
2017-08-22 | 9:30 | 1.7171 | 0 | 0 | 1.5 | 79.5535 | 0 | 23343.2825
2017-08-22 | 9:45 | 1.7265 | 0 | 0 | 1.5 | 80.1962 | 0 | 23531.8579
2017-08-22 | 10:00 | 1.6641 | 0 | 0 | 1.5 | 81.1412 | 0 | 23809.1455
2017-08-22 | 10:15 | 1.7218 | 0 | 0 | 1.5 | 81.6915 | 0 | 23970.6284
2017-08-22 | 10:30 | 1.7468 | 0 | 0 | 1.5 | 81.7106 | 0 | 23976.232
2017-08-22 | 10:45 | 1.7046 | 0 | 0 | 1.5 | 81.9709 | 0 | 24052.6044
2017-08-22 | 11:00 | 1.7093 | 0 | 0 | 1.5 | 82.5787 | 0 | 24230.9403
2017-08-22 | 11:15 | 1.7499 | 0 | 0 | 1.5 | 83.4725 | 0 | 24493.2065
2017-08-22 | 11:30 | 1.7483 | 0 | 0 | 1.5 | 83.8093 | 0 | 24592.0487
2017-08-22 | 11:45 | 1.7218 | 0 | 0 | 1.5 | 84.5537 | 0 | 24810.4679
2017-08-22 | 12:00 | 1.689 | 0 | 0 | 1.5 | 85.158 | 0 | 24987.7985
2017-08-22 | 12:15 | 1.7312 | 0 | 0 | 1.5 | 85.55 | 0 | 25102.8084
2017-08-22 | 12:30 | 1.7382 | 0 | 0 | 1.5 | 85.7842 | 0 | 25171.5361
2017-08-22 | 12:45 | 1.6992 | 0 | 0 | 1.5 | 86.0256 | 0 | 25242.3792
2017-08-22 | 13:00 | 1.7592 | 0 | 0 | 1.5 | 86.4053 | 0 | 25353.7694
2017-08-22 | 13:15 | 1.6867 | 0 | 0 | 1.5 | 87.398 | 0 | 25645.0844
2017-08-22 | 13:30 | 1.8411 | 0 | 0 | 1.5 | 86.2065 | 0 | 25295.4472
2017-08-22 | 13:45 | 1.7358 | 0 | 0 | 1.5 | 84.4926 | 0 | 24792.5426
2017-08-22 | 14:00 | 1.6844 | 0 | 0 | 1.5 | 84.9843 | 0 | 24936.808
2017-08-22 | 14:15 | 1.6563 | 0 | 0 | 1.5 | 86.4127 | 0 | 25355.9654
2017-08-22 | 14:30 | 1.8068 | 0 | 0 | 1.5 | 86.1517 | 0 | 25279.3846
2017-08-22 | 14:45 | 1.7015 | 0 | 0 | 1.5 | 85.2504 | 0 | 25014.911
2017-08-22 | 15:00 | 1.682 | 0 | 0 | 1.5 | 86.4666 | 0 | 25371.7592
2017-08-22 | 15:15 | 1.8396 | 0 | 0 | 1.5 | 86.7783 | 0 | 25463.2317
2017-08-22 | 15:30 | 1.7936 | 0 | 0 | 1.5 | 84.5816 | 0 | 24818.6704
2017-08-22 | 15:45 | 1.6594 | 0 | 0 | 1.5 | 86.0682 | 0 | 25254.8754
2017-08-22 | 16:00 | 1.8443 | 0 | 0 | 1.5 | 87.6007 | 0 | 25704.5574
2017-08-22 | 16:15 | 1.8482 | 0 | 0 | 1.5 | 85.0138 | 0 | 24945.4805
2017-08-22 | 16:30 | 1.682 | 0 | 0 | 1.5 | 85.3621 | 0 | 25047.6876
2017-08-22 | 16:45 | 1.6664 | 0 | 0 | 1.5 | 87.6811 | 0 | 25728.1329
2017-08-22 | 17:00 | 1.8778 | 0 | 0 | 1.5 | 86.9632 | 0 | 25517.5019
2017-08-22 | 17:15 | 1.7982 | 0 | 0 | 1.5 | 84.25 | 0 | 24721.3527
2017-08-22 | 17:30 | 1.7327 | 0 | 0 | 1.5 | 84.1309 | 0 | 24686.3978
2017-08-22 | 17:45 | 1.7327 | 0 | 0 | 1.5 | 84.4467 | 0 | 24779.0681
2017-08-22 | 18:00 | 1.7694 | 0 | 0 | 1.5 | 84.7746 | 0 | 24875.2912
2017-08-22 | 18:15 | 1.8419 | 0 | 0 | 1.5 | 82.9885 | 0 | 24351.2043
2017-08-22 | 18:30 | 1.7756 | 0 | 0 | 1.5 | 82.1681 | 0 | 24110.4565
2017-08-22 | 18:45 | 1.7819 | 0 | 0 | 1.5 | 82.1358 | 0 | 24100.9778
2017-08-22 | 19:00 | 1.7538 | 0 | 0 | 1.5 | 82.3157 | 0 | 24153.7774
2017-08-22 | 19:15 | 1.7358 | 0 | 0 | 1.5 | 82.2809 | 0 | 24143.5734
2017-08-22 | 19:30 | 1.7405 | 0 | 0 | 1.5 | 81.9666 | 0 | 24051.3509
2017-08-22 | 19:45 | 1.767 | 0 | 0 | 1.5 | 81.5208 | 0 | 23920.5313
2017-08-22 | 20:00 | 1.7702 | 0 | 0 | 1.5 | 81.1749 | 0 | 23819.0317
2017-08-22 | 20:15 | 1.7717 | 0 | 0 | 1.5 | 80.7301 | 0 | 23688.512
2017-08-22 | 20:30 | 1.753 | 0 | 0 | 1.5 | 80.241 | 0 | 23545.0058
2017-08-22 | 20:45 | 1.7678 | 0 | 0 | 1.5 | 79.6853 | 0 | 23381.9355
2017-08-22 | 21:00 | 1.7826 | 0 | 0 | 1.5 | 79.4786 | 0 | 23321.2921
2017-08-22 | 21:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 21:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 21:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 22:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 22:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 22:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 23:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 23:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-22 | 23:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 0:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 1:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 1:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 2:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 2:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 4:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 5:15 | 1.9698 | 0 | 0 | 1.5 | 96.2727 | 0 | 28249.1667
2017-08-23 | 5:30 | 1.9948 | 0 | 0 | 1.5 | 90.5167 | 0 | 26560.1751
2017-08-23 | 5:45 | 1.9301 | 0 | 0 | 1.5 | 85.8972 | 0 | 25204.6933
2017-08-23 | 6:00 | 1.8411 | 0 | 0 | 1.5 | 82.7646 | 0 | 24285.4945
2017-08-23 | 6:15 | 1.8216 | 0 | 0 | 1.5 | 80.8708 | 0 | 23729.7886
2017-08-23 | 6:30 | 1.7897 | 0 | 0 | 1.5 | 79.5828 | 0 | 23351.8814
2017-08-23 | 6:45 | 1.7756 | 0 | 0 | 1.5 | 79.1658 | 0 | 23229.5014
2017-08-23 | 7:00 | 1.7468 | 0 | 0 | 1.5 | 78.9314 | 0 | 23160.7335
2017-08-23 | 7:15 | 1.7725 | 0 | 0 | 1.5 | 78.5878 | 0 | 23059.9012
2017-08-23 | 7:30 | 1.7803 | 0 | 0 | 1.5 | 78.7892 | 0 | 23119.0068
2017-08-23 | 7:45 | 1.707 | 0 | 0 | 1.5 | 78.7657 | 0 | 23112.1071
2017-08-23 | 8:00 | 1.7397 | 0 | 0 | 1.5 | 79.127 | 0 | 23218.1088
2017-08-23 | 8:15 | 1.7499 | 0 | 0 | 1.5 | 79.8319 | 0 | 23424.9495
2017-08-23 | 8:30 | 1.7522 | 0 | 0 | 1.5 | 79.6466 | 0 | 23370.5922
2017-08-23 | 8:45 | 1.7397 | 0 | 0 | 1.5 | 79.7649 | 0 | 23405.2939
2017-08-23 | 9:00 | 1.7358 | 0 | 0 | 1.5 | 79.6457 | 0 | 23370.3169
2017-08-23 | 9:15 | 1.728 | 0 | 0 | 1.5 | 79.7155 | 0 | 23390.8053
2017-08-23 | 9:30 | 1.7218 | 0 | 0 | 1.5 | 79.5981 | 0 | 23356.3676
2017-08-23 | 9:45 | 1.7351 | 0 | 0 | 1.5 | 79.5451 | 0 | 23340.791
2017-08-23 | 10:00 | 1.739 | 0 | 0 | 1.5 | 80.1157 | 0 | 23508.2375
2017-08-23 | 10:15 | 1.7312 | 0 | 0 | 1.5 | 81.0188 | 0 | 23773.2393
2017-08-23 | 10:30 | 1.7366 | 0 | 0 | 1.5 | 81.3392 | 0 | 23867.2596
2017-08-23 | 10:45 | 1.6945 | 0 | 0 | 1.5 | 81.6092 | 0 | 23946.4798
2017-08-23 | 11:00 | 1.7187 | 0 | 0 | 1.5 | 82.2032 | 0 | 24120.7546
2017-08-23 | 11:15 | 1.7296 | 0 | 0 | 1.5 | 82.8996 | 0 | 24325.1171
2017-08-23 | 11:30 | 1.7241 | 0 | 0 | 1.5 | 83.1516 | 0 | 24399.0675
2017-08-23 | 11:45 | 1.6695 | 0 | 0 | 1.5 | 83.9393 | 0 | 24630.198
2017-08-23 | 12:00 | 1.7265 | 0 | 0 | 1.5 | 84.846 | 0 | 24896.2497
2017-08-23 | 12:15 | 1.7148 | 0 | 0 | 1.5 | 85.6078 | 0 | 25119.7865
2017-08-23 | 12:30 | 1.714 | 0 | 0 | 1.5 | 85.3712 | 0 | 25050.3381
2017-08-23 | 12:45 | 1.739 | 0 | 0 | 1.5 | 85.236 | 0 | 25010.6642
2017-08-23 | 13:00 | 1.6797 | 0 | 0 | 1.5 | 85.9382 | 0 | 25216.7127
2017-08-23 | 13:15 | 1.7436 | 0 | 0 | 1.5 | 86.8376 | 0 | 25480.6353
2017-08-23 | 13:30 | 1.7351 | 0 | 0 | 1.5 | 87.3317 | 0 | 25625.6259
2017-08-23 | 13:45 | 1.707 | 0 | 0 | 1.5 | 88.5782 | 0 | 25991.3797
2017-08-23 | 14:00 | 1.7382 | 0 | 0 | 1.5 | 89.642 | 0 | 26303.5258
2017-08-23 | 14:15 | 1.7546 | 0 | 0 | 1.5 | 90.2288 | 0 | 26475.6938
2017-08-23 | 14:30 | 1.7631 | 0 | 0 | 1.5 | 90.7174 | 0 | 26619.0815
2017-08-23 | 14:45 | 1.9028 | 0 | 0 | 1.5 | 88.0393 | 0 | 25833.2481
2017-08-23 | 15:00 | 1.6992 | 0 | 0 | 1.5 | 87.4124 | 0 | 25649.2886
2017-08-23 | 15:15 | 1.7132 | 0 | 0 | 1.5 | 88.4225 | 0 | 25945.6767
2017-08-23 | 15:30 | 1.746 | 0 | 0 | 1.5 | 89.5646 | 0 | 26280.8097
2017-08-23 | 15:45 | 1.753 | 0 | 0 | 1.5 | 89.73 | 0 | 26329.3334
2017-08-23 | 16:00 | 1.8996 | 0 | 0 | 1.5 | 87.1387 | 0 | 25568.9895
2017-08-23 | 16:15 | 1.7374 | 0 | 0 | 1.5 | 86.2965 | 0 | 25321.8614
2017-08-23 | 16:30 | 1.6875 | 0 | 0 | 1.5 | 87.2883 | 0 | 25612.8677
2017-08-23 | 16:45 | 1.7132 | 0 | 0 | 1.5 | 87.9481 | 0 | 25806.4733
2017-08-23 | 17:00 | 1.6984 | 0 | 0 | 1.5 | 88.735 | 0 | 26037.3822
2017-08-23 | 17:15 | 1.7569 | 0 | 0 | 1.5 | 88.8141 | 0 | 26060.6086
2017-08-23 | 17:30 | 1.7709 | 0 | 0 | 1.5 | 88.3069 | 0 | 25911.754
2017-08-23 | 17:45 | 1.7725 | 0 | 0 | 1.5 | 87.4646 | 0 | 25664.6147
2017-08-23 | 18:00 | 1.7507 | 0 | 0 | 1.5 | 86.9636 | 0 | 25517.614
2017-08-23 | 18:15 | 1.7826 | 0 | 0 | 1.5 | 86.4718 | 0 | 25373.3085
2017-08-23 | 18:30 | 1.7608 | 0 | 0 | 1.5 | 85.5493 | 0 | 25102.6159
2017-08-23 | 18:45 | 1.7951 | 0 | 0 | 1.5 | 84.18 | 0 | 24700.8306
2017-08-23 | 19:00 | 1.7904 | 0 | 0 | 1.5 | 82.6453 | 0 | 24250.4794
2017-08-23 | 19:15 | 1.785 | 0 | 0 | 1.5 | 81.4329 | 0 | 23894.726
2017-08-23 | 19:30 | 1.7873 | 0 | 0 | 1.5 | 80.5234 | 0 | 23627.8592
2017-08-23 | 19:45 | 1.7741 | 0 | 0 | 1.5 | 79.9269 | 0 | 23452.837
2017-08-23 | 20:00 | 1.7663 | 0 | 0 | 1.5 | 79.341 | 0 | 23280.906
2017-08-23 | 20:15 | 1.7717 | 0 | 0 | 1.5 | 78.9845 | 0 | 23176.3037
2017-08-23 | 20:30 | 1.7717 | 0 | 0 | 1.5 | 78.3998 | 0 | 23004.7557
2017-08-23 | 20:45 | 1.7624 | 0 | 0 | 1.5 | 78.1124 | 0 | 22920.4132
2017-08-23 | 21:00 | 1.7624 | 0 | 0 | 1.5 | 77.6442 | 0 | 22783.0411
2017-08-23 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 22:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 23:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 23:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 23:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 0:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 0:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 0:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 0:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 1:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 1:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 1:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 2:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 2:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 2:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 3:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 3:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 5:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-08-24 | 5:15 | 2.04 | 0 | 0 | 1.5 | 95.058 | 0 | 27892.7261
2017-08-24 | 5:30 | 1.9839 | 0 | 0 | 1.5 | 89.9782 | 0 | 26402.18
2017-08-24 | 5:45 | 1.9566 | 0 | 0 | 1.5 | 85.1776 | 0 | 24993.5562
2017-08-24 | 6:00 | 1.863 | 0 | 0 | 1.5 | 81.7571 | 0 | 23989.8676
2017-08-24 | 6:15 | 1.8045 | 0 | 0 | 1.5 | 80.1756 | 0 | 23525.8024
2017-08-24 | 6:30 | 1.7975 | 0 | 0 | 1.5 | 79.2512 | 0 | 23254.5635
2017-08-24 | 6:45 | 1.7975 | 0 | 0 | 1.5 | 78.5529 | 0 | 23049.6682
2017-08-24 | 7:00 | 1.7124 | 0 | 0 | 1.5 | 78.4578 | 0 | 23021.754
2017-08-24 | 7:15 | 1.7312 | 0 | 0 | 1.5 | 78.3213 | 0 | 22981.7083
2017-08-24 | 7:30 | 1.7702 | 0 | 0 | 1.5 | 78.2415 | 0 | 22958.303
2017-08-24 | 7:30 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 7:45 | 1.7546 | 0 | 0 | 1.5 | 78.0677 | 0 | 22907.2878
2017-08-24 | 8:00 | 1.7553 | 0 | 0 | 1.5 | 78.1184 | 0 | 22922.1594
2017-08-24 | 8:15 | 1.7132 | 0 | 0 | 1.5 | 79.1684 | 0 | 23230.2717
2017-08-24 | 8:30 | 1.6937 | 0 | 0 | 1.5 | 79.3675 | 0 | 23288.6833
2017-08-24 | 8:45 | 1.7655 | 0 | 0 | 1.5 | 79.4018 | 0 | 23298.7462
2017-08-24 | 9:00 | 1.7772 | 0 | 0 | 1.5 | 79.6328 | 0 | 23366.5335
2017-08-24 | 9:15 | 1.7273 | 0 | 0 | 1.5 | 79.5678 | 0 | 23347.4688
2017-08-24 | 9:30 | 1.7117 | 0 | 0 | 1.5 | 79.4366 | 0 | 23308.9613
2017-08-24 | 9:30 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 9:45 | 1.767 | 0 | 0 | 1.5 | 79.3533 | 0 | 23284.5149
2017-08-24 | 10:00 | 1.7296 | 0 | 0 | 1.5 | 79.8328 | 0 | 23425.2385
2017-08-24 | 10:15 | 1.7592 | 0 | 0 | 1.5 | 79.7241 | 0 | 23393.3238
2017-08-24 | 10:30 | 1.7241 | 0 | 0 | 1.5 | 79.542 | 0 | 23339.891
2017-08-24 | 10:45 | 1.6914 | 0 | 0 | 1.5 | 79.7013 | 0 | 23386.6392
2017-08-24 | 11:00 | 1.7397 | 0 | 0 | 1.5 | 80.8676 | 0 | 23728.8687
2017-08-24 | 11:15 | 1.7452 | 0 | 0 | 1.5 | 81.2597 | 0 | 23843.9236
2017-08-24 | 11:30 | 1.7078 | 0 | 0 | 1.5 | 81.5039 | 0 | 23915.5703
2017-08-24 | 11:45 | 1.7163 | 0 | 0 | 1.5 | 81.5849 | 0 | 23939.3383
2017-08-24 | 12:00 | 1.7093 | 0 | 0 | 1.5 | 81.9191 | 0 | 24037.4083
2017-08-24 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 12:15 | 1.6914 | 0 | 0 | 1.5 | 82.3945 | 0 | 24176.9095
2017-08-24 | 12:30 | 1.6883 | 0 | 0 | 1.5 | 82.8138 | 0 | 24299.9318
2017-08-24 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 12:45 | 1.7148 | 0 | 0 | 1.5 | 83.2215 | 0 | 24419.5738
2017-08-24 | 13:00 | 1.7249 | 0 | 0 | 1.5 | 83.4685 | 0 | 24492.0489
2017-08-24 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 13:15 | 1.7218 | 0 | 0 | 1.5 | 83.8317 | 0 | 24598.6034
2017-08-24 | 13:30 | 0.04012 | 0 | 0 | 1.5 | 100 | 0 | 29342.8571
2017-08-24 | 13:45 | 0.037 | 0 | 0 | 1.5 | 100 | 0 | 29342.8571
2017-08-24 | 14:00 | 1.8138 | 0 | 0 | 1.5 | 99.3795 | 0 | 29160.7806
2017-08-24 | 14:15 | 2.0361 | 0 | 0 | 1.5 | 95.6037 | 0 | 28052.8589
2017-08-24 | 14:30 | 1.8692 | 0 | 0 | 1.5 | 89.281 | 0 | 26197.589
2017-08-24 | 14:45 | 1.7694 | 0 | 0 | 1.5 | 87.7694 | 0 | 25754.0546
2017-08-24 | 15:00 | 1.8076 | 0 | 0 | 1.5 | 87.4754 | 0 | 25667.7913
2017-08-24 | 15:15 | 1.7694 | 0 | 0 | 1.5 | 87.2706 | 0 | 25607.6804
2017-08-24 | 15:30 | 1.7702 | 0 | 0 | 1.5 | 86.9827 | 0 | 25523.215
2017-08-24 | 15:45 | 1.7928 | 0 | 0 | 1.5 | 86.346 | 0 | 25336.3949
2017-08-24 | 16:00 | 1.7631 | 0 | 0 | 1.5 | 85.6183 | 0 | 25122.8493
2017-08-24 | 16:15 | 1.7452 | 0 | 0 | 1.5 | 85.9828 | 0 | 25229.8178
2017-08-24 | 16:30 | 1.7312 | 0 | 0 | 1.5 | 85.9075 | 0 | 25207.7153
2017-08-24 | 16:45 | 1.7616 | 0 | 0 | 1.5 | 85.6736 | 0 | 25139.0865
2017-08-24 | 17:00 | 1.767 | 0 | 0 | 1.5 | 85.5149 | 0 | 25092.5173
2017-08-24 | 17:15 | 1.7928 | 0 | 0 | 1.5 | 85.4243 | 0 | 25065.9262
2017-08-24 | 17:30 | 1.8201 | 0 | 0 | 1.5 | 84.4348 | 0 | 24775.5824
2017-08-24 | 17:45 | 1.7873 | 0 | 0 | 1.5 | 83.6156 | 0 | 24535.2084
2017-08-24 | 18:00 | 1.778 | 0 | 0 | 1.5 | 82.9784 | 0 | 24348.236
2017-08-24 | 18:15 | 1.7514 | 0 | 0 |  | 82.4771 | 0 | 24201.1523
2017-08-24 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 18:30 | 1.7608 | 0 | 0 | 1.5 | 81.9714 | 0 | 24052.7455
2017-08-24 | 18:45 | 1.7647 | 0 | 0 | 1.5 | 81.3456 | 0 | 23869.1244
2017-08-24 | 19:00 | 1.7538 | 0 | 0 | 1.5 | 80.7256 | 0 | 23687.2022
2017-08-24 | 19:15 | 1.7507 | 0 | 0 | 1.5 | 79.9468 | 0 | 23458.6733
2017-08-24 | 19:30 | 1.7795 | 0 | 0 | 1.5 | 79.2516 | 0 | 23254.6756
2017-08-24 | 19:45 | 1.7296 | 0 | 0 | 1.5 | 78.9307 | 0 | 23160.5143
2017-08-24 | 20:00 | 1.7663 | 0 | 0 | 1.5 | 78.8665 | 0 | 23141.6868
2017-08-24 | 20:15 | 1.7631 | 0 | 0 | 1.5 | 78.6826 | 0 | 23087.7168
2017-08-24 | 20:30 | 1.7803 | 0 | 0 | 1.5 | 78.382 | 0 | 22999.5239
2017-08-24 | 20:45 | 1.7787 | 0 | 0 |  | 78.167 | 0 | 22936.4446
2017-08-24 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-08-24 | 21:00 | 1.7842 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 21:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 21:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 21:45 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 22:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 22:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 22:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 22:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 23:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 23:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 23:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 0:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 0:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 0:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 0:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 1:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 1:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 1:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 1:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 2:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 2:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 2:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 2:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 3:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 3:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 3:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 3:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 4:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 4:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 4:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 4:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 5:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 5:15 | 2.1719 | 0 | 0 | 1.5 | 90.5127 | 0 | 26559.0219
2017-08-25 | 5:30 | 1.8193 | 0 | 0 | 1.5 | 86.3161 | 0 | 25327.6035
2017-08-25 | 5:45 | 1.7288 | 0 | 0 | 1.5 | 85.5946 | 0 | 25115.9003
2017-08-25 | 6:00 | 1.7912 | 0 | 0 | 1.5 | 85.391 | 0 | 25056.17
2017-08-25 | 6:15 | 1.7936 | 0 | 0 | 1.5 | 85.3931 | 0 | 25056.761
2017-08-25 | 6:30 | 1.7187 | 0 | 0 | 1.5 | 85.9318 | 0 | 25214.8544
2017-08-25 | 6:45 | 1.6929 | 0 | 0 | 1.5 | 86.7314 | 0 | 25449.4573
2017-08-25 | 7:00 | 1.7343 | 0 | 0 | 1.5 | 87.5005 | 0 | 25675.1344
2017-08-25 | 7:15 | 1.7655 | 0 | 0 | 1.5 | 88.0619 | 0 | 25839.8766
2017-08-25 | 7:30 | 1.7312 | 0 | 0 | 1.5 | 88.6462 | 0 | 26011.3149
2017-08-25 | 7:45 | 1.6781 | 0 | 0 | 1.5 | 90.0389 | 0 | 26419.9975
2017-08-25 | 8:00 | 1.785 | 0 | 0 | 1.5 | 90.2875 | 0 | 26492.9272
2017-08-25 | 8:15 | 1.8739 | 0 | 0 | 1.5 | 87.0136 | 0 | 25532.2684
2017-08-25 | 8:30 | 1.8466 | 0 | 0 | 1.5 | 84.4293 | 0 | 24773.9551
2017-08-25 | 8:45 | 1.7826 | 0 | 0 | 1.5 | 82.9587 | 0 | 24342.4669
2017-08-25 | 9:00 | 1.767 | 0 | 0 | 1.5 | 82.5536 | 0 | 24223.5972
2017-08-25 | 9:15 | 1.7678 | 0 | 0 | 1.5 | 82.3973 | 0 | 24177.7335
2017-08-25 | 9:30 | 1.7522 | 0 | 0 | 1.5 | 81.6811 | 0 | 23967.5749
2017-08-25 | 9:45 | 1.7709 | 0 | 0 | 1.5 | 81.5746 | 0 | 23936.3251
2017-08-25 | 10:00 | 1.7046 | 0 | 0 | 1.5 | 81.8865 | 0 | 24027.8493
2017-08-25 | 10:15 | 1.7717 | 0 | 0 | 1.5 | 82.2213 | 0 | 24126.0824
2017-08-25 | 10:30 | 1.7475 | 0 | 0 | 1.5 | 82.4891 | 0 | 24204.6714
2017-08-25 | 10:45 | 1.7421 | 0 | 0 | 1.5 | 82.5089 | 0 | 24210.4719
2017-08-25 | 11:00 | 1.682 | 0 | 0 | 1.5 | 82.968 | 0 | 24345.1935
2017-08-25 | 11:15 | 1.721 | 0 | 0 | 1.5 | 83.2814 | 0 | 24437.1452
2017-08-25 | 11:30 | 1.7327 | 0 | 0 | 1.5 | 83.8169 | 0 | 24594.2738
2017-08-25 | 11:45 | 1.7374 | 0 | 0 | 1.5 | 83.809 | 0 | 24591.9434
2017-08-25 | 12:00 | 1.7195 | 0 | 0 | 1.5 | 83.6774 | 0 | 24553.3417
2017-08-25 | 12:15 | 1.7234 | 0 | 0 | 1.5 | 83.8418 | 0 | 24601.5764
2017-08-25 | 12:30 | 1.6859 | 0 | 0 | 1.5 | 84.1686 | 0 | 24697.4838
2017-08-25 | 12:45 | 1.7218 | 0 | 0 | 1.5 | 84.2952 | 0 | 24734.6304
2017-08-25 | 13:00 | 1.7452 | 0 | 0 | 1.5 | 84.419 | 0 | 24770.9351
2017-08-25 | 13:15 | 1.7 | 0 | 0 | 1.5 | 84.6521 | 0 | 24839.3333
2017-08-25 | 13:30 | 1.7195 | 0 | 0 | 1.5 | 84.7708 | 0 | 24874.1742
2017-08-25 | 13:45 | 1.7085 | 0 | 0 | 1.5 | 84.9278 | 0 | 24920.2372
2017-08-25 | 14:00 | 1.7273 | 0 | 0 | 1.5 | 85.0716 | 0 | 24962.4342
2017-08-25 | 14:15 | 1.7655 | 0 | 0 | 1.5 | 85.195 | 0 | 24998.636
2017-08-25 | 14:30 | 1.7491 | 0 | 0 | 1.5 | 85.3285 | 0 | 25037.8084
2017-08-25 | 14:45 | 1.7015 | 0 | 0 | 1.5 | 85.8472 | 0 | 25190.0119
2017-08-25 | 15:00 | 1.7709 | 0 | 0 | 1.5 | 85.8809 | 0 | 25199.9069
2017-08-25 | 15:15 | 1.7078 | 0 | 0 | 1.5 | 85.9185 | 0 | 25210.9456
2017-08-25 | 15:30 | 1.7686 | 0 | 0 | 1.5 | 85.8861 | 0 | 25201.4292
2017-08-25 | 15:45 | 1.7413 | 0 | 0 | 1.5 | 85.908 | 0 | 25207.8676
2017-08-25 | 16:00 | 1.7343 | 0 | 0 | 1.5 | 85.8935 | 0 | 25203.6184
2017-08-25 | 16:15 | 1.7483 | 0 | 0 | 1.5 | 86.2118 | 0 | 25297.0074
2017-08-25 | 16:30 | 1.7647 | 0 | 0 | 1.5 | 85.884 | 0 | 25200.8068
2017-08-25 | 16:45 | 1.7546 | 0 | 0 | 1.5 | 85.6037 | 0 | 25118.5711
2017-08-25 | 17:00 | 1.7452 | 0 | 0 | 1.5 | 85.2103 | 0 | 25003.1334
2017-08-25 | 17:15 | 1.7772 | 0 | 0 | 1.5 | 84.7077 | 0 | 24855.667
2017-08-25 | 17:30 | 1.7569 | 0 | 0 | 1.5 | 83.8954 | 0 | 24617.3121
2017-08-25 | 17:45 | 1.7686 | 0 | 0 | 1.5 | 83.2583 | 0 | 24430.3731
2017-08-25 | 18:00 | 1.753 | 0 | 0 | 1.5 | 82.7566 | 0 | 24283.1442
2017-08-25 | 18:15 | 1.7507 | 0 | 0 | 1.5 | 82.2544 | 0 | 24135.7896
2017-08-25 | 18:30 | 1.7475 | 0 | 0 | 1.5 | 81.7732 | 0 | 23994.6047
2017-08-25 | 18:45 | 1.7491 | 0 | 0 | 1.5 | 81.3426 | 0 | 23868.2356
2017-08-25 | 19:00 | 1.7624 | 0 | 0 | 1.5 | 80.7293 | 0 | 23688.297
2017-08-25 | 19:15 | 1.7764 | 0 | 0 | 1.5 | 80.0342 | 0 | 23484.3219
2017-08-25 | 19:30 | 1.7858 | 0 | 0 | 1.5 | 79.4386 | 0 | 23309.5499
2017-08-25 | 19:45 | 1.7943 | 0 | 0 | 1.5 | 78.9353 | 0 | 23161.8664
2017-08-25 | 20:00 | 1.753 | 0 | 0 | 1.5 | 78.3433 | 0 | 22988.1514
2017-08-25 | 20:15 | 1.7078 | 0 | 0 | 1.5 | 78.1891 | 0 | 22942.903
2017-08-25 | 20:30 | 1.7709 | 0 | 0 | 1.5 | 78.4583 | 0 | 23021.9151
2017-08-25 | 20:45 | 1.778 | 0 | 0 | 1.5 | 77.7502 | 0 | 22814.143
2017-08-25 | 21:00 | 1.7834 | 0 | 0 | 1.5 | 78.1131 | 0 | 22920.6036
2017-08-25 | 21:15 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 21:30 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 21:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 22:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 22:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 22:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 23:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 0:15 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 0:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 0:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 0:45 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 0:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 1:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 1:15 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 1:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 1:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 1:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 1:45 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 1:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 2:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 2:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 2:15 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 2:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 2:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 2:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 2:45 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 2:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 3:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 3:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 3:15 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 3:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 3:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 3:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 3:45 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 3:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 4:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 4:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 4:15 | 0.03466 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 4:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 4:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 4:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 4:45 | 0.03544 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 4:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 5:00 | 0.03544 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-08-26 | 5:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 5:15 | 2.1492 | 0 | 0 |  | 91.8167 | 0 | 26941.6331
2017-08-26 | 5:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 5:30 | 1.973 | 0 | 0 | 1.5 | 85.0797 | 0 | 24964.8183
2017-08-26 | 5:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 5:45 | 1.7631 | 0 | 0 |  | 82.8022 | 0 | 24296.5225
2017-08-26 | 5:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 6:00 | 1.7031 | 0 | 0 | 1.5 | 83.1212 | 0 | 24390.1306
2017-08-26 | 6:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 6:15 | 1.6859 | 0 | 0 |  | 84.2223 | 0 | 24713.2239
2017-08-26 | 6:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 6:30 | 1.7007 | 0 | 0 | 1.5 | 85.3923 | 0 | 25056.5371
2017-08-26 | 6:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 6:45 | 1.7163 | 0 | 0 |  | 86.3232 | 0 | 25329.6833
2017-08-26 | 6:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 7:00 | 1.7031 | 0 | 0 | 1.5 | 87.2965 | 0 | 25615.2967
2017-08-26 | 7:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 7:15 | 1.8489 | 0 | 0 |  | 86.8659 | 0 | 25488.9229
2017-08-26 | 7:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 7:30 | 1.895 | 0 | 0 | 1.5 | 83.2919 | 0 | 24440.2256
2017-08-26 | 7:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 7:45 | 1.8396 | 0 | 0 |  | 81.1723 | 0 | 23818.2706
2017-08-26 | 7:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 8:00 | 1.7631 | 0 | 0 | 1.5 | 80.3388 | 0 | 23573.7055
2017-08-26 | 8:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 8:15 | 1.7709 | 0 | 0 |  | 80.1993 | 0 | 23532.7713
2017-08-26 | 8:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 8:30 | 1.7748 | 0 | 0 | 1.5 | 80.0865 | 0 | 23499.6567
2017-08-26 | 8:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 8:45 | 1.7616 | 0 | 0 |  | 80.1246 | 0 | 23510.839
2017-08-26 | 8:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 9:00 | 1.7109 | 0 | 0 | 1.5 | 80.0439 | 0 | 23487.1672
2017-08-26 | 9:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 9:15 | 1.7631 | 0 | 0 |  | 80.3355 | 0 | 23572.7295
2017-08-26 | 9:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 9:30 | 1.7085 | 0 | 0 | 1.5 | 80.3007 | 0 | 23562.5279
2017-08-26 | 9:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 9:45 | 1.7491 | 0 | 0 |  | 80.4371 | 0 | 23602.5554
2017-08-26 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 10:00 | 1.7764 | 0 | 0 | 1.5 | 80.0621 | 0 | 23492.4997
2017-08-26 | 10:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 10:15 | 1.7327 | 0 | 0 |  | 80.2832 | 0 | 23557.3744
2017-08-26 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 10:30 | 1.7553 | 0 | 0 | 1.5 | 80.2953 | 0 | 23560.9317
2017-08-26 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 10:45 | 1.7741 | 0 | 0 |  | 80.094 | 0 | 23501.873
2017-08-26 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 11:00 | 1.7585 | 0 | 0 | 1.5 | 79.9313 | 0 | 23454.1354
2017-08-26 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 11:15 | 1.7366 | 0 | 0 |  | 80.0606 | 0 | 23492.0742
2017-08-26 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 11:30 | 1.7366 | 0 | 0 | 1.5 | 80.0992 | 0 | 23503.3929
2017-08-26 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 11:45 | 1.7444 | 0 | 0 |  | 80.1083 | 0 | 23506.0549
2017-08-26 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 12:00 | 1.7733 | 0 | 0 | 1.5 | 80.0501 | 0 | 23488.9894
2017-08-26 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 12:15 | 1.7592 | 0 | 0 |  | 79.9601 | 0 | 23462.582
2017-08-26 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 12:30 | 1.7405 | 0 | 0 | 1.5 | 79.8867 | 0 | 23441.0279
2017-08-26 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 12:45 | 1.7577 | 0 | 0 |  | 79.8961 | 0 | 23443.8061
2017-08-26 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 13:00 | 1.7561 | 0 | 0 | 1.5 | 79.8999 | 0 | 23444.9208
2017-08-26 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 13:15 | 1.7397 | 0 | 0 |  | 79.8994 | 0 | 23444.753
2017-08-26 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 13:30 | 1.7546 | 0 | 0 | 1.5 | 79.8927 | 0 | 23442.8143
2017-08-26 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 13:45 | 1.7444 | 0 | 0 |  | 79.9819 | 0 | 23468.989
2017-08-26 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 14:00 | 1.753 | 0 | 0 | 1.5 | 80.0941 | 0 | 23501.8865
2017-08-26 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 14:15 | 1.7444 | 0 | 0 |  | 80.1666 | 0 | 23523.1674
2017-08-26 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 14:30 | 1.7546 | 0 | 0 | 1.5 | 80.2579 | 0 | 23549.9689
2017-08-26 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 14:45 | 1.7608 | 0 | 0 |  | 80.2146 | 0 | 23537.2599
2017-08-26 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 15:00 | 1.7444 | 0 | 0 | 1.5 | 80.3249 | 0 | 23569.6066
2017-08-26 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 15:15 | 1.7296 | 0 | 0 |  | 80.4389 | 0 | 23603.0794
2017-08-26 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 15:30 | 1.739 | 0 | 0 | 1.5 | 80.494 | 0 | 23619.2515
2017-08-26 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 15:45 | 1.7468 | 0 | 0 |  | 80.5461 | 0 | 23634.5127
2017-08-26 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 16:00 | 1.7319 | 0 | 0 | 1.5 | 80.5663 | 0 | 23640.4631
2017-08-26 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 16:15 | 1.739 | 0 | 0 |  | 80.6135 | 0 | 23654.2915
2017-08-26 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 16:30 | 1.7444 | 0 | 0 | 1.5 | 80.6258 | 0 | 23657.9113
2017-08-26 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 16:45 | 1.7522 | 0 | 0 |  | 80.6372 | 0 | 23661.247
2017-08-26 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 17:00 | 1.7358 | 0 | 0 | 1.5 | 80.6287 | 0 | 23658.7666
2017-08-26 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 17:15 | 1.7499 | 0 | 0 |  | 80.5825 | 0 | 23645.2181
2017-08-26 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 17:30 | 1.7436 | 0 | 0 | 1.5 | 80.435 | 0 | 23601.9131
2017-08-26 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 17:45 | 1.7553 | 0 | 0 |  | 80.3185 | 0 | 23567.7307
2017-08-26 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 18:00 | 1.7608 | 0 | 0 | 1.5 | 80.1541 | 0 | 23519.496
2017-08-26 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 18:15 | 1.7421 | 0 | 0 |  | 80.0053 | 0 | 23475.8394
2017-08-26 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 18:30 | 1.7538 | 0 | 0 | 1.5 | 79.7923 | 0 | 23413.3512
2017-08-26 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 18:45 | 1.746 | 0 | 0 |  | 79.643 | 0 | 23369.5446
2017-08-26 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 19:00 | 1.7616 | 0 | 0 | 1.5 | 79.4254 | 0 | 23305.6726
2017-08-26 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 19:15 | 1.7624 | 0 | 0 |  | 79.103 | 0 | 23211.0771
2017-08-26 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 19:30 | 1.7702 | 0 | 0 | 1.5 | 78.7968 | 0 | 23121.2187
2017-08-26 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 19:45 | 1.76 | 0 | 0 |  | 78.5204 | 0 | 23040.1179
2017-08-26 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 20:00 | 1.7756 | 0 | 0 | 1.5 | 78.198 | 0 | 22945.5224
2017-08-26 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 20:15 | 1.7756 | 0 | 0 |  | 77.8318 | 0 | 22838.0792
2017-08-26 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 77.5072 | 0 | 22742.8255
2017-08-26 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 20:45 | 1.7858 | 0 | 0 |  | 77.1954 | 0 | 22651.3506
2017-08-26 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-08-26 | 21:00 | 1.767 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 21:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 21:15 | 0.03856 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 21:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 21:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 21:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 21:45 | 0.03778 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 21:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 22:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 22:15 | 0.03622 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 22:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 22:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 22:45 | 0.03544 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 22:45 |  |  |  | 0 |  |  | 0
2017-08-26 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 23:00 |  |  |  | 0 |  |  | 0
2017-08-26 | 23:15 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 23:15 |  |  |  | 0 |  |  | 0
2017-08-26 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 23:30 |  |  |  | 0 |  |  | 0
2017-08-26 | 23:45 | 0.03388 | 0 | 0 |  | 0 | 0 | 0
2017-08-26 | 23:45 |  |  |  | 0 |  |  | 0
2017-08-27 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 0:00 |  |  |  | 0 |  |  | 0
2017-08-27 | 0:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 0:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 1:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 2:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 2:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 2:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 2:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 3:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 3:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 3:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 3:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 4:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 4:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 4:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 4:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 5:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 5:15 | 2.1079 | 0 | 0 | 1.5 | 91.7202 | 0 | 26913.3405
2017-08-27 | 5:30 | 1.9769 | 0 | 0 | 1.5 | 85.42 | 0 | 25064.6568
2017-08-27 | 5:45 | 1.8708 | 0 | 0 | 1.5 | 82.0067 | 0 | 24063.1197
2017-08-27 | 6:00 | 1.7842 | 0 | 0 | 1.5 | 80.5305 | 0 | 23629.9434
2017-08-27 | 6:15 | 1.778 | 0 | 0 | 1.5 | 79.8483 | 0 | 23429.7606
2017-08-27 | 6:30 | 1.7397 | 0 | 0 | 1.5 | 79.2225 | 0 | 23246.1438
2017-08-27 | 6:45 | 1.792 | 0 | 0 | 1.5 | 78.9296 | 0 | 23160.2121
2017-08-27 | 7:00 | 1.746 | 0 | 0 | 1.5 | 78.7447 | 0 | 23105.9463
2017-08-27 | 7:15 | 1.7936 | 0 | 0 | 1.5 | 78.5067 | 0 | 23036.1085
2017-08-27 | 7:30 | 1.7358 | 0 | 0 | 1.5 | 78.3745 | 0 | 22997.3164
2017-08-27 | 7:45 | 1.7943 | 0 | 0 | 1.5 | 78.3162 | 0 | 22980.2242
2017-08-27 | 8:00 | 1.682 | 0 | 0 | 1.5 | 78.5847 | 0 | 23058.9968
2017-08-27 | 8:15 | 1.7007 | 0 | 0 | 1.5 | 78.8482 | 0 | 23136.3252
2017-08-27 | 8:30 | 1.7273 | 0 | 0 | 1.5 | 78.7638 | 0 | 23111.5432
2017-08-27 | 8:45 | 1.7327 | 0 | 0 | 1.5 | 78.5747 | 0 | 23056.0505
2017-08-27 | 9:00 | 1.7187 | 0 | 0 | 1.5 | 78.5213 | 0 | 23040.3955
2017-08-27 | 9:15 | 1.7569 | 0 | 0 | 1.5 | 78.6625 | 0 | 23081.8224
2017-08-27 | 9:30 | 1.7678 | 0 | 0 | 1.5 | 78.8833 | 0 | 23146.6143
2017-08-27 | 9:45 | 1.7078 | 0 | 0 | 1.5 | 78.8211 | 0 | 23128.3534
2017-08-27 | 10:00 | 1.7429 | 0 | 0 | 1.5 | 79.1152 | 0 | 23214.6522
2017-08-27 | 10:15 | 1.7522 | 0 | 0 | 1.5 | 78.9277 | 0 | 23159.6367
2017-08-27 | 10:30 | 1.7608 | 0 | 0 | 1.5 | 78.6868 | 0 | 23088.9459
2017-08-27 | 10:45 | 1.7624 | 0 | 0 | 1.5 | 78.6264 | 0 | 23071.2334
2017-08-27 | 11:00 | 1.7444 | 0 | 0 | 1.5 | 78.8351 | 0 | 23132.4793
2017-08-27 | 11:15 | 1.7468 | 0 | 0 | 1.5 | 79.1772 | 0 | 23232.8638
2017-08-27 | 11:30 | 1.7249 | 0 | 0 | 1.5 | 79.4369 | 0 | 23309.0508
2017-08-27 | 11:45 | 1.739 | 0 | 0 | 1.5 | 79.6532 | 0 | 23372.5288
2017-08-27 | 12:00 | 1.746 | 0 | 0 | 1.5 | 79.7522 | 0 | 23401.5712
2017-08-27 | 12:15 | 1.7514 | 0 | 0 | 1.5 | 79.8928 | 0 | 23442.8413
2017-08-27 | 12:30 | 1.7546 | 0 | 0 | 1.5 | 79.8997 | 0 | 23444.856
2017-08-27 | 12:45 | 1.7491 | 0 | 0 | 1.5 | 79.9337 | 0 | 23454.8428
2017-08-27 | 13:00 | 1.7577 | 0 | 0 | 1.5 | 79.9841 | 0 | 23469.6314
2017-08-27 | 13:15 | 1.7343 | 0 | 0 | 1.5 | 80.2049 | 0 | 23534.4169
2017-08-27 | 13:30 | 1.7522 | 0 | 0 | 1.5 | 80.358 | 0 | 23579.327
2017-08-27 | 13:45 | 1.7296 | 0 | 0 | 1.5 | 80.5258 | 0 | 23628.5801
2017-08-27 | 14:00 | 1.746 | 0 | 0 | 1.5 | 80.5457 | 0 | 23634.4009
2017-08-27 | 14:15 | 1.7522 | 0 | 0 | 1.5 | 80.6082 | 0 | 23652.7581
2017-08-27 | 14:30 | 1.7413 | 0 | 0 | 1.5 | 80.7362 | 0 | 23690.3052
2017-08-27 | 14:45 | 1.7444 | 0 | 0 | 1.5 | 80.9025 | 0 | 23739.0994
2017-08-27 | 15:00 | 1.7475 | 0 | 0 | 1.5 | 80.9887 | 0 | 23764.4056
2017-08-27 | 15:15 | 1.7546 | 0 | 0 | 1.5 | 81.0319 | 0 | 23777.0676
2017-08-27 | 15:30 | 1.7538 | 0 | 0 | 1.5 | 81.121 | 0 | 23803.2062
2017-08-27 | 15:45 | 1.7335 | 0 | 0 | 1.5 | 81.2439 | 0 | 23839.2962
2017-08-27 | 16:00 | 1.7475 | 0 | 0 | 1.5 | 81.3039 | 0 | 23856.8811
2017-08-27 | 16:15 | 1.739 | 0 | 0 | 1.5 | 81.3185 | 0 | 23861.1748
2017-08-27 | 16:30 | 1.7327 | 0 | 0 | 1.5 | 81.3648 | 0 | 23874.7702
2017-08-27 | 16:45 | 1.7429 | 0 | 0 | 1.5 | 81.3894 | 0 | 23881.9698
2017-08-27 | 17:00 | 1.7374 | 0 | 0 | 1.5 | 81.5824 | 0 | 23938.6153
2017-08-27 | 17:15 | 1.7631 | 0 | 0 | 1.5 | 81.622 | 0 | 23950.2406
2017-08-27 | 17:30 | 1.7522 | 0 | 0 | 1.5 | 81.5263 | 0 | 23922.134
2017-08-27 | 17:45 | 1.7577 | 0 | 0 | 1.5 | 81.2444 | 0 | 23839.4238
2017-08-27 | 18:00 | 1.7616 | 0 | 0 | 1.5 | 80.9865 | 0 | 23763.7451
2017-08-27 | 18:15 | 1.7647 | 0 | 0 | 1.5 | 80.6664 | 0 | 23669.8145
2017-08-27 | 18:30 | 1.767 | 0 | 0 | 1.5 | 80.328 | 0 | 23570.5312
2017-08-27 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 80.0413 | 0 | 23486.4014
2017-08-27 | 19:00 | 1.7624 | 0 | 0 | 1.5 | 79.7929 | 0 | 23413.5055
2017-08-27 | 19:15 | 1.7569 | 0 | 0 | 1.5 | 79.565 | 0 | 23346.6516
2017-08-27 | 19:30 | 1.7663 | 0 | 0 | 1.5 | 79.2855 | 0 | 23264.6196
2017-08-27 | 19:45 | 1.76 | 0 | 0 | 1.5 | 78.9363 | 0 | 23162.1687
2017-08-27 | 20:00 | 1.7639 | 0 | 0 | 1.5 | 78.5772 | 0 | 23056.7826
2017-08-27 | 20:15 | 1.7577 | 0 | 0 | 1.5 | 78.2623 | 0 | 22964.3811
2017-08-27 | 20:30 | 1.7772 | 0 | 0 | 1.5 | 77.9166 | 0 | 22862.9464
2017-08-27 | 20:45 | 1.7616 | 0 | 0 | 1.5 | 77.6299 | 0 | 22778.8412
2017-08-27 | 21:00 | 1.7444 | 0 | 0 | 1.5 | 77.7832 | 0 | 22823.8097
2017-08-27 | 21:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 21:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 22:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-27 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 0:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 3:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 3:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 4:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 4:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 4:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 5:15 | 2.0783 | 0 | 0 | 1.5 | 93.06 | 0 | 27306.4555
2017-08-28 | 5:30 | 1.9745 | 0 | 0 | 1.5 | 87.9695 | 0 | 25812.7574
2017-08-28 | 5:45 | 1.8669 | 0 | 0 | 1.5 | 84.0069 | 0 | 24650.0214
2017-08-28 | 6:00 | 1.8271 | 0 | 0 | 1.5 | 81.7664 | 0 | 23992.5944
2017-08-28 | 6:15 | 1.7982 | 0 | 0 | 1.5 | 80.6693 | 0 | 23670.6719
2017-08-28 | 6:30 | 1.7936 | 0 | 0 | 1.5 | 80.1072 | 0 | 23505.7483
2017-08-28 | 6:45 | 1.7772 | 0 | 0 | 1.5 | 79.5798 | 0 | 23350.9947
2017-08-28 | 7:00 | 1.7842 | 0 | 0 | 1.5 | 79.1624 | 0 | 23228.5076
2017-08-28 | 7:15 | 1.7858 | 0 | 0 | 1.5 | 78.9499 | 0 | 23166.1669
2017-08-28 | 7:30 | 1.8006 | 0 | 0 | 1.5 | 78.6648 | 0 | 23082.494
2017-08-28 | 7:45 | 1.7468 | 0 | 0 | 1.5 | 78.6284 | 0 | 23071.8176
2017-08-28 | 8:00 | 1.7335 | 0 | 0 | 1.5 | 78.8753 | 0 | 23144.2593
2017-08-28 | 8:15 | 1.7288 | 0 | 0 | 1.5 | 79.4005 | 0 | 23298.3879
2017-08-28 | 8:30 | 1.7413 | 0 | 0 | 1.5 | 79.6709 | 0 | 23377.7225
2017-08-28 | 8:45 | 1.7421 | 0 | 0 | 1.5 | 79.6767 | 0 | 23379.4082
2017-08-28 | 9:00 | 1.7483 | 0 | 0 | 1.5 | 79.1195 | 0 | 23215.9216
2017-08-28 | 9:15 | 1.7405 | 0 | 0 | 1.5 | 79.6092 | 0 | 23359.6159
2017-08-28 | 9:30 | 1.7241 | 0 | 0 | 1.5 | 80.4003 | 0 | 23591.7584
2017-08-28 | 9:45 | 1.7031 | 0 | 0 | 1.5 | 81.0787 | 0 | 23790.8174
2017-08-28 | 10:00 | 1.6797 | 0 | 0 | 1.5 | 81.6928 | 0 | 23971.0113
2017-08-28 | 10:15 | 1.7234 | 0 | 0 | 1.5 | 82.2741 | 0 | 24141.581
2017-08-28 | 10:30 | 1.721 | 0 | 0 | 1.5 | 82.9981 | 0 | 24354.0051
2017-08-28 | 10:45 | 1.7507 | 0 | 0 | 1.5 | 83.2597 | 0 | 24430.7763
2017-08-28 | 11:00 | 1.7312 | 0 | 0 | 1.5 | 84.3047 | 0 | 24737.4221
2017-08-28 | 11:15 | 1.6844 | 0 | 0 | 1.5 | 85.2985 | 0 | 25029.0126
2017-08-28 | 11:30 | 1.6805 | 0 | 0 | 1.5 | 86.3121 | 0 | 25326.4462
2017-08-28 | 11:45 | 1.6812 | 0 | 0 | 1.5 | 87.4847 | 0 | 25670.5047
2017-08-28 | 12:00 | 1.7148 | 0 | 0 | 1.5 | 88.2546 | 0 | 25896.4191
2017-08-28 | 12:15 | 1.7951 | 0 | 0 | 1.5 | 88.4124 | 0 | 25942.7374
2017-08-28 | 12:30 | 1.8404 | 0 | 0 | 1.5 | 85.9188 | 0 | 25211.0196
2017-08-28 | 12:45 | 1.7608 | 0 | 0 | 1.5 | 85.4275 | 0 | 25066.8798
2017-08-28 | 13:00 | 1.6992 | 0 | 0 | 1.5 | 86.7714 | 0 | 25461.2194
2017-08-28 | 13:15 | 1.8216 | 0 | 0 | 1.5 | 86.8121 | 0 | 25473.1402
2017-08-28 | 13:30 | 1.7499 | 0 | 0 | 1.5 | 85.2786 | 0 | 25023.1652
2017-08-28 | 13:45 | 1.6469 | 0 | 0 | 1.5 | 86.7956 | 0 | 25468.3092
2017-08-28 | 14:00 | 1.7413 | 0 | 0 | 1.5 | 88.9118 | 0 | 26089.2616
2017-08-28 | 14:15 | 1.9059 | 0 | 0 | 1.5 | 86.0626 | 0 | 25253.2255
2017-08-28 | 14:30 | 1.6649 | 0 | 0 | 1.5 | 85.9854 | 0 | 25230.579
2017-08-28 | 14:45 | 1.6243 | 0 | 0 | 1.5 | 87.9787 | 0 | 25815.4549
2017-08-28 | 15:00 | 1.8372 | 0 | 0 | 1.5 | 87.5325 | 0 | 25684.5367
2017-08-28 | 15:15 | 1.7007 | 0 | 0 | 1.5 | 86.5155 | 0 | 25386.1114
2017-08-28 | 15:30 | 1.6571 | 0 | 0 | 1.5 | 88.1721 | 0 | 25872.2189
2017-08-28 | 15:45 | 1.831 | 0 | 0 | 1.5 | 88.6727 | 0 | 26019.1169
2017-08-28 | 16:00 | 1.8053 | 0 | 0 | 1.5 | 86.3748 | 0 | 25344.8459
2017-08-28 | 16:15 | 1.6539 | 0 | 0 | 1.5 | 87.5411 | 0 | 25687.0485
2017-08-28 | 16:30 | 1.6875 | 0 | 0 | 1.5 | 89.7143 | 0 | 26324.7439
2017-08-28 | 16:45 | 1.9386 | 0 | 0 | 1.5 | 87.1864 | 0 | 25582.9946
2017-08-28 | 17:00 | 1.7468 | 0 | 0 | 1.5 | 85.3484 | 0 | 25043.6714
2017-08-28 | 17:15 | 1.6298 | 0 | 0 | 1.5 | 86.9193 | 0 | 25504.6184
2017-08-28 | 17:30 | 1.8973 | 0 | 0 | 1.5 | 87.1614 | 0 | 25575.6586
2017-08-28 | 17:45 | 1.8099 | 0 | 0 | 1.5 | 84.1593 | 0 | 24694.7505
2017-08-28 | 18:00 | 1.7148 | 0 | 0 | 1.5 | 83.8378 | 0 | 24600.4032
2017-08-28 | 18:15 | 1.7507 | 0 | 0 | 1.5 | 84.1382 | 0 | 24688.5448
2017-08-28 | 18:30 | 1.7569 | 0 | 0 | 1.5 | 84.4732 | 0 | 24786.8475
2017-08-28 | 18:45 | 1.7858 | 0 | 0 | 1.5 | 84.3315 | 0 | 24745.2842
2017-08-28 | 19:00 | 1.7811 | 0 | 0 | 1.5 | 84.0183 | 0 | 24653.3639
2017-08-28 | 19:15 | 1.8014 | 0 | 0 | 1.5 | 83.6444 | 0 | 24543.655
2017-08-28 | 19:30 | 1.7912 | 0 | 0 | 1.5 | 83.1087 | 0 | 24386.4615
2017-08-28 | 19:45 | 1.746 | 0 | 0 | 1.5 | 82.6128 | 0 | 24240.9694
2017-08-28 | 20:00 | 1.7561 | 0 | 0 | 1.5 | 82.1402 | 0 | 24102.2742
2017-08-28 | 20:15 | 1.7639 | 0 | 0 | 1.5 | 81.6 | 0 | 23943.7576
2017-08-28 | 20:30 | 1.7803 | 0 | 0 | 1.5 | 81.0611 | 0 | 23785.6551
2017-08-28 | 20:45 | 1.7943 | 0 | 0 | 1.5 | 80.4884 | 0 | 23617.6018
2017-08-28 | 21:00 | 1.7694 | 0 | 0 | 1.5 | 79.9874 | 0 | 23470.5941
2017-08-28 | 21:15 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 23:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-28 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 1:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 1:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 2:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 2:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 2:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 2:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 5:15 | 1.8404 | 0 | 0 | 1.5 | 98.872 | 0 | 29011.8612
2017-08-29 | 5:30 | 2.0268 | 0 | 0 | 1.5 | 95.1799 | 0 | 27928.4889
2017-08-29 | 5:45 | 1.9613 | 0 | 0 | 1.5 | 89.2282 | 0 | 26182.0906
2017-08-29 | 6:00 | 1.8872 | 0 | 0 | 1.5 | 85.1993 | 0 | 24999.9007
2017-08-29 | 6:15 | 1.8232 | 0 | 0 | 1.5 | 82.799 | 0 | 24295.5844
2017-08-29 | 6:30 | 1.8185 | 0 | 0 | 1.5 | 81.2728 | 0 | 23847.7516
2017-08-29 | 6:45 | 1.817 | 0 | 0 | 1.5 | 80.2762 | 0 | 23555.3327
2017-08-29 | 7:00 | 1.7772 | 0 | 0 | 1.5 | 79.7865 | 0 | 23411.6361
2017-08-29 | 7:15 | 1.7265 | 0 | 0 | 1.5 | 79.3141 | 0 | 23273.0148
2017-08-29 | 7:30 | 1.778 | 0 | 0 | 1.5 | 79.2131 | 0 | 23243.3744
2017-08-29 | 7:45 | 1.6836 | 0 | 0 | 1.5 | 79.6772 | 0 | 23379.5805
2017-08-29 | 8:00 | 1.7499 | 0 | 0 | 1.5 | 80.1084 | 0 | 23506.1042
2017-08-29 | 8:15 | 1.7031 | 0 | 0 | 1.5 | 80.4843 | 0 | 23616.3838
2017-08-29 | 8:30 | 1.7179 | 0 | 0 | 1.5 | 80.9911 | 0 | 23765.1063
2017-08-29 | 8:45 | 1.7538 | 0 | 0 | 1.5 | 81.4413 | 0 | 23897.2175
2017-08-29 | 9:00 | 1.728 | 0 | 0 | 1.5 | 81.5508 | 0 | 23929.3427
2017-08-29 | 9:15 | 1.7054 | 0 | 0 | 1.5 | 81.7783 | 0 | 23996.0777
2017-08-29 | 9:30 | 1.7 | 0 | 0 | 1.5 | 82.4614 | 0 | 24196.5226
2017-08-29 | 9:45 | 1.7226 | 0 | 0 | 1.5 | 82.9371 | 0 | 24336.1068
2017-08-29 | 10:00 | 1.7312 | 0 | 0 | 1.5 | 83.3776 | 0 | 24465.3659
2017-08-29 | 10:15 | 1.7514 | 0 | 0 | 1.5 | 83.8249 | 0 | 24596.6221
2017-08-29 | 10:30 | 1.7608 | 0 | 0 | 1.5 | 84.0745 | 0 | 24669.8675
2017-08-29 | 10:45 | 1.7249 | 0 | 0 | 1.5 | 84.2455 | 0 | 24720.0273
2017-08-29 | 11:00 | 1.7039 | 0 | 0 | 1.5 | 84.936 | 0 | 24922.6574
2017-08-29 | 11:15 | 1.753 | 0 | 0 | 1.5 | 85.4369 | 0 | 25069.6178
2017-08-29 | 11:30 | 1.76 | 0 | 0 | 1.5 | 85.4524 | 0 | 25074.1669
2017-08-29 | 11:45 | 1.7327 | 0 | 0 | 1.5 | 85.5639 | 0 | 25106.883
2017-08-29 | 12:00 | 1.714 | 0 | 0 | 1.5 | 85.9076 | 0 | 25207.7534
2017-08-29 | 12:15 | 1.7195 | 0 | 0 | 1.5 | 86.2676 | 0 | 25313.3698
2017-08-29 | 12:30 | 1.7335 | 0 | 0 | 1.5 | 86.5162 | 0 | 25386.3129
2017-08-29 | 12:45 | 1.6929 | 0 | 0 | 1.5 | 86.7796 | 0 | 25463.6214
2017-08-29 | 13:00 | 1.7546 | 0 | 0 | 1.5 | 87.6306 | 0 | 25713.315
2017-08-29 | 13:15 | 1.7124 | 0 | 0 | 1.5 | 88.2592 | 0 | 25897.7736
2017-08-29 | 13:30 | 1.7054 | 0 | 0 | 1.5 | 88.9736 | 0 | 26107.4016
2017-08-29 | 13:45 | 1.8677 | 0 | 0 | 1.5 | 89.2583 | 0 | 26190.9267
2017-08-29 | 14:00 | 1.7639 | 0 | 0 | 1.5 | 86.7777 | 0 | 25463.0527
2017-08-29 | 14:15 | 1.6851 | 0 | 0 | 1.5 | 87.5213 | 0 | 25681.255
2017-08-29 | 14:30 | 1.6984 | 0 | 0 | 1.5 | 88.8975 | 0 | 26085.0685
2017-08-29 | 14:45 | 1.9277 | 0 | 0 | 1.5 | 88.0853 | 0 | 25846.7361
2017-08-29 | 15:00 | 1.7109 | 0 | 0 | 1.5 | 86.7672 | 0 | 25459.9767
2017-08-29 | 15:15 | 1.6664 | 0 | 0 | 1.5 | 88.7559 | 0 | 26043.5228
2017-08-29 | 15:30 | 1.8474 | 0 | 0 | 1.5 | 89.8139 | 0 | 26353.952
2017-08-29 | 15:45 | 1.8092 | 0 | 0 | 1.5 | 86.6864 | 0 | 25436.2648
2017-08-29 | 16:00 | 1.6922 | 0 | 0 | 1.5 | 86.8709 | 0 | 25490.4073
2017-08-29 | 16:15 | 1.6656 | 0 | 0 | 1.5 | 88.4106 | 0 | 25942.2046
2017-08-29 | 16:30 | 1.8411 | 0 | 0 | 1.5 | 89.2376 | 0 | 26184.8732
2017-08-29 | 16:45 | 1.8068 | 0 | 0 | 1.5 | 86.4693 | 0 | 25372.5497
2017-08-29 | 17:00 | 1.721 | 0 | 0 | 1.5 | 86.3322 | 0 | 25332.3294
2017-08-29 | 17:15 | 1.7288 | 0 | 0 | 1.5 | 87.7856 | 0 | 25758.8097
2017-08-29 | 17:30 | 1.7405 | 0 | 0 | 1.5 | 87.4189 | 0 | 25651.2073
2017-08-29 | 17:45 | 1.7491 | 0 | 0 | 1.5 | 87.2298 | 0 | 25595.7127
2017-08-29 | 18:00 | 1.7358 | 0 | 0 | 1.5 | 86.7542 | 0 | 25456.1665
2017-08-29 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 86.2161 | 0 | 25298.2612
2017-08-29 | 18:30 | 1.7717 | 0 | 0 | 1.5 | 85.6847 | 0 | 25142.3415
2017-08-29 | 18:45 | 1.7795 | 0 | 0 | 1.5 | 84.6552 | 0 | 24840.2647
2017-08-29 | 19:00 | 1.8146 | 0 | 0 | 1.5 | 83.6672 | 0 | 24550.3531
2017-08-29 | 19:15 | 1.7858 | 0 | 0 | 1.5 | 82.8712 | 0 | 24316.7646
2017-08-29 | 19:30 | 1.7959 | 0 | 0 | 1.5 | 82.2486 | 0 | 24134.0948
2017-08-29 | 19:45 | 1.8029 | 0 | 0 | 1.5 | 81.607 | 0 | 23945.8284
2017-08-29 | 20:00 | 1.7717 | 0 | 0 | 1.5 | 81.1253 | 0 | 23804.4847
2017-08-29 | 20:15 | 1.7725 | 0 | 0 | 1.5 | 80.4288 | 0 | 23600.1132
2017-08-29 | 20:30 | 1.7577 | 0 | 0 | 1.5 | 79.8868 | 0 | 23441.0837
2017-08-29 | 20:45 | 1.7881 | 0 | 0 | 1.5 | 79.1106 | 0 | 23213.298
2017-08-29 | 21:00 | 1.7858 | 0 | 0 | 1.5 | 78.6281 | 0 | 23071.7369
2017-08-29 | 21:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 21:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 21:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 22:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 22:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 23:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 0:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 0:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 2:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 2:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 3:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 3:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 3:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 3:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 4:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 4:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 4:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 4:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 5:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 5:15 | 2.0026 | 0 | 0 | 1.5 | 95.7495 | 0 | 28095.6358
2017-08-30 | 5:30 | 2.0369 | 0 | 0 | 1.5 | 90.216 | 0 | 26471.9552
2017-08-30 | 5:45 | 1.9215 | 0 | 0 | 1.5 | 85.4331 | 0 | 25068.4984
2017-08-30 | 6:00 | 1.8864 | 0 | 0 | 1.5 | 82.624 | 0 | 24244.2514
2017-08-30 | 6:15 | 1.8115 | 0 | 0 | 1.5 | 81.2997 | 0 | 23855.6475
2017-08-30 | 6:30 | 1.7959 | 0 | 0 | 1.5 | 80.2063 | 0 | 23534.8174
2017-08-30 | 6:45 | 1.7702 | 0 | 0 | 1.5 | 79.5851 | 0 | 23352.5328
2017-08-30 | 7:00 | 1.7639 | 0 | 0 | 1.5 | 79.332 | 0 | 23278.271
2017-08-30 | 7:15 | 1.7819 | 0 | 0 | 1.5 | 79.153 | 0 | 23225.7426
2017-08-30 | 7:30 | 1.7686 | 0 | 0 | 1.5 | 78.9944 | 0 | 23179.2072
2017-08-30 | 7:45 | 1.7522 | 0 | 0 | 1.5 | 78.9794 | 0 | 23174.8172
2017-08-30 | 8:00 | 1.7273 | 0 | 0 | 1.5 | 79.1624 | 0 | 23228.5208
2017-08-30 | 8:15 | 1.7569 | 0 | 0 | 1.5 | 79.962 | 0 | 23463.146
2017-08-30 | 8:30 | 1.7374 | 0 | 0 | 1.5 | 79.8281 | 0 | 23423.8324
2017-08-30 | 8:45 | 1.7054 | 0 | 0 | 1.5 | 80.4085 | 0 | 23594.1448
2017-08-30 | 9:00 | 1.7553 | 0 | 0 | 1.5 | 80.6367 | 0 | 23661.1014
2017-08-30 | 9:15 | 1.7741 | 0 | 0 | 1.5 | 80.4323 | 0 | 23601.1273
2017-08-30 | 9:30 | 1.76 | 0 | 0 | 1.5 | 80.3296 | 0 | 23571.0124
2017-08-30 | 9:45 | 1.7405 | 0 | 0 | 1.5 | 80.536 | 0 | 23631.5687
2017-08-30 | 10:00 | 1.7553 | 0 | 0 | 1.5 | 80.6532 | 0 | 23665.9392
2017-08-30 | 10:15 | 1.6968 | 0 | 0 | 1.5 | 81.1241 | 0 | 23804.1176
2017-08-30 | 10:30 | 1.7257 | 0 | 0 | 1.5 | 81.3542 | 0 | 23871.6608
2017-08-30 | 10:45 | 1.7288 | 0 | 0 | 1.5 | 81.2731 | 0 | 23847.8614
2017-08-30 | 11:00 | 1.7507 | 0 | 0 | 1.5 | 81.0342 | 0 | 23777.7525
2017-08-30 | 11:15 | 1.7491 | 0 | 0 | 1.5 | 81.2051 | 0 | 23827.9035
2017-08-30 | 11:30 | 1.753 | 0 | 0 | 1.5 | 81.4337 | 0 | 23894.9834
2017-08-30 | 11:45 | 1.7265 | 0 | 0 | 1.5 | 81.8302 | 0 | 24011.3231
2017-08-30 | 12:00 | 1.7007 | 0 | 0 | 1.5 | 82.236 | 0 | 24130.4011
2017-08-30 | 12:15 | 1.7226 | 0 | 0 | 1.5 | 82.7687 | 0 | 24286.69
2017-08-30 | 12:30 | 1.7647 | 0 | 0 | 1.5 | 83.2041 | 0 | 24414.4719
2017-08-30 | 12:45 | 1.7639 | 0 | 0 | 1.5 | 83.4196 | 0 | 24477.6899
2017-08-30 | 13:00 | 1.7046 | 0 | 0 | 1.5 | 83.7998 | 0 | 24589.2412
2017-08-30 | 13:15 | 1.6929 | 0 | 0 | 1.5 | 84.4234 | 0 | 24772.2312
2017-08-30 | 13:30 | 1.7273 | 0 | 0 | 1.5 | 84.6028 | 0 | 24824.8717
2017-08-30 | 13:45 | 1.6992 | 0 | 0 | 1.5 | 85.1525 | 0 | 24986.1665
2017-08-30 | 14:00 | 1.6929 | 0 | 0 | 1.5 | 86.1942 | 0 | 25291.8427
2017-08-30 | 14:15 | 1.7452 | 0 | 0 | 1.5 | 86.2509 | 0 | 25308.4784
2017-08-30 | 14:30 | 1.7163 | 0 | 0 | 1.5 | 86.3165 | 0 | 25327.7176
2017-08-30 | 14:45 | 1.7452 | 0 | 0 | 1.5 | 86.8078 | 0 | 25471.8999
2017-08-30 | 15:00 | 1.7241 | 0 | 0 | 1.5 | 87.3644 | 0 | 25635.2231
2017-08-30 | 15:04 |  |  |  |  | 87.5727 |  | 25696.3437
2017-08-30 | 15:06 |  |  |  |  | 87.7569 |  | 25750.3877
2017-08-30 | 15:08 |  |  |  |  | 87.8638 |  | 25781.7561
2017-08-30 | 15:10 |  |  |  |  | 87.9395 |  | 25803.9683
2017-08-30 | 15:12 |  |  |  |  | 87.9965 |  | 25820.6844
2017-08-30 | 15:14 |  |  |  |  | 88.0433 |  | 25834.4233
2017-08-30 | 15:15 | 1.7483 | 0 | 0 | 1.5 | 88.02 | 0 | 25827.5864
2017-08-30 | 15:16 |  |  |  |  | 87.9793 |  | 25815.6318
2017-08-30 | 15:18 |  |  |  |  | 87.9476 |  | 25806.3257
2017-08-30 | 15:20 |  |  |  |  | 88.0366 |  | 25832.4488
2017-08-30 | 15:22 |  |  |  |  | 88.1081 |  | 25853.4298
2017-08-30 | 15:24 |  |  |  |  | 88.1489 |  | 25865.4067
2017-08-30 | 15:26 |  |  |  |  | 88.2219 |  | 25886.8287
2017-08-30 | 15:28 |  |  |  |  | 88.2316 |  | 25889.6806
2017-08-30 | 15:30 | 1.7483 | 0 | 0 | 1.5 | 88.204 | 0 | 25881.5857
2017-08-30 | 15:32 |  |  |  |  | 88.2378 |  | 25891.4804
2017-08-30 | 15:34 |  |  |  |  | 88.3176 |  | 25914.8972
2017-08-30 | 15:36 |  |  |  |  | 88.3565 |  | 25926.3213
2017-08-30 | 15:38 |  |  |  |  | 88.4331 |  | 25948.7932
2017-08-30 | 15:40 |  |  |  |  | 88.4321 |  | 25948.5042
2017-08-30 | 15:42 |  |  |  |  | 88.3165 |  | 25914.5906
2017-08-30 | 15:44 |  |  |  |  | 88.2442 |  | 25893.3634
2017-08-30 | 15:45 | 1.7842 | 0 | 0 | 1.5 | 88.2547 | 0 | 25896.4637
2017-08-30 | 15:46 |  |  |  |  | 88.224 |  | 25887.4308
2017-08-30 | 15:48 |  |  |  |  | 88.1374 |  | 25862.0308
2017-08-30 | 15:50 |  |  |  |  | 88.1007 |  | 25851.2537
2017-08-30 | 15:52 |  |  |  |  | 87.9835 |  | 25816.8833
2017-08-30 | 15:54 |  |  |  |  | 87.8619 |  | 25781.1851
2017-08-30 | 15:56 |  |  |  |  | 87.7022 |  | 25734.3318
2017-08-30 | 15:58 |  |  |  |  | 87.6555 |  | 25720.6311
2017-08-30 | 16:00 | 1.7241 | 0 | 0 | 1.5 | 87.7151 | 0 | 25738.113
2017-08-30 | 16:02 |  |  |  |  | 87.8855 |  | 25788.1117
2017-08-30 | 16:04 |  |  |  |  | 87.9561 |  | 25808.8375
2017-08-30 | 16:06 |  |  |  |  | 88.0864 |  | 25847.0539
2017-08-30 | 16:08 |  |  |  |  | 88.19 |  | 25877.471
2017-08-30 | 16:10 |  |  |  |  | 88.2384 |  | 25891.6732
2017-08-30 | 16:12 |  |  |  |  | 88.2694 |  | 25900.7689
2017-08-30 | 16:14 |  |  |  |  | 88.2288 |  | 25888.8458
2017-08-30 | 16:15 | 1.7413 | 0 | 0 | 1.5 | 88.2448 | 0 | 25893.5582
2017-08-30 | 16:16 |  |  |  |  | 88.2174 |  | 25885.5101
2017-08-30 | 16:18 |  |  |  |  | 88.212 |  | 25883.925
2017-08-30 | 16:20 |  |  |  |  | 88.2217 |  | 25886.7727
2017-08-30 | 16:22 |  |  |  |  | 88.2275 |  | 25888.4763
2017-08-30 | 16:24 |  |  |  |  | 88.2647 |  | 25899.3942
2017-08-30 | 16:26 |  |  |  |  | 88.2276 |  | 25888.503
2017-08-30 | 16:28 |  |  |  |  | 88.2225 |  | 25887.0165
2017-08-30 | 16:30 | 1.7468 | 0 | 0 | 1.5 | 88.2741 | 0 | 25902.1413
2017-08-30 | 16:32 |  |  |  |  | 88.2156 |  | 25884.9839
2017-08-30 | 16:34 |  |  |  |  | 88.1526 |  | 25866.4836
2017-08-30 | 16:36 |  |  |  |  | 88.0134 |  | 25825.6453
2017-08-30 | 16:38 |  |  |  |  | 87.9119 |  | 25795.853
2017-08-30 | 16:40 |  |  |  |  | 87.9401 |  | 25804.1429
2017-08-30 | 16:42 |  |  |  |  | 87.9455 |  | 25805.7213
2017-08-30 | 16:44 |  |  |  |  | 87.9269 |  | 25800.2632
2017-08-30 | 16:45 | 1.7514 | 0 | 0 | 1.5 | 87.9078 | 0 | 25794.6734
2017-08-30 | 16:46 |  |  |  |  | 87.9453 |  | 25805.6629
2017-08-30 | 16:48 |  |  |  |  | 87.8836 |  | 25787.5633
2017-08-30 | 16:50 |  |  |  |  | 87.8989 |  | 25792.0384
2017-08-30 | 16:52 |  |  |  |  | 87.8462 |  | 25776.5914
2017-08-30 | 16:54 |  |  |  |  | 87.8256 |  | 25770.5471
2017-08-30 | 16:56 |  |  |  |  | 87.827 |  | 25770.95
2017-08-30 | 16:58 |  |  |  |  | 87.7736 |  | 25755.2724
2017-08-30 | 17:00 | 1.7834 | 0 | 0 | 1.5 | 87.7106 | 0 | 25736.8054
2017-08-30 | 17:02 |  |  |  |  | 87.7255 |  | 25741.1778
2017-08-30 | 17:04 |  |  |  |  | 87.795 |  | 25761.5743
2017-08-30 | 17:06 |  |  |  |  | 87.795 |  | 25761.5743
2017-08-30 | 17:08 |  |  |  |  | 87.8264 |  | 25770.7663
2017-08-30 | 17:10 |  |  |  |  | 87.829 |  | 25771.5365
2017-08-30 | 17:12 |  |  |  |  | 87.7538 |  | 25749.4766
2017-08-30 | 17:14 |  |  |  |  | 87.752 |  | 25748.9572
2017-08-30 | 17:15 | 1.7522 | 0 | 0 | 1.5 | 87.7591 | 0 | 25751.03
2017-08-30 | 17:16 |  |  |  |  | 87.7197 |  | 25739.4516
2017-08-30 | 17:18 |  |  |  |  | 87.6259 |  | 25711.9359
2017-08-30 | 17:20 |  |  |  |  | 87.4514 |  | 25660.7329
2017-08-30 | 17:22 |  |  |  |  | 87.3251 |  | 25623.6761
2017-08-30 | 17:24 |  |  |  |  | 87.0935 |  | 25555.714
2017-08-30 | 17:26 |  |  |  |  | 86.8276 |  | 25477.7115
2017-08-30 | 17:28 |  |  |  |  | 86.699 |  | 25439.9696
2017-08-30 | 17:30 | 1.7811 | 0 | 0 | 1.5 | 86.6332 | 0 | 25420.652
2017-08-30 | 17:32 |  |  |  |  | 86.5581 |  | 25398.6079
2017-08-30 | 17:34 |  |  |  |  | 86.5159 |  | 25386.2322
2017-08-30 | 17:36 |  |  |  |  | 86.4492 |  | 25366.6729
2017-08-30 | 17:38 |  |  |  |  | 86.36 |  | 25340.4826
2017-08-30 | 17:40 |  |  |  |  | 86.2825 |  | 25317.7601
2017-08-30 | 17:42 |  |  |  |  | 86.1394 |  | 25275.7758
2017-08-30 | 17:44 |  |  |  |  | 85.8683 |  | 25196.2243
2017-08-30 | 17:45 | 1.8201 | 0 | 0 | 1.5 | 85.7861 | 0 | 25172.0846
2017-08-30 | 17:46 |  |  |  |  | 85.7236 |  | 25153.7497
2017-08-30 | 17:48 |  |  |  |  | 85.6618 |  | 25135.612
2017-08-30 | 17:50 |  |  |  |  | 85.5928 |  | 25115.3765
2017-08-30 | 17:52 |  |  |  |  | 85.5149 |  | 25092.5061
2017-08-30 | 17:54 |  |  |  |  | 85.4324 |  | 25068.3059
2017-08-30 | 17:56 |  |  |  |  | 85.3555 |  | 25045.7445
2017-08-30 | 17:58 |  |  |  |  | 85.318 |  | 25034.7392
2017-08-30 | 18:00 | 1.7678 | 0 | 0 | 1.5 | 85.2673 | 0 | 25019.8676
2017-08-30 | 18:02 |  |  |  |  | 85.0771 |  | 24964.0393
2017-08-30 | 18:04 |  |  |  |  | 84.9138 |  | 24916.1494
2017-08-30 | 18:06 |  |  |  |  | 84.8319 |  | 24892.1059
2017-08-30 | 18:08 |  |  |  |  | 84.765 |  | 24872.4705
2017-08-30 | 18:10 |  |  |  |  | 84.6296 |  | 24832.7338
2017-08-30 | 18:12 |  |  |  |  | 84.4993 |  | 24794.5016
2017-08-30 | 18:14 |  |  |  |  | 84.4035 |  | 24766.3949
2017-08-30 | 18:15 | 1.8037 | 0 | 0 | 1.5 | 84.3104 | 0 | 24739.0876
2017-08-30 | 18:16 |  |  |  |  | 84.2168 |  | 24711.6168
2017-08-30 | 18:18 |  |  |  |  | 84.0723 |  | 24669.2228
2017-08-30 | 18:20 |  |  |  |  | 84.0253 |  | 24655.4167
2017-08-30 | 18:22 |  |  |  |  | 83.9812 |  | 24642.475
2017-08-30 | 18:24 |  |  |  |  | 83.8986 |  | 24618.2346
2017-08-30 | 18:26 |  |  |  |  | 83.7994 |  | 24589.1382
2017-08-30 | 18:28 |  |  |  |  | 83.6406 |  | 24542.54
2017-08-30 | 18:30 | 1.8099 | 0 | 0 | 1.5 | 83.4391 | 0 | 24483.4209
2017-08-30 | 18:32 |  |  |  |  | 83.3184 |  | 24447.985
2017-08-30 | 18:34 |  |  |  |  | 83.2408 |  | 24425.2196
2017-08-30 | 18:36 |  |  |  |  | 83.1719 |  | 24405.0021
2017-08-30 | 18:38 |  |  |  |  | 83.1166 |  | 24388.7808
2017-08-30 | 18:40 |  |  |  |  | 83.014 |  | 24358.6683
2017-08-30 | 18:42 |  |  |  |  | 82.8273 |  | 24303.9034
2017-08-30 | 18:44 |  |  |  |  | 82.6769 |  | 24259.7767
2017-08-30 | 18:45 | 1.7858 | 0 | 0 | 1.5 | 82.6004 | 0 | 24237.3071
2017-08-30 | 18:46 |  |  |  |  | 82.496 |  | 24206.6752
2017-08-30 | 18:48 |  |  |  |  | 82.409 |  | 24181.1698
2017-08-30 | 18:50 |  |  |  |  | 82.3084 |  | 24151.6439
2017-08-30 | 18:52 |  |  |  |  | 82.246 |  | 24133.3292
2017-08-30 | 18:54 |  |  |  |  | 82.0466 |  | 24074.8078
2017-08-30 | 18:56 |  |  |  |  | 81.8767 |  | 24024.9681
2017-08-30 | 18:58 |  |  |  |  | 81.6854 |  | 23968.8264
2017-08-30 | 19:00 | 1.7819 | 0 | 0 | 1.5 | 81.5453 | 0 | 23927.7329
2017-08-30 | 19:02 |  |  |  |  | 81.4698 |  | 23905.5612
2017-08-30 | 19:04 |  |  |  |  | 81.4131 |  | 23888.9211
2017-08-30 | 19:06 |  |  |  |  | 81.304 |  | 23856.9125
2017-08-30 | 19:08 |  |  |  |  | 81.1242 |  | 23804.169
2017-08-30 | 19:10 |  |  |  |  | 80.9831 |  | 23762.7691
2017-08-30 | 19:12 |  |  |  |  | 80.8968 |  | 23737.4427
2017-08-30 | 19:14 |  |  |  |  | 80.8677 |  | 23728.9066
2017-08-30 | 19:15 | 1.7538 | 0 | 0 | 1.5 | 80.8544 | 0 | 23724.9958
2017-08-30 | 19:16 |  |  |  |  | 80.8575 |  | 23725.9092
2017-08-30 | 19:18 |  |  |  |  | 80.7314 |  | 23688.897
2017-08-30 | 19:20 |  |  |  |  | 80.5981 |  | 23649.7804
2017-08-30 | 19:22 |  |  |  |  | 80.4967 |  | 23620.0217
2017-08-30 | 19:24 |  |  |  |  | 80.3807 |  | 23586.0004
2017-08-30 | 19:26 |  |  |  |  | 80.2867 |  | 23558.4176
2017-08-30 | 19:28 |  |  |  |  | 80.271 |  | 23553.8013
2017-08-30 | 19:30 | 1.7507 | 0 | 0 | 1.5 | 80.2803 | 0 | 23556.5214
2017-08-30 | 19:32 |  |  |  |  | 80.1619 |  | 23521.8018
2017-08-30 | 19:34 |  |  |  |  | 80.0157 |  | 23478.8928
2017-08-30 | 19:36 |  |  |  |  | 79.9235 |  | 23451.834
2017-08-30 | 19:38 |  |  |  |  | 79.8641 |  | 23434.4126
2017-08-30 | 19:40 |  |  |  |  | 79.9435 |  | 23457.695
2017-08-30 | 19:42 |  |  |  |  | 79.9693 |  | 23465.2795
2017-08-30 | 19:44 |  |  |  |  | 79.9348 |  | 23455.1404
2017-08-30 | 19:45 | 1.7592 | 0 | 0 | 1.5 | 79.8971 | 0 | 23444.0972
2017-08-30 | 19:46 |  |  |  |  | 79.8577 |  | 23432.5276
2017-08-30 | 19:48 |  |  |  |  | 79.7474 |  | 23400.1519
2017-08-30 | 19:50 |  |  |  |  | 79.6635 |  | 23375.5576
2017-08-30 | 19:52 |  |  |  |  | 79.5881 |  | 23353.4348
2017-08-30 | 19:54 |  |  |  |  | 79.5491 |  | 23341.9908
2017-08-30 | 19:56 |  |  |  |  | 79.568 |  | 23347.5384
2017-08-30 | 19:58 |  |  |  |  | 79.596 |  | 23355.7409
2017-08-30 | 20:00 | 1.7686 | 0 | 0 | 1.5 | 79.5461 | 0 | 23341.0997
2017-08-30 | 20:02 |  |  |  |  | 79.4475 |  | 23312.1603
2017-08-30 | 20:04 |  |  |  |  | 79.408 |  | 23300.5707
2017-08-30 | 20:06 |  |  |  |  | 79.3094 |  | 23271.6334
2017-08-30 | 20:08 |  |  |  |  | 79.2716 |  | 23260.5632
2017-08-30 | 20:10 |  |  |  |  | 79.2411 |  | 23251.6107
2017-08-30 | 20:12 |  |  |  |  | 79.2502 |  | 23254.268
2017-08-30 | 20:14 |  |  |  |  | 79.2691 |  | 23259.8064
2017-08-30 | 20:15 | 1.7577 | 0 | 0 | 1.5 | 79.2465 | 0 | 23253.2002
2017-08-30 | 20:16 |  |  |  |  | 79.2043 |  | 23240.8134
2017-08-30 | 20:18 |  |  |  |  | 79.1011 |  | 23210.5242
2017-08-30 | 20:20 |  |  |  |  | 78.9677 |  | 23171.3674
2017-08-30 | 20:22 |  |  |  |  | 78.8406 |  | 23134.0755
2017-08-30 | 20:24 |  |  |  |  | 78.7372 |  | 23103.7459
2017-08-30 | 20:26 |  |  |  |  | 78.6564 |  | 23080.0448
2017-08-30 | 20:28 |  |  |  |  | 78.5625 |  | 23052.4865
2017-08-30 | 20:30 | 1.7795 | 0 | 0 | 1.5 | 78.4576 | 0 | 23021.698
2017-08-30 | 20:32 |  |  |  |  | 78.4368 |  | 23015.5841
2017-08-30 | 20:34 |  |  |  |  | 78.4642 |  | 23023.6501
2017-08-30 | 20:36 |  |  |  |  | 78.4412 |  | 23016.8805
2017-08-30 | 20:38 |  |  |  |  | 78.3347 |  | 22985.6262
2017-08-30 | 20:40 |  |  |  |  | 78.294 |  | 22973.7051
2017-08-30 | 20:42 |  |  |  |  | 78.1882 |  | 22942.6659
2017-08-30 | 20:44 |  |  |  |  | 78.1121 |  | 22920.3105
2017-08-30 | 20:45 | 1.7795 | 0 | 0 | 1.5 | 78.0529 | 0 | 22902.938
2017-08-30 | 20:46 |  |  |  |  | 77.9916 |  | 22884.9705
2017-08-30 | 20:48 |  |  |  |  | 77.9489 |  | 22872.4449
2017-08-30 | 20:50 |  |  |  |  | 77.8752 |  | 22850.8148
2017-08-30 | 20:52 |  |  |  |  | 77.8461 |  | 22842.2676
2017-08-30 | 20:54 |  |  |  |  | 77.8307 |  | 22837.7523
2017-08-30 | 20:56 |  |  |  |  | 77.8679 |  | 22848.6658
2017-08-30 | 20:58 |  |  |  |  | 77.8767 |  | 22851.2538
2017-08-30 | 21:00 | 1.7694 | 0 | 0 | 1.5 | 77.7891 | 0 | 22825.5536
2017-08-30 | 21:02 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:04 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:06 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:08 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:10 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:12 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:14 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 21:16 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:18 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:20 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:22 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:24 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:26 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:28 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 21:32 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:34 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:36 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:38 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:40 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:42 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:44 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 21:46 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:48 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:50 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:52 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:54 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:56 |  |  |  |  | 0 |  | 0
2017-08-30 | 21:58 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 22:02 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:04 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:06 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:08 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:10 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:12 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:14 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 22:16 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:18 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:20 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:22 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:24 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:26 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:28 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 22:32 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:34 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:36 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:38 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:40 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:42 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:44 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 22:46 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:48 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:50 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:52 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:54 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:56 |  |  |  |  | 0 |  | 0
2017-08-30 | 22:58 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 23:02 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:04 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:06 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:08 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:10 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:12 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:14 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 23:16 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:18 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:20 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:22 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:24 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:26 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:28 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 23:32 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:34 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:36 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:38 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:40 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:42 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:44 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 23:46 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:48 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:50 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:52 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:54 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:56 |  |  |  |  | 0 |  | 0
2017-08-30 | 23:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 0:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 0:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 0:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 0:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 0:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 1:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 1:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 1:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 1:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 1:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 2:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 2:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 2:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 2:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 2:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 3:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 3:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 3:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 3:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 3:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 4:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 4:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 4:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 4:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 4:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 5:02 |  |  |  |  | 69.625 |  | 20429.9643
2017-08-31 | 5:04 |  |  |  |  | 99.9967 |  | 29341.8923
2017-08-31 | 5:06 |  |  |  |  | 99.2769 |  | 29130.6725
2017-08-31 | 5:08 |  |  |  |  | 97.9582 |  | 28743.7276
2017-08-31 | 5:10 |  |  |  |  | 96.9947 |  | 28461.0245
2017-08-31 | 5:12 |  |  |  |  | 96.1192 |  | 28204.109
2017-08-31 | 5:14 |  |  |  |  | 95.2766 |  | 27956.8755
2017-08-31 | 5:15 | 2.0018 | 0 | 0 | 1.5 | 94.9097 | 0 | 27849.2238
2017-08-31 | 5:16 |  |  |  |  | 94.5279 |  | 27737.1981
2017-08-31 | 5:18 |  |  |  |  | 93.9338 |  | 27562.8496
2017-08-31 | 5:20 |  |  |  |  | 93.392 |  | 27403.8718
2017-08-31 | 5:22 |  |  |  |  | 92.7319 |  | 27210.1787
2017-08-31 | 5:24 |  |  |  |  | 92.1174 |  | 27029.8885
2017-08-31 | 5:26 |  |  |  |  | 91.3789 |  | 26813.173
2017-08-31 | 5:28 |  |  |  |  | 90.7105 |  | 26617.0621
2017-08-31 | 5:30 | 2.0096 | 0 | 0 | 1.5 | 89.9262 | 0 | 26386.9123
2017-08-31 | 5:32 |  |  |  |  | 89.101 |  | 26144.7897
2017-08-31 | 5:34 |  |  |  |  | 88.3458 |  | 25923.1781
2017-08-31 | 5:36 |  |  |  |  | 87.6769 |  | 25726.8972
2017-08-31 | 5:38 |  |  |  |  | 87.0074 |  | 25530.4459
2017-08-31 | 5:40 |  |  |  |  | 86.4371 |  | 25363.1268
2017-08-31 | 5:42 |  |  |  |  | 85.8543 |  | 25192.0937
2017-08-31 | 5:44 |  |  |  |  | 85.3197 |  | 25035.2315
2017-08-31 | 5:45 | 1.9285 | 0 | 0 | 1.5 | 85.0567 | 0 | 24958.071
2017-08-31 | 5:46 |  |  |  |  | 84.8122 |  | 24886.3233
2017-08-31 | 5:48 |  |  |  |  | 84.359 |  | 24753.3456
2017-08-31 | 5:50 |  |  |  |  | 83.9251 |  | 24626.0116
2017-08-31 | 5:52 |  |  |  |  | 83.5519 |  | 24516.5176
2017-08-31 | 5:54 |  |  |  |  | 83.1674 |  | 24403.6925
2017-08-31 | 5:56 |  |  |  |  | 82.8077 |  | 24298.1343
2017-08-31 | 5:58 |  |  |  |  | 82.4996 |  | 24207.7518
2017-08-31 | 6:00 | 1.8482 | 0 | 0 | 1.5 | 82.2053 | 0 | 24121.3767
2017-08-31 | 6:02 |  |  |  |  | 81.9158 |  | 24036.4435
2017-08-31 | 6:04 |  |  |  |  | 81.6928 |  | 23971.0089
2017-08-31 | 6:06 |  |  |  |  | 81.5652 |  | 23933.5513
2017-08-31 | 6:08 |  |  |  |  | 81.4212 |  | 23891.312
2017-08-31 | 6:10 |  |  |  |  | 81.2105 |  | 23829.4839
2017-08-31 | 6:12 |  |  |  |  | 80.9985 |  | 23767.2689
2017-08-31 | 6:14 |  |  |  |  | 80.7647 |  | 23698.6732
2017-08-31 | 6:15 | 1.8216 | 0 | 0 | 1.5 | 80.6641 | 0 | 23669.1631
2017-08-31 | 6:16 |  |  |  |  | 80.5868 |  | 23646.4808
2017-08-31 | 6:18 |  |  |  |  | 80.3663 |  | 23581.7739
2017-08-31 | 6:20 |  |  |  |  | 80.1729 |  | 23525.0186
2017-08-31 | 6:22 |  |  |  |  | 79.9555 |  | 23461.2343
2017-08-31 | 6:24 |  |  |  |  | 79.8173 |  | 23420.6716
2017-08-31 | 6:26 |  |  |  |  | 79.6376 |  | 23367.9484
2017-08-31 | 6:28 |  |  |  |  | 79.4255 |  | 23305.7063
2017-08-31 | 6:30 | 1.8209 | 0 | 0 | 1.5 | 79.2485 | 0 | 23253.7689
2017-08-31 | 6:32 |  |  |  |  | 79.0843 |  | 23205.5902
2017-08-31 | 6:34 |  |  |  |  | 79.0331 |  | 23190.582
2017-08-31 | 6:36 |  |  |  |  | 78.952 |  | 23166.7849
2017-08-31 | 6:38 |  |  |  |  | 78.9281 |  | 23159.7731
2017-08-31 | 6:40 |  |  |  |  | 78.7996 |  | 23122.0426
2017-08-31 | 6:42 |  |  |  |  | 78.7024 |  | 23093.5419
2017-08-31 | 6:44 |  |  |  |  | 78.5578 |  | 23051.1121
2017-08-31 | 6:45 | 1.7756 | 0 | 0 | 1.5 | 78.5266 | 0 | 23041.9445
2017-08-31 | 6:46 |  |  |  |  | 78.468 |  | 23024.7449
2017-08-31 | 6:48 |  |  |  |  | 78.4211 |  | 23010.9814
2017-08-31 | 6:50 |  |  |  |  | 78.3504 |  | 22990.2401
2017-08-31 | 6:52 |  |  |  |  | 78.2764 |  | 22968.5269
2017-08-31 | 6:54 |  |  |  |  | 78.1539 |  | 22932.5805
2017-08-31 | 6:56 |  |  |  |  | 78.0558 |  | 22903.7934
2017-08-31 | 6:58 |  |  |  |  | 77.9904 |  | 22884.6146
2017-08-31 | 7:00 | 1.7538 | 0 | 0 | 1.5 | 78.0223 | 0 | 22893.9811
2017-08-31 | 7:02 |  |  |  |  | 78.0424 |  | 22899.8623
2017-08-31 | 7:04 |  |  |  |  | 78.0231 |  | 22894.1962
2017-08-31 | 7:06 |  |  |  |  | 77.9799 |  | 22881.5362
2017-08-31 | 7:08 |  |  |  |  | 77.906 |  | 22859.8524
2017-08-31 | 7:10 |  |  |  |  | 77.8457 |  | 22842.1625
2017-08-31 | 7:12 |  |  |  |  | 77.8154 |  | 22833.2637
2017-08-31 | 7:14 |  |  |  |  | 77.7701 |  | 22819.9614
2017-08-31 | 7:15 | 1.7764 | 0 | 0 | 1.5 | 77.7567 | 0 | 22816.0415
2017-08-31 | 7:16 |  |  |  |  | 77.7085 |  | 22801.8953
2017-08-31 | 7:18 |  |  |  |  | 77.6771 |  | 22792.6919
2017-08-31 | 7:20 |  |  |  |  | 77.7883 |  | 22825.3097
2017-08-31 | 7:22 |  |  |  |  | 77.8146 |  | 22833.0263
2017-08-31 | 7:24 |  |  |  |  | 77.7805 |  | 22823.0283
2017-08-31 | 7:26 |  |  |  |  | 77.7478 |  | 22813.4403
2017-08-31 | 7:28 |  |  |  |  | 77.7311 |  | 22808.5151
2017-08-31 | 7:30 | 1.7741 | 0 | 0 | 1.5 | 77.6934 | 0 | 22797.4716
2017-08-31 | 7:32 |  |  |  |  | 77.6444 |  | 22783.086
2017-08-31 | 7:34 |  |  |  |  | 77.6275 |  | 22778.1182
2017-08-31 | 7:36 |  |  |  |  | 77.5971 |  | 22769.2171
2017-08-31 | 7:38 |  |  |  |  | 77.5739 |  | 22762.4028
2017-08-31 | 7:40 |  |  |  |  | 77.5622 |  | 22758.9617
2017-08-31 | 7:42 |  |  |  |  | 77.5602 |  | 22758.3731
2017-08-31 | 7:44 |  |  |  |  | 77.6221 |  | 22776.5534
2017-08-31 | 7:45 | 1.7265 | 0 | 0 | 1.5 | 77.6801 | 0 | 22793.5493
2017-08-31 | 7:46 |  |  |  |  | 77.7345 |  | 22809.5359
2017-08-31 | 7:48 |  |  |  |  | 77.7939 |  | 22826.9529
2017-08-31 | 7:50 |  |  |  |  | 77.8084 |  | 22831.2041
2017-08-31 | 7:52 |  |  |  |  | 77.8312 |  | 22837.9046
2017-08-31 | 7:54 |  |  |  |  | 77.9496 |  | 22872.6354
2017-08-31 | 7:56 |  |  |  |  | 78.0506 |  | 22902.2687
2017-08-31 | 7:58 |  |  |  |  | 78.1695 |  | 22937.1565
2017-08-31 | 8:00 | 1.689 | 0 | 0 | 1.5 | 78.3472 | 0 | 22989.2976
2017-08-31 | 8:02 |  |  |  |  | 78.4893 |  | 23031.0043
2017-08-31 | 8:04 |  |  |  |  | 78.6442 |  | 23076.4517
2017-08-31 | 8:06 |  |  |  |  | 78.7988 |  | 23121.8231
2017-08-31 | 8:08 |  |  |  |  | 78.9839 |  | 23176.1335
2017-08-31 | 8:10 |  |  |  |  | 79.1037 |  | 23211.2807
2017-08-31 | 8:12 |  |  |  |  | 79.2313 |  | 23248.7339
2017-08-31 | 8:14 |  |  |  |  | 79.3132 |  | 23272.7619
2017-08-31 | 8:15 | 1.7312 | 0 | 0 | 1.5 | 79.352 | 0 | 23284.132
2017-08-31 | 8:16 |  |  |  |  | 79.3575 |  | 23285.7461
2017-08-31 | 8:18 |  |  |  |  | 79.4001 |  | 23298.2714
2017-08-31 | 8:20 |  |  |  |  | 79.4569 |  | 23314.934
2017-08-31 | 8:22 |  |  |  |  | 79.5325 |  | 23337.0993
2017-08-31 | 8:24 |  |  |  |  | 79.5729 |  | 23348.9688
2017-08-31 | 8:26 |  |  |  |  | 79.5679 |  | 23347.5046
2017-08-31 | 8:28 |  |  |  |  | 79.6117 |  | 23360.3547
2017-08-31 | 8:30 | 1.7413 | 0 | 0 | 1.5 | 79.6252 | 0 | 23364.3014
2017-08-31 | 8:32 |  |  |  |  | 79.6481 |  | 23371.0153
2017-08-31 | 8:34 |  |  |  |  | 79.7202 |  | 23392.173
2017-08-31 | 8:36 |  |  |  |  | 79.762 |  | 23404.4568
2017-08-31 | 8:38 |  |  |  |  | 79.8253 |  | 23423.0108
2017-08-31 | 8:40 |  |  |  |  | 80.0095 |  | 23477.0818
2017-08-31 | 8:42 |  |  |  |  | 80.1363 |  | 23514.2909
2017-08-31 | 8:44 |  |  |  |  | 80.2939 |  | 23560.5355
2017-08-31 | 8:45 | 1.7257 | 0 | 0 | 1.5 | 80.3031 | 0 | 23563.2195
2017-08-31 | 8:46 |  |  |  |  | 80.3376 |  | 23573.3495
2017-08-31 | 8:48 |  |  |  |  | 80.2799 |  | 23556.4228
2017-08-31 | 8:50 |  |  |  |  | 80.2978 |  | 23561.6594
2017-08-31 | 8:52 |  |  |  |  | 80.3081 |  | 23564.6793
2017-08-31 | 8:54 |  |  |  |  | 80.3877 |  | 23588.0533
2017-08-31 | 8:56 |  |  |  |  | 80.3706 |  | 23583.0207
2017-08-31 | 8:58 |  |  |  |  | 80.4033 |  | 23592.6114
2017-08-31 | 9:00 | 1.7436 | 0 | 0 | 1.5 | 80.4234 | 0 | 23598.526
2017-08-31 | 9:02 |  |  |  |  | 80.4464 |  | 23605.2755
2017-08-31 | 9:04 |  |  |  |  | 80.5602 |  | 23638.672
2017-08-31 | 9:06 |  |  |  |  | 80.6775 |  | 23673.083
2017-08-31 | 9:08 |  |  |  |  | 80.8255 |  | 23716.5022
2017-08-31 | 9:10 |  |  |  |  | 81.003 |  | 23768.6031
2017-08-31 | 9:12 |  |  |  |  | 81.1472 |  | 23810.912
2017-08-31 | 9:14 |  |  |  |  | 81.1211 |  | 23803.2488
2017-08-31 | 9:15 | 1.7397 | 0 | 0 | 1.5 | 81.1332 | 0 | 23806.7861
2017-08-31 | 9:16 |  |  |  |  | 81.1318 |  | 23806.3896
2017-08-31 | 9:18 |  |  |  |  | 81.1686 |  | 23817.1913
2017-08-31 | 9:20 |  |  |  |  | 81.1761 |  | 23819.392
2017-08-31 | 9:22 |  |  |  |  | 81.1816 |  | 23821.0082
2017-08-31 | 9:24 |  |  |  |  | 80.6905 |  | 23676.8888
2017-08-31 | 9:26 |  |  |  |  | 80.0768 |  | 23496.8336
2017-08-31 | 9:28 |  |  |  |  | 79.6454 |  | 23370.2295
2017-08-31 | 9:30 | 1.8677 | 0 | 0 | 1.5 | 79.2647 | 0 | 23258.5327
2017-08-31 | 9:32 |  |  |  |  | 79.0184 |  | 23186.248
2017-08-31 | 9:34 |  |  |  |  | 78.7298 |  | 23101.581
2017-08-31 | 9:36 |  |  |  |  | 78.4692 |  | 23025.1097
2017-08-31 | 9:38 |  |  |  |  | 78.8294 |  | 23130.8003
2017-08-31 | 9:40 |  |  |  |  | 79.1462 |  | 23223.7435
2017-08-31 | 9:42 |  |  |  |  | 79.3682 |  | 23288.9049
2017-08-31 | 9:44 |  |  |  |  | 79.5348 |  | 23337.7822
2017-08-31 | 9:45 | 1.6937 | 0 | 0 | 1.5 | 79.6162 | 0 | 23361.662
2017-08-31 | 9:46 |  |  |  |  | 79.6315 |  | 23366.1708
2017-08-31 | 9:48 |  |  |  |  | 79.7158 |  | 23390.8904
2017-08-31 | 9:50 |  |  |  |  | 79.8953 |  | 23443.5664
2017-08-31 | 9:52 |  |  |  |  | 80.111 |  | 23506.8607
2017-08-31 | 9:54 |  |  |  |  | 80.3566 |  | 23578.9218
2017-08-31 | 9:56 |  |  |  |  | 80.6 |  | 23650.3514
2017-08-31 | 9:58 |  |  |  |  | 80.8114 |  | 23712.3651
2017-08-31 | 10:00 | 1.6937 | 0 | 0 | 1.5 | 80.9663 | 0 | 23757.8372
2017-08-31 | 10:02 |  |  |  |  | 81.1689 |  | 23817.2788
2017-08-31 | 10:04 |  |  |  |  | 81.3444 |  | 23868.7593
2017-08-31 | 10:06 |  |  |  |  | 81.4684 |  | 23905.1536
2017-08-31 | 10:08 |  |  |  |  | 81.6701 |  | 23964.351
2017-08-31 | 10:10 |  |  |  |  | 81.9148 |  | 24036.1548
2017-08-31 | 10:12 |  |  |  |  | 82.0138 |  | 24065.1813
2017-08-31 | 10:14 |  |  |  |  | 82.0507 |  | 24076.0144
2017-08-31 | 10:15 | 1.721 | 0 | 0 | 1.5 | 82.1003 | 0 | 24090.5726
2017-08-31 | 10:16 |  |  |  |  | 82.091 |  | 24087.8525
2017-08-31 | 10:18 |  |  |  |  | 82.1182 |  | 24095.8223
2017-08-31 | 10:20 |  |  |  |  | 82.1759 |  | 24112.7558
2017-08-31 | 10:22 |  |  |  |  | 82.3143 |  | 24153.3698
2017-08-31 | 10:24 |  |  |  |  | 82.4358 |  | 24189.0231
2017-08-31 | 10:26 |  |  |  |  | 82.4654 |  | 24197.6913
2017-08-31 | 10:28 |  |  |  |  | 82.46 |  | 24196.1241
2017-08-31 | 10:30 | 1.7522 | 0 | 0 | 1.5 | 82.4463 | 0 | 24192.0857
2017-08-31 | 10:32 |  |  |  |  | 82.4506 |  | 24193.3527
2017-08-31 | 10:34 |  |  |  |  | 82.4991 |  | 24207.5975
2017-08-31 | 10:36 |  |  |  |  | 82.615 |  | 24241.6029
2017-08-31 | 10:38 |  |  |  |  | 82.6642 |  | 24256.0425
2017-08-31 | 10:40 |  |  |  |  | 82.6779 |  | 24260.0519
2017-08-31 | 10:42 |  |  |  |  | 82.6118 |  | 24240.6539
2017-08-31 | 10:44 |  |  |  |  | 82.6211 |  | 24243.3916
2017-08-31 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 82.5978 | 0 | 24236.5459
2017-08-31 | 10:46 |  |  |  |  | 82.6271 |  | 24245.1513
2017-08-31 | 10:48 |  |  |  |  | 82.7294 |  | 24275.172
2017-08-31 | 10:50 |  |  |  |  | 82.8039 |  | 24297.026
2017-08-31 | 10:52 |  |  |  |  | 82.8773 |  | 24318.5622
2017-08-31 | 10:54 |  |  |  |  | 82.8262 |  | 24303.5765
2017-08-31 | 10:56 |  |  |  |  | 82.7613 |  | 24284.5297
2017-08-31 | 10:58 |  |  |  |  | 82.6851 |  | 24262.1766
2017-08-31 | 11:00 | 1.7561 | 0 | 0 | 1.5 | 82.6893 | 0 | 24263.4123
2017-08-31 | 11:02 |  |  |  |  | 82.7557 |  | 24282.8754
2017-08-31 | 11:04 |  |  |  |  | 82.7678 |  | 24286.4238
2017-08-31 | 11:06 |  |  |  |  | 82.8 |  | 24295.8778
2017-08-31 | 11:08 |  |  |  |  | 82.7603 |  | 24284.2319
2017-08-31 | 11:10 |  |  |  |  | 82.7661 |  | 24285.9514
2017-08-31 | 11:12 |  |  |  |  | 82.8401 |  | 24307.6575
2017-08-31 | 11:14 |  |  |  |  | 82.9262 |  | 24332.9055
2017-08-31 | 11:15 | 1.7163 | 0 | 0 | 1.5 | 82.946 | 0 | 24338.726
2017-08-31 | 11:16 |  |  |  |  | 82.957 |  | 24341.9452
2017-08-31 | 11:18 |  |  |  |  | 83.0515 |  | 24369.6848
2017-08-31 | 11:20 |  |  |  |  | 83.1329 |  | 24393.5537
2017-08-31 | 11:22 |  |  |  |  | 83.1665 |  | 24403.4241
2017-08-31 | 11:24 |  |  |  |  | 83.2395 |  | 24424.8505
2017-08-31 | 11:26 |  |  |  |  | 83.3268 |  | 24450.4698
2017-08-31 | 11:28 |  |  |  |  | 83.5612 |  | 24519.2556
2017-08-31 | 11:30 | 1.6664 | 0 | 0 | 1.5 | 83.7938 | 0 | 24587.4906
2017-08-31 | 11:32 |  |  |  |  | 84.0008 |  | 24648.2485
2017-08-31 | 11:34 |  |  |  |  | 84.1734 |  | 24698.8943
2017-08-31 | 11:36 |  |  |  |  | 84.2206 |  | 24712.7339
2017-08-31 | 11:38 |  |  |  |  | 84.2368 |  | 24717.4886
2017-08-31 | 11:40 |  |  |  |  | 84.2398 |  | 24718.3639
2017-08-31 | 11:42 |  |  |  |  | 84.2221 |  | 24713.1769
2017-08-31 | 11:44 |  |  |  |  | 84.4012 |  | 24765.73
2017-08-31 | 11:45 | 1.6968 | 0 | 0 | 1.5 | 84.4687 | 0 | 24785.5355
2017-08-31 | 11:46 |  |  |  |  | 84.5381 |  | 24805.9077
2017-08-31 | 11:48 |  |  |  |  | 84.7599 |  | 24870.9661
2017-08-31 | 11:50 |  |  |  |  | 84.9109 |  | 24915.2988
2017-08-31 | 11:52 |  |  |  |  | 85.1131 |  | 24974.6013
2017-08-31 | 11:54 |  |  |  |  | 85.1634 |  | 24989.3654
2017-08-31 | 11:56 |  |  |  |  | 85.1124 |  | 24974.4044
2017-08-31 | 11:58 |  |  |  |  | 85.0698 |  | 24961.9034
2017-08-31 | 12:00 | 1.7117 | 0 | 0 | 1.5 | 85.2528 | 0 | 25015.6208
2017-08-31 | 12:02 |  |  |  |  | 85.4372 |  | 25069.7276
2017-08-31 | 12:04 |  |  |  |  | 85.6574 |  | 25134.3291
2017-08-31 | 12:06 |  |  |  |  | 85.767 |  | 25166.4968
2017-08-31 | 12:08 |  |  |  |  | 85.7808 |  | 25170.5353
2017-08-31 | 12:10 |  |  |  |  | 85.6922 |  | 25144.5442
2017-08-31 | 12:12 |  |  |  |  | 85.6652 |  | 25136.6038
2017-08-31 | 12:14 |  |  |  |  | 85.6701 |  | 25138.0609
2017-08-31 | 12:15 | 1.7226 | 0 | 0 | 1.5 | 85.7282 | 0 | 25155.1153
2017-08-31 | 12:16 |  |  |  |  | 85.7236 |  | 25153.7588
2017-08-31 | 12:18 |  |  |  |  | 85.7722 |  | 25168.0279
2017-08-31 | 12:20 |  |  |  |  | 85.8317 |  | 25185.4831
2017-08-31 | 12:22 |  |  |  |  | 85.8496 |  | 25190.7328
2017-08-31 | 12:24 |  |  |  |  | 85.8403 |  | 25188.0083
2017-08-31 | 12:26 |  |  |  |  | 85.832 |  | 25185.5614
2017-08-31 | 12:28 |  |  |  |  | 85.9074 |  | 25207.6862
2017-08-31 | 12:30 | 1.7163 | 0 | 0 | 1.5 | 86.0303 | 0 | 25243.758
2017-08-31 | 12:32 |  |  |  |  | 86.1321 |  | 25273.6199
2017-08-31 | 12:34 |  |  |  |  | 86.2122 |  | 25297.1083
2017-08-31 | 12:36 |  |  |  |  | 86.2815 |  | 25317.4488
2017-08-31 | 12:38 |  |  |  |  | 86.3388 |  | 25334.2681
2017-08-31 | 12:40 |  |  |  |  | 86.4109 |  | 25355.4349
2017-08-31 | 12:42 |  |  |  |  | 86.3797 |  | 25346.2629
2017-08-31 | 12:44 |  |  |  |  | 86.3319 |  | 25332.2443
2017-08-31 | 12:45 | 1.7748 | 0 | 0 | 1.5 | 86.2928 | 0 | 25320.7598
2017-08-31 | 12:46 |  |  |  |  | 86.2579 |  | 25310.5312
2017-08-31 | 12:48 |  |  |  |  | 86.2208 |  | 25299.6468
2017-08-31 | 12:50 |  |  |  |  | 86.2722 |  | 25314.7175
2017-08-31 | 12:52 |  |  |  |  | 86.3785 |  | 25345.9137
2017-08-31 | 12:54 |  |  |  |  | 86.5515 |  | 25396.6804
2017-08-31 | 12:56 |  |  |  |  | 86.6585 |  | 25428.0934
2017-08-31 | 12:58 |  |  |  |  | 86.7424 |  | 25452.6877
2017-08-31 | 13:00 | 1.7569 | 0 | 0 | 1.5 | 86.7313 | 0 | 25449.4482
2017-08-31 | 13:02 |  |  |  |  | 86.6226 |  | 25417.5493
2017-08-31 | 13:04 |  |  |  |  | 86.6021 |  | 25411.5273
2017-08-31 | 13:06 |  |  |  |  | 86.6713 |  | 25431.8454
2017-08-31 | 13:08 |  |  |  |  | 86.7006 |  | 25440.4285
2017-08-31 | 13:10 |  |  |  |  | 86.7349 |  | 25450.4869
2017-08-31 | 13:12 |  |  |  |  | 86.8032 |  | 25470.5525
2017-08-31 | 13:14 |  |  |  |  | 86.875 |  | 25491.6115
2017-08-31 | 13:15 | 1.7241 | 0 | 0 | 1.5 | 86.9161 | 0 | 25503.6624
2017-08-31 | 13:16 |  |  |  |  | 86.9379 |  | 25510.0518
2017-08-31 | 13:18 |  |  |  |  | 87.0222 |  | 25534.7937
2017-08-31 | 13:20 |  |  |  |  | 86.946 |  | 25512.4447
2017-08-31 | 13:22 |  |  |  |  | 86.9432 |  | 25511.6298
2017-08-31 | 13:24 |  |  |  |  | 86.9679 |  | 25518.8564
2017-08-31 | 13:26 |  |  |  |  | 87.1234 |  | 25564.4898
2017-08-31 | 13:28 |  |  |  |  | 87.1936 |  | 25585.0856
2017-08-31 | 13:30 | 1.7187 | 0 | 0 | 1.5 | 87.2863 | 0 | 25612.299
2017-08-31 | 13:32 |  |  |  |  | 87.4286 |  | 25654.048
2017-08-31 | 13:34 |  |  |  |  | 87.5621 |  | 25693.2184
2017-08-31 | 13:36 |  |  |  |  | 87.6642 |  | 25723.1854
2017-08-31 | 13:38 |  |  |  |  | 87.857 |  | 25779.7657
2017-08-31 | 13:40 |  |  |  |  | 87.9314 |  | 25801.5751
2017-08-31 | 13:42 |  |  |  |  | 88.0237 |  | 25828.6633
2017-08-31 | 13:44 |  |  |  |  | 88.1537 |  | 25866.8236
2017-08-31 | 13:45 | 1.7132 | 0 | 0 | 1.5 | 88.2602 | 0 | 25898.0647
2017-08-31 | 13:46 |  |  |  |  | 88.3606 |  | 25927.5255
2017-08-31 | 13:48 |  |  |  |  | 88.4739 |  | 25960.7657
2017-08-31 | 13:50 |  |  |  |  | 88.655 |  | 26013.9141
2017-08-31 | 13:52 |  |  |  |  | 88.7494 |  | 26041.5976
2017-08-31 | 13:54 |  |  |  |  | 88.8962 |  | 26084.6967
2017-08-31 | 13:56 |  |  |  |  | 88.8682 |  | 26076.4628
2017-08-31 | 13:58 |  |  |  |  | 88.7172 |  | 26032.1683
2017-08-31 | 14:00 | 1.7912 | 0 | 0 | 1.5 | 88.5945 | 0 | 25996.1458
2017-08-31 | 14:02 |  |  |  |  | 88.3969 |  | 25938.1749
2017-08-31 | 14:04 |  |  |  |  | 88.0524 |  | 25837.0941
2017-08-31 | 14:06 |  |  |  |  | 87.5584 |  | 25692.1348
2017-08-31 | 14:08 |  |  |  |  | 87.0529 |  | 25543.8019
2017-08-31 | 14:10 |  |  |  |  | 86.6251 |  | 25418.2858
2017-08-31 | 14:12 |  |  |  |  | 86.3173 |  | 25327.9661
2017-08-31 | 14:14 |  |  |  |  | 86.0465 |  | 25248.5086
2017-08-31 | 14:15 | 1.8185 | 0 | 0 | 1.5 | 85.9559 | 0 | 25221.931
2017-08-31 | 14:16 |  |  |  |  | 85.8554 |  | 25192.425
2017-08-31 | 14:18 |  |  |  |  | 85.5916 |  | 25115.0338
2017-08-31 | 14:20 |  |  |  |  | 85.5399 |  | 25099.8445
2017-08-31 | 14:22 |  |  |  |  | 85.6699 |  | 25137.9849
2017-08-31 | 14:24 |  |  |  |  | 85.7378 |  | 25157.9225
2017-08-31 | 14:26 |  |  |  |  | 85.8044 |  | 25177.4751
2017-08-31 | 14:28 |  |  |  |  | 85.8991 |  | 25205.2616
2017-08-31 | 14:30 | 1.7187 | 0 | 0 | 1.5 | 86.0071 | 0 | 25236.939
2017-08-31 | 14:32 |  |  |  |  | 86.0691 |  | 25255.1442
2017-08-31 | 14:34 |  |  |  |  | 86.116 |  | 25268.8963
2017-08-31 | 14:36 |  |  |  |  | 86.1833 |  | 25288.6303
2017-08-31 | 14:38 |  |  |  |  | 86.4022 |  | 25352.8647
2017-08-31 | 14:40 |  |  |  |  | 86.6878 |  | 25436.6653
2017-08-31 | 14:42 |  |  |  |  | 86.902 |  | 25499.5344
2017-08-31 | 14:44 |  |  |  |  | 87.2049 |  | 25588.4054
2017-08-31 | 14:45 | 1.6851 | 0 | 0 | 1.5 | 87.3274 | 0 | 25624.3475
2017-08-31 | 14:46 |  |  |  |  | 87.4222 |  | 25652.1586
2017-08-31 | 14:48 |  |  |  |  | 87.7047 |  | 25735.0639
2017-08-31 | 14:50 |  |  |  |  | 87.9903 |  | 25818.8601
2017-08-31 | 14:52 |  |  |  |  | 88.2396 |  | 25892.0157
2017-08-31 | 14:54 |  |  |  |  | 88.4062 |  | 25940.895
2017-08-31 | 14:56 |  |  |  |  | 88.6357 |  | 26008.2548
2017-08-31 | 14:58 |  |  |  |  | 88.8895 |  | 26082.729
2017-08-31 | 15:00 | 1.6532 | 0 | 0 | 1.5 | 89.1854 | 0 | 26169.5539
2017-08-31 | 15:02 |  |  |  |  | 89.294 |  | 26201.3994
2017-08-31 | 15:04 |  |  |  |  | 89.1958 |  | 26172.5897
2017-08-31 | 15:06 |  |  |  |  | 88.8268 |  | 26064.3269
2017-08-31 | 15:08 |  |  |  |  | 88.3337 |  | 25919.6276
2017-08-31 | 15:10 |  |  |  |  | 87.9859 |  | 25817.5772
2017-08-31 | 15:12 |  |  |  |  | 87.6407 |  | 25716.2725
2017-08-31 | 15:14 |  |  |  |  | 87.238 |  | 25598.1326
2017-08-31 | 15:15 | 1.8942 | 0 | 0 | 1.5 | 87.0192 | 0 | 25533.916
2017-08-31 | 15:16 |  |  |  |  | 86.7482 |  | 25454.4116
2017-08-31 | 15:18 |  |  |  |  | 86.267 |  | 25313.1932
2017-08-31 | 15:20 |  |  |  |  | 86.045 |  | 25248.0473
2017-08-31 | 15:22 |  |  |  |  | 85.9192 |  | 25211.1563
2017-08-31 | 15:24 |  |  |  |  | 85.8625 |  | 25194.5139
2017-08-31 | 15:26 |  |  |  |  | 85.7065 |  | 25148.7238
2017-08-31 | 15:28 |  |  |  |  | 85.566 |  | 25107.5185
2017-08-31 | 15:30 | 1.7678 | 0 | 0 | 1.5 | 85.5015 | 0 | 25088.5795
2017-08-31 | 15:32 |  |  |  |  | 85.4913 |  | 25085.5974
2017-08-31 | 15:34 |  |  |  |  | 85.546 |  | 25101.6532
2017-08-31 | 15:36 |  |  |  |  | 85.635 |  | 25127.7519
2017-08-31 | 15:38 |  |  |  |  | 85.7745 |  | 25168.6861
2017-08-31 | 15:40 |  |  |  |  | 85.8082 |  | 25178.5723
2017-08-31 | 15:42 |  |  |  |  | 85.9441 |  | 25218.4656
2017-08-31 | 15:44 |  |  |  |  | 86.0989 |  | 25263.8793
2017-08-31 | 15:45 | 1.6937 | 0 | 0 | 1.5 | 86.1585 | 0 | 25281.3659
2017-08-31 | 15:46 |  |  |  |  | 86.1879 |  | 25290.0026
2017-08-31 | 15:48 |  |  |  |  | 86.3519 |  | 25338.112
2017-08-31 | 15:50 |  |  |  |  | 86.5422 |  | 25393.9468
2017-08-31 | 15:52 |  |  |  |  | 86.6969 |  | 25439.3607
2017-08-31 | 15:54 |  |  |  |  | 86.8715 |  | 25490.5931
2017-08-31 | 15:56 |  |  |  |  | 87.0278 |  | 25536.4345
2017-08-31 | 15:58 |  |  |  |  | 87.156 |  | 25574.0691
2017-08-31 | 16:00 | 1.7062 | 0 | 0 | 1.5 | 87.2969 | 0 | 25615.4085
2017-08-31 | 16:02 |  |  |  |  | 87.4705 |  | 25666.3318
2017-08-31 | 16:04 |  |  |  |  | 87.6891 |  | 25730.4991
2017-08-31 | 16:06 |  |  |  |  | 87.8039 |  | 25764.1644
2017-08-31 | 16:08 |  |  |  |  | 87.7051 |  | 25735.1713
2017-08-31 | 16:10 |  |  |  |  | 87.4527 |  | 25661.1223
2017-08-31 | 16:12 |  |  |  |  | 87.0167 |  | 25533.1974
2017-08-31 | 16:14 |  |  |  |  | 86.7261 |  | 25447.9013
2017-08-31 | 16:15 | 1.8575 | 0 | 0 | 1.5 | 86.5719 | 0 | 25402.6733
2017-08-31 | 16:16 |  |  |  |  | 86.3631 |  | 25341.3893
2017-08-31 | 16:18 |  |  |  |  | 85.9981 |  | 25234.3131
2017-08-31 | 16:20 |  |  |  |  | 85.692 |  | 25144.4814
2017-08-31 | 16:22 |  |  |  |  | 85.4271 |  | 25066.7502
2017-08-31 | 16:24 |  |  |  |  | 85.3454 |  | 25042.7647
2017-08-31 | 16:26 |  |  |  |  | 85.3227 |  | 25036.1115
2017-08-31 | 16:28 |  |  |  |  | 85.3225 |  | 25036.0487
2017-08-31 | 16:30 | 1.7507 | 0 | 0 | 1.5 | 85.3463 | 0 | 25043.0311
2017-08-31 | 16:32 |  |  |  |  | 85.3835 |  | 25053.9493
2017-08-31 | 16:34 |  |  |  |  | 85.3799 |  | 25052.9082
2017-08-31 | 16:36 |  |  |  |  | 85.3187 |  | 25034.9384
2017-08-31 | 16:38 |  |  |  |  | 85.2473 |  | 25014.0067
2017-08-31 | 16:40 |  |  |  |  | 85.2417 |  | 25012.3388
2017-08-31 | 16:42 |  |  |  |  | 85.3326 |  | 25039.0305
2017-08-31 | 16:44 |  |  |  |  | 85.4927 |  | 25086.0049
2017-08-31 | 16:45 | 1.7163 | 0 | 0 | 1.5 | 85.5202 | 0 | 25094.0642
2017-08-31 | 16:46 |  |  |  |  | 85.6108 |  | 25120.6418
2017-08-31 | 16:48 |  |  |  |  | 85.7552 |  | 25163.0223
2017-08-31 | 16:50 |  |  |  |  | 85.8635 |  | 25194.8115
2017-08-31 | 16:52 |  |  |  |  | 86.0631 |  | 25253.3643
2017-08-31 | 16:54 |  |  |  |  | 86.1991 |  | 25293.2779
2017-08-31 | 16:56 |  |  |  |  | 86.3299 |  | 25331.6689
2017-08-31 | 16:58 |  |  |  |  | 86.4222 |  | 25358.7436
2017-08-31 | 17:00 | 1.7187 | 0 | 0 | 1.5 | 86.5352 | 0 | 25391.8984
2017-08-31 | 17:02 |  |  |  |  | 86.6599 |  | 25428.4965
2017-08-31 | 17:04 |  |  |  |  | 86.6466 |  | 25424.5787
2017-08-31 | 17:06 |  |  |  |  | 86.6365 |  | 25421.6191
2017-08-31 | 17:08 |  |  |  |  | 86.723 |  | 25446.9993
2017-08-31 | 17:10 |  |  |  |  | 86.7887 |  | 25466.2743
2017-08-31 | 17:12 |  |  |  |  | 86.829 |  | 25478.1191
2017-08-31 | 17:14 |  |  |  |  | 86.8302 |  | 25478.4727
2017-08-31 | 17:15 | 1.7522 | 0 | 0 | 1.5 | 86.8477 | 0 | 25483.6039
2017-08-31 | 17:16 |  |  |  |  | 86.8331 |  | 25479.301
2017-08-31 | 17:18 |  |  |  |  | 86.8384 |  | 25480.8591
2017-08-31 | 17:20 |  |  |  |  | 86.8504 |  | 25484.3897
2017-08-31 | 17:22 |  |  |  |  | 86.7849 |  | 25465.1572
2017-08-31 | 17:24 |  |  |  |  | 86.7607 |  | 25458.0718
2017-08-31 | 17:26 |  |  |  |  | 86.696 |  | 25439.0899
2017-08-31 | 17:28 |  |  |  |  | 86.5654 |  | 25400.7637
2017-08-31 | 17:30 | 1.7366 | 0 | 0 | 1.5 | 86.5487 | 0 | 25395.8676
2017-08-31 | 17:32 |  |  |  |  | 86.569 |  | 25401.8113
2017-08-31 | 17:34 |  |  |  |  | 86.5807 |  | 25405.259
2017-08-31 | 17:36 |  |  |  |  | 86.567 |  | 25401.227
2017-08-31 | 17:38 |  |  |  |  | 86.5293 |  | 25390.1768
2017-08-31 | 17:40 |  |  |  |  | 86.5239 |  | 25388.5941
2017-08-31 | 17:42 |  |  |  |  | 86.4574 |  | 25369.0617
2017-08-31 | 17:44 |  |  |  |  | 86.4494 |  | 25366.7266
2017-08-31 | 17:45 | 1.76 | 0 | 0 | 1.5 | 86.385 | 0 | 25347.8301
2017-08-31 | 17:46 |  |  |  |  | 86.3816 |  | 25346.8315
2017-08-31 | 17:48 |  |  |  |  | 86.268 |  | 25313.5042
2017-08-31 | 17:50 |  |  |  |  | 86.2085 |  | 25296.0247
2017-08-31 | 17:52 |  |  |  |  | 86.1391 |  | 25275.666
2017-08-31 | 17:54 |  |  |  |  | 85.9237 |  | 25212.4727
2017-08-31 | 17:56 |  |  |  |  | 85.7425 |  | 25159.2861
2017-08-31 | 17:58 |  |  |  |  | 85.6399 |  | 25129.1847
2017-08-31 | 18:00 | 1.7897 | 0 | 0 | 1.5 | 85.5626 | 0 | 25106.5179
2017-08-31 | 18:02 |  |  |  |  | 85.5163 |  | 25092.9313
2017-08-31 | 18:04 |  |  |  |  | 85.4484 |  | 25072.9893
2017-08-31 | 18:06 |  |  |  |  | 85.3942 |  | 25057.1101
2017-08-31 | 18:08 |  |  |  |  | 85.3258 |  | 25037.027
2017-08-31 | 18:10 |  |  |  |  | 85.1826 |  | 24995.0136
2017-08-31 | 18:12 |  |  |  |  | 85.0183 |  | 24946.7968
2017-08-31 | 18:14 |  |  |  |  | 84.9153 |  | 24916.5634
2017-08-31 | 18:15 | 1.7733 | 0 | 0 | 1.5 | 84.8756 | 0 | 24904.9381
2017-08-31 | 18:16 |  |  |  |  | 84.8292 |  | 24891.3157
2017-08-31 | 18:18 |  |  |  |  | 84.8348 |  | 24892.9656
2017-08-31 | 18:20 |  |  |  |  | 84.8485 |  | 24896.9818
2017-08-31 | 18:22 |  |  |  |  | 84.8332 |  | 24892.4844
2017-08-31 | 18:24 |  |  |  |  | 84.7553 |  | 24869.6272
2017-08-31 | 18:26 |  |  |  |  | 84.6019 |  | 24824.6073
2017-08-31 | 18:28 |  |  |  |  | 84.4386 |  | 24776.6884
2017-08-31 | 18:30 | 1.778 | 0 | 0 | 1.5 | 84.3556 | 0 | 24752.3473
2017-08-31 | 18:32 |  |  |  |  | 84.3359 |  | 24746.5691
2017-08-31 | 18:34 |  |  |  |  | 84.2568 |  | 24723.3495
2017-08-31 | 18:36 |  |  |  |  | 84.2773 |  | 24729.3716
2017-08-31 | 18:38 |  |  |  |  | 84.1028 |  | 24678.1662
2017-08-31 | 18:40 |  |  |  |  | 83.9042 |  | 24619.891
2017-08-31 | 18:42 |  |  |  |  | 83.8064 |  | 24591.1957
2017-08-31 | 18:44 |  |  |  |  | 83.7929 |  | 24587.2242
2017-08-31 | 18:45 | 1.7873 | 0 | 0 | 1.5 | 83.7344 | 0 | 24570.0783
2017-08-31 | 18:46 |  |  |  |  | 83.7421 |  | 24572.3391
2017-08-31 | 18:48 |  |  |  |  | 83.6056 |  | 24532.2647
2017-08-31 | 18:50 |  |  |  |  | 83.4469 |  | 24485.7111
2017-08-31 | 18:52 |  |  |  |  | 83.3236 |  | 24449.5185
2017-08-31 | 18:54 |  |  |  |  | 83.2793 |  | 24436.5363
2017-08-31 | 18:56 |  |  |  |  | 83.2427 |  | 24425.7839
2017-08-31 | 18:58 |  |  |  |  | 83.188 |  | 24409.7213
2017-08-31 | 19:00 | 1.7624 | 0 | 0 | 1.5 | 83.1515 | 0 | 24399.0294
2017-08-31 | 19:02 |  |  |  |  | 82.9859 |  | 24350.4232
2017-08-31 | 19:04 |  |  |  |  | 82.8415 |  | 24308.0739
2017-08-31 | 19:06 |  |  |  |  | 82.6767 |  | 24259.6916
2017-08-31 | 19:08 |  |  |  |  | 82.6212 |  | 24243.4254
2017-08-31 | 19:10 |  |  |  |  | 82.5873 |  | 24233.4878
2017-08-31 | 19:12 |  |  |  |  | 82.5689 |  | 24228.0612
2017-08-31 | 19:14 |  |  |  |  | 82.4914 |  | 24205.3319
2017-08-31 | 19:15 | 1.7998 | 0 | 0 | 1.5 | 82.4253 | 0 | 24185.9269
2017-08-31 | 19:16 |  |  |  |  | 82.3604 |  | 24166.8869
2017-08-31 | 19:18 |  |  |  |  | 82.2021 |  | 24120.4457
2017-08-31 | 19:20 |  |  |  |  | 82.0877 |  | 24086.8674
2017-08-31 | 19:22 |  |  |  |  | 82.0795 |  | 24084.4745
2017-08-31 | 19:24 |  |  |  |  | 82.0739 |  | 24082.8378
2017-08-31 | 19:26 |  |  |  |  | 82.022 |  | 24067.6059
2017-08-31 | 19:28 |  |  |  |  | 81.9618 |  | 24049.945
2017-08-31 | 19:30 | 1.792 | 0 | 0 | 1.5 | 81.8172 | 0 | 24007.5041
2017-08-31 | 19:32 |  |  |  |  | 81.6772 |  | 23966.413
2017-08-31 | 19:34 |  |  |  |  | 81.5753 |  | 23936.5311
2017-08-31 | 19:36 |  |  |  |  | 81.4365 |  | 23895.7871
2017-08-31 | 19:38 |  |  |  |  | 81.3854 |  | 23880.8014
2017-08-31 | 19:40 |  |  |  |  | 81.4148 |  | 23889.4358
2017-08-31 | 19:42 |  |  |  |  | 81.3971 |  | 23884.2445
2017-08-31 | 19:44 |  |  |  |  | 81.3449 |  | 23868.9096
2017-08-31 | 19:45 | 1.792 | 0 | 0 | 1.5 | 81.2656 | 0 | 23845.6607
2017-08-31 | 19:46 |  |  |  |  | 81.1958 |  | 23825.1679
2017-08-31 | 19:48 |  |  |  |  | 81.0756 |  | 23789.9063
2017-08-31 | 19:50 |  |  |  |  | 80.9603 |  | 23756.0596
2017-08-31 | 19:52 |  |  |  |  | 80.9543 |  | 23754.3181
2017-08-31 | 19:54 |  |  |  |  | 80.9416 |  | 23750.5907
2017-08-31 | 19:56 |  |  |  |  | 80.9186 |  | 23743.8298
2017-08-31 | 19:58 |  |  |  |  | 80.8367 |  | 23719.7974
2017-08-31 | 20:00 | 1.7873 | 0 | 0 | 1.5 | 80.7461 | 0 | 23693.2019
2017-08-31 | 20:02 |  |  |  |  | 80.5814 |  | 23644.8956
2017-08-31 | 20:04 |  |  |  |  | 80.5472 |  | 23634.8619
2017-08-31 | 20:06 |  |  |  |  | 80.4309 |  | 23600.722
2017-08-31 | 20:08 |  |  |  |  | 80.3569 |  | 23579.0001
2017-08-31 | 20:10 |  |  |  |  | 80.3793 |  | 23585.5975
2017-08-31 | 20:12 |  |  |  |  | 80.342 |  | 23574.6459
2017-08-31 | 20:14 |  |  |  |  | 80.2986 |  | 23561.9143
2017-08-31 | 20:15 | 1.792 | 0 | 0 | 1.5 | 80.1818 | 0 | 23527.6313
2017-08-31 | 20:16 |  |  |  |  | 80.1247 |  | 23510.8704
2017-08-31 | 20:18 |  |  |  |  | 80.0617 |  | 23492.3988
2017-08-31 | 20:20 |  |  |  |  | 79.9145 |  | 23449.2081
2017-08-31 | 20:22 |  |  |  |  | 79.8552 |  | 23431.7867
2017-08-31 | 20:24 |  |  |  |  | 79.7235 |  | 23393.1401
2017-08-31 | 20:26 |  |  |  |  | 79.6242 |  | 23364.0126
2017-08-31 | 20:28 |  |  |  |  | 79.5824 |  | 23351.7426
2017-08-31 | 20:30 | 1.7569 | 0 | 0 | 1.5 | 79.593 | 0 | 23354.8656
2017-08-31 | 20:32 |  |  |  |  | 79.5861 |  | 23352.8482
2017-08-31 | 20:34 |  |  |  |  | 79.5059 |  | 23329.3021
2017-08-31 | 20:36 |  |  |  |  | 79.3877 |  | 23294.6135
2017-08-31 | 20:38 |  |  |  |  | 79.2847 |  | 23264.398
2017-08-31 | 20:40 |  |  |  |  | 79.1668 |  | 23229.8148
2017-08-31 | 20:42 |  |  |  |  | 79.0742 |  | 23202.6372
2017-08-31 | 20:44 |  |  |  |  | 78.9464 |  | 23165.1259
2017-08-31 | 20:45 | 1.7865 | 0 | 0 | 1.5 | 78.9323 | 0 | 23160.9865
2017-08-31 | 20:46 |  |  |  |  | 78.8632 |  | 23140.7085
2017-08-31 | 20:48 |  |  |  |  | 78.7498 |  | 23107.4396
2017-08-31 | 20:50 |  |  |  |  | 78.6499 |  | 23078.1351
2017-08-31 | 20:52 |  |  |  |  | 78.6362 |  | 23074.1011
2017-08-31 | 20:54 |  |  |  |  | 78.6151 |  | 23067.9312
2017-08-31 | 20:56 |  |  |  |  | 78.6072 |  | 23065.5919
2017-08-31 | 20:58 |  |  |  |  | 78.4978 |  | 23033.5026
2017-08-31 | 21:00 | 1.7834 | 0 | 0 | 1.5 | 78.3962 | 0 | 23003.6812
2017-08-31 | 21:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:15 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 21:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 21:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 21:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 21:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 22:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 22:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 22:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 22:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 22:58 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 23:02 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:04 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:06 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:08 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:10 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:12 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:14 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 23:16 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:18 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:20 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:22 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:24 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:26 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:28 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 23:32 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:34 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:36 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:38 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:40 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:42 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:44 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 23:46 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:48 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:50 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:52 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:54 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:56 |  |  |  |  | 0 |  | 0
2017-08-31 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 5:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-01 | 5:04 |  |  |  |  | 100 |  | 29342.8571
2017-09-01 | 5:06 |  |  |  |  | 98.9203 |  | 29026.0479
2017-09-01 | 5:08 |  |  |  |  | 96.9844 |  | 28458.0069
2017-09-01 | 5:10 |  |  |  |  | 95.5812 |  | 28046.257
2017-09-01 | 5:12 |  |  |  |  | 94.3681 |  | 27690.2977
2017-09-01 | 5:14 |  |  |  |  | 93.2474 |  | 27361.4464
2017-09-01 | 5:15 | 2.1321 | 0 | 0 | 1.5 | 92.6889 | 0 | 27197.5615
2017-09-01 | 5:16 |  |  |  |  | 92.1927 |  | 27051.9866
2017-09-01 | 5:18 |  |  |  |  | 91.2659 |  | 26780.0294
2017-09-01 | 5:20 |  |  |  |  | 90.4253 |  | 26533.3554
2017-09-01 | 5:22 |  |  |  |  | 89.6286 |  | 26299.5924
2017-09-01 | 5:24 |  |  |  |  | 88.8445 |  | 26069.5074
2017-09-01 | 5:26 |  |  |  |  | 88.113 |  | 25854.8691
2017-09-01 | 5:28 |  |  |  |  | 87.4743 |  | 25667.4533
2017-09-01 | 5:30 | 1.9574 | 0 | 0 | 1.5 | 86.8593 | 0 | 25487.0088
2017-09-01 | 5:32 |  |  |  |  | 86.2696 |  | 25313.952
2017-09-01 | 5:34 |  |  |  |  | 85.7516 |  | 25161.9792
2017-09-01 | 5:36 |  |  |  |  | 85.2485 |  | 25014.3447
2017-09-01 | 5:38 |  |  |  |  | 84.7523 |  | 24868.7566
2017-09-01 | 5:40 |  |  |  |  | 84.313 |  | 24739.8352
2017-09-01 | 5:42 |  |  |  |  | 83.8691 |  | 24609.582
2017-09-01 | 5:44 |  |  |  |  | 83.4669 |  | 24491.5832
2017-09-01 | 5:45 | 1.8661 | 0 | 0 | 1.5 | 83.2998 | 0 | 24442.536
2017-09-01 | 5:46 |  |  |  |  | 83.1356 |  | 24394.3706
2017-09-01 | 5:48 |  |  |  |  | 82.786 |  | 24291.7762
2017-09-01 | 5:50 |  |  |  |  | 82.5853 |  | 24232.8857
2017-09-01 | 5:52 |  |  |  |  | 82.3761 |  | 24171.4876
2017-09-01 | 5:54 |  |  |  |  | 82.1358 |  | 24101.0004
2017-09-01 | 5:56 |  |  |  |  | 81.8781 |  | 24025.3845
2017-09-01 | 5:58 |  |  |  |  | 81.6496 |  | 23958.3337
2017-09-01 | 6:00 | 1.8388 | 0 | 0 | 1.5 | 81.4844 | 0 | 23909.8414
2017-09-01 | 6:02 |  |  |  |  | 81.2589 |  | 23843.6818
2017-09-01 | 6:04 |  |  |  |  | 81.1625 |  | 23815.3938
2017-09-01 | 6:06 |  |  |  |  | 81.0647 |  | 23786.6982
2017-09-01 | 6:08 |  |  |  |  | 81.0124 |  | 23771.3478
2017-09-01 | 6:10 |  |  |  |  | 80.86 |  | 23726.6255
2017-09-01 | 6:12 |  |  |  |  | 80.7116 |  | 23683.1033
2017-09-01 | 6:14 |  |  |  |  | 80.5818 |  | 23644.9898
2017-09-01 | 6:15 | 1.7936 | 0 | 0 | 1.5 | 80.4976 | 0 | 23620.3084
2017-09-01 | 6:16 |  |  |  |  | 80.3997 |  | 23591.5635
2017-09-01 | 6:18 |  |  |  |  | 80.2521 |  | 23548.245
2017-09-01 | 6:20 |  |  |  |  | 80.1989 |  | 23532.6481
2017-09-01 | 6:22 |  |  |  |  | 80.193 |  | 23530.9312
2017-09-01 | 6:24 |  |  |  |  | 80.0874 |  | 23499.9455
2017-09-01 | 6:26 |  |  |  |  | 80.0016 |  | 23474.7669
2017-09-01 | 6:28 |  |  |  |  | 79.8874 |  | 23441.2427
2017-09-01 | 6:30 | 1.785 | 0 | 0 | 1.5 | 79.763 | 0 | 23404.7546
2017-09-01 | 6:32 |  |  |  |  | 79.6516 |  | 23372.0473
2017-09-01 | 6:34 |  |  |  |  | 79.5857 |  | 23352.7118
2017-09-01 | 6:36 |  |  |  |  | 79.5569 |  | 23344.2652
2017-09-01 | 6:38 |  |  |  |  | 79.5435 |  | 23340.3365
2017-09-01 | 6:40 |  |  |  |  | 79.4512 |  | 23313.2506
2017-09-01 | 6:42 |  |  |  |  | 79.3637 |  | 23287.5774
2017-09-01 | 6:44 |  |  |  |  | 79.2634 |  | 23258.1588
2017-09-01 | 6:45 | 1.792 | 0 | 0 | 1.5 | 79.1909 | 0 | 23236.8756
2017-09-01 | 6:46 |  |  |  |  | 79.1332 |  | 23219.9445
2017-09-01 | 6:48 |  |  |  |  | 79.0043 |  | 23182.1174
2017-09-01 | 6:50 |  |  |  |  | 79.0561 |  | 23197.3317
2017-09-01 | 6:52 |  |  |  |  | 79.0561 |  | 23197.3138
2017-09-01 | 6:54 |  |  |  |  | 79.0526 |  | 23196.2883
2017-09-01 | 6:56 |  |  |  |  | 78.9691 |  | 23171.7905
2017-09-01 | 6:58 |  |  |  |  | 78.9254 |  | 23158.963
2017-09-01 | 7:00 | 1.7312 | 0 | 0 | 1.5 | 79.0101 | 0 | 23183.819
2017-09-01 | 7:02 |  |  |  |  | 79.0685 |  | 23200.9538
2017-09-01 | 7:04 |  |  |  |  | 79.0875 |  | 23206.5213
2017-09-01 | 7:06 |  |  |  |  | 78.9963 |  | 23179.7647
2017-09-01 | 7:08 |  |  |  |  | 78.9519 |  | 23166.74
2017-09-01 | 7:10 |  |  |  |  | 78.828 |  | 23130.3772
2017-09-01 | 7:12 |  |  |  |  | 78.6785 |  | 23086.5146
2017-09-01 | 7:14 |  |  |  |  | 78.6245 |  | 23070.6671
2017-09-01 | 7:15 | 1.7553 | 0 | 0 | 1.5 | 78.6165 | 0 | 23068.3364
2017-09-01 | 7:16 |  |  |  |  | 78.571 |  | 23054.9672
2017-09-01 | 7:18 |  |  |  |  | 78.6806 |  | 23087.1393
2017-09-01 | 7:20 |  |  |  |  | 78.5543 |  | 23050.0778
2017-09-01 | 7:22 |  |  |  |  | 78.4435 |  | 23017.5633
2017-09-01 | 7:24 |  |  |  |  | 78.3946 |  | 23003.229
2017-09-01 | 7:26 |  |  |  |  | 78.2655 |  | 22965.3236
2017-09-01 | 7:28 |  |  |  |  | 78.2247 |  | 22953.3667
2017-09-01 | 7:30 | 1.7195 | 0 | 0 | 1.5 | 78.3333 | 0 | 22985.2345
2017-09-01 | 7:32 |  |  |  |  | 78.4266 |  | 23012.6111
2017-09-01 | 7:34 |  |  |  |  | 78.5013 |  | 23034.5211
2017-09-01 | 7:36 |  |  |  |  | 78.5241 |  | 23041.2259
2017-09-01 | 7:38 |  |  |  |  | 78.4874 |  | 23030.4468
2017-09-01 | 7:40 |  |  |  |  | 78.4397 |  | 23016.4371
2017-09-01 | 7:42 |  |  |  |  | 78.4184 |  | 23010.1868
2017-09-01 | 7:44 |  |  |  |  | 78.5228 |  | 23040.8365
2017-09-01 | 7:45 | 1.7397 | 0 | 0 | 1.5 | 78.5711 | 0 | 23055.0162
2017-09-01 | 7:46 |  |  |  |  | 78.6502 |  | 23078.2067
2017-09-01 | 7:48 |  |  |  |  | 78.8313 |  | 23131.342
2017-09-01 | 7:50 |  |  |  |  | 78.842 |  | 23134.5075
2017-09-01 | 7:52 |  |  |  |  | 78.857 |  | 23138.8954
2017-09-01 | 7:54 |  |  |  |  | 78.8869 |  | 23147.673
2017-09-01 | 7:56 |  |  |  |  | 78.9503 |  | 23166.272
2017-09-01 | 7:58 |  |  |  |  | 79.0168 |  | 23185.7776
2017-09-01 | 8:00 | 1.7397 | 0 | 0 | 1.5 | 79.054 | 0 | 23196.7093
2017-09-01 | 8:02 |  |  |  |  | 79.0517 |  | 23196.0174
2017-09-01 | 8:04 |  |  |  |  | 79.1152 |  | 23214.6701
2017-09-01 | 8:06 |  |  |  |  | 79.27 |  | 23260.0773
2017-09-01 | 8:08 |  |  |  |  | 79.3719 |  | 23289.9973
2017-09-01 | 8:10 |  |  |  |  | 79.4678 |  | 23318.1198
2017-09-01 | 8:12 |  |  |  |  | 79.5082 |  | 23329.9667
2017-09-01 | 8:14 |  |  |  |  | 79.5621 |  | 23345.7875
2017-09-01 | 8:15 | 1.7202 | 0 | 0 | 1.5 | 79.6115 | 0 | 23360.2808
2017-09-01 | 8:16 |  |  |  |  | 79.6324 |  | 23366.4082
2017-09-01 | 8:18 |  |  |  |  | 79.6141 |  | 23361.0419
2017-09-01 | 8:20 |  |  |  |  | 79.6071 |  | 23358.9868
2017-09-01 | 8:22 |  |  |  |  | 79.6142 |  | 23361.0757
2017-09-01 | 8:24 |  |  |  |  | 79.6198 |  | 23362.7186
2017-09-01 | 8:26 |  |  |  |  | 79.5907 |  | 23354.1781
2017-09-01 | 8:28 |  |  |  |  | 79.6309 |  | 23365.9938
2017-09-01 | 8:30 | 1.746 | 0 | 0 | 1.5 | 79.6296 | 0 | 23365.6089
2017-09-01 | 8:32 |  |  |  |  | 79.6669 |  | 23376.545
2017-09-01 | 8:34 |  |  |  |  | 79.6818 |  | 23380.9035
2017-09-01 | 8:36 |  |  |  |  | 79.7153 |  | 23390.7516
2017-09-01 | 8:38 |  |  |  |  | 79.7371 |  | 23397.1384
2017-09-01 | 8:40 |  |  |  |  | 79.7429 |  | 23398.8399
2017-09-01 | 8:42 |  |  |  |  | 79.8045 |  | 23416.9239
2017-09-01 | 8:44 |  |  |  |  | 79.8487 |  | 23429.8882
2017-09-01 | 8:45 | 1.7522 | 0 | 0 | 1.5 | 79.8231 | 0 | 23422.3638
2017-09-01 | 8:46 |  |  |  |  | 79.8088 |  | 23418.1687
2017-09-01 | 8:48 |  |  |  |  | 79.8177 |  | 23420.7925
2017-09-01 | 8:50 |  |  |  |  | 79.8635 |  | 23434.2336
2017-09-01 | 8:52 |  |  |  |  | 79.8852 |  | 23440.6136
2017-09-01 | 8:54 |  |  |  |  | 79.9048 |  | 23446.3648
2017-09-01 | 8:56 |  |  |  |  | 79.9797 |  | 23468.342
2017-09-01 | 8:58 |  |  |  |  | 80.0066 |  | 23476.2109
2017-09-01 | 9:00 | 1.7429 | 0 | 0 | 1.5 | 80.0136 | 0 | 23478.2684
2017-09-01 | 9:02 |  |  |  |  | 80.0497 |  | 23488.8574
2017-09-01 | 9:04 |  |  |  |  | 80.169 |  | 23523.8793
2017-09-01 | 9:06 |  |  |  |  | 80.2209 |  | 23539.1158
2017-09-01 | 9:08 |  |  |  |  | 80.2992 |  | 23562.0757
2017-09-01 | 9:10 |  |  |  |  | 80.3015 |  | 23562.7585
2017-09-01 | 9:12 |  |  |  |  | 80.3444 |  | 23575.3419
2017-09-01 | 9:14 |  |  |  |  | 80.3177 |  | 23567.5156
2017-09-01 | 9:15 | 1.7561 | 0 | 0 | 1.5 | 80.3219 | 0 | 23568.7492
2017-09-01 | 9:16 |  |  |  |  | 80.3092 |  | 23565.0106
2017-09-01 | 9:18 |  |  |  |  | 80.4069 |  | 23593.688
2017-09-01 | 9:20 |  |  |  |  | 80.4977 |  | 23620.3263
2017-09-01 | 9:22 |  |  |  |  | 80.6468 |  | 23664.0724
2017-09-01 | 9:24 |  |  |  |  | 80.8506 |  | 23723.8764
2017-09-01 | 9:26 |  |  |  |  | 80.9025 |  | 23739.115
2017-09-01 | 9:28 |  |  |  |  | 80.9192 |  | 23744.002
2017-09-01 | 9:30 | 1.7655 | 0 | 0 | 1.5 | 80.8836 | 0 | 23733.5586
2017-09-01 | 9:32 |  |  |  |  | 80.9443 |  | 23751.3832
2017-09-01 | 9:34 |  |  |  |  | 80.9384 |  | 23749.637
2017-09-01 | 9:36 |  |  |  |  | 80.9694 |  | 23758.7439
2017-09-01 | 9:38 |  |  |  |  | 81.0185 |  | 23773.141
2017-09-01 | 9:40 |  |  |  |  | 81.0287 |  | 23776.1295
2017-09-01 | 9:42 |  |  |  |  | 81.0153 |  | 23772.2096
2017-09-01 | 9:44 |  |  |  |  | 81.0512 |  | 23782.7425
2017-09-01 | 9:45 | 1.7514 | 0 | 0 | 1.5 | 81.0569 | 0 | 23784.4104
2017-09-01 | 9:46 |  |  |  |  | 81.087 |  | 23793.2487
2017-09-01 | 9:48 |  |  |  |  | 81.1598 |  | 23814.6012
2017-09-01 | 9:50 |  |  |  |  | 81.2005 |  | 23826.5467
2017-09-01 | 9:52 |  |  |  |  | 81.3448 |  | 23868.8826
2017-09-01 | 9:54 |  |  |  |  | 81.522 |  | 23920.8805
2017-09-01 | 9:56 |  |  |  |  | 81.6198 |  | 23949.5781
2017-09-01 | 9:58 |  |  |  |  | 81.5839 |  | 23939.0428
2017-09-01 | 10:00 | 1.7296 | 0 | 0 | 1.5 | 81.6112 | 0 | 23947.064
2017-09-01 | 10:02 |  |  |  |  | 81.6639 |  | 23962.511
2017-09-01 | 10:04 |  |  |  |  | 81.6961 |  | 23971.9784
2017-09-01 | 10:06 |  |  |  |  | 81.7913 |  | 23999.9014
2017-09-01 | 10:08 |  |  |  |  | 81.7792 |  | 23996.3485
2017-09-01 | 10:10 |  |  |  |  | 81.7918 |  | 24000.0469
2017-09-01 | 10:12 |  |  |  |  | 81.8376 |  | 24013.5036
2017-09-01 | 10:14 |  |  |  |  | 81.8537 |  | 24018.2093
2017-09-01 | 10:15 | 1.7429 | 0 | 0 | 1.5 | 81.8162 | 0 | 24007.2086
2017-09-01 | 10:16 |  |  |  |  | 81.8779 |  | 24025.324
2017-09-01 | 10:18 |  |  |  |  | 82.03 |  | 24069.9454
2017-09-01 | 10:20 |  |  |  |  | 82.1549 |  | 24106.5902
2017-09-01 | 10:22 |  |  |  |  | 82.3015 |  | 24149.6177
2017-09-01 | 10:24 |  |  |  |  | 82.3995 |  | 24178.3714
2017-09-01 | 10:26 |  |  |  |  | 82.4314 |  | 24187.7382
2017-09-01 | 10:28 |  |  |  |  | 82.4982 |  | 24207.3287
2017-09-01 | 10:30 | 1.7117 | 0 | 0 | 1.5 | 82.6029 | 0 | 24238.048
2017-09-01 | 10:32 |  |  |  |  | 82.6057 |  | 24238.8852
2017-09-01 | 10:34 |  |  |  |  | 82.6705 |  | 24257.8738
2017-09-01 | 10:36 |  |  |  |  | 82.7462 |  | 24280.104
2017-09-01 | 10:38 |  |  |  |  | 82.8788 |  | 24319.0076
2017-09-01 | 10:40 |  |  |  |  | 83.0745 |  | 24376.4433
2017-09-01 | 10:42 |  |  |  |  | 83.2349 |  | 24423.4981
2017-09-01 | 10:44 |  |  |  |  | 83.342 |  | 24454.9137
2017-09-01 | 10:45 | 1.7358 | 0 | 0 | 1.5 | 83.3508 | 0 | 24457.5015
2017-09-01 | 10:46 |  |  |  |  | 83.3521 |  | 24457.8956
2017-09-01 | 10:48 |  |  |  |  | 83.3968 |  | 24470.9919
2017-09-01 | 10:50 |  |  |  |  | 83.424 |  | 24478.9995
2017-09-01 | 10:52 |  |  |  |  | 83.479 |  | 24495.1293
2017-09-01 | 10:54 |  |  |  |  | 83.6225 |  | 24537.2254
2017-09-01 | 10:56 |  |  |  |  | 83.8505 |  | 24604.1286
2017-09-01 | 10:58 |  |  |  |  | 84.0295 |  | 24656.6459
2017-09-01 | 11:00 | 1.6976 | 0 | 0 | 1.5 | 84.1496 | 0 | 24691.9095
2017-09-01 | 11:02 |  |  |  |  | 84.1992 |  | 24706.4609
2017-09-01 | 11:04 |  |  |  |  | 84.3191 |  | 24741.6351
2017-09-01 | 11:06 |  |  |  |  | 84.3046 |  | 24737.3772
2017-09-01 | 11:08 |  |  |  |  | 84.3596 |  | 24753.5204
2017-09-01 | 11:10 |  |  |  |  | 84.3546 |  | 24752.0404
2017-09-01 | 11:12 |  |  |  |  | 84.4034 |  | 24766.3682
2017-09-01 | 11:14 |  |  |  |  | 84.528 |  | 24802.9235
2017-09-01 | 11:15 | 1.6945 | 0 | 0 | 1.5 | 84.5693 | 0 | 24815.0483
2017-09-01 | 11:16 |  |  |  |  | 84.6267 |  | 24831.8967
2017-09-01 | 11:18 |  |  |  |  | 84.6927 |  | 24851.2477
2017-09-01 | 11:20 |  |  |  |  | 84.7665 |  | 24872.9004
2017-09-01 | 11:22 |  |  |  |  | 84.7643 |  | 24872.2666
2017-09-01 | 11:24 |  |  |  |  | 84.6723 |  | 24845.2659
2017-09-01 | 11:26 |  |  |  |  | 84.5951 |  | 24822.6061
2017-09-01 | 11:28 |  |  |  |  | 84.5552 |  | 24810.9022
2017-09-01 | 11:30 | 1.7826 | 0 | 0 | 1.5 | 84.4362 | 0 | 24776.0056
2017-09-01 | 11:32 |  |  |  |  | 84.5101 |  | 24797.6917
2017-09-01 | 11:34 |  |  |  |  | 84.6168 |  | 24828.973
2017-09-01 | 11:36 |  |  |  |  | 84.6996 |  | 24853.2759
2017-09-01 | 11:38 |  |  |  |  | 84.7533 |  | 24869.0362
2017-09-01 | 11:40 |  |  |  |  | 84.67 |  | 24844.5945
2017-09-01 | 11:42 |  |  |  |  | 84.4581 |  | 24782.4126
2017-09-01 | 11:44 |  |  |  |  | 84.1831 |  | 24701.7306
2017-09-01 | 11:45 | 1.8482 | 0 | 0 | 1.5 | 84.0126 | 0 | 24651.694
2017-09-01 | 11:46 |  |  |  |  | 83.8922 |  | 24616.3675
2017-09-01 | 11:48 |  |  |  |  | 83.7297 |  | 24568.6745
2017-09-01 | 11:50 |  |  |  |  | 83.6463 |  | 24544.2214
2017-09-01 | 11:52 |  |  |  |  | 83.5443 |  | 24514.2858
2017-09-01 | 11:54 |  |  |  |  | 83.5292 |  | 24509.8664
2017-09-01 | 11:56 |  |  |  |  | 83.3711 |  | 24463.4745
2017-09-01 | 11:58 |  |  |  |  | 83.256 |  | 24429.6971
2017-09-01 | 12:00 | 1.7444 | 0 | 0 | 1.5 | 83.2491 | 0 | 24427.6665
2017-09-01 | 12:02 |  |  |  |  | 83.2049 |  | 24414.6958
2017-09-01 | 12:04 |  |  |  |  | 83.3253 |  | 24450.0199
2017-09-01 | 12:06 |  |  |  |  | 83.535 |  | 24511.5457
2017-09-01 | 12:08 |  |  |  |  | 83.7175 |  | 24565.1082
2017-09-01 | 12:10 |  |  |  |  | 83.9135 |  | 24622.6246
2017-09-01 | 12:12 |  |  |  |  | 83.9462 |  | 24632.2039
2017-09-01 | 12:14 |  |  |  |  | 83.9542 |  | 24634.5748
2017-09-01 | 12:15 | 1.7655 | 0 | 0 | 1.5 | 83.9488 | 0 | 24632.9873
2017-09-01 | 12:16 |  |  |  |  | 83.9169 |  | 24623.6164
2017-09-01 | 12:18 |  |  |  |  | 83.8826 |  | 24613.5556
2017-09-01 | 12:20 |  |  |  |  | 83.9567 |  | 24635.2866
2017-09-01 | 12:22 |  |  |  |  | 84.0844 |  | 24672.7642
2017-09-01 | 12:24 |  |  |  |  | 84.1492 |  | 24691.7684
2017-09-01 | 12:26 |  |  |  |  | 84.2393 |  | 24718.2163
2017-09-01 | 12:28 |  |  |  |  | 84.2755 |  | 24728.8255
2017-09-01 | 12:30 | 1.7499 | 0 | 0 | 1.5 | 84.2431 | 0 | 24719.329
2017-09-01 | 12:32 |  |  |  |  | 84.2389 |  | 24718.0863
2017-09-01 | 12:34 |  |  |  |  | 84.1816 |  | 24701.2784
2017-09-01 | 12:36 |  |  |  |  | 84.293 |  | 24733.9766
2017-09-01 | 12:38 |  |  |  |  | 84.427 |  | 24773.2922
2017-09-01 | 12:40 |  |  |  |  | 84.4268 |  | 24773.2429
2017-09-01 | 12:42 |  |  |  |  | 84.4693 |  | 24785.6969
2017-09-01 | 12:44 |  |  |  |  | 84.4854 |  | 24790.4226
2017-09-01 | 12:45 | 1.7569 | 0 | 0 | 1.5 | 84.471 | 0 | 24786.2119
2017-09-01 | 12:46 |  |  |  |  | 84.4447 |  | 24778.495
2017-09-01 | 12:48 |  |  |  |  | 84.4954 |  | 24793.3757
2017-09-01 | 12:50 |  |  |  |  | 84.5693 |  | 24815.0618
2017-09-01 | 12:52 |  |  |  |  | 84.7127 |  | 24857.1265
2017-09-01 | 12:54 |  |  |  |  | 84.8956 |  | 24910.799
2017-09-01 | 12:56 |  |  |  |  | 85.0106 |  | 24944.5292
2017-09-01 | 12:58 |  |  |  |  | 85.1686 |  | 24990.9036
2017-09-01 | 13:00 | 1.7538 | 0 | 0 | 1.5 | 85.1569 | 0 | 24987.4605
2017-09-01 | 13:02 |  |  |  |  | 85.1167 |  | 24975.6646
2017-09-01 | 13:04 |  |  |  |  | 85.0644 |  | 24960.3142
2017-09-01 | 13:06 |  |  |  |  | 85.126 |  | 24978.3915
2017-09-01 | 13:08 |  |  |  |  | 85.2327 |  | 25009.7217
2017-09-01 | 13:10 |  |  |  |  | 85.3184 |  | 25034.8465
2017-09-01 | 13:12 |  |  |  |  | 85.4099 |  | 25061.7085
2017-09-01 | 13:14 |  |  |  |  | 85.535 |  | 25098.4029
2017-09-01 | 13:15 | 1.6945 | 0 | 0 | 1.5 | 85.587 | 0 | 25113.6615
2017-09-01 | 13:16 |  |  |  |  | 85.6047 |  | 25118.8642
2017-09-01 | 13:18 |  |  |  |  | 85.6021 |  | 25118.0943
2017-09-01 | 13:20 |  |  |  |  | 85.4985 |  | 25087.6927
2017-09-01 | 13:22 |  |  |  |  | 85.5697 |  | 25108.6022
2017-09-01 | 13:24 |  |  |  |  | 85.7038 |  | 25147.9471
2017-09-01 | 13:26 |  |  |  |  | 85.8663 |  | 25195.6131
2017-09-01 | 13:28 |  |  |  |  | 86.0538 |  | 25250.6509
2017-09-01 | 13:30 | 1.7382 | 0 | 0 | 1.5 | 86.1388 | 0 | 25275.5765
2017-09-01 | 13:32 |  |  |  |  | 86.2629 |  | 25311.991
2017-09-01 | 13:34 |  |  |  |  | 86.2712 |  | 25314.4447
2017-09-01 | 13:36 |  |  |  |  | 86.361 |  | 25340.7714
2017-09-01 | 13:38 |  |  |  |  | 86.516 |  | 25386.2727
2017-09-01 | 13:40 |  |  |  |  | 86.6766 |  | 25433.4035
2017-09-01 | 13:42 |  |  |  |  | 86.8636 |  | 25488.2738
2017-09-01 | 13:44 |  |  |  |  | 86.8468 |  | 25483.3398
2017-09-01 | 13:45 | 1.7936 | 0 | 0 | 1.5 | 86.7903 | 0 | 25466.7444
2017-09-01 | 13:46 |  |  |  |  | 86.6427 |  | 25423.4369
2017-09-01 | 13:48 |  |  |  |  | 86.4504 |  | 25367.02
2017-09-01 | 13:50 |  |  |  |  | 85.9562 |  | 25221.9959
2017-09-01 | 13:52 |  |  |  |  | 85.597 |  | 25116.6189
2017-09-01 | 13:54 |  |  |  |  | 85.3352 |  | 25039.7717
2017-09-01 | 13:56 |  |  |  |  | 85.0771 |  | 24964.0616
2017-09-01 | 13:58 |  |  |  |  | 84.8936 |  | 24910.2078
2017-09-01 | 14:00 | 1.8006 | 0 | 0 | 1.5 | 84.7389 | 0 | 24864.8164
2017-09-01 | 14:02 |  |  |  |  | 84.6186 |  | 24829.5258
2017-09-01 | 14:04 |  |  |  |  | 84.7253 |  | 24860.8226
2017-09-01 | 14:06 |  |  |  |  | 84.8687 |  | 24902.9143
2017-09-01 | 14:08 |  |  |  |  | 84.9357 |  | 24922.5608
2017-09-01 | 14:10 |  |  |  |  | 85.0442 |  | 24954.4016
2017-09-01 | 14:12 |  |  |  |  | 85.051 |  | 24956.3876
2017-09-01 | 14:14 |  |  |  |  | 84.9925 |  | 24939.239
2017-09-01 | 14:15 | 1.7226 | 0 | 0 | 1.5 | 85.0529 | 0 | 24956.9427
2017-09-01 | 14:16 |  |  |  |  | 85.118 |  | 24976.0678
2017-09-01 | 14:18 |  |  |  |  | 85.3431 |  | 25042.1157
2017-09-01 | 14:20 |  |  |  |  | 85.5336 |  | 25097.9997
2017-09-01 | 14:22 |  |  |  |  | 85.7778 |  | 25169.6623
2017-09-01 | 14:24 |  |  |  |  | 86.0958 |  | 25262.9773
2017-09-01 | 14:26 |  |  |  |  | 86.306 |  | 25324.6507
2017-09-01 | 14:28 |  |  |  |  | 86.3815 |  | 25346.8048
2017-09-01 | 14:30 | 1.7975 | 0 | 0 | 1.5 | 86.2839 | 0 | 25318.1674
2017-09-01 | 14:32 |  |  |  |  | 86.0528 |  | 25250.3534
2017-09-01 | 14:34 |  |  |  |  | 85.779 |  | 25170.0024
2017-09-01 | 14:36 |  |  |  |  | 85.5846 |  | 25112.9722
2017-09-01 | 14:38 |  |  |  |  | 85.3966 |  | 25057.793
2017-09-01 | 14:40 |  |  |  |  | 85.1707 |  | 24991.5057
2017-09-01 | 14:42 |  |  |  |  | 84.8472 |  | 24896.5809
2017-09-01 | 14:44 |  |  |  |  | 84.5837 |  | 24819.2816
2017-09-01 | 14:45 | 1.7873 | 0 | 0 | 1.5 | 84.5521 | 0 | 24810.0066
2017-09-01 | 14:46 |  |  |  |  | 84.4938 |  | 24792.8874
2017-09-01 | 14:48 |  |  |  |  | 84.4992 |  | 24794.4837
2017-09-01 | 14:50 |  |  |  |  | 84.5464 |  | 24808.3344
2017-09-01 | 14:52 |  |  |  |  | 84.5945 |  | 24822.4559
2017-09-01 | 14:54 |  |  |  |  | 84.7161 |  | 24858.116
2017-09-01 | 14:56 |  |  |  |  | 84.771 |  | 24874.2458
2017-09-01 | 14:58 |  |  |  |  | 84.8601 |  | 24900.3668
2017-09-01 | 15:00 | 1.7007 | 0 | 0 | 1.5 | 84.9901 | 0 | 24938.5271
2017-09-01 | 15:02 |  |  |  |  | 85.1491 |  | 24985.1703
2017-09-01 | 15:04 |  |  |  |  | 85.3075 |  | 25031.6608
2017-09-01 | 15:06 |  |  |  |  | 85.4682 |  | 25078.8209
2017-09-01 | 15:08 |  |  |  |  | 85.6279 |  | 25125.6721
2017-09-01 | 15:10 |  |  |  |  | 85.7487 |  | 25161.1171
2017-09-01 | 15:12 |  |  |  |  | 85.8792 |  | 25199.4256
2017-09-01 | 15:14 |  |  |  |  | 85.973 |  | 25226.9366
2017-09-01 | 15:15 | 1.7452 | 0 | 0 | 1.5 | 85.9849 | 0 | 25230.429
2017-09-01 | 15:16 |  |  |  |  | 85.9719 |  | 25226.6077
2017-09-01 | 15:18 |  |  |  |  | 85.8653 |  | 25195.3332
2017-09-01 | 15:20 |  |  |  |  | 85.7798 |  | 25170.2377
2017-09-01 | 15:22 |  |  |  |  | 85.6113 |  | 25120.7962
2017-09-01 | 15:24 |  |  |  |  | 85.2944 |  | 25027.8148
2017-09-01 | 15:26 |  |  |  |  | 85.0231 |  | 24948.1983
2017-09-01 | 15:28 |  |  |  |  | 84.7139 |  | 24857.4848
2017-09-01 | 15:30 | 1.8107 | 0 | 0 | 1.5 | 84.6259 | 0 | 24831.6502
2017-09-01 | 15:32 |  |  |  |  | 84.4915 |  | 24792.2339
2017-09-01 | 15:34 |  |  |  |  | 84.4591 |  | 24782.6993
2017-09-01 | 15:36 |  |  |  |  | 84.4388 |  | 24776.7532
2017-09-01 | 15:38 |  |  |  |  | 84.282 |  | 24730.7416
2017-09-01 | 15:40 |  |  |  |  | 84.2984 |  | 24735.5482
2017-09-01 | 15:42 |  |  |  |  | 84.4231 |  | 24772.1438
2017-09-01 | 15:44 |  |  |  |  | 84.5656 |  | 24813.9512
2017-09-01 | 15:45 | 1.7062 | 0 | 0 | 1.5 | 84.6658 | 0 | 24843.3518
2017-09-01 | 15:46 |  |  |  |  | 84.7244 |  | 24860.5629
2017-09-01 | 15:48 |  |  |  |  | 84.8364 |  | 24893.4357
2017-09-01 | 15:50 |  |  |  |  | 84.9994 |  | 24941.2651
2017-09-01 | 15:52 |  |  |  |  | 85.1129 |  | 24974.5634
2017-09-01 | 15:54 |  |  |  |  | 85.1223 |  | 24977.3078
2017-09-01 | 15:56 |  |  |  |  | 85.103 |  | 24971.6643
2017-09-01 | 15:58 |  |  |  |  | 85.084 |  | 24966.0698
2017-09-01 | 16:00 | 1.7546 | 0 | 0 | 1.5 | 85.0838 | 0 | 24966.0182
2017-09-01 | 16:02 |  |  |  |  | 84.9657 |  | 24931.359
2017-09-01 | 16:04 |  |  |  |  | 84.7274 |  | 24861.4358
2017-09-01 | 16:06 |  |  |  |  | 84.3279 |  | 24744.2276
2017-09-01 | 16:08 |  |  |  |  | 83.947 |  | 24632.4345
2017-09-01 | 16:10 |  |  |  |  | 83.5792 |  | 24524.5144
2017-09-01 | 16:12 |  |  |  |  | 83.1973 |  | 24412.4617
2017-09-01 | 16:14 |  |  |  |  | 82.8597 |  | 24313.4087
2017-09-01 | 16:15 | 1.8692 | 0 | 0 | 1.5 | 82.7245 | 0 | 24273.7327
2017-09-01 | 16:16 |  |  |  |  | 82.56 |  | 24225.4508
2017-09-01 | 16:18 |  |  |  |  | 82.3129 |  | 24152.9646
2017-09-01 | 16:20 |  |  |  |  | 82.1542 |  | 24106.3799
2017-09-01 | 16:22 |  |  |  |  | 82.0014 |  | 24061.5504
2017-09-01 | 16:24 |  |  |  |  | 81.8974 |  | 24031.0459
2017-09-01 | 16:26 |  |  |  |  | 81.7929 |  | 24000.3829
2017-09-01 | 16:28 |  |  |  |  | 81.6057 |  | 23945.4454
2017-09-01 | 16:30 | 1.8029 | 0 | 0 | 1.5 | 81.4311 | 0 | 23894.2245
2017-09-01 | 16:32 |  |  |  |  | 81.3148 |  | 23860.0733
2017-09-01 | 16:34 |  |  |  |  | 81.3614 |  | 23873.7541
2017-09-01 | 16:36 |  |  |  |  | 81.3997 |  | 23884.9965
2017-09-01 | 16:38 |  |  |  |  | 81.4304 |  | 23894.0007
2017-09-01 | 16:40 |  |  |  |  | 81.4385 |  | 23896.3736
2017-09-01 | 16:42 |  |  |  |  | 81.3783 |  | 23878.7259
2017-09-01 | 16:44 |  |  |  |  | 81.3659 |  | 23875.0836
2017-09-01 | 16:45 | 1.7366 | 0 | 0 | 1.5 | 81.3776 | 0 | 23878.5068
2017-09-01 | 16:46 |  |  |  |  | 81.4123 |  | 23888.704
2017-09-01 | 16:48 |  |  |  |  | 81.565 |  | 23933.5
2017-09-01 | 16:50 |  |  |  |  | 81.6081 |  | 23946.1441
2017-09-01 | 16:52 |  |  |  |  | 81.6979 |  | 23972.491
2017-09-01 | 16:54 |  |  |  |  | 81.7497 |  | 23987.7118
2017-09-01 | 16:56 |  |  |  |  | 81.7923 |  | 24000.1969
2017-09-01 | 16:58 |  |  |  |  | 81.8004 |  | 24002.5813
2017-09-01 | 17:00 | 1.7475 | 0 | 0 | 1.5 | 81.8791 | 0 | 24025.6776
2017-09-01 | 17:02 |  |  |  |  | 81.9584 |  | 24048.9442
2017-09-01 | 17:04 |  |  |  |  | 82.0758 |  | 24083.3886
2017-09-01 | 17:06 |  |  |  |  | 82.1126 |  | 24094.17
2017-09-01 | 17:08 |  |  |  |  | 82.121 |  | 24096.6348
2017-09-01 | 17:10 |  |  |  |  | 82.14 |  | 24102.2094
2017-09-01 | 17:12 |  |  |  |  | 82.0715 |  | 24082.1192
2017-09-01 | 17:14 |  |  |  |  | 82.1277 |  | 24098.6072
2017-09-01 | 17:15 | 1.7421 | 0 | 0 | 1.5 | 82.1175 | 0 | 24095.6319
2017-09-01 | 17:16 |  |  |  |  | 82.1044 |  | 24091.7636
2017-09-01 | 17:18 |  |  |  |  | 82.1362 |  | 24101.1102
2017-09-01 | 17:20 |  |  |  |  | 82.1037 |  | 24091.5799
2017-09-01 | 17:22 |  |  |  |  | 82.0324 |  | 24070.6549
2017-09-01 | 17:24 |  |  |  |  | 81.9302 |  | 24040.6545
2017-09-01 | 17:26 |  |  |  |  | 81.8456 |  | 24015.8454
2017-09-01 | 17:28 |  |  |  |  | 81.8496 |  | 24017.0006
2017-09-01 | 17:30 | 1.7288 | 0 | 0 | 1.5 | 81.9273 | 0 | 24039.8015
2017-09-01 | 17:32 |  |  |  |  | 81.8985 |  | 24031.3505
2017-09-01 | 17:34 |  |  |  |  | 81.9514 |  | 24046.8734
2017-09-01 | 17:36 |  |  |  |  | 81.8315 |  | 24011.6925
2017-09-01 | 17:38 |  |  |  |  | 81.7394 |  | 23984.683
2017-09-01 | 17:40 |  |  |  |  | 81.6594 |  | 23961.2125
2017-09-01 | 17:42 |  |  |  |  | 81.6414 |  | 23955.9047
2017-09-01 | 17:44 |  |  |  |  | 81.6457 |  | 23957.1717
2017-09-01 | 17:45 | 1.7452 | 0 | 0 | 1.5 | 81.6288 | 0 | 23952.2131
2017-09-01 | 17:46 |  |  |  |  | 81.6649 |  | 23962.8223
2017-09-01 | 17:48 |  |  |  |  | 81.7001 |  | 23973.129
2017-09-01 | 17:50 |  |  |  |  | 81.5447 |  | 23927.5495
2017-09-01 | 17:52 |  |  |  |  | 81.3198 |  | 23861.5419
2017-09-01 | 17:54 |  |  |  |  | 81.2305 |  | 23835.3628
2017-09-01 | 17:56 |  |  |  |  | 81.0923 |  | 23794.7845
2017-09-01 | 17:58 |  |  |  |  | 81.0708 |  | 23788.487
2017-09-01 | 18:00 | 1.7522 | 0 | 0 | 1.5 | 81.073 | 0 | 23789.1252
2017-09-01 | 18:02 |  |  |  |  | 81.0231 |  | 23774.4819
2017-09-01 | 18:04 |  |  |  |  | 80.9921 |  | 23765.4085
2017-09-01 | 18:06 |  |  |  |  | 80.8512 |  | 23724.0509
2017-09-01 | 18:08 |  |  |  |  | 80.7259 |  | 23687.2717
2017-09-01 | 18:10 |  |  |  |  | 80.6353 |  | 23660.6918
2017-09-01 | 18:12 |  |  |  |  | 80.5795 |  | 23644.3138
2017-09-01 | 18:14 |  |  |  |  | 80.5515 |  | 23636.1133
2017-09-01 | 18:15 | 1.7421 | 0 | 0 | 1.5 | 80.5853 | 0 | 23646.0306
2017-09-01 | 18:16 |  |  |  |  | 80.5968 |  | 23649.3977
2017-09-01 | 18:18 |  |  |  |  | 80.5525 |  | 23636.4
2017-09-01 | 18:20 |  |  |  |  | 80.491 |  | 23618.3539
2017-09-01 | 18:22 |  |  |  |  | 80.3803 |  | 23585.8728
2017-09-01 | 18:24 |  |  |  |  | 80.3032 |  | 23563.2553
2017-09-01 | 18:26 |  |  |  |  | 80.2268 |  | 23540.8259
2017-09-01 | 18:28 |  |  |  |  | 80.2348 |  | 23543.1901
2017-09-01 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 80.2293 | 0 | 23541.5759
2017-09-01 | 18:32 |  |  |  |  | 80.2152 |  | 23537.4389
2017-09-01 | 18:34 |  |  |  |  | 80.1025 |  | 23504.3489
2017-09-01 | 18:36 |  |  |  |  | 80.03 |  | 23483.0815
2017-09-01 | 18:38 |  |  |  |  | 79.9333 |  | 23454.7085
2017-09-01 | 18:40 |  |  |  |  | 79.8181 |  | 23420.9134
2017-09-01 | 18:42 |  |  |  |  | 79.7544 |  | 23402.2202
2017-09-01 | 18:44 |  |  |  |  | 79.7537 |  | 23402.0099
2017-09-01 | 18:45 | 1.7421 | 0 | 0 | 1.5 | 79.7921 | 0 | 23413.2951
2017-09-01 | 18:46 |  |  |  |  | 79.7881 |  | 23412.1041
2017-09-01 | 18:48 |  |  |  |  | 79.7837 |  | 23410.8168
2017-09-01 | 18:50 |  |  |  |  | 79.7069 |  | 23388.28
2017-09-01 | 18:52 |  |  |  |  | 79.6308 |  | 23365.9425
2017-09-01 | 18:54 |  |  |  |  | 79.5824 |  | 23351.7605
2017-09-01 | 18:56 |  |  |  |  | 79.4879 |  | 23324.0209
2017-09-01 | 18:58 |  |  |  |  | 79.4685 |  | 23318.3346
2017-09-01 | 19:00 | 1.7608 | 0 | 0 | 1.5 | 79.4126 | 0 | 23301.9228
2017-09-01 | 19:02 |  |  |  |  | 79.3826 |  | 23293.127
2017-09-01 | 19:04 |  |  |  |  | 79.4076 |  | 23300.4566
2017-09-01 | 19:06 |  |  |  |  | 79.3296 |  | 23277.575
2017-09-01 | 19:08 |  |  |  |  | 79.255 |  | 23255.6852
2017-09-01 | 19:10 |  |  |  |  | 79.1768 |  | 23232.7274
2017-09-01 | 19:12 |  |  |  |  | 79.0706 |  | 23201.5805
2017-09-01 | 19:14 |  |  |  |  | 78.957 |  | 23168.2421
2017-09-01 | 19:15 | 1.7858 | 0 | 0 | 1.5 | 78.9176 | 0 | 23156.6816
2017-09-01 | 19:16 |  |  |  |  | 78.8957 |  | 23150.2388
2017-09-01 | 19:18 |  |  |  |  | 78.9278 |  | 23159.6681
2017-09-01 | 19:20 |  |  |  |  | 78.9374 |  | 23162.4844
2017-09-01 | 19:22 |  |  |  |  | 78.8753 |  | 23144.2748
2017-09-01 | 19:24 |  |  |  |  | 78.7612 |  | 23110.7908
2017-09-01 | 19:26 |  |  |  |  | 78.6487 |  | 23077.7792
2017-09-01 | 19:28 |  |  |  |  | 78.5651 |  | 23053.25
2017-09-01 | 19:30 | 1.7741 | 0 | 0 | 1.5 | 78.494 | 0 | 23032.3764
2017-09-01 | 19:32 |  |  |  |  | 78.4201 |  | 23010.7061
2017-09-01 | 19:34 |  |  |  |  | 78.3366 |  | 22986.1993
2017-09-01 | 19:36 |  |  |  |  | 78.2851 |  | 22971.0994
2017-09-01 | 19:38 |  |  |  |  | 78.1727 |  | 22938.1078
2017-09-01 | 19:40 |  |  |  |  | 78.1779 |  | 22939.6301
2017-09-01 | 19:42 |  |  |  |  | 78.1681 |  | 22936.7469
2017-09-01 | 19:44 |  |  |  |  | 78.1133 |  | 22920.6731
2017-09-01 | 19:45 | 1.8123 | 0 | 0 | 1.5 | 77.9948 | 0 | 22885.9039
2017-09-01 | 19:46 |  |  |  |  | 77.9516 |  | 22873.2398
2017-09-01 | 19:48 |  |  |  |  | 77.8292 |  | 22837.3089
2017-09-01 | 19:50 |  |  |  |  | 77.7575 |  | 22816.2809
2017-09-01 | 19:52 |  |  |  |  | 77.6402 |  | 22781.8568
2017-09-01 | 19:54 |  |  |  |  | 77.5766 |  | 22763.2018
2017-09-01 | 19:56 |  |  |  |  | 77.4861 |  | 22736.6488
2017-09-01 | 19:58 |  |  |  |  | 77.382 |  | 22706.102
2017-09-01 | 20:00 | 1.7538 | 0 | 0 | 1.5 | 77.3992 | 0 | 22711.1323
2017-09-01 | 20:02 |  |  |  |  | 77.4245 |  | 22718.5469
2017-09-01 | 20:04 |  |  |  |  | 77.3831 |  | 22706.4087
2017-09-01 | 20:06 |  |  |  |  | 77.3056 |  | 22683.6592
2017-09-01 | 20:08 |  |  |  |  | 77.1941 |  | 22650.943
2017-09-01 | 20:10 |  |  |  |  | 77.0804 |  | 22617.6025
2017-09-01 | 20:12 |  |  |  |  | 77.0348 |  | 22604.206
2017-09-01 | 20:14 |  |  |  |  | 76.9453 |  | 22577.9398
2017-09-01 | 20:15 | 1.7678 | 0 | 0 | 1.5 | 76.9268 | 0 | 22572.5222
2017-09-01 | 20:16 |  |  |  |  | 76.8671 |  | 22554.9954
2017-09-01 | 20:18 |  |  |  |  | 76.8135 |  | 22539.2641
2017-09-01 | 20:20 |  |  |  |  | 76.771 |  | 22526.8148
2017-09-01 | 20:22 |  |  |  |  | 76.6719 |  | 22497.739
2017-09-01 | 20:24 |  |  |  |  | 76.6282 |  | 22484.9112
2017-09-01 | 20:26 |  |  |  |  | 76.5251 |  | 22454.6464
2017-09-01 | 20:28 |  |  |  |  | 76.4983 |  | 22446.7954
2017-09-01 | 20:30 | 1.7803 | 0 | 0 | 1.5 | 76.4978 | 0 | 22446.6499
2017-09-01 | 20:32 |  |  |  |  | 76.531 |  | 22456.377
2017-09-01 | 20:34 |  |  |  |  | 76.5577 |  | 22464.2212
2017-09-01 | 20:36 |  |  |  |  | 76.4988 |  | 22446.923
2017-09-01 | 20:38 |  |  |  |  | 76.4398 |  | 22429.6292
2017-09-01 | 20:40 |  |  |  |  | 76.3875 |  | 22414.2876
2017-09-01 | 20:42 |  |  |  |  | 76.3349 |  | 22398.8474
2017-09-01 | 20:44 |  |  |  |  | 76.2657 |  | 22378.5225
2017-09-01 | 20:45 | 1.7702 | 0 | 0 | 1.5 | 76.2518 | 0 | 22374.4479
2017-09-01 | 20:46 |  |  |  |  | 76.215 |  | 22363.6553
2017-09-01 | 20:48 |  |  |  |  | 76.1484 |  | 22344.1071
2017-09-01 | 20:50 |  |  |  |  | 76.1307 |  | 22338.9267
2017-09-01 | 20:52 |  |  |  |  | 76.0907 |  | 22327.1916
2017-09-01 | 20:54 |  |  |  |  | 76.0122 |  | 22304.1645
2017-09-01 | 20:56 |  |  |  |  | 75.9646 |  | 22290.1794
2017-09-01 | 20:58 |  |  |  |  | 75.9177 |  | 22276.4296
2017-09-01 | 21:00 | 1.7195 | 0 | 0 | 1.5 | 76.0447 | 0 | 22313.6947
2017-09-01 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:15 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-01 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-01 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:15 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 0:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 0:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:45 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 0:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 1:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:15 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 1:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 1:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:45 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 1:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 2:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:15 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 2:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 2:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:45 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 2:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 3:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:15 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 3:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 3:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:45 | 0.03466 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 3:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 4:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:15 | 0.03466 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 4:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 4:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:45 | 0.03544 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 4:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 5:00 | 0.03544 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-02 | 5:00 |  |  |  | 1.5 | 25 |  | 7335.7143
2017-09-02 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-02 | 5:04 |  |  |  |  | 99.9697 |  | 29333.9742
2017-09-02 | 5:06 |  |  |  |  | 98.868 |  | 29010.686
2017-09-02 | 5:08 |  |  |  |  | 96.951 |  | 28448.199
2017-09-02 | 5:10 |  |  |  |  | 95.5327 |  | 28032.0301
2017-09-02 | 5:12 |  |  |  |  | 94.3343 |  | 27680.3669
2017-09-02 | 5:14 |  |  |  |  | 93.2628 |  | 27365.9684
2017-09-02 | 5:15 | 2.1212 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 5:15 |  |  |  | 1.5 | 92.6879 |  | 27197.2816
2017-09-02 | 5:16 |  |  |  |  | 92.212 |  | 27057.6281
2017-09-02 | 5:18 |  |  |  |  | 91.2543 |  | 26776.6333
2017-09-02 | 5:20 |  |  |  |  | 90.332 |  | 26505.99
2017-09-02 | 5:22 |  |  |  |  | 89.4082 |  | 26234.928
2017-09-02 | 5:24 |  |  |  |  | 88.445 |  | 25952.2967
2017-09-02 | 5:26 |  |  |  |  | 87.5397 |  | 25686.6388
2017-09-02 | 5:28 |  |  |  |  | 86.6233 |  | 25417.7394
2017-09-02 | 5:30 | 2.0081 | 0 | 0 | 1.5 | 85.828 | 0 | 25184.3971
2017-09-02 | 5:30 |  |  |  | 1.5 | 85.828 |  | 25184.3971
2017-09-02 | 5:32 |  |  |  |  | 85.0589 |  | 24958.72
2017-09-02 | 5:34 |  |  |  |  | 84.3847 |  | 24760.8966
2017-09-02 | 5:36 |  |  |  |  | 83.7541 |  | 24575.8339
2017-09-02 | 5:38 |  |  |  |  | 83.1494 |  | 24398.4138
2017-09-02 | 5:40 |  |  |  |  | 82.5938 |  | 24235.3907
2017-09-02 | 5:42 |  |  |  |  | 82.0317 |  | 24070.4334
2017-09-02 | 5:44 |  |  |  |  | 81.6302 |  | 23952.6227
2017-09-02 | 5:45 | 1.8723 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 5:45 |  |  |  | 1.5 | 81.4616 |  | 23903.1568
2017-09-02 | 5:46 |  |  |  |  | 81.3197 |  | 23861.5105
2017-09-02 | 5:48 |  |  |  |  | 81.0647 |  | 23786.6982
2017-09-02 | 5:50 |  |  |  |  | 80.7133 |  | 23683.5778
2017-09-02 | 5:52 |  |  |  |  | 80.4416 |  | 23603.8764
2017-09-02 | 5:54 |  |  |  |  | 80.2147 |  | 23537.2778
2017-09-02 | 5:56 |  |  |  |  | 79.9469 |  | 23458.7067
2017-09-02 | 5:58 |  |  |  |  | 79.7214 |  | 23392.5245
2017-09-02 | 6:00 | 1.7811 | 0 | 0 | 1.5 | 79.572 | 0 | 23348.7024
2017-09-02 | 6:00 |  |  |  | 1.5 | 79.572 |  | 23348.7024
2017-09-02 | 6:02 |  |  |  |  | 79.4905 |  | 23324.7888
2017-09-02 | 6:04 |  |  |  |  | 79.301 |  | 23269.1844
2017-09-02 | 6:06 |  |  |  |  | 79.0834 |  | 23205.3326
2017-09-02 | 6:08 |  |  |  |  | 78.8716 |  | 23143.1847
2017-09-02 | 6:10 |  |  |  |  | 78.8629 |  | 23140.6348
2017-09-02 | 6:12 |  |  |  |  | 78.8983 |  | 23151.0111
2017-09-02 | 6:14 |  |  |  |  | 78.8252 |  | 23129.5532
2017-09-02 | 6:15 | 1.8076 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 6:15 |  |  |  | 1.5 | 78.7278 |  | 23100.9765
2017-09-02 | 6:16 |  |  |  |  | 78.6463 |  | 23077.0583
2017-09-02 | 6:18 |  |  |  |  | 78.549 |  | 23048.5241
2017-09-02 | 6:20 |  |  |  |  | 78.4768 |  | 23027.3283
2017-09-02 | 6:22 |  |  |  |  | 78.3126 |  | 22979.1496
2017-09-02 | 6:24 |  |  |  |  | 78.2311 |  | 22955.2294
2017-09-02 | 6:26 |  |  |  |  | 78.2169 |  | 22951.0653
2017-09-02 | 6:28 |  |  |  |  | 78.2179 |  | 22951.3675
2017-09-02 | 6:30 | 1.7904 | 0 | 0 | 1.5 | 78.0415 | 0 | 22899.5915
2017-09-02 | 6:30 |  |  |  | 1.5 | 78.0415 |  | 22899.5915
2017-09-02 | 6:32 |  |  |  |  | 77.9706 |  | 22878.7894
2017-09-02 | 6:34 |  |  |  |  | 77.9339 |  | 22868.035
2017-09-02 | 6:36 |  |  |  |  | 78.0081 |  | 22889.8194
2017-09-02 | 6:38 |  |  |  |  | 78.1169 |  | 22921.7298
2017-09-02 | 6:40 |  |  |  |  | 77.9799 |  | 22881.523
2017-09-02 | 6:42 |  |  |  |  | 77.9101 |  | 22861.0614
2017-09-02 | 6:44 |  |  |  |  | 77.8312 |  | 22837.909
2017-09-02 | 6:45 | 1.739 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 6:45 |  |  |  | 1.5 | 77.8704 |  | 22849.4114
2017-09-02 | 6:46 |  |  |  |  | 77.8911 |  | 22855.4669
2017-09-02 | 6:48 |  |  |  |  | 77.9158 |  | 22862.7181
2017-09-02 | 6:50 |  |  |  |  | 77.8149 |  | 22833.1182
2017-09-02 | 6:52 |  |  |  |  | 77.7249 |  | 22806.7017
2017-09-02 | 6:54 |  |  |  |  | 77.6467 |  | 22783.7573
2017-09-02 | 6:56 |  |  |  |  | 77.7278 |  | 22807.5567
2017-09-02 | 6:58 |  |  |  |  | 77.8246 |  | 22835.95
2017-09-02 | 7:00 | 1.7912 | 0 | 0 | 1.5 | 77.6963 | 0 | 22798.3155
2017-09-02 | 7:00 |  |  |  | 1.5 | 77.6963 |  | 22798.3155
2017-09-02 | 7:02 |  |  |  |  | 77.6222 |  | 22776.5804
2017-09-02 | 7:04 |  |  |  |  | 77.576 |  | 22763.0005
2017-09-02 | 7:06 |  |  |  |  | 77.6554 |  | 22786.3052
2017-09-02 | 7:08 |  |  |  |  | 77.7622 |  | 22817.6557
2017-09-02 | 7:10 |  |  |  |  | 77.667 |  | 22789.728
2017-09-02 | 7:12 |  |  |  |  | 77.5853 |  | 22765.754
2017-09-02 | 7:14 |  |  |  |  | 77.5126 |  | 22744.3968
2017-09-02 | 7:15 | 1.7436 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 7:15 |  |  |  | 1.5 | 77.5411 |  | 22752.7786
2017-09-02 | 7:16 |  |  |  |  | 77.5884 |  | 22766.6428
2017-09-02 | 7:18 |  |  |  |  | 77.7163 |  | 22804.1899
2017-09-02 | 7:20 |  |  |  |  | 77.6267 |  | 22777.8788
2017-09-02 | 7:22 |  |  |  |  | 77.5074 |  | 22742.8792
2017-09-02 | 7:24 |  |  |  |  | 77.4734 |  | 22732.9214
2017-09-02 | 7:26 |  |  |  |  | 77.5637 |  | 22759.4118
2017-09-02 | 7:28 |  |  |  |  | 77.6634 |  | 22788.6737
2017-09-02 | 7:30 | 1.7865 | 0 | 0 | 1.5 | 77.5828 | 0 | 22765.0243
2017-09-02 | 7:30 |  |  |  | 1.5 | 77.5828 |  | 22765.0243
2017-09-02 | 7:32 |  |  |  |  | 77.4615 |  | 22729.4223
2017-09-02 | 7:34 |  |  |  |  | 77.409 |  | 22714.0114
2017-09-02 | 7:36 |  |  |  |  | 77.4945 |  | 22739.0981
2017-09-02 | 7:38 |  |  |  |  | 77.5574 |  | 22757.5583
2017-09-02 | 7:40 |  |  |  |  | 77.4599 |  | 22728.9545
2017-09-02 | 7:42 |  |  |  |  | 77.3513 |  | 22697.0958
2017-09-02 | 7:44 |  |  |  |  | 77.3074 |  | 22684.1876
2017-09-02 | 7:45 | 1.7444 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 7:45 |  |  |  | 1.5 | 77.3008 |  | 22682.278
2017-09-02 | 7:46 |  |  |  |  | 77.3763 |  | 22704.4028
2017-09-02 | 7:48 |  |  |  |  | 77.4736 |  | 22732.9596
2017-09-02 | 7:50 |  |  |  |  | 77.3994 |  | 22711.1883
2017-09-02 | 7:52 |  |  |  |  | 77.2578 |  | 22669.6406
2017-09-02 | 7:54 |  |  |  |  | 77.1548 |  | 22639.4139
2017-09-02 | 7:56 |  |  |  |  | 77.1024 |  | 22624.0386
2017-09-02 | 7:58 |  |  |  |  | 77.0231 |  | 22600.7832
2017-09-02 | 8:00 | 1.7553 | 0 | 0 | 1.5 | 77.0014 | 0 | 22594.4076
2017-09-02 | 8:00 |  |  |  | 1.5 | 77.0014 |  | 22594.4076
2017-09-02 | 8:02 |  |  |  |  | 77.0795 |  | 22617.3337
2017-09-02 | 8:04 |  |  |  |  | 77.1612 |  | 22641.3101
2017-09-02 | 8:06 |  |  |  |  | 77.1119 |  | 22626.837
2017-09-02 | 8:08 |  |  |  |  | 77.0565 |  | 22610.5819
2017-09-02 | 8:10 |  |  |  |  | 77.183 |  | 22647.7083
2017-09-02 | 8:12 |  |  |  |  | 77.3906 |  | 22708.6229
2017-09-02 | 8:14 |  |  |  |  | 77.4902 |  | 22737.8466
2017-09-02 | 8:15 | 1.7452 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 8:15 |  |  |  | 1.5 | 77.4984 |  | 22740.2307
2017-09-02 | 8:16 |  |  |  |  | 77.4905 |  | 22737.9182
2017-09-02 | 8:18 |  |  |  |  | 77.5156 |  | 22745.2947
2017-09-02 | 8:20 |  |  |  |  | 77.4701 |  | 22731.9475
2017-09-02 | 8:22 |  |  |  |  | 77.4423 |  | 22723.7967
2017-09-02 | 8:24 |  |  |  |  | 77.4307 |  | 22720.3938
2017-09-02 | 8:26 |  |  |  |  | 77.5103 |  | 22743.741
2017-09-02 | 8:28 |  |  |  |  | 77.6483 |  | 22784.2162
2017-09-02 | 8:30 | 1.7647 | 0 | 0 | 1.5 | 77.6545 | 0 | 22786.0634
2017-09-02 | 8:30 |  |  |  | 1.5 | 77.6545 |  | 22786.0634
2017-09-02 | 8:32 |  |  |  |  | 77.5712 |  | 22761.5991
2017-09-02 | 8:34 |  |  |  |  | 77.5365 |  | 22751.4309
2017-09-02 | 8:36 |  |  |  |  | 77.5327 |  | 22750.3094
2017-09-02 | 8:38 |  |  |  |  | 77.4539 |  | 22727.1861
2017-09-02 | 8:40 |  |  |  |  | 77.5488 |  | 22755.0216
2017-09-02 | 8:42 |  |  |  |  | 77.6929 |  | 22797.3172
2017-09-02 | 8:44 |  |  |  |  | 77.819 |  | 22834.318
2017-09-02 | 8:45 | 1.7397 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 8:45 |  |  |  | 1.5 | 77.8119 |  | 22832.2226
2017-09-02 | 8:46 |  |  |  |  | 77.7911 |  | 22826.1266
2017-09-02 | 8:48 |  |  |  |  | 77.8342 |  | 22838.7752
2017-09-02 | 8:50 |  |  |  |  | 77.777 |  | 22822.0031
2017-09-02 | 8:52 |  |  |  |  | 77.7709 |  | 22820.2167
2017-09-02 | 8:54 |  |  |  |  | 77.7447 |  | 22812.5245
2017-09-02 | 8:56 |  |  |  |  | 77.6894 |  | 22796.2897
2017-09-02 | 8:58 |  |  |  |  | 77.6707 |  | 22790.7914
2017-09-02 | 9:00 | 1.7257 | 0 | 0 | 1.5 | 77.7878 | 0 | 22825.1686
2017-09-02 | 9:00 |  |  |  | 1.5 | 77.7878 |  | 22825.1686
2017-09-02 | 9:02 |  |  |  |  | 77.9538 |  | 22873.8689
2017-09-02 | 9:04 |  |  |  |  | 78.0712 |  | 22908.3289
2017-09-02 | 9:06 |  |  |  |  | 78.076 |  | 22909.7168
2017-09-02 | 9:08 |  |  |  |  | 78.0969 |  | 22915.8577
2017-09-02 | 9:10 |  |  |  |  | 78.1015 |  | 22917.2254
2017-09-02 | 9:12 |  |  |  |  | 78.0984 |  | 22916.2876
2017-09-02 | 9:14 |  |  |  |  | 78.0966 |  | 22915.7814
2017-09-02 | 9:15 | 1.7475 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 9:15 |  |  |  | 1.5 | 78.1168 |  | 22921.7004
2017-09-02 | 9:16 |  |  |  |  | 78.0946 |  | 22915.1793
2017-09-02 | 9:18 |  |  |  |  | 78.0512 |  | 22902.448
2017-09-02 | 9:20 |  |  |  |  | 78.022 |  | 22893.8828
2017-09-02 | 9:22 |  |  |  |  | 77.9196 |  | 22863.8419
2017-09-02 | 9:24 |  |  |  |  | 77.8757 |  | 22850.9425
2017-09-02 | 9:26 |  |  |  |  | 77.8125 |  | 22832.4151
2017-09-02 | 9:28 |  |  |  |  | 77.7603 |  | 22817.0937
2017-09-02 | 9:30 | 1.7093 | 0 | 0 | 1.5 | 77.8464 | 0 | 22842.3706
2017-09-02 | 9:30 |  |  |  | 1.5 | 77.8464 |  | 22842.3706
2017-09-02 | 9:32 |  |  |  |  | 77.9478 |  | 22872.1116
2017-09-02 | 9:34 |  |  |  |  | 78.0651 |  | 22906.529
2017-09-02 | 9:36 |  |  |  |  | 78.0874 |  | 22913.0681
2017-09-02 | 9:38 |  |  |  |  | 78.1299 |  | 22925.542
2017-09-02 | 9:40 |  |  |  |  | 78.1444 |  | 22929.8002
2017-09-02 | 9:42 |  |  |  |  | 78.2106 |  | 22949.2208
2017-09-02 | 9:44 |  |  |  |  | 78.1594 |  | 22934.2014
2017-09-02 | 9:45 | 1.7577 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 9:45 |  |  |  | 1.5 | 78.1645 |  | 22935.7034
2017-09-02 | 9:46 |  |  |  |  | 78.159 |  | 22934.0781
2017-09-02 | 9:48 |  |  |  |  | 78.1223 |  | 22923.319
2017-09-02 | 9:50 |  |  |  |  | 78.0973 |  | 22915.9674
2017-09-02 | 9:52 |  |  |  |  | 78.0512 |  | 22902.4568
2017-09-02 | 9:54 |  |  |  |  | 78.0258 |  | 22895.0043
2017-09-02 | 9:56 |  |  |  |  | 77.9713 |  | 22879.0201
2017-09-02 | 9:58 |  |  |  |  | 77.9509 |  | 22873.0294
2017-09-02 | 10:00 | 1.7631 | 0 | 0 | 1.5 | 77.9287 | 0 | 22866.5127
2017-09-02 | 10:00 |  |  |  | 1.5 | 77.9287 |  | 22866.5127
2017-09-02 | 10:02 |  |  |  |  | 77.9373 |  | 22869.0356
2017-09-02 | 10:04 |  |  |  |  | 77.9157 |  | 22862.6911
2017-09-02 | 10:06 |  |  |  |  | 77.8287 |  | 22837.1546
2017-09-02 | 10:08 |  |  |  |  | 77.7813 |  | 22823.2546
2017-09-02 | 10:10 |  |  |  |  | 77.7354 |  | 22809.7733
2017-09-02 | 10:12 |  |  |  |  | 77.6871 |  | 22795.6291
2017-09-02 | 10:14 |  |  |  |  | 77.656 |  | 22786.4953
2017-09-02 | 10:15 | 1.7639 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 10:15 |  |  |  | 1.5 | 77.6727 |  | 22791.3915
2017-09-02 | 10:16 |  |  |  |  | 77.634 |  | 22780.0478
2017-09-02 | 10:18 |  |  |  |  | 77.6461 |  | 22783.5918
2017-09-02 | 10:20 |  |  |  |  | 77.5801 |  | 22764.225
2017-09-02 | 10:22 |  |  |  |  | 77.5464 |  | 22754.3165
2017-09-02 | 10:24 |  |  |  |  | 77.5638 |  | 22759.4341
2017-09-02 | 10:26 |  |  |  |  | 77.5238 |  | 22747.7102
2017-09-02 | 10:28 |  |  |  |  | 77.5286 |  | 22749.1184
2017-09-02 | 10:30 | 1.7585 | 0 | 0 | 1.5 | 77.4771 | 0 | 22733.9804
2017-09-02 | 10:30 |  |  |  | 1.5 | 77.4771 |  | 22733.9804
2017-09-02 | 10:32 |  |  |  |  | 77.4553 |  | 22727.6001
2017-09-02 | 10:34 |  |  |  |  | 77.4764 |  | 22733.7879
2017-09-02 | 10:36 |  |  |  |  | 77.4527 |  | 22726.8366
2017-09-02 | 10:38 |  |  |  |  | 77.4297 |  | 22720.0871
2017-09-02 | 10:40 |  |  |  |  | 77.4313 |  | 22720.564
2017-09-02 | 10:42 |  |  |  |  | 77.45 |  | 22726.042
2017-09-02 | 10:44 |  |  |  |  | 77.4569 |  | 22728.0546
2017-09-02 | 10:45 | 1.7436 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 10:45 |  |  |  | 1.5 | 77.496 |  | 22739.5277
2017-09-02 | 10:46 |  |  |  |  | 77.4888 |  | 22737.4144
2017-09-02 | 10:48 |  |  |  |  | 77.5025 |  | 22741.4464
2017-09-02 | 10:50 |  |  |  |  | 77.5236 |  | 22747.6498
2017-09-02 | 10:52 |  |  |  |  | 77.5492 |  | 22755.1516
2017-09-02 | 10:54 |  |  |  |  | 77.5439 |  | 22753.5891
2017-09-02 | 10:56 |  |  |  |  | 77.6078 |  | 22772.3468
2017-09-02 | 10:58 |  |  |  |  | 77.592 |  | 22767.7173
2017-09-02 | 11:00 | 1.7429 | 0 | 0 | 1.5 | 77.6111 | 0 | 22773.3163
2017-09-02 | 11:00 |  |  |  | 1.5 | 77.6111 |  | 22773.3163
2017-09-02 | 11:02 |  |  |  |  | 77.6429 |  | 22782.6449
2017-09-02 | 11:04 |  |  |  |  | 77.6907 |  | 22796.6746
2017-09-02 | 11:06 |  |  |  |  | 77.7122 |  | 22802.9854
2017-09-02 | 11:08 |  |  |  |  | 77.7486 |  | 22813.6507
2017-09-02 | 11:10 |  |  |  |  | 77.7918 |  | 22826.3238
2017-09-02 | 11:12 |  |  |  |  | 77.7955 |  | 22827.4207
2017-09-02 | 11:14 |  |  |  |  | 77.84 |  | 22840.49
2017-09-02 | 11:15 | 1.728 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 11:15 |  |  |  | 1.5 | 77.8379 |  | 22839.8767
2017-09-02 | 11:16 |  |  |  |  | 77.8381 |  | 22839.9284
2017-09-02 | 11:18 |  |  |  |  | 77.8882 |  | 22854.623
2017-09-02 | 11:20 |  |  |  |  | 77.9293 |  | 22866.6714
2017-09-02 | 11:22 |  |  |  |  | 77.9566 |  | 22874.704
2017-09-02 | 11:24 |  |  |  |  | 77.9461 |  | 22871.599
2017-09-02 | 11:26 |  |  |  |  | 77.9492 |  | 22872.5101
2017-09-02 | 11:28 |  |  |  |  | 77.9918 |  | 22885.031
2017-09-02 | 11:30 | 1.7444 | 0 | 0 | 1.5 | 77.9908 | 0 | 22884.7311
2017-09-02 | 11:30 |  |  |  | 1.5 | 77.9908 |  | 22884.7311
2017-09-02 | 11:32 |  |  |  |  | 78.0205 |  | 22893.4506
2017-09-02 | 11:34 |  |  |  |  | 78.0139 |  | 22891.5187
2017-09-02 | 11:36 |  |  |  |  | 78.0457 |  | 22900.8315
2017-09-02 | 11:38 |  |  |  |  | 78.0526 |  | 22902.8553
2017-09-02 | 11:40 |  |  |  |  | 78.0707 |  | 22908.179
2017-09-02 | 11:42 |  |  |  |  | 78.1067 |  | 22918.75
2017-09-02 | 11:44 |  |  |  |  | 78.1146 |  | 22921.0669
2017-09-02 | 11:45 | 1.7335 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 11:45 |  |  |  | 1.5 | 78.1277 |  | 22924.9017
2017-09-02 | 11:46 |  |  |  |  | 78.1044 |  | 22918.0696
2017-09-02 | 11:48 |  |  |  |  | 78.1331 |  | 22926.4757
2017-09-02 | 11:50 |  |  |  |  | 78.1115 |  | 22920.1582
2017-09-02 | 11:52 |  |  |  |  | 78.1527 |  | 22932.2425
2017-09-02 | 11:54 |  |  |  |  | 78.1879 |  | 22942.5741
2017-09-02 | 11:56 |  |  |  |  | 78.1927 |  | 22943.9778
2017-09-02 | 11:58 |  |  |  |  | 78.2113 |  | 22949.4444
2017-09-02 | 12:00 | 1.76 | 0 | 0 | 1.5 | 78.2211 | 0 | 22952.3077
2017-09-02 | 12:00 |  |  |  | 1.5 | 78.2211 |  | 22952.3077
2017-09-02 | 12:02 |  |  |  |  | 78.2187 |  | 22951.6117
2017-09-02 | 12:04 |  |  |  |  | 78.2388 |  | 22957.4949
2017-09-02 | 12:06 |  |  |  |  | 78.2702 |  | 22966.7159
2017-09-02 | 12:08 |  |  |  |  | 78.3014 |  | 22975.8744
2017-09-02 | 12:10 |  |  |  |  | 78.3048 |  | 22976.855
2017-09-02 | 12:12 |  |  |  |  | 78.3137 |  | 22979.4809
2017-09-02 | 12:14 |  |  |  |  | 78.3502 |  | 22990.182
2017-09-02 | 12:15 | 1.7468 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 12:15 |  |  |  | 1.5 | 78.3516 |  | 22990.6072
2017-09-02 | 12:16 |  |  |  |  | 78.3532 |  | 22991.0661
2017-09-02 | 12:18 |  |  |  |  | 78.3579 |  | 22992.4384
2017-09-02 | 12:20 |  |  |  |  | 78.3707 |  | 22996.2017
2017-09-02 | 12:22 |  |  |  |  | 78.3885 |  | 23001.4291
2017-09-02 | 12:24 |  |  |  |  | 78.4015 |  | 23005.2302
2017-09-02 | 12:26 |  |  |  |  | 78.3927 |  | 23002.6603
2017-09-02 | 12:28 |  |  |  |  | 78.4214 |  | 23011.0935
2017-09-02 | 12:30 | 1.7397 | 0 | 0 | 1.5 | 78.4383 | 0 | 23016.0521
2017-09-02 | 12:30 |  |  |  | 1.5 | 78.4383 |  | 23016.0521
2017-09-02 | 12:32 |  |  |  |  | 78.4464 |  | 23018.4251
2017-09-02 | 12:34 |  |  |  |  | 78.4415 |  | 23016.9834
2017-09-02 | 12:36 |  |  |  |  | 78.4675 |  | 23024.6129
2017-09-02 | 12:38 |  |  |  |  | 78.4823 |  | 23028.9536
2017-09-02 | 12:40 |  |  |  |  | 78.4633 |  | 23023.3793
2017-09-02 | 12:42 |  |  |  |  | 78.5142 |  | 23038.3157
2017-09-02 | 12:44 |  |  |  |  | 78.519 |  | 23039.7171
2017-09-02 | 12:45 | 1.7491 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 12:45 |  |  |  | 1.5 | 78.5285 |  | 23042.5088
2017-09-02 | 12:46 |  |  |  |  | 78.5042 |  | 23035.3629
2017-09-02 | 12:48 |  |  |  |  | 78.5584 |  | 23051.2891
2017-09-02 | 12:50 |  |  |  |  | 78.5777 |  | 23056.9349
2017-09-02 | 12:52 |  |  |  |  | 78.6067 |  | 23065.4643
2017-09-02 | 12:54 |  |  |  |  | 78.641 |  | 23075.5069
2017-09-02 | 12:56 |  |  |  |  | 78.6673 |  | 23083.2305
2017-09-02 | 12:58 |  |  |  |  | 78.6781 |  | 23086.4048
2017-09-02 | 13:00 | 1.7725 | 0 | 0 | 1.5 | 78.6799 | 0 | 23086.9444
2017-09-02 | 13:00 |  |  |  | 1.5 | 78.6799 |  | 23086.9444
2017-09-02 | 13:02 |  |  |  |  | 78.7592 |  | 23110.2042
2017-09-02 | 13:04 |  |  |  |  | 78.7912 |  | 23119.5978
2017-09-02 | 13:06 |  |  |  |  | 78.8156 |  | 23126.7436
2017-09-02 | 13:08 |  |  |  |  | 78.8411 |  | 23134.2322
2017-09-02 | 13:10 |  |  |  |  | 78.8496 |  | 23136.7261
2017-09-02 | 13:12 |  |  |  |  | 78.858 |  | 23139.1885
2017-09-02 | 13:14 |  |  |  |  | 78.8614 |  | 23140.1959
2017-09-02 | 13:15 | 1.7522 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 13:15 |  |  |  | 1.5 | 78.9066 |  | 23153.4377
2017-09-02 | 13:16 |  |  |  |  | 78.9274 |  | 23159.5516
2017-09-02 | 13:18 |  |  |  |  | 78.9504 |  | 23166.3101
2017-09-02 | 13:20 |  |  |  |  | 78.951 |  | 23166.4894
2017-09-02 | 13:22 |  |  |  |  | 78.9961 |  | 23179.7222
2017-09-02 | 13:24 |  |  |  |  | 79.0235 |  | 23187.7389
2017-09-02 | 13:26 |  |  |  |  | 79.0784 |  | 23203.8596
2017-09-02 | 13:28 |  |  |  |  | 79.0766 |  | 23203.3223
2017-09-02 | 13:30 | 1.7343 | 0 | 0 | 1.5 | 79.113 | 0 | 23214.0052
2017-09-02 | 13:30 |  |  |  | 1.5 | 79.113 |  | 23214.0052
2017-09-02 | 13:32 |  |  |  |  | 79.1339 |  | 23220.1528
2017-09-02 | 13:34 |  |  |  |  | 79.1364 |  | 23220.8691
2017-09-02 | 13:36 |  |  |  |  | 79.1364 |  | 23220.8714
2017-09-02 | 13:38 |  |  |  |  | 79.1466 |  | 23223.8644
2017-09-02 | 13:40 |  |  |  |  | 79.1746 |  | 23232.0783
2017-09-02 | 13:42 |  |  |  |  | 79.2359 |  | 23250.0728
2017-09-02 | 13:44 |  |  |  |  | 79.249 |  | 23253.9077
2017-09-02 | 13:45 | 1.746 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 13:45 |  |  |  | 1.5 | 79.2299 |  | 23248.3087
2017-09-02 | 13:46 |  |  |  |  | 79.2554 |  | 23255.7926
2017-09-02 | 13:48 |  |  |  |  | 79.2661 |  | 23258.9402
2017-09-02 | 13:50 |  |  |  |  | 79.2928 |  | 23266.7733
2017-09-02 | 13:52 |  |  |  |  | 79.3147 |  | 23273.2006
2017-09-02 | 13:54 |  |  |  |  | 79.3402 |  | 23280.6889
2017-09-02 | 13:56 |  |  |  |  | 79.3221 |  | 23275.3564
2017-09-02 | 13:58 |  |  |  |  | 79.3515 |  | 23283.9844
2017-09-02 | 14:00 | 1.7499 | 0 | 0 | 1.5 | 79.4024 | 0 | 23298.9454
2017-09-02 | 14:00 |  |  |  | 1.5 | 79.4024 |  | 23298.9454
2017-09-02 | 14:02 |  |  |  |  | 79.3565 |  | 23285.4709
2017-09-02 | 14:04 |  |  |  |  | 79.404 |  | 23299.402
2017-09-02 | 14:06 |  |  |  |  | 79.3779 |  | 23291.7368
2017-09-02 | 14:08 |  |  |  |  | 79.4104 |  | 23301.267
2017-09-02 | 14:10 |  |  |  |  | 79.4413 |  | 23310.3404
2017-09-02 | 14:12 |  |  |  |  | 79.4613 |  | 23316.2169
2017-09-02 | 14:14 |  |  |  |  | 79.4677 |  | 23318.0952
2017-09-02 | 14:15 | 1.7499 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 14:15 |  |  |  | 1.5 | 79.4427 |  | 23310.7635
2017-09-02 | 14:16 |  |  |  |  | 79.4765 |  | 23320.6852
2017-09-02 | 14:18 |  |  |  |  | 79.4571 |  | 23314.9722
2017-09-02 | 14:20 |  |  |  |  | 79.5042 |  | 23328.7915
2017-09-02 | 14:22 |  |  |  |  | 79.5138 |  | 23331.6345
2017-09-02 | 14:24 |  |  |  |  | 79.531 |  | 23336.6671
2017-09-02 | 14:26 |  |  |  |  | 79.5575 |  | 23344.4533
2017-09-02 | 14:28 |  |  |  |  | 79.6163 |  | 23361.7069
2017-09-02 | 14:30 | 1.7366 | 0 | 0 | 1.5 | 79.6168 | 0 | 23361.8321
2017-09-02 | 14:30 |  |  |  | 1.5 | 79.6168 |  | 23361.8321
2017-09-02 | 14:32 |  |  |  |  | 79.6246 |  | 23364.1291
2017-09-02 | 14:34 |  |  |  |  | 79.6706 |  | 23377.6418
2017-09-02 | 14:36 |  |  |  |  | 79.6894 |  | 23383.16
2017-09-02 | 14:38 |  |  |  |  | 79.6874 |  | 23382.5646
2017-09-02 | 14:40 |  |  |  |  | 79.6877 |  | 23382.6541
2017-09-02 | 14:42 |  |  |  |  | 79.6873 |  | 23382.5444
2017-09-02 | 14:44 |  |  |  |  | 79.731 |  | 23395.352
2017-09-02 | 14:45 | 1.7327 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 14:45 |  |  |  | 1.5 | 79.7362 |  | 23396.8743
2017-09-02 | 14:46 |  |  |  |  | 79.7726 |  | 23407.5574
2017-09-02 | 14:48 |  |  |  |  | 79.7592 |  | 23403.6419
2017-09-02 | 14:50 |  |  |  |  | 79.791 |  | 23412.9615
2017-09-02 | 14:52 |  |  |  |  | 79.8002 |  | 23415.6502
2017-09-02 | 14:54 |  |  |  |  | 79.8389 |  | 23427.0003
2017-09-02 | 14:56 |  |  |  |  | 79.8318 |  | 23424.9316
2017-09-02 | 14:58 |  |  |  |  | 79.8731 |  | 23437.0587
2017-09-02 | 15:00 | 1.7468 | 0 | 0 | 1.5 | 79.8734 | 0 | 23437.128
2017-09-02 | 15:00 |  |  |  | 1.5 | 79.8734 |  | 23437.128
2017-09-02 | 15:02 |  |  |  |  | 79.8581 |  | 23432.6596
2017-09-02 | 15:04 |  |  |  |  | 79.8954 |  | 23443.5843
2017-09-02 | 15:06 |  |  |  |  | 79.9393 |  | 23456.4837
2017-09-02 | 15:08 |  |  |  |  | 79.9317 |  | 23454.2563
2017-09-02 | 15:10 |  |  |  |  | 79.9501 |  | 23459.6448
2017-09-02 | 15:12 |  |  |  |  | 79.9753 |  | 23467.0345
2017-09-02 | 15:14 |  |  |  |  | 80.0103 |  | 23477.3168
2017-09-02 | 15:15 | 1.7296 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 15:15 |  |  |  | 1.5 | 80.032 |  | 23483.6792
2017-09-02 | 15:16 |  |  |  |  | 80.0161 |  | 23479.007
2017-09-02 | 15:18 |  |  |  |  | 80.0696 |  | 23494.7025
2017-09-02 | 15:20 |  |  |  |  | 80.039 |  | 23485.7233
2017-09-02 | 15:22 |  |  |  |  | 80.0767 |  | 23496.7978
2017-09-02 | 15:24 |  |  |  |  | 80.1191 |  | 23509.2336
2017-09-02 | 15:26 |  |  |  |  | 80.1192 |  | 23509.2562
2017-09-02 | 15:28 |  |  |  |  | 80.1206 |  | 23509.6682
2017-09-02 | 15:30 | 1.7585 | 0 | 0 | 1.5 | 80.1472 | 0 | 23517.4922
2017-09-02 | 15:30 |  |  |  | 1.5 | 80.1472 |  | 23517.4922
2017-09-02 | 15:32 |  |  |  |  | 80.1584 |  | 23520.7742
2017-09-02 | 15:34 |  |  |  |  | 80.2057 |  | 23534.6495
2017-09-02 | 15:36 |  |  |  |  | 80.2337 |  | 23542.8679
2017-09-02 | 15:38 |  |  |  |  | 80.2689 |  | 23553.1972
2017-09-02 | 15:40 |  |  |  |  | 80.2408 |  | 23544.9474
2017-09-02 | 15:42 |  |  |  |  | 80.2614 |  | 23550.9985
2017-09-02 | 15:44 |  |  |  |  | 80.3171 |  | 23567.3366
2017-09-02 | 15:45 | 1.7343 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 15:45 |  |  |  | 1.5 | 80.3136 |  | 23566.3023
2017-09-02 | 15:46 |  |  |  |  | 80.2823 |  | 23557.1326
2017-09-02 | 15:48 |  |  |  |  | 80.3091 |  | 23564.9792
2017-09-02 | 15:50 |  |  |  |  | 80.3533 |  | 23577.9546
2017-09-02 | 15:52 |  |  |  |  | 80.3579 |  | 23579.3111
2017-09-02 | 15:54 |  |  |  |  | 80.3475 |  | 23576.2665
2017-09-02 | 15:56 |  |  |  |  | 80.3349 |  | 23572.5482
2017-09-02 | 15:58 |  |  |  |  | 80.3825 |  | 23586.5221
2017-09-02 | 16:00 | 1.7382 | 0 | 0 | 1.5 | 80.3908 | 0 | 23588.9667
2017-09-02 | 16:00 |  |  |  | 1.5 | 80.3908 |  | 23588.9667
2017-09-02 | 16:02 |  |  |  |  | 80.4058 |  | 23593.3523
2017-09-02 | 16:04 |  |  |  |  | 80.4144 |  | 23595.8799
2017-09-02 | 16:06 |  |  |  |  | 80.399 |  | 23591.3576
2017-09-02 | 16:08 |  |  |  |  | 80.4307 |  | 23600.6704
2017-09-02 | 16:10 |  |  |  |  | 80.4622 |  | 23609.9119
2017-09-02 | 16:12 |  |  |  |  | 80.4541 |  | 23607.5231
2017-09-02 | 16:14 |  |  |  |  | 80.4729 |  | 23613.0616
2017-09-02 | 16:15 |  | 0 |  |  |  | 0 | 0
2017-09-02 | 16:15 | 1.7296 |  | 0 | 1.5 | 80.5083 |  | 23623.429
2017-09-02 | 16:16 |  |  |  |  | 80.4669 |  | 23611.2954
2017-09-02 | 16:18 |  |  |  |  | 80.4741 |  | 23613.3929
2017-09-02 | 16:20 |  |  |  |  | 80.4674 |  | 23611.4363
2017-09-02 | 16:22 |  |  |  |  | 80.4779 |  | 23614.5011
2017-09-02 | 16:24 |  |  |  |  | 80.4862 |  | 23616.9568
2017-09-02 | 16:26 |  |  |  |  | 80.5113 |  | 23624.3266
2017-09-02 | 16:28 |  |  |  |  | 80.4922 |  | 23618.7189
2017-09-02 | 16:30 | 1.7413 | 0 | 0 | 1.5 | 80.5152 | 0 | 23625.4639
2017-09-02 | 16:30 |  |  |  | 1.5 | 80.5152 |  | 23625.4639
2017-09-02 | 16:32 |  |  |  |  | 80.4999 |  | 23620.9754
2017-09-02 | 16:34 |  |  |  |  | 80.477 |  | 23614.2415
2017-09-02 | 16:36 |  |  |  |  | 80.5134 |  | 23624.9446
2017-09-02 | 16:38 |  |  |  |  | 80.5199 |  | 23626.8295
2017-09-02 | 16:40 |  |  |  |  | 80.521 |  | 23627.152
2017-09-02 | 16:42 |  |  |  |  | 80.5187 |  | 23626.4959
2017-09-02 | 16:44 |  |  |  |  | 80.5181 |  | 23626.3125
2017-09-02 | 16:45 | 1.7639 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 16:45 |  |  |  | 1.5 | 80.4929 |  | 23618.9269
2017-09-02 | 16:46 |  |  |  |  | 80.5022 |  | 23621.6379
2017-09-02 | 16:48 |  |  |  |  | 80.4928 |  | 23618.8732
2017-09-02 | 16:50 |  |  |  |  | 80.5031 |  | 23621.8955
2017-09-02 | 16:52 |  |  |  |  | 80.4961 |  | 23619.8427
2017-09-02 | 16:54 |  |  |  |  | 80.4717 |  | 23612.6945
2017-09-02 | 16:56 |  |  |  |  | 80.4839 |  | 23616.2764
2017-09-02 | 16:58 |  |  |  |  | 80.4706 |  | 23612.3767
2017-09-02 | 17:00 | 1.7577 | 0 | 0 | 1.5 | 80.4337 | 0 | 23601.5548
2017-09-02 | 17:00 |  |  |  | 1.5 | 80.4337 |  | 23601.5548
2017-09-02 | 17:02 |  |  |  |  | 80.4543 |  | 23607.6015
2017-09-02 | 17:04 |  |  |  |  | 80.4115 |  | 23595.0178
2017-09-02 | 17:06 |  |  |  |  | 80.4135 |  | 23595.6266
2017-09-02 | 17:08 |  |  |  |  | 80.4033 |  | 23592.6158
2017-09-02 | 17:10 |  |  |  |  | 80.4161 |  | 23596.3699
2017-09-02 | 17:12 |  |  |  |  | 80.4059 |  | 23593.3881
2017-09-02 | 17:14 |  |  |  |  | 80.4441 |  | 23604.6085
2017-09-02 | 17:15 | 1.7343 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 17:15 |  |  |  | 1.5 | 80.4025 |  | 23592.3942
2017-09-02 | 17:16 |  |  |  |  | 80.4301 |  | 23600.4981
2017-09-02 | 17:18 |  |  |  |  | 80.3989 |  | 23591.3262
2017-09-02 | 17:20 |  |  |  |  | 80.3632 |  | 23580.8449
2017-09-02 | 17:22 |  |  |  |  | 80.3345 |  | 23572.4519
2017-09-02 | 17:24 |  |  |  |  | 80.3019 |  | 23562.8838
2017-09-02 | 17:26 |  |  |  |  | 80.2498 |  | 23547.5713
2017-09-02 | 17:28 |  |  |  |  | 80.27 |  | 23553.5238
2017-09-02 | 17:30 | 1.7647 | 0 | 0 | 1.5 | 80.2122 | 0 | 23536.5413
2017-09-02 | 17:30 |  |  |  | 1.5 | 80.2122 |  | 23536.5413
2017-09-02 | 17:32 |  |  |  |  | 80.1931 |  | 23530.9491
2017-09-02 | 17:34 |  |  |  |  | 80.1873 |  | 23529.2387
2017-09-02 | 17:36 |  |  |  |  | 80.1787 |  | 23526.729
2017-09-02 | 17:38 |  |  |  |  | 80.1494 |  | 23518.1257
2017-09-02 | 17:40 |  |  |  |  | 80.1038 |  | 23504.7295
2017-09-02 | 17:42 |  |  |  |  | 80.0986 |  | 23503.2275
2017-09-02 | 17:44 |  |  |  |  | 80.0653 |  | 23493.4533
2017-09-02 | 17:45 | 1.7577 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 17:45 |  |  |  | 1.5 | 80.0811 |  | 23498.0716
2017-09-02 | 17:46 |  |  |  |  | 80.0239 |  | 23481.2904
2017-09-02 | 17:48 |  |  |  |  | 80.0149 |  | 23478.6511
2017-09-02 | 17:50 |  |  |  |  | 80.0014 |  | 23474.7088
2017-09-02 | 17:52 |  |  |  |  | 79.9685 |  | 23465.0333
2017-09-02 | 17:54 |  |  |  |  | 79.9838 |  | 23469.524
2017-09-02 | 17:56 |  |  |  |  | 79.9355 |  | 23455.369
2017-09-02 | 17:58 |  |  |  |  | 79.8653 |  | 23434.7662
2017-09-02 | 18:00 | 1.7585 | 0 | 0 | 1.5 | 79.8541 | 0 | 23431.4821
2017-09-02 | 18:00 |  |  |  | 1.5 | 79.8541 |  | 23431.4821
2017-09-02 | 18:02 |  |  |  |  | 79.8135 |  | 23419.5545
2017-09-02 | 18:04 |  |  |  |  | 79.7872 |  | 23411.8556
2017-09-02 | 18:06 |  |  |  |  | 79.7712 |  | 23407.141
2017-09-02 | 18:08 |  |  |  |  | 79.7457 |  | 23399.675
2017-09-02 | 18:10 |  |  |  |  | 79.6738 |  | 23378.5687
2017-09-02 | 18:12 |  |  |  |  | 79.6494 |  | 23371.4138
2017-09-02 | 18:14 |  |  |  |  | 79.6213 |  | 23363.162
2017-09-02 | 18:15 | 1.7499 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 18:15 |  |  |  | 1.5 | 79.5912 |  | 23354.3236
2017-09-02 | 18:16 |  |  |  |  | 79.6167 |  | 23361.8054
2017-09-02 | 18:18 |  |  |  |  | 79.5376 |  | 23338.6058
2017-09-02 | 18:20 |  |  |  |  | 79.5352 |  | 23337.903
2017-09-02 | 18:22 |  |  |  |  | 79.5229 |  | 23334.2918
2017-09-02 | 18:24 |  |  |  |  | 79.4888 |  | 23324.2874
2017-09-02 | 18:26 |  |  |  |  | 79.4446 |  | 23311.3052
2017-09-02 | 18:28 |  |  |  |  | 79.4613 |  | 23316.2301
2017-09-02 | 18:30 | 1.7663 | 0 | 0 | 1.5 | 79.4095 | 0 | 23301.0161
2017-09-02 | 18:30 |  |  |  | 1.5 | 79.4095 |  | 23301.0161
2017-09-02 | 18:32 |  |  |  |  | 79.3733 |  | 23290.3846
2017-09-02 | 18:34 |  |  |  |  | 79.3198 |  | 23274.6959
2017-09-02 | 18:36 |  |  |  |  | 79.2868 |  | 23265.0025
2017-09-02 | 18:38 |  |  |  |  | 79.2402 |  | 23251.3264
2017-09-02 | 18:40 |  |  |  |  | 79.1728 |  | 23231.5654
2017-09-02 | 18:42 |  |  |  |  | 79.119 |  | 23215.7693
2017-09-02 | 18:44 |  |  |  |  | 79.0586 |  | 23198.0638
2017-09-02 | 18:45 | 1.7491 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 18:45 |  |  |  | 1.5 | 79.0525 |  | 23196.2572
2017-09-02 | 18:46 |  |  |  |  | 79.0443 |  | 23193.8481
2017-09-02 | 18:48 |  |  |  |  | 78.9381 |  | 23162.6901
2017-09-02 | 18:50 |  |  |  |  | 78.8962 |  | 23150.4042
2017-09-02 | 18:52 |  |  |  |  | 78.8581 |  | 23139.2311
2017-09-02 | 18:54 |  |  |  |  | 78.8345 |  | 23132.2956
2017-09-02 | 18:56 |  |  |  |  | 78.7532 |  | 23108.4313
2017-09-02 | 18:58 |  |  |  |  | 78.7095 |  | 23095.6194
2017-09-02 | 19:00 |  | 0 |  | 1.5 | 78.6772 | 0 | 23086.1384
2017-09-02 | 19:00 | 1.7616 |  | 0 | 1.5 | 78.6772 |  | 23086.1384
2017-09-02 | 19:02 |  |  |  |  | 78.6144 |  | 23067.7187
2017-09-02 | 19:04 |  |  |  |  | 78.5525 |  | 23049.5405
2017-09-02 | 19:06 |  |  |  |  | 78.5043 |  | 23035.4031
2017-09-02 | 19:08 |  |  |  |  | 78.4385 |  | 23016.0967
2017-09-02 | 19:10 |  |  |  |  | 78.4251 |  | 23012.168
2017-09-02 | 19:12 |  |  |  |  | 78.3857 |  | 23000.6007
2017-09-02 | 19:14 |  |  |  |  | 78.3637 |  | 22994.1623
2017-09-02 | 19:15 | 1.767 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 19:15 |  |  |  | 1.5 | 78.3299 |  | 22984.2224
2017-09-02 | 19:16 |  |  |  |  | 78.3119 |  | 22978.9548
2017-09-02 | 19:18 |  |  |  |  | 78.2735 |  | 22967.6942
2017-09-02 | 19:20 |  |  |  |  | 78.2615 |  | 22964.1528
2017-09-02 | 19:22 |  |  |  |  | 78.1827 |  | 22941.0406
2017-09-02 | 19:24 |  |  |  |  | 78.1396 |  | 22928.3921
2017-09-02 | 19:26 |  |  |  |  | 78.1092 |  | 22919.4821
2017-09-02 | 19:28 |  |  |  |  | 78.0521 |  | 22902.7188
2017-09-02 | 19:30 | 1.7608 | 0 | 0 | 1.5 | 78.0313 | 0 | 22896.605
2017-09-02 | 19:30 |  |  |  | 1.5 | 78.0313 |  | 22896.605
2017-09-02 | 19:32 |  |  |  |  | 77.9895 |  | 22884.3391
2017-09-02 | 19:34 |  |  |  |  | 77.9726 |  | 22879.403
2017-09-02 | 19:36 |  |  |  |  | 77.9332 |  | 22867.8132
2017-09-02 | 19:38 |  |  |  |  | 77.8963 |  | 22857.0115
2017-09-02 | 19:40 |  |  |  |  | 77.8506 |  | 22843.5997
2017-09-02 | 19:42 |  |  |  |  | 77.7947 |  | 22827.1924
2017-09-02 | 19:44 |  |  |  |  | 77.7943 |  | 22827.0826
2017-09-02 | 19:45 | 1.7592 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 19:45 |  |  |  | 1.5 | 77.7422 |  | 22811.7768
2017-09-02 | 19:46 |  |  |  |  | 77.7432 |  | 22812.0746
2017-09-02 | 19:48 |  |  |  |  | 77.6834 |  | 22794.5367
2017-09-02 | 19:50 |  |  |  |  | 77.6157 |  | 22774.6728
2017-09-02 | 19:52 |  |  |  |  | 77.5982 |  | 22769.5395
2017-09-02 | 19:54 |  |  |  |  | 77.5261 |  | 22748.3839
2017-09-02 | 19:56 |  |  |  |  | 77.5077 |  | 22742.9643
2017-09-02 | 19:58 |  |  |  |  | 77.464 |  | 22730.1567
2017-09-02 | 20:00 |  | 0 |  | 1.5 | 77.4476 | 0 | 22725.3278
2017-09-02 | 20:00 | 1.767 |  | 0 | 1.5 | 77.4476 |  | 22725.3278
2017-09-02 | 20:02 |  |  |  |  | 77.3884 |  | 22707.9759
2017-09-02 | 20:04 |  |  |  |  | 77.365 |  | 22701.0985
2017-09-02 | 20:06 |  |  |  |  | 77.3226 |  | 22688.6671
2017-09-02 | 20:08 |  |  |  |  | 77.3062 |  | 22683.8516
2017-09-02 | 20:10 |  |  |  |  | 77.2441 |  | 22665.6265
2017-09-02 | 20:12 |  |  |  |  | 77.1976 |  | 22651.9929
2017-09-02 | 20:14 |  |  |  |  | 77.1597 |  | 22640.8488
2017-09-02 | 20:15 | 1.7585 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 20:15 |  |  |  | 1.5 | 77.1515 |  | 22638.4424
2017-09-02 | 20:16 |  |  |  |  | 77.1278 |  | 22631.5113
2017-09-02 | 20:18 |  |  |  |  | 77.0546 |  | 22610.0288
2017-09-02 | 20:20 |  |  |  |  | 77.048 |  | 22608.0746
2017-09-02 | 20:22 |  |  |  |  | 77.0032 |  | 22594.9334
2017-09-02 | 20:24 |  |  |  |  | 76.9819 |  | 22588.6854
2017-09-02 | 20:26 |  |  |  |  | 76.9424 |  | 22577.1023
2017-09-02 | 20:28 |  |  |  |  | 76.9305 |  | 22573.6099
2017-09-02 | 20:30 | 1.7514 | 0 | 0 | 1.5 | 76.8901 | 0 | 22561.7607
2017-09-02 | 20:30 |  |  |  | 1.5 | 76.8901 |  | 22561.7607
2017-09-02 | 20:32 |  |  |  |  | 76.8455 |  | 22548.6756
2017-09-02 | 20:34 |  |  |  |  | 76.8165 |  | 22540.1597
2017-09-02 | 20:36 |  |  |  |  | 76.7673 |  | 22525.7112
2017-09-02 | 20:38 |  |  |  |  | 76.6969 |  | 22505.0683
2017-09-02 | 20:40 |  |  |  |  | 76.7091 |  | 22508.6525
2017-09-02 | 20:42 |  |  |  |  | 76.6534 |  | 22492.31
2017-09-02 | 20:44 |  |  |  |  | 76.628 |  | 22484.8372
2017-09-02 | 20:45 | 1.76 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 20:45 |  |  |  | 1.5 | 76.6292 |  | 22485.1999
2017-09-02 | 20:46 |  |  |  |  | 76.6223 |  | 22483.1741
2017-09-02 | 20:48 |  |  |  |  | 76.5938 |  | 22474.8058
2017-09-02 | 20:50 |  |  |  |  | 76.5569 |  | 22463.993
2017-09-02 | 20:52 |  |  |  |  | 76.5179 |  | 22452.5466
2017-09-02 | 20:54 |  |  |  |  | 76.4983 |  | 22446.7998
2017-09-02 | 20:56 |  |  |  |  | 76.4712 |  | 22438.8458
2017-09-02 | 20:58 |  |  |  |  | 76.4521 |  | 22433.2202
2017-09-02 | 21:00 | 1.767 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 21:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:15 | 0.03934 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 21:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 21:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:45 | 0.03778 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 21:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 22:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:15 | 0.03622 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 22:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 22:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:45 | 0.03544 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 22:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 23:00 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:15 | 0.03466 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 23:15 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 23:30 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:45 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-02 | 23:45 |  |  |  | 0 | 0 |  | 0
2017-09-02 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-02 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-03 | 0:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:15 |  | 0 |  | 0 |  |  | 0
2017-09-03 | 0:15 | 0.03388 |  | 0 |  | 0 | 0 | 0
2017-09-03 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 0:30 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-09-03 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:45 |  | 0 |  | 0 |  |  | 0
2017-09-03 | 0:45 | 0.0331 |  | 0 |  | 0 | 0 | 0
2017-09-03 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 1:00 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-09-03 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:15 |  | 0 |  | 0 |  |  | 0
2017-09-03 | 1:15 | 0.0331 |  | 0 |  | 0 | 0 | 0
2017-09-03 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 1:30 | 0.0331 | 0 | 0 |  | 0 | 0 | 0
2017-09-03 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:45 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 1:45 | 0.0331 |  | 0 |  |  | 0 | 0
2017-09-03 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:00 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 2:00 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:15 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 2:15 | 0.0331 |  | 0 |  |  | 0 | 0
2017-09-03 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 2:30 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:45 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:45 |  | 0 |  | 0 |  |  | 0
2017-09-03 | 2:45 | 0.0331 |  | 0 |  |  | 0 | 0
2017-09-03 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 3:00 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:15 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:15 |  | 0 |  | 0 |  | 0 | 0
2017-09-03 | 3:15 | 0.0331 |  | 0 |  |  |  | 0
2017-09-03 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 3:30 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:45 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 3:45 | 0.0331 |  | 0 |  |  | 0 | 0
2017-09-03 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 4:00 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:15 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:15 |  | 0 |  | 0 |  | 0 | 0
2017-09-03 | 4:15 | 0.0331 |  | 0 |  |  |  | 0
2017-09-03 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 4:30 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:45 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:45 |  | 0 |  | 0 |  |  | 0
2017-09-03 | 4:45 | 0.03388 |  | 0 |  |  | 0 | 0
2017-09-03 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 5:00 |  | 0 |  | 0 | 25 |  | 7335.7143
2017-09-03 | 5:00 | 0.03388 |  | 0 |  |  | 0 | 0
2017-09-03 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-03 | 5:04 |  |  |  |  | 99.9479 |  | 29327.5601
2017-09-03 | 5:06 |  |  |  |  | 98.8247 |  | 28998.0017
2017-09-03 | 5:08 |  |  |  |  | 97.0561 |  | 28479.0325
2017-09-03 | 5:10 |  |  |  |  | 95.7631 |  | 28099.6317
2017-09-03 | 5:12 |  |  |  |  | 94.68 |  | 27781.8104
2017-09-03 | 5:14 |  |  |  |  | 93.6761 |  | 27487.2448
2017-09-03 | 5:15 |  |  |  |  | 93.1532 |  | 27333.821
2017-09-03 | 5:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-09-03 | 5:15 | 2.0962 |  | 0 |  |  |  | 0
2017-09-03 | 5:16 |  |  |  |  | 92.7198 |  | 27206.6414
2017-09-03 | 5:18 |  |  |  |  | 91.8794 |  | 26960.0417
2017-09-03 | 5:20 |  |  |  |  | 91.1856 |  | 26756.4603
2017-09-03 | 5:22 |  |  |  |  | 90.5784 |  | 26578.2794
2017-09-03 | 5:24 |  |  |  |  | 90.0469 |  | 26422.3438
2017-09-03 | 5:26 |  |  |  |  | 89.5136 |  | 26265.8577
2017-09-03 | 5:28 |  |  |  |  | 89.0263 |  | 26122.8729
2017-09-03 | 5:30 |  |  |  | 1.5 | 88.5786 |  | 25991.5006
2017-09-03 | 5:30 | 1.8903 | 0 | 0 |  | 88.5786 | 0 | 25991.5006
2017-09-03 | 5:32 |  |  |  |  | 88.0652 |  | 25840.835
2017-09-03 | 5:34 |  |  |  |  | 87.5475 |  | 25688.9382
2017-09-03 | 5:36 |  |  |  |  | 87.0303 |  | 25537.1778
2017-09-03 | 5:38 |  |  |  |  | 86.4668 |  | 25371.8443
2017-09-03 | 5:40 |  |  |  |  | 85.945 |  | 25218.7253
2017-09-03 | 5:42 |  |  |  |  | 85.3844 |  | 25054.2178
2017-09-03 | 5:44 |  |  |  |  | 84.8852 |  | 24907.7409
2017-09-03 | 5:45 |  | 0 |  | 1.5 |  | 0 | 0
2017-09-03 | 5:45 | 1.9207 |  | 0 |  | 84.6305 |  | 24833.0114
2017-09-03 | 5:46 |  |  |  |  | 84.3522 |  | 24751.3397
2017-09-03 | 5:48 |  |  |  |  | 83.8733 |  | 24610.8267
2017-09-03 | 5:50 |  |  |  |  | 83.3997 |  | 24471.8648
2017-09-03 | 5:52 |  |  |  |  | 82.9101 |  | 24328.1907
2017-09-03 | 5:54 |  |  |  |  | 82.5043 |  | 24209.1286
2017-09-03 | 5:56 |  |  |  |  | 82.0763 |  | 24083.5408
2017-09-03 | 5:58 |  |  |  |  | 81.6691 |  | 23964.0356
2017-09-03 | 6:00 |  |  |  | 1.5 | 81.3355 |  | 23866.1537
2017-09-03 | 6:00 | 1.8567 | 0 | 0 |  | 81.3355 | 0 | 23866.1537
2017-09-03 | 6:02 |  |  |  |  | 80.9682 |  | 23758.3812
2017-09-03 | 6:04 |  |  |  |  | 80.6427 |  | 23662.8655
2017-09-03 | 6:06 |  |  |  |  | 80.3515 |  | 23577.4217
2017-09-03 | 6:08 |  |  |  |  | 80.1004 |  | 23503.7357
2017-09-03 | 6:10 |  |  |  |  | 79.9194 |  | 23450.6251
2017-09-03 | 6:12 |  |  |  |  | 79.6993 |  | 23386.0547
2017-09-03 | 6:14 |  |  |  |  | 79.4934 |  | 23325.626
2017-09-03 | 6:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-09-03 | 6:15 | 1.8037 |  | 0 |  | 79.4068 |  | 23300.2236
2017-09-03 | 6:16 |  |  |  |  | 79.2952 |  | 23267.4673
2017-09-03 | 6:18 |  |  |  |  | 79.1197 |  | 23215.9888
2017-09-03 | 6:20 |  |  |  |  | 79.0703 |  | 23201.491
2017-09-03 | 6:22 |  |  |  |  | 78.9902 |  | 23177.9915
2017-09-03 | 6:24 |  |  |  |  | 78.8768 |  | 23144.7135
2017-09-03 | 6:26 |  |  |  |  | 78.7748 |  | 23114.7914
2017-09-03 | 6:28 |  |  |  |  | 78.6483 |  | 23077.6495
2017-09-03 | 6:30 |  |  |  | 1.5 | 78.5673 |  | 23053.9038
2017-09-03 | 6:30 | 1.7826 | 0 | 0 |  | 78.5673 | 0 | 23053.9038
2017-09-03 | 6:32 |  |  |  |  | 78.4276 |  | 23012.9112
2017-09-03 | 6:34 |  |  |  |  | 78.3237 |  | 22982.4226
2017-09-03 | 6:36 |  |  |  |  | 78.2042 |  | 22947.3379
2017-09-03 | 6:38 |  |  |  |  | 78.1123 |  | 22920.3865
2017-09-03 | 6:40 |  |  |  |  | 78.0427 |  | 22899.9474
2017-09-03 | 6:42 |  |  |  |  | 78.0686 |  | 22907.5454
2017-09-03 | 6:44 |  |  |  |  | 78.0598 |  | 22904.9733
2017-09-03 | 6:45 |  | 0 |  | 1.5 |  |  | 0
2017-09-03 | 6:45 | 1.7904 |  | 0 |  | 78.0047 | 0 | 22888.8165
2017-09-03 | 6:46 |  |  |  |  | 77.9869 |  | 22883.5759
2017-09-03 | 6:48 |  |  |  |  | 77.8897 |  | 22855.0528
2017-09-03 | 6:50 |  |  |  |  | 77.8093 |  | 22831.475
2017-09-03 | 6:52 |  |  |  |  | 77.7245 |  | 22806.5852
2017-09-03 | 6:54 |  |  |  |  | 77.6694 |  | 22790.4085
2017-09-03 | 6:56 |  |  |  |  | 77.7065 |  | 22801.2929
2017-09-03 | 6:58 |  |  |  |  | 77.6793 |  | 22793.3166
2017-09-03 | 7:00 |  |  |  | 1.5 | 77.6022 |  | 22770.7036
2017-09-03 | 7:00 | 1.7928 | 0 | 0 |  | 77.6022 | 0 | 22770.7036
2017-09-03 | 7:02 |  |  |  |  | 77.56 |  | 22758.308
2017-09-03 | 7:04 |  |  |  |  | 77.444 |  | 22724.287
2017-09-03 | 7:06 |  |  |  |  | 77.413 |  | 22715.191
2017-09-03 | 7:08 |  |  |  |  | 77.2967 |  | 22681.0714
2017-09-03 | 7:10 |  |  |  |  | 77.3328 |  | 22691.6513
2017-09-03 | 7:12 |  |  |  |  | 77.3328 |  | 22691.658
2017-09-03 | 7:14 |  |  |  |  | 77.3112 |  | 22685.3182
2017-09-03 | 7:15 |  | 0 |  | 1.5 |  | 0 | 0
2017-09-03 | 7:15 | 1.7834 |  | 0 |  | 77.2914 |  | 22679.5019
2017-09-03 | 7:16 |  |  |  |  | 77.2047 |  | 22654.0572
2017-09-03 | 7:18 |  |  |  |  | 77.134 |  | 22633.3112
2017-09-03 | 7:20 |  |  |  |  | 77.0813 |  | 22617.8643
2017-09-03 | 7:22 |  |  |  |  | 76.9911 |  | 22591.3897
2017-09-03 | 7:24 |  |  |  |  | 76.973 |  | 22586.0839
2017-09-03 | 7:26 |  |  |  |  | 76.9832 |  | 22589.0681
2017-09-03 | 7:28 |  |  |  |  | 77.0385 |  | 22605.3008
2017-09-03 | 7:30 |  |  |  | 1.5 | 77.0009 |  | 22594.2597
2017-09-03 | 7:30 | 1.7702 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 7:32 |  |  |  |  | 76.9458 |  | 22578.083
2017-09-03 | 7:34 |  |  |  |  | 76.9364 |  | 22575.3271
2017-09-03 | 7:36 |  |  |  |  | 76.8648 |  | 22554.3194
2017-09-03 | 7:38 |  |  |  |  | 76.7682 |  | 22525.9821
2017-09-03 | 7:40 |  |  |  |  | 76.8144 |  | 22539.5485
2017-09-03 | 7:42 |  |  |  |  | 76.8461 |  | 22548.8481
2017-09-03 | 7:44 |  |  |  |  | 76.888 |  | 22561.1383
2017-09-03 | 7:45 |  | 0 |  | 1.5 | 76.8385 |  | 22546.6048
2017-09-03 | 7:45 | 1.7873 |  | 0 |  |  | 0 | 0
2017-09-03 | 7:46 |  |  |  |  | 76.7839 |  | 22530.5892
2017-09-03 | 7:48 |  |  |  |  | 76.7377 |  | 22517.0296
2017-09-03 | 7:50 |  |  |  |  | 76.6922 |  | 22503.6871
2017-09-03 | 7:52 |  |  |  |  | 76.636 |  | 22487.1811
2017-09-03 | 7:54 |  |  |  |  | 76.5918 |  | 22474.2172
2017-09-03 | 7:56 |  |  |  |  | 76.6534 |  | 22492.2968
2017-09-03 | 7:58 |  |  |  |  | 76.7407 |  | 22517.9005
2017-09-03 | 8:00 |  | 0 |  | 1.5 | 76.7031 |  | 22506.8951
2017-09-03 | 8:00 | 1.7553 |  | 0 |  |  | 0 | 0
2017-09-03 | 8:02 |  |  |  |  | 76.6791 |  | 22499.8479
2017-09-03 | 8:04 |  |  |  |  | 76.6688 |  | 22496.8165
2017-09-03 | 8:06 |  |  |  |  | 76.6615 |  | 22494.663
2017-09-03 | 8:08 |  |  |  |  | 76.6543 |  | 22492.5518
2017-09-03 | 8:10 |  |  |  |  | 76.7789 |  | 22529.1185
2017-09-03 | 8:12 |  |  |  |  | 76.8799 |  | 22558.7677
2017-09-03 | 8:14 |  |  |  |  | 77.0169 |  | 22598.9586
2017-09-03 | 8:15 |  | 0 |  | 1.5 | 77.0189 |  | 22599.5496
2017-09-03 | 8:15 | 1.7483 |  | 0 |  |  | 0 | 0
2017-09-03 | 8:16 |  |  |  |  | 77.0257 |  | 22601.5308
2017-09-03 | 8:18 |  |  |  |  | 77.0671 |  | 22613.6826
2017-09-03 | 8:20 |  |  |  |  | 77.0594 |  | 22611.4437
2017-09-03 | 8:22 |  |  |  |  | 77.1023 |  | 22624.023
2017-09-03 | 8:24 |  |  |  |  | 77.0921 |  | 22621.0389
2017-09-03 | 8:26 |  |  |  |  | 77.106 |  | 22625.0952
2017-09-03 | 8:28 |  |  |  |  | 77.1253 |  | 22630.7748
2017-09-03 | 8:30 |  |  |  | 1.5 | 77.1102 |  | 22626.3379
2017-09-03 | 8:30 | 1.7429 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 8:32 |  |  |  |  | 77.076 |  | 22616.2862
2017-09-03 | 8:34 |  |  |  |  | 77.1098 |  | 22626.219
2017-09-03 | 8:36 |  |  |  |  | 77.231 |  | 22661.7785
2017-09-03 | 8:38 |  |  |  |  | 77.3356 |  | 22692.4685
2017-09-03 | 8:40 |  |  |  |  | 77.3619 |  | 22700.1965
2017-09-03 | 8:42 |  |  |  |  | 77.3469 |  | 22695.7951
2017-09-03 | 8:44 |  |  |  |  | 77.3278 |  | 22690.1739
2017-09-03 | 8:45 |  | 0 |  | 1.5 | 77.2875 |  | 22678.3648
2017-09-03 | 8:45 | 1.7655 |  | 0 |  |  | 0 | 0
2017-09-03 | 8:46 |  |  |  |  | 77.2666 |  | 22672.2286
2017-09-03 | 8:48 |  |  |  |  | 77.1966 |  | 22651.6886
2017-09-03 | 8:50 |  |  |  |  | 77.1617 |  | 22641.458
2017-09-03 | 8:52 |  |  |  |  | 77.097 |  | 22622.4717
2017-09-03 | 8:54 |  |  |  |  | 77.0642 |  | 22612.8519
2017-09-03 | 8:56 |  |  |  |  | 77.0421 |  | 22606.3463
2017-09-03 | 8:58 |  |  |  |  | 76.9873 |  | 22590.2837
2017-09-03 | 9:00 |  |  |  | 1.5 | 76.9713 |  | 22585.5692
2017-09-03 | 9:00 | 1.7569 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 9:02 |  |  |  |  | 76.9713 |  | 22585.5804
2017-09-03 | 9:04 |  |  |  |  | 76.9159 |  | 22569.3095
2017-09-03 | 9:06 |  |  |  |  | 76.8979 |  | 22564.0442
2017-09-03 | 9:08 |  |  |  |  | 76.8654 |  | 22554.4984
2017-09-03 | 9:10 |  |  |  |  | 76.8431 |  | 22547.9593
2017-09-03 | 9:12 |  |  |  |  | 76.8486 |  | 22549.5688
2017-09-03 | 9:14 |  |  |  |  | 76.7841 |  | 22530.6476
2017-09-03 | 9:15 |  | 0 |  | 1.5 | 76.8185 |  | 22540.7327
2017-09-03 | 9:15 | 1.7577 |  | 0 |  |  | 0 | 0
2017-09-03 | 9:16 |  |  |  |  | 76.8002 |  | 22535.3847
2017-09-03 | 9:18 |  |  |  |  | 76.8439 |  | 22548.2011
2017-09-03 | 9:20 |  |  |  |  | 76.8465 |  | 22548.9511
2017-09-03 | 9:22 |  |  |  |  | 76.8634 |  | 22553.9276
2017-09-03 | 9:24 |  |  |  |  | 76.8873 |  | 22560.928
2017-09-03 | 9:26 |  |  |  |  | 76.9042 |  | 22565.891
2017-09-03 | 9:28 |  |  |  |  | 76.8871 |  | 22560.8719
2017-09-03 | 9:30 |  |  |  | 1.5 | 76.8606 |  | 22553.0949
2017-09-03 | 9:30 | 1.7678 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 9:32 |  |  |  |  | 76.8786 |  | 22558.3804
2017-09-03 | 9:34 |  |  |  |  | 76.8795 |  | 22558.6401
2017-09-03 | 9:36 |  |  |  |  | 76.8852 |  | 22560.3123
2017-09-03 | 9:38 |  |  |  |  | 76.9305 |  | 22573.6167
2017-09-03 | 9:40 |  |  |  |  | 76.9549 |  | 22580.7626
2017-09-03 | 9:42 |  |  |  |  | 76.9528 |  | 22580.1648
2017-09-03 | 9:44 |  |  |  |  | 76.9903 |  | 22591.1523
2017-09-03 | 9:45 |  | 0 |  | 1.5 | 76.9971 |  | 22593.1628
2017-09-03 | 9:45 | 1.7413 |  | 0 |  |  | 0 | 0
2017-09-03 | 9:46 |  |  |  |  | 76.9847 |  | 22589.5138
2017-09-03 | 9:48 |  |  |  |  | 77.0158 |  | 22598.6297
2017-09-03 | 9:50 |  |  |  |  | 77.0439 |  | 22606.8748
2017-09-03 | 9:52 |  |  |  |  | 77.0515 |  | 22609.1245
2017-09-03 | 9:54 |  |  |  |  | 77.1215 |  | 22629.6422
2017-09-03 | 9:56 |  |  |  |  | 77.1213 |  | 22629.604
2017-09-03 | 9:58 |  |  |  |  | 77.1301 |  | 22632.1786
2017-09-03 | 10:00 |  |  |  | 1.5 | 77.1658 |  | 22642.6601
2017-09-03 | 10:00 | 1.7405 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 10:02 |  |  |  |  | 77.1578 |  | 22640.3162
2017-09-03 | 10:04 |  |  |  |  | 77.1975 |  | 22651.9639
2017-09-03 | 10:06 |  |  |  |  | 77.2551 |  | 22668.8504
2017-09-03 | 10:08 |  |  |  |  | 77.2284 |  | 22661.0305
2017-09-03 | 10:10 |  |  |  |  | 77.2516 |  | 22667.8296
2017-09-03 | 10:12 |  |  |  |  | 77.3152 |  | 22686.4866
2017-09-03 | 10:14 |  |  |  |  | 77.3343 |  | 22692.0855
2017-09-03 | 10:15 |  | 0 |  | 1.5 | 77.3341 |  | 22692.0477
2017-09-03 | 10:15 | 1.7358 |  | 0 |  |  | 0 | 0
2017-09-03 | 10:16 |  |  |  |  | 77.3262 |  | 22689.7217
2017-09-03 | 10:18 |  |  |  |  | 77.3389 |  | 22693.4356
2017-09-03 | 10:20 |  |  |  |  | 77.3943 |  | 22709.7062
2017-09-03 | 10:22 |  |  |  |  | 77.3957 |  | 22710.1158
2017-09-03 | 10:24 |  |  |  |  | 77.4096 |  | 22714.186
2017-09-03 | 10:26 |  |  |  |  | 77.4337 |  | 22721.2512
2017-09-03 | 10:28 |  |  |  |  | 77.4394 |  | 22722.919
2017-09-03 | 10:30 |  |  |  | 1.5 | 77.4309 |  | 22720.4296
2017-09-03 | 10:30 | 1.7444 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 10:32 |  |  |  |  | 77.481 |  | 22735.1444
2017-09-03 | 10:34 |  |  |  |  | 77.5378 |  | 22751.8047
2017-09-03 | 10:36 |  |  |  |  | 77.5347 |  | 22750.8936
2017-09-03 | 10:38 |  |  |  |  | 77.5698 |  | 22761.1871
2017-09-03 | 10:40 |  |  |  |  | 77.6268 |  | 22777.9213
2017-09-03 | 10:42 |  |  |  |  | 77.6564 |  | 22786.6006
2017-09-03 | 10:44 |  |  |  |  | 77.7236 |  | 22806.339
2017-09-03 | 10:45 |  | 0 |  | 1.5 | 77.7568 |  | 22816.0682
2017-09-03 | 10:45 | 1.7327 |  | 0 |  |  | 0 | 0
2017-09-03 | 10:46 |  |  |  |  | 77.7572 |  | 22816.1891
2017-09-03 | 10:48 |  |  |  |  | 77.7889 |  | 22825.4955
2017-09-03 | 10:50 |  |  |  |  | 77.8102 |  | 22831.7482
2017-09-03 | 10:52 |  |  |  |  | 77.8679 |  | 22848.657
2017-09-03 | 10:54 |  |  |  |  | 77.8937 |  | 22856.2348
2017-09-03 | 10:56 |  |  |  |  | 78.0003 |  | 22887.5069
2017-09-03 | 10:58 |  |  |  |  | 77.996 |  | 22886.2622
2017-09-03 | 11:00 |  |  |  | 1.5 | 78.0449 |  | 22900.6076
2017-09-03 | 11:00 | 1.721 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 11:02 |  |  |  |  | 78.0738 |  | 22909.0745
2017-09-03 | 11:04 |  |  |  |  | 78.1338 |  | 22926.6749
2017-09-03 | 11:06 |  |  |  |  | 78.163 |  | 22935.2536
2017-09-03 | 11:08 |  |  |  |  | 78.215 |  | 22950.528
2017-09-03 | 11:10 |  |  |  |  | 78.2594 |  | 22963.5483
2017-09-03 | 11:12 |  |  |  |  | 78.2982 |  | 22974.9184
2017-09-03 | 11:14 |  |  |  |  | 78.358 |  | 22992.4698
2017-09-03 | 11:15 |  | 0 |  | 1.5 | 78.383 |  | 22999.8149
2017-09-03 | 11:15 | 1.721 |  | 0 |  |  | 0 | 0
2017-09-03 | 11:16 |  |  |  |  | 78.4028 |  | 23005.6354
2017-09-03 | 11:18 |  |  |  |  | 78.4739 |  | 23026.4911
2017-09-03 | 11:20 |  |  |  |  | 78.5052 |  | 23035.6719
2017-09-03 | 11:22 |  |  |  |  | 78.5352 |  | 23044.4745
2017-09-03 | 11:24 |  |  |  |  | 78.5505 |  | 23048.9742
2017-09-03 | 11:26 |  |  |  |  | 78.6133 |  | 23067.3986
2017-09-03 | 11:28 |  |  |  |  | 78.6317 |  | 23072.7804
2017-09-03 | 11:30 |  |  |  | 1.5 | 78.6482 |  | 23077.6384
2017-09-03 | 11:30 | 1.7421 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 11:32 |  |  |  |  | 78.6675 |  | 23083.293
2017-09-03 | 11:34 |  |  |  |  | 78.6819 |  | 23087.5266
2017-09-03 | 11:36 |  |  |  |  | 78.6669 |  | 23083.1073
2017-09-03 | 11:38 |  |  |  |  | 78.7154 |  | 23097.3497
2017-09-03 | 11:40 |  |  |  |  | 78.7344 |  | 23102.9128
2017-09-03 | 11:42 |  |  |  |  | 78.7703 |  | 23113.4616
2017-09-03 | 11:44 |  |  |  |  | 78.7531 |  | 23108.409
2017-09-03 | 11:45 |  | 0 |  | 1.5 | 78.803 |  | 23123.0655
2017-09-03 | 11:45 | 1.7335 |  | 0 |  |  | 0 | 0
2017-09-03 | 11:46 |  |  |  |  | 78.8186 |  | 23127.6368
2017-09-03 | 11:48 |  |  |  |  | 78.8158 |  | 23126.8041
2017-09-03 | 11:50 |  |  |  |  | 78.8558 |  | 23138.5348
2017-09-03 | 11:52 |  |  |  |  | 78.8726 |  | 23143.4644
2017-09-03 | 11:54 |  |  |  |  | 78.8889 |  | 23148.2687
2017-09-03 | 11:56 |  |  |  |  | 78.9251 |  | 23158.8911
2017-09-03 | 11:58 |  |  |  |  | 78.9448 |  | 23164.647
2017-09-03 | 12:00 |  |  |  | 1.5 | 78.9454 |  | 23164.8348
2017-09-03 | 12:00 | 1.7444 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 12:02 |  |  |  |  | 78.9932 |  | 23178.8736
2017-09-03 | 12:04 |  |  |  |  | 79.0205 |  | 23186.8704
2017-09-03 | 12:06 |  |  |  |  | 79.0277 |  | 23188.9925
2017-09-03 | 12:08 |  |  |  |  | 79.0654 |  | 23200.0606
2017-09-03 | 12:10 |  |  |  |  | 79.0581 |  | 23197.8936
2017-09-03 | 12:12 |  |  |  |  | 79.0792 |  | 23204.0902
2017-09-03 | 12:14 |  |  |  |  | 79.145 |  | 23223.3899
2017-09-03 | 12:15 |  | 0 |  | 1.5 | 79.1464 |  | 23223.8198
2017-09-03 | 12:15 | 1.7538 |  | 0 |  |  | 0 | 0
2017-09-03 | 12:16 |  |  |  |  | 79.1443 |  | 23223.2086
2017-09-03 | 12:18 |  |  |  |  | 79.1825 |  | 23234.3976
2017-09-03 | 12:20 |  |  |  |  | 79.2031 |  | 23240.4419
2017-09-03 | 12:22 |  |  |  |  | 79.2152 |  | 23244.0127
2017-09-03 | 12:24 |  |  |  |  | 79.2583 |  | 23256.6521
2017-09-03 | 12:26 |  |  |  |  | 79.2899 |  | 23265.9338
2017-09-03 | 12:28 |  |  |  |  | 79.2933 |  | 23266.93
2017-09-03 | 12:30 |  |  |  | 1.5 | 79.297 |  | 23268.0089
2017-09-03 | 12:30 | 1.7397 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 12:32 |  |  |  |  | 79.3239 |  | 23275.896
2017-09-03 | 12:34 |  |  |  |  | 79.3409 |  | 23280.8814
2017-09-03 | 12:36 |  |  |  |  | 79.4226 |  | 23304.8689
2017-09-03 | 12:38 |  |  |  |  | 79.4766 |  | 23320.7075
2017-09-03 | 12:40 |  |  |  |  | 79.5282 |  | 23335.859
2017-09-03 | 12:42 |  |  |  |  | 79.5938 |  | 23355.1094
2017-09-03 | 12:44 |  |  |  |  | 79.6364 |  | 23367.6036
2017-09-03 | 12:45 |  | 0 |  | 1.5 | 79.7234 |  | 23393.109
2017-09-03 | 12:45 | 1.7358 |  | 0 |  |  | 0 | 0
2017-09-03 | 12:46 |  |  |  |  | 79.732 |  | 23395.643
2017-09-03 | 12:48 |  |  |  |  | 79.7794 |  | 23409.5609
2017-09-03 | 12:50 |  |  |  |  | 79.8385 |  | 23426.8861
2017-09-03 | 12:52 |  |  |  |  | 79.8815 |  | 23439.5009
2017-09-03 | 12:54 |  |  |  |  | 79.9298 |  | 23453.69
2017-09-03 | 12:56 |  |  |  |  | 79.9859 |  | 23470.1622
2017-09-03 | 12:58 |  |  |  |  | 80.0467 |  | 23487.9774
2017-09-03 | 13:00 |  |  |  | 1.5 | 80.0395 |  | 23485.8709
2017-09-03 | 13:00 | 1.7475 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 13:02 |  |  |  |  | 80.0902 |  | 23500.7404
2017-09-03 | 13:04 |  |  |  |  | 80.1102 |  | 23506.6145
2017-09-03 | 13:06 |  |  |  |  | 80.154 |  | 23519.4667
2017-09-03 | 13:08 |  |  |  |  | 80.1564 |  | 23520.1741
2017-09-03 | 13:10 |  |  |  |  | 80.1871 |  | 23529.1918
2017-09-03 | 13:12 |  |  |  |  | 80.2092 |  | 23535.666
2017-09-03 | 13:14 |  |  |  |  | 80.2214 |  | 23539.2499
2017-09-03 | 13:15 |  | 0 |  | 1.5 | 80.2543 | 0 | 23548.9055
2017-09-03 | 13:15 | 1.7569 |  | 0 |  |  |  | 0
2017-09-03 | 13:16 |  |  |  |  | 80.2352 |  | 23543.311
2017-09-03 | 13:18 |  |  |  |  | 80.2494 |  | 23547.4727
2017-09-03 | 13:20 |  |  |  |  | 80.2527 |  | 23548.4263
2017-09-03 | 13:22 |  |  |  |  | 80.2573 |  | 23549.7919
2017-09-03 | 13:24 |  |  |  |  | 80.2886 |  | 23558.9572
2017-09-03 | 13:26 |  |  |  |  | 80.2963 |  | 23561.2406
2017-09-03 | 13:28 |  |  |  |  | 80.3355 |  | 23572.7339
2017-09-03 | 13:30 |  |  |  | 1.5 | 80.3334 |  | 23572.1274
2017-09-03 | 13:30 | 1.7436 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 13:32 |  |  |  |  | 80.3219 |  | 23568.7336
2017-09-03 | 13:34 |  |  |  |  | 80.3657 |  | 23581.5993
2017-09-03 | 13:36 |  |  |  |  | 80.3699 |  | 23582.8126
2017-09-03 | 13:38 |  |  |  |  | 80.3603 |  | 23580.0007
2017-09-03 | 13:40 |  |  |  |  | 80.3746 |  | 23584.1914
2017-09-03 | 13:42 |  |  |  |  | 80.4092 |  | 23594.3664
2017-09-03 | 13:44 |  |  |  |  | 80.4273 |  | 23599.6586
2017-09-03 | 13:45 |  | 0 |  | 1.5 | 80.4373 |  | 23602.5891
2017-09-03 | 13:45 | 1.7483 |  | 0 |  |  | 0 | 0
2017-09-03 | 13:46 |  |  |  |  | 80.4327 |  | 23601.257
2017-09-03 | 13:48 |  |  |  |  | 80.4749 |  | 23613.6279
2017-09-03 | 13:50 |  |  |  |  | 80.4618 |  | 23609.7931
2017-09-03 | 13:52 |  |  |  |  | 80.5252 |  | 23628.4079
2017-09-03 | 13:54 |  |  |  |  | 80.5384 |  | 23632.2674
2017-09-03 | 13:56 |  |  |  |  | 80.5236 |  | 23627.9264
2017-09-03 | 13:58 |  |  |  |  | 80.5445 |  | 23634.0494
2017-09-03 | 14:00 |  |  |  | 1.5 | 80.5513 |  | 23636.0461
2017-09-03 | 14:00 | 1.7561 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 14:02 |  |  |  |  | 80.5597 |  | 23638.5086
2017-09-03 | 14:04 |  |  |  |  | 80.5943 |  | 23648.6768
2017-09-03 | 14:06 |  |  |  |  | 80.6139 |  | 23654.4212
2017-09-03 | 14:08 |  |  |  |  | 80.6177 |  | 23655.5228
2017-09-03 | 14:10 |  |  |  |  | 80.6192 |  | 23655.9861
2017-09-03 | 14:12 |  |  |  |  | 80.6327 |  | 23659.935
2017-09-03 | 14:14 |  |  |  |  | 80.6347 |  | 23660.5172
2017-09-03 | 14:15 |  | 0 |  | 1.5 | 80.6621 |  | 23668.5789
2017-09-03 | 14:15 | 1.7436 |  | 0 |  |  | 0 | 0
2017-09-03 | 14:16 |  |  |  |  | 80.6453 |  | 23663.6493
2017-09-03 | 14:18 |  |  |  |  | 80.6863 |  | 23675.6643
2017-09-03 | 14:20 |  |  |  |  | 80.6915 |  | 23677.1798
2017-09-03 | 14:22 |  |  |  |  | 80.6767 |  | 23672.8547
2017-09-03 | 14:24 |  |  |  |  | 80.6983 |  | 23679.1857
2017-09-03 | 14:26 |  |  |  |  | 80.7304 |  | 23688.5948
2017-09-03 | 14:28 |  |  |  |  | 80.7628 |  | 23698.1248
2017-09-03 | 14:30 |  |  |  | 1.5 | 80.7613 |  | 23697.6638
2017-09-03 | 14:30 | 1.7421 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 14:32 |  |  |  |  | 80.7611 |  | 23697.6256
2017-09-03 | 14:34 |  |  |  |  | 80.8001 |  | 23709.0497
2017-09-03 | 14:36 |  |  |  |  | 80.8367 |  | 23719.8065
2017-09-03 | 14:38 |  |  |  |  | 80.8336 |  | 23718.8975
2017-09-03 | 14:40 |  |  |  |  | 80.8637 |  | 23727.727
2017-09-03 | 14:42 |  |  |  |  | 80.8788 |  | 23732.1484
2017-09-03 | 14:44 |  |  |  |  | 80.8811 |  | 23732.8177
2017-09-03 | 14:45 |  | 0 |  | 1.5 | 80.9274 |  | 23746.4178
2017-09-03 | 14:45 | 1.739 |  | 0 |  |  | 0 | 0
2017-09-03 | 14:46 |  |  |  |  | 80.8883 |  | 23734.9266
2017-09-03 | 14:48 |  |  |  |  | 80.9564 |  | 23754.9314
2017-09-03 | 14:50 |  |  |  |  | 80.9722 |  | 23759.5678
2017-09-03 | 14:52 |  |  |  |  | 81.005 |  | 23769.1738
2017-09-03 | 14:54 |  |  |  |  | 81.0162 |  | 23772.4558
2017-09-03 | 14:56 |  |  |  |  | 81.0708 |  | 23788.4849
2017-09-03 | 14:58 |  |  |  |  | 81.0915 |  | 23794.5516
2017-09-03 | 15:00 |  |  |  | 1.5 | 81.1435 |  | 23809.8327
2017-09-03 | 15:00 | 1.7288 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 15:02 |  |  |  |  | 81.1199 |  | 23802.884
2017-09-03 | 15:04 |  |  |  |  | 81.1185 |  | 23802.49
2017-09-03 | 15:06 |  |  |  |  | 81.1557 |  | 23813.4146
2017-09-03 | 15:08 |  |  |  |  | 81.1935 |  | 23824.503
2017-09-03 | 15:10 |  |  |  |  | 81.1784 |  | 23820.0526
2017-09-03 | 15:12 |  |  |  |  | 81.1897 |  | 23823.3633
2017-09-03 | 15:14 |  |  |  |  | 81.258 |  | 23843.4265
2017-09-03 | 15:15 |  | 0 |  | 1.5 | 81.283 |  | 23850.7516
2017-09-03 | 15:15 | 1.7507 |  | 0 |  |  | 0 | 0
2017-09-03 | 15:16 |  |  |  |  | 81.2922 |  | 23853.4626
2017-09-03 | 15:18 |  |  |  |  | 81.26 |  | 23843.9952
2017-09-03 | 15:20 |  |  |  |  | 81.2946 |  | 23854.1586
2017-09-03 | 15:22 |  |  |  |  | 81.357 |  | 23872.4621
2017-09-03 | 15:24 |  |  |  |  | 81.3424 |  | 23868.1728
2017-09-03 | 15:26 |  |  |  |  | 81.3677 |  | 23875.5986
2017-09-03 | 15:28 |  |  |  |  | 81.3875 |  | 23881.4126
2017-09-03 | 15:30 |  |  |  | 1.5 | 81.4228 |  | 23891.7844
2017-09-03 | 15:30 | 1.7421 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 15:32 |  |  |  |  | 81.4215 |  | 23891.388
2017-09-03 | 15:34 |  |  |  |  | 81.4458 |  | 23898.5318
2017-09-03 | 15:36 |  |  |  |  | 81.4683 |  | 23905.1404
2017-09-03 | 15:38 |  |  |  |  | 81.5007 |  | 23914.6457
2017-09-03 | 15:40 |  |  |  |  | 81.5015 |  | 23914.8787
2017-09-03 | 15:42 |  |  |  |  | 81.4988 |  | 23914.0814
2017-09-03 | 15:44 |  |  |  |  | 81.5649 |  | 23933.4662
2017-09-03 | 15:45 |  | 0 |  | 1.5 | 81.5926 |  | 23941.5904
2017-09-03 | 15:45 | 1.7257 |  | 0 |  |  | 0 | 0
2017-09-03 | 15:46 |  |  |  |  | 81.6101 |  | 23946.7239
2017-09-03 | 15:48 |  |  |  |  | 81.6318 |  | 23953.1107
2017-09-03 | 15:50 |  |  |  |  | 81.6528 |  | 23959.2782
2017-09-03 | 15:52 |  |  |  |  | 81.6822 |  | 23967.8839
2017-09-03 | 15:54 |  |  |  |  | 81.7455 |  | 23986.4603
2017-09-03 | 15:56 |  |  |  |  | 81.7343 |  | 23983.1674
2017-09-03 | 15:58 |  |  |  |  | 81.7528 |  | 23988.6185
2017-09-03 | 16:00 |  |  |  | 1.5 | 81.7898 |  | 23999.4516
2017-09-03 | 16:00 | 1.7444 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 16:02 |  |  |  |  | 81.8136 |  | 24006.4542
2017-09-03 | 16:04 |  |  |  |  | 81.8696 |  | 24022.8792
2017-09-03 | 16:06 |  |  |  |  | 81.8917 |  | 24029.3513
2017-09-03 | 16:08 |  |  |  |  | 81.8916 |  | 24029.329
2017-09-03 | 16:10 |  |  |  |  | 81.8894 |  | 24028.6888
2017-09-03 | 16:12 |  |  |  |  | 81.8959 |  | 24030.5937
2017-09-03 | 16:14 |  |  |  |  | 81.9062 |  | 24033.616
2017-09-03 | 16:15 |  | 0 |  | 1.5 | 81.8973 |  | 24031.0057
2017-09-03 | 16:15 | 1.7616 |  | 0 |  |  | 0 | 0
2017-09-03 | 16:16 |  |  |  |  | 81.9138 |  | 24035.8613
2017-09-03 | 16:18 |  |  |  |  | 81.8731 |  | 24023.8936
2017-09-03 | 16:20 |  |  |  |  | 81.9076 |  | 24034.0415
2017-09-03 | 16:22 |  |  |  |  | 81.9341 |  | 24041.7983
2017-09-03 | 16:24 |  |  |  |  | 81.9168 |  | 24036.7278
2017-09-03 | 16:26 |  |  |  |  | 81.8839 |  | 24027.077
2017-09-03 | 16:28 |  |  |  |  | 81.8955 |  | 24030.4796
2017-09-03 | 16:30 |  |  |  | 1.5 | 81.8815 |  | 24026.3739
2017-09-03 | 16:30 | 1.7639 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 16:32 |  |  |  |  | 81.8788 |  | 24025.5746
2017-09-03 | 16:34 |  |  |  |  | 81.9086 |  | 24034.337
2017-09-03 | 16:36 |  |  |  |  | 81.8734 |  | 24023.9942
2017-09-03 | 16:38 |  |  |  |  | 81.9095 |  | 24034.6011
2017-09-03 | 16:40 |  |  |  |  | 81.9362 |  | 24042.4139
2017-09-03 | 16:42 |  |  |  |  | 81.9124 |  | 24035.4494
2017-09-03 | 16:44 |  |  |  |  | 81.8881 |  | 24028.3194
2017-09-03 | 16:45 |  | 0 |  | 1.5 | 81.9094 |  | 24034.545
2017-09-03 | 16:45 | 1.7468 |  | 0 |  |  | 0 | 0
2017-09-03 | 16:46 |  |  |  |  | 81.8771 |  | 24025.0866
2017-09-03 | 16:48 |  |  |  |  | 81.8678 |  | 24022.3554
2017-09-03 | 16:50 |  |  |  |  | 81.8402 |  | 24014.2671
2017-09-03 | 16:52 |  |  |  |  | 81.8314 |  | 24011.6814
2017-09-03 | 16:54 |  |  |  |  | 81.8569 |  | 24019.1565
2017-09-03 | 16:56 |  |  |  |  | 81.8616 |  | 24020.5467
2017-09-03 | 16:58 |  |  |  |  | 81.779 |  | 23996.2904
2017-09-03 | 17:00 |  |  |  | 1.5 | 81.7566 |  | 23989.7288
2017-09-03 | 17:00 | 1.7616 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 17:02 |  |  |  |  | 81.7469 |  | 23986.8655
2017-09-03 | 17:04 |  |  |  |  | 81.692 |  | 23970.7651
2017-09-03 | 17:06 |  |  |  |  | 81.7135 |  | 23977.087
2017-09-03 | 17:08 |  |  |  |  | 81.661 |  | 23961.6849
2017-09-03 | 17:10 |  |  |  |  | 81.6029 |  | 23944.6329
2017-09-03 | 17:12 |  |  |  |  | 81.5956 |  | 23942.468
2017-09-03 | 17:14 |  |  |  |  | 81.5656 |  | 23933.6813
2017-09-03 | 17:15 |  | 0 |  | 1.5 | 81.5526 | 0 | 23929.8485
2017-09-03 | 17:15 | 1.7647 |  | 0 |  |  |  | 0
2017-09-03 | 17:16 |  |  |  |  | 81.5529 |  | 23929.9471
2017-09-03 | 17:18 |  |  |  |  | 81.49 |  | 23911.4825
2017-09-03 | 17:20 |  |  |  |  | 81.4608 |  | 23902.9218
2017-09-03 | 17:22 |  |  |  |  | 81.3937 |  | 23883.2304
2017-09-03 | 17:24 |  |  |  |  | 81.3395 |  | 23867.34
2017-09-03 | 17:26 |  |  |  |  | 81.2623 |  | 23844.6689
2017-09-03 | 17:28 |  |  |  |  | 81.1816 |  | 23820.9883
2017-09-03 | 17:30 |  |  |  | 1.5 | 81.1308 |  | 23806.1077
2017-09-03 | 17:30 | 1.7764 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 17:32 |  |  |  |  | 81.0664 |  | 23787.1997
2017-09-03 | 17:34 |  |  |  |  | 81.0045 |  | 23769.0239
2017-09-03 | 17:36 |  |  |  |  | 80.9403 |  | 23750.1922
2017-09-03 | 17:38 |  |  |  |  | 80.9337 |  | 23748.2579
2017-09-03 | 17:40 |  |  |  |  | 80.9042 |  | 23739.6144
2017-09-03 | 17:42 |  |  |  |  | 80.8954 |  | 23737.022
2017-09-03 | 17:44 |  |  |  |  | 80.8525 |  | 23724.4427
2017-09-03 | 17:45 |  | 0 |  | 1.5 | 80.8546 |  | 23725.0606
2017-09-03 | 17:45 | 1.7772 |  | 0 |  |  | 0 | 0
2017-09-03 | 17:46 |  |  |  |  | 80.8184 |  | 23714.4224
2017-09-03 | 17:48 |  |  |  |  | 80.7875 |  | 23705.3513
2017-09-03 | 17:50 |  |  |  |  | 80.8025 |  | 23709.7751
2017-09-03 | 17:52 |  |  |  |  | 80.7868 |  | 23705.1588
2017-09-03 | 17:54 |  |  |  |  | 80.757 |  | 23696.4167
2017-09-03 | 17:56 |  |  |  |  | 80.7094 |  | 23682.4563
2017-09-03 | 17:58 |  |  |  |  | 80.7313 |  | 23688.8791
2017-09-03 | 18:00 |  |  |  | 1.5 | 80.6954 |  | 23678.3283
2017-09-03 | 18:00 | 1.753 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 18:02 |  |  |  |  | 80.6459 |  | 23663.8238
2017-09-03 | 18:04 |  |  |  |  | 80.62 |  | 23656.2167
2017-09-03 | 18:06 |  |  |  |  | 80.6123 |  | 23653.9488
2017-09-03 | 18:08 |  |  |  |  | 80.5893 |  | 23647.2149
2017-09-03 | 18:10 |  |  |  |  | 80.565 |  | 23640.0623
2017-09-03 | 18:12 |  |  |  |  | 80.5331 |  | 23630.716
2017-09-03 | 18:14 |  |  |  |  | 80.4882 |  | 23617.5235
2017-09-03 | 18:15 |  | 0 |  | 1.5 | 80.5003 |  | 23621.0827
2017-09-03 | 18:15 | 1.7561 |  | 0 |  |  | 0 | 0
2017-09-03 | 18:16 |  |  |  |  | 80.4323 |  | 23601.1205
2017-09-03 | 18:18 |  |  |  |  | 80.4123 |  | 23595.2731
2017-09-03 | 18:20 |  |  |  |  | 80.3724 |  | 23583.5647
2017-09-03 | 18:22 |  |  |  |  | 80.3301 |  | 23571.1512
2017-09-03 | 18:24 |  |  |  |  | 80.282 |  | 23557.032
2017-09-03 | 18:26 |  |  |  |  | 80.2013 |  | 23533.3467
2017-09-03 | 18:28 |  |  |  |  | 80.1836 |  | 23528.1595
2017-09-03 | 18:30 |  |  |  | 1.5 | 80.0815 |  | 23498.2104
2017-09-03 | 18:30 | 1.7772 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 18:32 |  |  |  |  | 80.034 |  | 23484.2658
2017-09-03 | 18:34 |  |  |  |  | 79.9543 |  | 23460.8649
2017-09-03 | 18:36 |  |  |  |  | 79.9133 |  | 23448.8387
2017-09-03 | 18:38 |  |  |  |  | 79.8323 |  | 23425.0772
2017-09-03 | 18:40 |  |  |  |  | 79.762 |  | 23404.4389
2017-09-03 | 18:42 |  |  |  |  | 79.7326 |  | 23395.8176
2017-09-03 | 18:44 |  |  |  |  | 79.6951 |  | 23384.81
2017-09-03 | 18:45 |  | 0 |  | 1.5 | 79.6446 | 0 | 23370.0012
2017-09-03 | 18:45 | 1.7655 |  | 0 |  |  |  | 0
2017-09-03 | 18:46 |  |  |  |  | 79.6492 |  | 23371.351
2017-09-03 | 18:48 |  |  |  |  | 79.5778 |  | 23350.3969
2017-09-03 | 18:50 |  |  |  |  | 79.5171 |  | 23332.5973
2017-09-03 | 18:52 |  |  |  |  | 79.4378 |  | 23309.324
2017-09-03 | 18:54 |  |  |  |  | 79.3864 |  | 23294.2353
2017-09-03 | 18:56 |  |  |  |  | 79.3128 |  | 23272.641
2017-09-03 | 18:58 |  |  |  |  | 79.3003 |  | 23268.9673
2017-09-03 | 19:00 |  |  |  | 1.5 | 79.2465 |  | 23253.2002
2017-09-03 | 19:00 | 1.76 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 19:02 |  |  |  |  | 79.1911 |  | 23236.9407
2017-09-03 | 19:04 |  |  |  |  | 79.1375 |  | 23221.2115
2017-09-03 | 19:06 |  |  |  |  | 79.072 |  | 23201.9925
2017-09-03 | 19:08 |  |  |  |  | 79.0576 |  | 23197.7727
2017-09-03 | 19:10 |  |  |  |  | 78.9778 |  | 23174.3471
2017-09-03 | 19:12 |  |  |  |  | 78.9711 |  | 23172.3838
2017-09-03 | 19:14 |  |  |  |  | 78.9342 |  | 23161.5531
2017-09-03 | 19:15 |  | 0 |  | 1.5 | 78.918 |  | 23156.789
2017-09-03 | 19:15 | 1.7678 |  | 0 |  |  | 0 | 0
2017-09-03 | 19:16 |  |  |  |  | 78.8923 |  | 23149.2514
2017-09-03 | 19:18 |  |  |  |  | 78.8586 |  | 23139.3699
2017-09-03 | 19:20 |  |  |  |  | 78.7979 |  | 23121.5411
2017-09-03 | 19:22 |  |  |  |  | 78.7219 |  | 23099.2684
2017-09-03 | 19:24 |  |  |  |  | 78.6695 |  | 23083.8907
2017-09-03 | 19:26 |  |  |  |  | 78.6249 |  | 23070.7924
2017-09-03 | 19:28 |  |  |  |  | 78.5915 |  | 23060.9869
2017-09-03 | 19:30 |  | 0 |  | 1.5 | 78.5297 |  | 23042.8624
2017-09-03 | 19:30 | 1.7772 |  | 0 |  |  | 0 | 0
2017-09-03 | 19:32 |  |  |  |  | 78.5208 |  | 23040.2365
2017-09-03 | 19:34 |  |  |  |  | 78.4538 |  | 23020.5809
2017-09-03 | 19:36 |  |  |  |  | 78.38 |  | 22998.9396
2017-09-03 | 19:38 |  |  |  |  | 78.3722 |  | 22996.6403
2017-09-03 | 19:40 |  |  |  |  | 78.3453 |  | 22988.7559
2017-09-03 | 19:42 |  |  |  |  | 78.2815 |  | 22970.0249
2017-09-03 | 19:44 |  |  |  |  | 78.2552 |  | 22962.3104
2017-09-03 | 19:45 |  | 0 |  | 1.5 | 78.2271 |  | 22954.0518
2017-09-03 | 19:45 | 1.7538 |  | 0 |  |  | 0 | 0
2017-09-03 | 19:46 |  |  |  |  | 78.2183 |  | 22951.4952
2017-09-03 | 19:48 |  |  |  |  | 78.1787 |  | 22939.8651
2017-09-03 | 19:50 |  |  |  |  | 78.1132 |  | 22920.655
2017-09-03 | 19:52 |  |  |  |  | 78.0524 |  | 22902.7948
2017-09-03 | 19:54 |  |  |  |  | 78.0272 |  | 22895.4116
2017-09-03 | 19:56 |  |  |  |  | 77.9819 |  | 22882.1184
2017-09-03 | 19:58 |  |  |  |  | 77.9382 |  | 22869.3088
2017-09-03 | 20:00 |  |  |  | 1.5 | 77.9138 |  | 22862.1248
2017-09-03 | 20:00 | 1.7772 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 20:02 |  |  |  |  | 77.8624 |  | 22847.0381
2017-09-03 | 20:04 |  |  |  |  | 77.8266 |  | 22836.5343
2017-09-03 | 20:06 |  |  |  |  | 77.8191 |  | 22834.3406
2017-09-03 | 20:08 |  |  |  |  | 77.7842 |  | 22824.112
2017-09-03 | 20:10 |  |  |  |  | 77.7264 |  | 22807.1562
2017-09-03 | 20:12 |  |  |  |  | 77.7156 |  | 22803.9772
2017-09-03 | 20:14 |  |  |  |  | 77.6805 |  | 22793.6682
2017-09-03 | 20:15 |  | 0 |  | 1.5 | 77.6033 |  | 22771.0328
2017-09-03 | 20:15 | 1.7709 |  | 0 |  |  | 0 | 0
2017-09-03 | 20:16 |  |  |  |  | 77.6635 |  | 22788.6849
2017-09-03 | 20:18 |  |  |  |  | 77.5666 |  | 22760.2713
2017-09-03 | 20:20 |  |  |  |  | 77.5365 |  | 22751.4197
2017-09-03 | 20:22 |  |  |  |  | 77.4903 |  | 22737.8601
2017-09-03 | 20:24 |  |  |  |  | 77.4523 |  | 22726.7248
2017-09-03 | 20:26 |  |  |  |  | 77.4428 |  | 22723.9399
2017-09-03 | 20:28 |  |  |  |  | 77.4168 |  | 22716.3128
2017-09-03 | 20:30 |  |  |  | 1.5 | 77.388 |  | 22707.855
2017-09-03 | 20:30 | 1.7787 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 20:32 |  |  |  |  | 77.3858 |  | 22707.21
2017-09-03 | 20:34 |  |  |  |  | 77.3227 |  | 22688.6917
2017-09-03 | 20:36 |  |  |  |  | 77.3234 |  | 22688.9021
2017-09-03 | 20:38 |  |  |  |  | 77.28 |  | 22676.1618
2017-09-03 | 20:40 |  |  |  |  | 77.2264 |  | 22660.4375
2017-09-03 | 20:42 |  |  |  |  | 77.1888 |  | 22649.4075
2017-09-03 | 20:44 |  |  |  |  | 77.1314 |  | 22632.5659
2017-09-03 | 20:45 |  |  |  | 1.5 | 77.1362 |  | 22633.9559
2017-09-03 | 20:45 | 1.7772 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 20:46 |  |  |  |  | 77.1266 |  | 22631.1621
2017-09-03 | 20:48 |  |  |  |  | 77.087 |  | 22619.5412
2017-09-03 | 20:50 |  |  |  |  | 77.043 |  | 22606.6104
2017-09-03 | 20:52 |  |  |  |  | 77.012 |  | 22597.5305
2017-09-03 | 20:54 |  |  |  |  | 76.9726 |  | 22585.9697
2017-09-03 | 20:56 |  |  |  |  | 76.9474 |  | 22578.5709
2017-09-03 | 20:58 |  |  |  |  | 76.9117 |  | 22568.0985
2017-09-03 | 21:00 |  |  |  | 1.5 | 0 |  | 0
2017-09-03 | 21:00 | 1.7624 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:15 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 21:15 | 0.037 |  | 0 |  |  | 0 | 0
2017-09-03 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 21:30 | 0.037 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:45 |  | 0 |  | 0 | 0 | 0 | 0
2017-09-03 | 21:45 | 0.037 |  | 0 |  |  |  | 0
2017-09-03 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 22:00 | 0.03622 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:15 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 22:15 | 0.03544 |  | 0 |  |  | 0 | 0
2017-09-03 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 22:30 | 0.03466 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:45 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 22:45 | 0.03466 |  | 0 |  |  | 0 | 0
2017-09-03 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:00 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 23:00 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:15 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 23:15 | 0.03388 |  | 0 |  |  | 0 | 0
2017-09-03 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:30 |  |  |  | 0 | 0 |  | 0
2017-09-03 | 23:30 | 0.03388 | 0 | 0 |  |  | 0 | 0
2017-09-03 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:45 |  | 0 |  | 0 | 0 |  | 0
2017-09-03 | 23:45 | 0.0331 |  | 0 |  |  | 0 | 0
2017-09-03 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-03 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:00 |  |  |  | 0 | 0 |  | 0
2017-09-04 | 0:00 | 0.0331 | 0 | 0 |  |  | 0 | 0
2017-09-04 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-04 | 5:04 |  |  |  |  | 99.9531 |  | 29329.1003
2017-09-04 | 5:06 |  |  |  |  | 98.7773 |  | 28984.0882
2017-09-04 | 5:08 |  |  |  |  | 97.1034 |  | 28492.9122
2017-09-04 | 5:10 |  |  |  |  | 95.8258 |  | 28118.0382
2017-09-04 | 5:12 |  |  |  |  | 94.7506 |  | 27802.5408
2017-09-04 | 5:14 |  |  |  |  | 93.8391 |  | 27535.0786
2017-09-04 | 5:15 | 2.0619 | 0 | 0 | 1.5 | 93.3562 | 0 | 27393.3723
2017-09-04 | 5:16 |  |  |  |  | 92.9182 |  | 27264.8427
2017-09-04 | 5:18 |  |  |  |  | 92.1648 |  | 27043.7797
2017-09-04 | 5:20 |  |  |  |  | 91.4635 |  | 26838.0112
2017-09-04 | 5:22 |  |  |  |  | 90.8657 |  | 26662.5858
2017-09-04 | 5:24 |  |  |  |  | 90.3476 |  | 26510.5637
2017-09-04 | 5:26 |  |  |  |  | 89.8619 |  | 26368.0378
2017-09-04 | 5:28 |  |  |  |  | 89.4053 |  | 26234.0818
2017-09-04 | 5:30 | 1.8934 | 0 | 0 | 1.5 | 88.9613 | 0 | 26103.7792
2017-09-04 | 5:32 |  |  |  |  | 88.5816 |  | 25992.3668
2017-09-04 | 5:34 |  |  |  |  | 88.1773 |  | 25873.7456
2017-09-04 | 5:36 |  |  |  |  | 87.7101 |  | 25736.642
2017-09-04 | 5:38 |  |  |  |  | 87.2738 |  | 25608.6209
2017-09-04 | 5:40 |  |  |  |  | 86.8427 |  | 25482.1329
2017-09-04 | 5:42 |  |  |  |  | 86.3657 |  | 25342.1707
2017-09-04 | 5:44 |  |  |  |  | 85.8506 |  | 25191.0057
2017-09-04 | 5:45 | 1.909 | 0 | 0 | 1.5 | 85.6299 | 0 | 25126.2563
2017-09-04 | 5:46 |  |  |  |  | 85.3633 |  | 25048.0212
2017-09-04 | 5:48 |  |  |  |  | 84.9247 |  | 24919.3372
2017-09-04 | 5:50 |  |  |  |  | 84.417 |  | 24770.3709
2017-09-04 | 5:52 |  |  |  |  | 83.9797 |  | 24642.0293
2017-09-04 | 5:54 |  |  |  |  | 83.5293 |  | 24509.8867
2017-09-04 | 5:56 |  |  |  |  | 83.0944 |  | 24382.2752
2017-09-04 | 5:58 |  |  |  |  | 82.6483 |  | 24251.3793
2017-09-04 | 6:00 | 1.9059 | 0 | 0 | 1.5 | 82.2232 | 0 | 24126.622
2017-09-04 | 6:02 |  |  |  |  | 81.8357 |  | 24012.9305
2017-09-04 | 6:04 |  |  |  |  | 81.497 |  | 23913.56
2017-09-04 | 6:06 |  |  |  |  | 81.2132 |  | 23830.2741
2017-09-04 | 6:08 |  |  |  |  | 80.924 |  | 23745.4213
2017-09-04 | 6:10 |  |  |  |  | 80.6526 |  | 23665.7737
2017-09-04 | 6:12 |  |  |  |  | 80.3863 |  | 23587.6392
2017-09-04 | 6:14 |  |  |  |  | 80.1668 |  | 23523.2322
2017-09-04 | 6:15 | 1.8255 | 0 | 0 | 1.5 | 80.0654 | 0 | 23493.4736
2017-09-04 | 6:16 |  |  |  |  | 79.947 |  | 23458.7358
2017-09-04 | 6:18 |  |  |  |  | 79.7264 |  | 23393.9998
2017-09-04 | 6:20 |  |  |  |  | 79.5635 |  | 23346.2038
2017-09-04 | 6:22 |  |  |  |  | 79.3582 |  | 23285.97
2017-09-04 | 6:24 |  |  |  |  | 79.2112 |  | 23242.8307
2017-09-04 | 6:26 |  |  |  |  | 79.0666 |  | 23200.3963
2017-09-04 | 6:28 |  |  |  |  | 78.8725 |  | 23143.4444
2017-09-04 | 6:30 | 1.8318 | 0 | 0 | 1.5 | 78.737 | 0 | 23103.6763
2017-09-04 | 6:32 |  |  |  |  | 78.6057 |  | 23065.153
2017-09-04 | 6:34 |  |  |  |  | 78.4472 |  | 23018.6378
2017-09-04 | 6:36 |  |  |  |  | 78.2996 |  | 22975.326
2017-09-04 | 6:38 |  |  |  |  | 78.1273 |  | 22924.7809
2017-09-04 | 6:40 |  |  |  |  | 78.0952 |  | 22915.363
2017-09-04 | 6:42 |  |  |  |  | 78.0856 |  | 22912.551
2017-09-04 | 6:44 |  |  |  |  | 78.0888 |  | 22913.4912
2017-09-04 | 6:45 | 1.7819 | 0 | 0 | 1.5 | 78.0251 | 0 | 22894.7916
2017-09-04 | 6:46 |  |  |  |  | 77.9445 |  | 22871.1533
2017-09-04 | 6:48 |  |  |  |  | 77.8781 |  | 22851.6499
2017-09-04 | 6:50 |  |  |  |  | 77.7762 |  | 22821.759
2017-09-04 | 6:52 |  |  |  |  | 77.7645 |  | 22818.3361
2017-09-04 | 6:54 |  |  |  |  | 77.6417 |  | 22782.3046
2017-09-04 | 6:56 |  |  |  |  | 77.5418 |  | 22752.9734
2017-09-04 | 6:58 |  |  |  |  | 77.4723 |  | 22732.5722
2017-09-04 | 7:00 | 1.7452 | 0 | 0 | 1.5 | 77.4745 | 0 | 22733.2415
2017-09-04 | 7:02 |  |  |  |  | 77.5303 |  | 22749.5928
2017-09-04 | 7:04 |  |  |  |  | 77.5603 |  | 22758.3998
2017-09-04 | 7:06 |  |  |  |  | 77.4617 |  | 22729.4783
2017-09-04 | 7:08 |  |  |  |  | 77.4112 |  | 22714.6672
2017-09-04 | 7:10 |  |  |  |  | 77.3537 |  | 22697.7874
2017-09-04 | 7:12 |  |  |  |  | 77.3116 |  | 22685.4188
2017-09-04 | 7:14 |  |  |  |  | 77.2365 |  | 22663.3879
2017-09-04 | 7:15 | 1.7764 | 0 | 0 | 1.5 | 77.2009 | 0 | 22652.9601
2017-09-04 | 7:16 |  |  |  |  | 77.1567 |  | 22639.9691
2017-09-04 | 7:18 |  |  |  |  | 77.0544 |  | 22609.9707
2017-09-04 | 7:20 |  |  |  |  | 77.1046 |  | 22624.6832
2017-09-04 | 7:22 |  |  |  |  | 77.0798 |  | 22617.4256
2017-09-04 | 7:24 |  |  |  |  | 77.0812 |  | 22617.8285
2017-09-04 | 7:26 |  |  |  |  | 77.0234 |  | 22600.8592
2017-09-04 | 7:28 |  |  |  |  | 76.9732 |  | 22586.1264
2017-09-04 | 7:30 | 1.7803 | 0 | 0 | 1.5 | 76.9049 | 0 | 22566.1037
2017-09-04 | 7:32 |  |  |  |  | 76.823 |  | 22542.0538
2017-09-04 | 7:34 |  |  |  |  | 76.7703 |  | 22526.5889
2017-09-04 | 7:36 |  |  |  |  | 76.8835 |  | 22559.8109
2017-09-04 | 7:38 |  |  |  |  | 76.943 |  | 22577.2725
2017-09-04 | 7:40 |  |  |  |  | 76.918 |  | 22569.9521
2017-09-04 | 7:42 |  |  |  |  | 76.8923 |  | 22562.4054
2017-09-04 | 7:44 |  |  |  |  | 76.8825 |  | 22559.5265
2017-09-04 | 7:45 | 1.746 | 0 | 0 | 1.5 | 76.8744 | 0 | 22557.1401
2017-09-04 | 7:46 |  |  |  |  | 76.858 |  | 22552.3449
2017-09-04 | 7:48 |  |  |  |  | 76.7703 |  | 22526.5956
2017-09-04 | 7:50 |  |  |  |  | 76.6793 |  | 22499.8881
2017-09-04 | 7:52 |  |  |  |  | 76.6251 |  | 22484.0068
2017-09-04 | 7:54 |  |  |  |  | 76.5755 |  | 22469.4531
2017-09-04 | 7:56 |  |  |  |  | 76.6791 |  | 22499.8411
2017-09-04 | 7:58 |  |  |  |  | 76.7324 |  | 22515.4671
2017-09-04 | 8:00 | 1.7733 | 0 | 0 | 1.5 | 76.7042 | 0 | 22507.2176
2017-09-04 | 8:02 |  |  |  |  | 76.6963 |  | 22504.8737
2017-09-04 | 8:04 |  |  |  |  | 76.6637 |  | 22495.3323
2017-09-04 | 8:06 |  |  |  |  | 76.6509 |  | 22491.5714
2017-09-04 | 8:08 |  |  |  |  | 76.6117 |  | 22480.0555
2017-09-04 | 8:10 |  |  |  |  | 76.5927 |  | 22474.4745
2017-09-04 | 8:12 |  |  |  |  | 76.5625 |  | 22465.6115
2017-09-04 | 8:14 |  |  |  |  | 76.5661 |  | 22466.6928
2017-09-04 | 8:15 | 1.7179 | 0 | 0 | 1.5 | 76.6519 | 0 | 22491.8646
2017-09-04 | 8:16 |  |  |  |  | 76.7083 |  | 22508.3951
2017-09-04 | 8:18 |  |  |  |  | 76.7941 |  | 22533.5781
2017-09-04 | 8:20 |  |  |  |  | 76.8256 |  | 22542.817
2017-09-04 | 8:22 |  |  |  |  | 76.8214 |  | 22541.5834
2017-09-04 | 8:24 |  |  |  |  | 76.8089 |  | 22537.9343
2017-09-04 | 8:26 |  |  |  |  | 76.7961 |  | 22534.1711
2017-09-04 | 8:28 |  |  |  |  | 76.7901 |  | 22532.4049
2017-09-04 | 8:30 | 1.7585 | 0 | 0 | 1.5 | 76.7763 | 0 | 22528.3618
2017-09-04 | 8:32 |  |  |  |  | 76.7688 |  | 22526.1499
2017-09-04 | 8:34 |  |  |  |  | 76.7541 |  | 22521.8606
2017-09-04 | 8:36 |  |  |  |  | 76.7399 |  | 22517.6742
2017-09-04 | 8:38 |  |  |  |  | 76.7591 |  | 22523.3045
2017-09-04 | 8:40 |  |  |  |  | 76.7744 |  | 22527.8066
2017-09-04 | 8:42 |  |  |  |  | 76.729 |  | 22514.4888
2017-09-04 | 8:44 |  |  |  |  | 76.6688 |  | 22496.8053
2017-09-04 | 8:45 | 1.7202 | 0 | 0 | 1.5 | 76.7237 | 0 | 22512.926
2017-09-04 | 8:46 |  |  |  |  | 76.7914 |  | 22532.7811
2017-09-04 | 8:48 |  |  |  |  | 76.8432 |  | 22548.0018
2017-09-04 | 8:50 |  |  |  |  | 76.8455 |  | 22548.6624
2017-09-04 | 8:52 |  |  |  |  | 76.8137 |  | 22539.3381
2017-09-04 | 8:54 |  |  |  |  | 76.8529 |  | 22550.8472
2017-09-04 | 8:56 |  |  |  |  | 76.8706 |  | 22556.0409
2017-09-04 | 8:58 |  |  |  |  | 76.8802 |  | 22558.8461
2017-09-04 | 9:00 | 1.7592 | 0 | 0 | 1.5 | 76.8629 | 0 | 22553.7618
2017-09-04 | 9:02 |  |  |  |  | 76.802 |  | 22535.8973
2017-09-04 | 9:04 |  |  |  |  | 76.8063 |  | 22537.1667
2017-09-04 | 9:06 |  |  |  |  | 76.73 |  | 22514.7799
2017-09-04 | 9:08 |  |  |  |  | 76.7415 |  | 22518.1399
2017-09-04 | 9:10 |  |  |  |  | 76.6503 |  | 22491.3766
2017-09-04 | 9:12 |  |  |  |  | 76.5988 |  | 22476.2879
2017-09-04 | 9:14 |  |  |  |  | 76.4907 |  | 22444.5703
2017-09-04 | 9:15 | 1.778 | 0 | 0 | 1.5 | 76.4997 | 0 | 22447.1851
2017-09-04 | 9:16 |  |  |  |  | 76.4641 |  | 22436.7437
2017-09-04 | 9:18 |  |  |  |  | 76.4173 |  | 22423.0318
2017-09-04 | 9:20 |  |  |  |  | 76.4421 |  | 22430.3009
2017-09-04 | 9:22 |  |  |  |  | 76.4543 |  | 22433.8737
2017-09-04 | 9:24 |  |  |  |  | 76.4462 |  | 22431.494
2017-09-04 | 9:26 |  |  |  |  | 76.4584 |  | 22435.0715
2017-09-04 | 9:28 |  |  |  |  | 76.4893 |  | 22444.1584
2017-09-04 | 9:30 | 1.767 | 0 | 0 | 1.5 | 76.4519 | 0 | 22433.1821
2017-09-04 | 9:32 |  |  |  |  | 76.471 |  | 22438.7854
2017-09-04 | 9:34 |  |  |  |  | 76.5234 |  | 22454.1449
2017-09-04 | 9:36 |  |  |  |  | 76.5236 |  | 22454.2232
2017-09-04 | 9:38 |  |  |  |  | 76.481 |  | 22441.7024
2017-09-04 | 9:40 |  |  |  |  | 76.5056 |  | 22448.9313
2017-09-04 | 9:42 |  |  |  |  | 76.495 |  | 22445.8329
2017-09-04 | 9:44 |  |  |  |  | 76.5143 |  | 22451.4809
2017-09-04 | 9:45 | 1.7514 | 0 | 0 | 1.5 | 76.5364 | 0 | 22457.9598
2017-09-04 | 9:46 |  |  |  |  | 76.5495 |  | 22461.8216
2017-09-04 | 9:48 |  |  |  |  | 76.591 |  | 22474
2017-09-04 | 9:50 |  |  |  |  | 76.5823 |  | 22471.441
2017-09-04 | 9:52 |  |  |  |  | 76.5539 |  | 22463.0998
2017-09-04 | 9:54 |  |  |  |  | 76.5437 |  | 22460.1223
2017-09-04 | 9:56 |  |  |  |  | 76.5629 |  | 22465.7526
2017-09-04 | 9:58 |  |  |  |  | 76.5756 |  | 22469.4554
2017-09-04 | 10:00 | 1.7327 | 0 | 0 | 1.5 | 76.5595 | 0 | 22464.743
2017-09-04 | 10:02 |  |  |  |  | 76.5828 |  | 22471.5778
2017-09-04 | 10:04 |  |  |  |  | 76.6127 |  | 22480.3669
2017-09-04 | 10:06 |  |  |  |  | 76.6164 |  | 22481.4434
2017-09-04 | 10:08 |  |  |  |  | 76.6381 |  | 22487.7991
2017-09-04 | 10:10 |  |  |  |  | 76.6303 |  | 22485.5068
2017-09-04 | 10:12 |  |  |  |  | 76.6464 |  | 22490.2393
2017-09-04 | 10:14 |  |  |  |  | 76.6836 |  | 22501.1618
2017-09-04 | 10:15 | 1.739 | 0 | 0 | 1.5 | 76.6745 | 0 | 22498.4867
2017-09-04 | 10:16 |  |  |  |  | 76.6817 |  | 22500.6023
2017-09-04 | 10:18 |  |  |  |  | 76.6998 |  | 22505.9101
2017-09-04 | 10:20 |  |  |  |  | 76.7277 |  | 22514.088
2017-09-04 | 10:22 |  |  |  |  | 76.7435 |  | 22518.7221
2017-09-04 | 10:24 |  |  |  |  | 76.775 |  | 22527.9724
2017-09-04 | 10:26 |  |  |  |  | 76.8089 |  | 22537.9367
2017-09-04 | 10:28 |  |  |  |  | 76.8225 |  | 22541.9126
2017-09-04 | 10:30 | 1.7397 | 0 | 0 | 1.5 | 76.8516 | 0 | 22550.442
2017-09-04 | 10:32 |  |  |  |  | 76.9129 |  | 22568.4433
2017-09-04 | 10:34 |  |  |  |  | 76.8704 |  | 22555.9602
2017-09-04 | 10:36 |  |  |  |  | 76.9196 |  | 22570.4133
2017-09-04 | 10:38 |  |  |  |  | 76.9665 |  | 22584.1722
2017-09-04 | 10:40 |  |  |  |  | 76.9629 |  | 22583.1112
2017-09-04 | 10:42 |  |  |  |  | 76.9603 |  | 22582.3477
2017-09-04 | 10:44 |  |  |  |  | 76.9787 |  | 22587.7632
2017-09-04 | 10:45 | 1.7413 | 0 | 0 | 1.5 | 76.9685 | 0 | 22584.7564
2017-09-04 | 10:46 |  |  |  |  | 76.9842 |  | 22589.3524
2017-09-04 | 10:48 |  |  |  |  | 77.0037 |  | 22595.0857
2017-09-04 | 10:50 |  |  |  |  | 77.0212 |  | 22600.2145
2017-09-04 | 10:52 |  |  |  |  | 77.0564 |  | 22610.5596
2017-09-04 | 10:54 |  |  |  |  | 77.1096 |  | 22626.1697
2017-09-04 | 10:56 |  |  |  |  | 77.1402 |  | 22635.1516
2017-09-04 | 10:58 |  |  |  |  | 77.1713 |  | 22644.2652
2017-09-04 | 11:00 | 1.7312 | 0 | 0 | 1.5 | 77.1954 | 0 | 22651.3506
2017-09-04 | 11:02 |  |  |  |  | 77.2212 |  | 22658.9173
2017-09-04 | 11:04 |  |  |  |  | 77.2331 |  | 22662.4096
2017-09-04 | 11:06 |  |  |  |  | 77.2568 |  | 22669.3519
2017-09-04 | 11:08 |  |  |  |  | 77.3077 |  | 22684.3018
2017-09-04 | 11:10 |  |  |  |  | 77.3379 |  | 22693.1557
2017-09-04 | 11:12 |  |  |  |  | 77.3609 |  | 22699.8919
2017-09-04 | 11:14 |  |  |  |  | 77.4262 |  | 22719.0684
2017-09-04 | 11:15 | 1.7319 | 0 | 0 | 1.5 | 77.4612 | 0 | 22729.3193
2017-09-04 | 11:16 |  |  |  |  | 77.4793 |  | 22734.6342
2017-09-04 | 11:18 |  |  |  |  | 77.5446 |  | 22753.8038
2017-09-04 | 11:20 |  |  |  |  | 77.6207 |  | 22776.1191
2017-09-04 | 11:22 |  |  |  |  | 77.6634 |  | 22788.6646
2017-09-04 | 11:24 |  |  |  |  | 77.7131 |  | 22803.2586
2017-09-04 | 11:26 |  |  |  |  | 77.7678 |  | 22819.2921
2017-09-04 | 11:28 |  |  |  |  | 77.843 |  | 22841.3676
2017-09-04 | 11:30 | 1.7436 | 0 | 0 | 1.5 | 77.8677 | 0 | 22848.6121
2017-09-04 | 11:32 |  |  |  |  | 77.9162 |  | 22862.839
2017-09-04 | 11:34 |  |  |  |  | 77.9457 |  | 22871.4936
2017-09-04 | 11:36 |  |  |  |  | 77.9758 |  | 22880.3364
2017-09-04 | 11:38 |  |  |  |  | 77.9827 |  | 22882.3578
2017-09-04 | 11:40 |  |  |  |  | 78.0266 |  | 22895.2191
2017-09-04 | 11:42 |  |  |  |  | 78.0089 |  | 22890.0278
2017-09-04 | 11:44 |  |  |  |  | 78.0249 |  | 22894.7223
2017-09-04 | 11:45 | 1.7694 | 0 | 0 | 1.5 | 78.034 | 0 | 22897.4063
2017-09-04 | 11:46 |  |  |  |  | 78.0303 |  | 22896.3183
2017-09-04 | 11:48 |  |  |  |  | 78.0444 |  | 22900.4577
2017-09-04 | 11:50 |  |  |  |  | 78.0708 |  | 22908.1969
2017-09-04 | 11:52 |  |  |  |  | 78.1434 |  | 22929.5159
2017-09-04 | 11:54 |  |  |  |  | 78.105 |  | 22918.2351
2017-09-04 | 11:56 |  |  |  |  | 78.1144 |  | 22920.9933
2017-09-04 | 11:58 |  |  |  |  | 78.1582 |  | 22933.861
2017-09-04 | 12:00 | 1.7561 | 0 | 0 | 1.5 | 78.1543 | 0 | 22932.7172
2017-09-04 | 12:02 |  |  |  |  | 78.1754 |  | 22938.8936
2017-09-04 | 12:04 |  |  |  |  | 78.1542 |  | 22932.6858
2017-09-04 | 12:06 |  |  |  |  | 78.1287 |  | 22925.184
2017-09-04 | 12:08 |  |  |  |  | 78.1827 |  | 22941.0315
2017-09-04 | 12:10 |  |  |  |  | 78.1804 |  | 22940.3599
2017-09-04 | 12:12 |  |  |  |  | 78.1848 |  | 22941.663
2017-09-04 | 12:14 |  |  |  |  | 78.2111 |  | 22949.3617
2017-09-04 | 12:15 | 1.7429 | 0 | 0 | 1.5 | 78.2169 | 0 | 22951.0832
2017-09-04 | 12:16 |  |  |  |  | 78.2332 |  | 22955.8652
2017-09-04 | 12:18 |  |  |  |  | 78.2167 |  | 22951.016
2017-09-04 | 12:20 |  |  |  |  | 78.2229 |  | 22952.8361
2017-09-04 | 12:22 |  |  |  |  | 78.2089 |  | 22948.717
2017-09-04 | 12:24 |  |  |  |  | 78.2096 |  | 22948.9385
2017-09-04 | 12:26 |  |  |  |  | 78.2367 |  | 22956.8925
2017-09-04 | 12:28 |  |  |  |  | 78.2706 |  | 22966.83
2017-09-04 | 12:30 | 1.7249 | 0 | 0 | 1.5 | 78.2994 | 0 | 22975.2699
2017-09-04 | 12:32 |  |  |  |  | 78.3209 |  | 22981.6033
2017-09-04 | 12:34 |  |  |  |  | 78.3308 |  | 22984.5024
2017-09-04 | 12:36 |  |  |  |  | 78.3253 |  | 22982.8791
2017-09-04 | 12:38 |  |  |  |  | 78.3499 |  | 22990.1057
2017-09-04 | 12:40 |  |  |  |  | 78.3766 |  | 22997.9479
2017-09-04 | 12:42 |  |  |  |  | 78.3936 |  | 23002.9288
2017-09-04 | 12:44 |  |  |  |  | 78.4026 |  | 23005.5705
2017-09-04 | 12:45 | 1.7421 | 0 | 0 | 1.5 | 78.4187 | 0 | 23010.2739
2017-09-04 | 12:46 |  |  |  |  | 78.4408 |  | 23016.7819
2017-09-04 | 12:48 |  |  |  |  | 78.4521 |  | 23020.0906
2017-09-04 | 12:50 |  |  |  |  | 78.4651 |  | 23023.9098
2017-09-04 | 12:52 |  |  |  |  | 78.5134 |  | 23038.0695
2017-09-04 | 12:54 |  |  |  |  | 78.5339 |  | 23044.0983
2017-09-04 | 12:56 |  |  |  |  | 78.5273 |  | 23042.1505
2017-09-04 | 12:58 |  |  |  |  | 78.5516 |  | 23049.2697
2017-09-04 | 13:00 | 1.7624 | 0 | 0 | 1.5 | 78.5709 | 0 | 23054.9469
2017-09-04 | 13:02 |  |  |  |  | 78.5996 |  | 23063.3554
2017-09-04 | 13:04 |  |  |  |  | 78.6132 |  | 23067.3537
2017-09-04 | 13:06 |  |  |  |  | 78.6182 |  | 23068.8267
2017-09-04 | 13:08 |  |  |  |  | 78.6436 |  | 23076.2727
2017-09-04 | 13:10 |  |  |  |  | 78.6427 |  | 23076.0286
2017-09-04 | 13:12 |  |  |  |  | 78.641 |  | 23075.5227
2017-09-04 | 13:14 |  |  |  |  | 78.651 |  | 23078.4374
2017-09-04 | 13:15 | 1.7382 | 0 | 0 | 1.5 | 78.6765 | 0 | 23085.928
2017-09-04 | 13:16 |  |  |  |  | 78.655 |  | 23079.6375
2017-09-04 | 13:18 |  |  |  |  | 78.719 |  | 23098.4064
2017-09-04 | 13:20 |  |  |  |  | 78.7348 |  | 23103.0496
2017-09-04 | 13:22 |  |  |  |  | 78.7344 |  | 23102.9128
2017-09-04 | 13:24 |  |  |  |  | 78.7448 |  | 23105.9709
2017-09-04 | 13:26 |  |  |  |  | 78.7692 |  | 23113.1371
2017-09-04 | 13:28 |  |  |  |  | 78.7584 |  | 23109.9648
2017-09-04 | 13:30 | 1.7351 | 0 | 0 | 1.5 | 78.781 | 0 | 23116.6048
2017-09-04 | 13:32 |  |  |  |  | 78.77 |  | 23113.3653
2017-09-04 | 13:34 |  |  |  |  | 78.8109 |  | 23125.3827
2017-09-04 | 13:36 |  |  |  |  | 78.804 |  | 23123.3475
2017-09-04 | 13:38 |  |  |  |  | 78.8303 |  | 23131.0532
2017-09-04 | 13:40 |  |  |  |  | 78.8609 |  | 23140.0527
2017-09-04 | 13:42 |  |  |  |  | 78.8771 |  | 23144.7807
2017-09-04 | 13:44 |  |  |  |  | 78.8858 |  | 23147.362
2017-09-04 | 13:45 | 1.753 | 0 | 0 | 1.5 | 78.8821 | 0 | 23146.256
2017-09-04 | 13:46 |  |  |  |  | 78.8826 |  | 23146.4195
2017-09-04 | 13:48 |  |  |  |  | 78.9176 |  | 23156.686
2017-09-04 | 13:50 |  |  |  |  | 78.9594 |  | 23168.9475
2017-09-04 | 13:52 |  |  |  |  | 78.9297 |  | 23160.2435
2017-09-04 | 13:54 |  |  |  |  | 78.9935 |  | 23178.9543
2017-09-04 | 13:56 |  |  |  |  | 78.9784 |  | 23174.5106
2017-09-04 | 13:58 |  |  |  |  | 78.9993 |  | 23180.6535
2017-09-04 | 14:00 | 1.7374 | 0 | 0 | 1.5 | 78.9938 | 0 | 23179.035
2017-09-04 | 14:02 |  |  |  |  | 79.0066 |  | 23182.7847
2017-09-04 | 14:04 |  |  |  |  | 79.0299 |  | 23189.6395
2017-09-04 | 14:06 |  |  |  |  | 79.025 |  | 23188.2022
2017-09-04 | 14:08 |  |  |  |  | 79.0332 |  | 23190.5955
2017-09-04 | 14:10 |  |  |  |  | 79.0404 |  | 23192.7087
2017-09-04 | 14:12 |  |  |  |  | 79.0429 |  | 23193.4496
2017-09-04 | 14:14 |  |  |  |  | 79.0502 |  | 23195.5764
2017-09-04 | 14:15 | 1.7553 | 0 | 0 | 1.5 | 79.0394 | 0 | 23192.4288
2017-09-04 | 14:16 |  |  |  |  | 79.0464 |  | 23194.4661
2017-09-04 | 14:18 |  |  |  |  | 79.069 |  | 23201.1128
2017-09-04 | 14:20 |  |  |  |  | 79.0392 |  | 23192.3616
2017-09-04 | 14:22 |  |  |  |  | 78.9953 |  | 23179.478
2017-09-04 | 14:24 |  |  |  |  | 78.9915 |  | 23178.3768
2017-09-04 | 14:26 |  |  |  |  | 78.9853 |  | 23176.5364
2017-09-04 | 14:28 |  |  |  |  | 78.9859 |  | 23176.711
2017-09-04 | 14:30 | 1.7624 | 0 | 0 | 1.5 | 78.953 | 0 | 23167.0713
2017-09-04 | 14:32 |  |  |  |  | 78.9627 |  | 23169.9258
2017-09-04 | 14:34 |  |  |  |  | 78.9633 |  | 23170.0778
2017-09-04 | 14:36 |  |  |  |  | 78.9659 |  | 23170.8568
2017-09-04 | 14:38 |  |  |  |  | 78.9587 |  | 23168.7435
2017-09-04 | 14:40 |  |  |  |  | 78.9713 |  | 23172.4396
2017-09-04 | 14:42 |  |  |  |  | 78.9624 |  | 23169.8248
2017-09-04 | 14:44 |  |  |  |  | 78.9669 |  | 23171.1323
2017-09-04 | 14:45 | 1.7491 | 0 | 0 | 1.5 | 78.9734 | 0 | 23173.0619
2017-09-04 | 14:46 |  |  |  |  | 78.9797 |  | 23174.9135
2017-09-04 | 14:48 |  |  |  |  | 78.9735 |  | 23173.071
2017-09-04 | 14:50 |  |  |  |  | 79.0053 |  | 23182.4018
2017-09-04 | 14:52 |  |  |  |  | 79.0445 |  | 23193.9086
2017-09-04 | 14:54 |  |  |  |  | 79.0396 |  | 23192.4872
2017-09-04 | 14:56 |  |  |  |  | 79.077 |  | 23203.4588
2017-09-04 | 14:58 |  |  |  |  | 79.0859 |  | 23206.0738
2017-09-04 | 15:00 | 1.7608 | 0 | 0 | 1.5 | 79.1419 | 0 | 23222.4856
2017-09-04 | 15:02 |  |  |  |  | 79.1574 |  | 23227.0457
2017-09-04 | 15:04 |  |  |  |  | 79.1983 |  | 23239.0561
2017-09-04 | 15:06 |  |  |  |  | 79.2127 |  | 23243.2761
2017-09-04 | 15:08 |  |  |  |  | 79.25 |  | 23254.2187
2017-09-04 | 15:10 |  |  |  |  | 79.247 |  | 23253.339
2017-09-04 | 15:12 |  |  |  |  | 79.2608 |  | 23257.3842
2017-09-04 | 15:14 |  |  |  |  | 79.2951 |  | 23267.4605
2017-09-04 | 15:15 | 1.7491 | 0 | 0 | 1.5 | 79.3158 | 0 | 23273.5116
2017-09-04 | 15:16 |  |  |  |  | 79.3061 |  | 23270.6777
2017-09-04 | 15:18 |  |  |  |  | 79.3033 |  | 23269.8446
2017-09-04 | 15:20 |  |  |  |  | 79.3312 |  | 23278.0383
2017-09-04 | 15:22 |  |  |  |  | 79.343 |  | 23281.4949
2017-09-04 | 15:24 |  |  |  |  | 79.3579 |  | 23285.8647
2017-09-04 | 15:26 |  |  |  |  | 79.3475 |  | 23282.8247
2017-09-04 | 15:28 |  |  |  |  | 79.3674 |  | 23288.6742
2017-09-04 | 15:30 | 1.7585 | 0 | 0 | 1.5 | 79.3617 | 0 | 23286.9976
2017-09-04 | 15:32 |  |  |  |  | 79.376 |  | 23291.1951
2017-09-04 | 15:34 |  |  |  |  | 79.4033 |  | 23299.1828
2017-09-04 | 15:36 |  |  |  |  | 79.4138 |  | 23302.2855
2017-09-04 | 15:38 |  |  |  |  | 79.3935 |  | 23296.3216
2017-09-04 | 15:40 |  |  |  |  | 79.4454 |  | 23311.5379
2017-09-04 | 15:42 |  |  |  |  | 79.4074 |  | 23300.3982
2017-09-04 | 15:44 |  |  |  |  | 79.3777 |  | 23291.6743
2017-09-04 | 15:45 | 1.7468 | 0 | 0 | 1.5 | 79.4061 | 0 | 23300.0065
2017-09-04 | 15:46 |  |  |  |  | 79.3834 |  | 23293.3509
2017-09-04 | 15:48 |  |  |  |  | 79.4064 |  | 23300.105
2017-09-04 | 15:50 |  |  |  |  | 79.4087 |  | 23300.7767
2017-09-04 | 15:52 |  |  |  |  | 79.3861 |  | 23294.157
2017-09-04 | 15:54 |  |  |  |  | 79.3807 |  | 23292.5607
2017-09-04 | 15:56 |  |  |  |  | 79.4012 |  | 23298.5939
2017-09-04 | 15:58 |  |  |  |  | 79.3763 |  | 23291.2825
2017-09-04 | 16:00 | 1.7335 | 0 | 0 | 1.5 | 79.3696 | 0 | 23289.2946
2017-09-04 | 16:02 |  |  |  |  | 79.3612 |  | 23286.843
2017-09-04 | 16:04 |  |  |  |  | 79.3636 |  | 23287.5504
2017-09-04 | 16:06 |  |  |  |  | 79.3834 |  | 23293.3486
2017-09-04 | 16:08 |  |  |  |  | 79.387 |  | 23294.4166
2017-09-04 | 16:10 |  |  |  |  | 79.3854 |  | 23293.9554
2017-09-04 | 16:12 |  |  |  |  | 79.3863 |  | 23294.2083
2017-09-04 | 16:14 |  |  |  |  | 79.4035 |  | 23299.2679
2017-09-04 | 16:15 | 1.7577 | 0 | 0 | 1.5 | 79.3594 | 0 | 23286.3057
2017-09-04 | 16:16 |  |  |  |  | 79.3929 |  | 23296.1402
2017-09-04 | 16:18 |  |  |  |  | 79.3906 |  | 23295.4733
2017-09-04 | 16:20 |  |  |  |  | 79.4065 |  | 23300.1229
2017-09-04 | 16:22 |  |  |  |  | 79.4058 |  | 23299.9193
2017-09-04 | 16:24 |  |  |  |  | 79.4112 |  | 23301.52
2017-09-04 | 16:26 |  |  |  |  | 79.38 |  | 23292.3503
2017-09-04 | 16:28 |  |  |  |  | 79.3817 |  | 23292.8538
2017-09-04 | 16:30 | 1.7405 | 0 | 0 | 1.5 | 79.3767 | 0 | 23291.3943
2017-09-04 | 16:32 |  |  |  |  | 79.3955 |  | 23296.8993
2017-09-04 | 16:34 |  |  |  |  | 79.3728 |  | 23290.2617
2017-09-04 | 16:36 |  |  |  |  | 79.3249 |  | 23276.1871
2017-09-04 | 16:38 |  |  |  |  | 79.2982 |  | 23268.3517
2017-09-04 | 16:40 |  |  |  |  | 79.2642 |  | 23258.376
2017-09-04 | 16:42 |  |  |  |  | 79.2749 |  | 23261.5101
2017-09-04 | 16:44 |  |  |  |  | 79.3578 |  | 23285.8515
2017-09-04 | 16:45 | 1.7327 | 0 | 0 | 1.5 | 79.3767 | 0 | 23291.4011
2017-09-04 | 16:46 |  |  |  |  | 79.3796 |  | 23292.2382
2017-09-04 | 16:48 |  |  |  |  | 79.3647 |  | 23287.8752
2017-09-04 | 16:50 |  |  |  |  | 79.3589 |  | 23286.178
2017-09-04 | 16:52 |  |  |  |  | 79.4141 |  | 23302.3551
2017-09-04 | 16:54 |  |  |  |  | 79.4176 |  | 23303.3982
2017-09-04 | 16:56 |  |  |  |  | 79.4283 |  | 23306.5232
2017-09-04 | 16:58 |  |  |  |  | 79.4785 |  | 23321.256
2017-09-04 | 17:00 | 1.7343 | 0 | 0 | 1.5 | 79.4629 | 0 | 23316.6826
2017-09-04 | 17:02 |  |  |  |  | 79.4876 |  | 23323.9224
2017-09-04 | 17:04 |  |  |  |  | 79.468 |  | 23318.1958
2017-09-04 | 17:06 |  |  |  |  | 79.4656 |  | 23317.4907
2017-09-04 | 17:08 |  |  |  |  | 79.4823 |  | 23322.3821
2017-09-04 | 17:10 |  |  |  |  | 79.4125 |  | 23301.8938
2017-09-04 | 17:12 |  |  |  |  | 79.3989 |  | 23297.9111
2017-09-04 | 17:14 |  |  |  |  | 79.3362 |  | 23279.5025
2017-09-04 | 17:15 | 1.7694 | 0 | 0 | 1.5 | 79.3483 | 0 | 23283.0486
2017-09-04 | 17:16 |  |  |  |  | 79.3341 |  | 23278.8981
2017-09-04 | 17:18 |  |  |  |  | 79.2917 |  | 23266.4397
2017-09-04 | 17:20 |  |  |  |  | 79.275 |  | 23261.5482
2017-09-04 | 17:22 |  |  |  |  | 79.2316 |  | 23248.817
2017-09-04 | 17:24 |  |  |  |  | 79.1405 |  | 23222.0847
2017-09-04 | 17:26 |  |  |  |  | 79.12 |  | 23216.056
2017-09-04 | 17:28 |  |  |  |  | 79.0519 |  | 23196.087
2017-09-04 | 17:30 | 1.7561 | 0 | 0 | 1.5 | 79.0243 | 0 | 23187.976
2017-09-04 | 17:32 |  |  |  |  | 78.9786 |  | 23174.5754
2017-09-04 | 17:34 |  |  |  |  | 78.9364 |  | 23162.1933
2017-09-04 | 17:36 |  |  |  |  | 78.8902 |  | 23148.6516
2017-09-04 | 17:38 |  |  |  |  | 78.8472 |  | 23136.0095
2017-09-04 | 17:40 |  |  |  |  | 78.8259 |  | 23129.7703
2017-09-04 | 17:42 |  |  |  |  | 78.8157 |  | 23126.7639
2017-09-04 | 17:44 |  |  |  |  | 78.7627 |  | 23111.2163
2017-09-04 | 17:45 | 1.746 | 0 | 0 | 1.5 | 78.7741 | 0 | 23114.5652
2017-09-04 | 17:46 |  |  |  |  | 78.7414 |  | 23104.9859
2017-09-04 | 17:48 |  |  |  |  | 78.722 |  | 23099.2863
2017-09-04 | 17:50 |  |  |  |  | 78.6979 |  | 23092.2256
2017-09-04 | 17:52 |  |  |  |  | 78.6254 |  | 23070.9288
2017-09-04 | 17:54 |  |  |  |  | 78.6031 |  | 23064.3986
2017-09-04 | 17:56 |  |  |  |  | 78.5862 |  | 23059.4264
2017-09-04 | 17:58 |  |  |  |  | 78.5473 |  | 23048.0206
2017-09-04 | 18:00 | 1.7522 | 0 | 0 | 1.5 | 78.482 | 0 | 23028.8482
2017-09-04 | 18:02 |  |  |  |  | 78.4567 |  | 23021.4362
2017-09-04 | 18:04 |  |  |  |  | 78.4549 |  | 23020.9169
2017-09-04 | 18:06 |  |  |  |  | 78.4254 |  | 23012.2666
2017-09-04 | 18:08 |  |  |  |  | 78.3772 |  | 22998.1201
2017-09-04 | 18:10 |  |  |  |  | 78.3247 |  | 22982.7045
2017-09-04 | 18:12 |  |  |  |  | 78.2847 |  | 22970.9762
2017-09-04 | 18:14 |  |  |  |  | 78.2813 |  | 22969.9621
2017-09-04 | 18:15 | 1.7624 | 0 | 0 | 1.5 | 78.2828 | 0 | 22970.4055
2017-09-04 | 18:16 |  |  |  |  | 78.26 |  | 22963.7071
2017-09-04 | 18:18 |  |  |  |  | 78.2644 |  | 22965.0035
2017-09-04 | 18:20 |  |  |  |  | 78.2061 |  | 22947.9133
2017-09-04 | 18:22 |  |  |  |  | 78.1654 |  | 22935.9496
2017-09-04 | 18:24 |  |  |  |  | 78.1583 |  | 22933.8836
2017-09-04 | 18:26 |  |  |  |  | 78.1016 |  | 22917.2277
2017-09-04 | 18:28 |  |  |  |  | 78.0618 |  | 22905.5754
2017-09-04 | 18:30 | 1.7522 | 0 | 0 | 1.5 | 78.0309 | 0 | 22896.4976
2017-09-04 | 18:32 |  |  |  |  | 77.9889 |  | 22884.1712
2017-09-04 | 18:34 |  |  |  |  | 77.972 |  | 22879.2237
2017-09-04 | 18:36 |  |  |  |  | 77.9448 |  | 22871.2272
2017-09-04 | 18:38 |  |  |  |  | 77.8817 |  | 22852.7157
2017-09-04 | 18:40 |  |  |  |  | 77.8708 |  | 22849.5164
2017-09-04 | 18:42 |  |  |  |  | 77.8516 |  | 22843.8885
2017-09-04 | 18:44 |  |  |  |  | 77.7928 |  | 22826.6393
2017-09-04 | 18:45 | 1.7452 | 0 | 0 | 1.5 | 77.8159 | 0 | 22833.4204
2017-09-04 | 18:46 |  |  |  |  | 77.781 |  | 22823.156
2017-09-04 | 18:48 |  |  |  |  | 77.7672 |  | 22819.1064
2017-09-04 | 18:50 |  |  |  |  | 77.755 |  | 22815.5512
2017-09-04 | 18:52 |  |  |  |  | 77.705 |  | 22800.8789
2017-09-04 | 18:54 |  |  |  |  | 77.6871 |  | 22795.6268
2017-09-04 | 18:56 |  |  |  |  | 77.6664 |  | 22789.5467
2017-09-04 | 18:58 |  |  |  |  | 77.6328 |  | 22779.6831
2017-09-04 | 19:00 | 1.7507 | 0 | 0 | 1.5 | 77.6352 | 0 | 22780.377
2017-09-04 | 19:02 |  |  |  |  | 77.613 |  | 22773.8782
2017-09-04 | 19:04 |  |  |  |  | 77.5761 |  | 22763.0495
2017-09-04 | 19:06 |  |  |  |  | 77.539 |  | 22752.1471
2017-09-04 | 19:08 |  |  |  |  | 77.5159 |  | 22745.3886
2017-09-04 | 19:10 |  |  |  |  | 77.4782 |  | 22734.3272
2017-09-04 | 19:12 |  |  |  |  | 77.4663 |  | 22730.8284
2017-09-04 | 19:14 |  |  |  |  | 77.4529 |  | 22726.8815
2017-09-04 | 19:15 | 1.7569 | 0 | 0 | 1.5 | 77.426 | 0 | 22719.0147
2017-09-04 | 19:16 |  |  |  |  | 77.4175 |  | 22716.5164
2017-09-04 | 19:18 |  |  |  |  | 77.3846 |  | 22706.8655
2017-09-04 | 19:20 |  |  |  |  | 77.378 |  | 22704.9066
2017-09-04 | 19:22 |  |  |  |  | 77.3033 |  | 22682.9989
2017-09-04 | 19:24 |  |  |  |  | 77.3086 |  | 22684.5614
2017-09-04 | 19:26 |  |  |  |  | 77.2656 |  | 22671.9376
2017-09-04 | 19:28 |  |  |  |  | 77.2388 |  | 22664.0663
2017-09-04 | 19:30 | 1.7483 | 0 | 0 | 1.5 | 77.1675 | 0 | 22643.1569
2017-09-04 | 19:32 |  |  |  |  | 77.133 |  | 22633.0269
2017-09-04 | 19:34 |  |  |  |  | 77.1107 |  | 22626.4878
2017-09-04 | 19:36 |  |  |  |  | 77.1267 |  | 22631.1645
2017-09-04 | 19:38 |  |  |  |  | 77.0626 |  | 22612.3727
2017-09-04 | 19:40 |  |  |  |  | 77.0591 |  | 22611.3475
2017-09-04 | 19:42 |  |  |  |  | 77.0441 |  | 22606.9508
2017-09-04 | 19:44 |  |  |  |  | 77.0197 |  | 22599.7847
2017-09-04 | 19:45 | 1.7436 | 0 | 0 | 1.5 | 77.0108 | 0 | 22597.1564
2017-09-04 | 19:46 |  |  |  |  | 76.9782 |  | 22587.6109
2017-09-04 | 19:48 |  |  |  |  | 76.9519 |  | 22579.9008
2017-09-04 | 19:50 |  |  |  |  | 76.9174 |  | 22569.764
2017-09-04 | 19:52 |  |  |  |  | 76.8613 |  | 22553.2962
2017-09-04 | 19:54 |  |  |  |  | 76.8413 |  | 22547.4467
2017-09-04 | 19:56 |  |  |  |  | 76.8246 |  | 22542.5306
2017-09-04 | 19:58 |  |  |  |  | 76.8006 |  | 22535.4942
2017-09-04 | 20:00 | 1.7873 | 0 | 0 | 1.5 | 76.7397 | 0 | 22517.634
2017-09-04 | 20:02 |  |  |  |  | 76.7382 |  | 22517.1775
2017-09-04 | 20:04 |  |  |  |  | 76.7117 |  | 22509.4113
2017-09-04 | 20:06 |  |  |  |  | 76.6743 |  | 22498.4195
2017-09-04 | 20:08 |  |  |  |  | 76.6408 |  | 22488.5873
2017-09-04 | 20:10 |  |  |  |  | 76.6458 |  | 22490.0559
2017-09-04 | 20:12 |  |  |  |  | 76.5696 |  | 22467.7025
2017-09-04 | 20:14 |  |  |  |  | 76.5584 |  | 22464.4093
2017-09-04 | 20:15 | 1.7577 | 0 | 0 | 1.5 | 76.5497 | 0 | 22461.8773
2017-09-04 | 20:16 |  |  |  |  | 76.5359 |  | 22457.8054
2017-09-04 | 20:18 |  |  |  |  | 76.5138 |  | 22451.3265
2017-09-04 | 20:20 |  |  |  |  | 76.496 |  | 22446.1149
2017-09-04 | 20:22 |  |  |  |  | 76.4823 |  | 22442.0897
2017-09-04 | 20:24 |  |  |  |  | 76.4489 |  | 22432.3044
2017-09-04 | 20:26 |  |  |  |  | 76.4155 |  | 22422.4857
2017-09-04 | 20:28 |  |  |  |  | 76.4095 |  | 22420.7395
2017-09-04 | 20:30 | 1.7608 | 0 | 0 | 1.5 | 76.3851 | 0 | 22413.5758
2017-09-04 | 20:32 |  |  |  |  | 76.3528 |  | 22404.1015
2017-09-04 | 20:34 |  |  |  |  | 76.3819 |  | 22412.6265
2017-09-04 | 20:36 |  |  |  |  | 76.3147 |  | 22392.926
2017-09-04 | 20:38 |  |  |  |  | 76.3059 |  | 22390.3315
2017-09-04 | 20:40 |  |  |  |  | 76.2696 |  | 22379.6886
2017-09-04 | 20:42 |  |  |  |  | 76.2455 |  | 22372.6123
2017-09-04 | 20:44 |  |  |  |  | 76.2246 |  | 22366.4714
2017-09-04 | 20:45 | 1.7639 | 0 | 0 | 1.5 | 76.2264 | 0 | 22367.0154
2017-09-04 | 20:46 |  |  |  |  | 76.1885 |  | 22355.8871
2017-09-04 | 20:48 |  |  |  |  | 76.1761 |  | 22352.2515
2017-09-04 | 20:50 |  |  |  |  | 76.1323 |  | 22339.3991
2017-09-04 | 20:52 |  |  |  |  | 76.1248 |  | 22337.2007
2017-09-04 | 20:54 |  |  |  |  | 76.0997 |  | 22329.8175
2017-09-04 | 20:56 |  |  |  |  | 76.0633 |  | 22319.1569
2017-09-04 | 20:58 |  |  |  |  | 76.052 |  | 22315.8391
2017-09-04 | 21:00 | 1.7678 | 0 | 0 | 1.5 | 76.0333 | 0 | 22310.332
2017-09-04 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-04 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-04 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-05 | 5:04 |  |  |  |  | 99.9056 |  | 29315.1669
2017-09-05 | 5:06 |  |  |  |  | 98.6045 |  | 28933.382
2017-09-05 | 5:08 |  |  |  |  | 96.6245 |  | 28352.3993
2017-09-05 | 5:10 |  |  |  |  | 95.1509 |  | 27920.002
2017-09-05 | 5:12 |  |  |  |  | 93.9046 |  | 27554.3067
2017-09-05 | 5:14 |  |  |  |  | 92.8894 |  | 27256.3963
2017-09-05 | 5:15 | 2.1204 | 0 | 0 | 1.5 | 92.3093 | 0 | 27086.2004
2017-09-05 | 5:16 |  |  |  |  | 91.8681 |  | 26956.7218
2017-09-05 | 5:18 |  |  |  |  | 90.9993 |  | 26701.7917
2017-09-05 | 5:20 |  |  |  |  | 90.3536 |  | 26512.3143
2017-09-05 | 5:22 |  |  |  |  | 89.7431 |  | 26333.1973
2017-09-05 | 5:24 |  |  |  |  | 89.2208 |  | 26179.9416
2017-09-05 | 5:26 |  |  |  |  | 88.6907 |  | 26024.3845
2017-09-05 | 5:28 |  |  |  |  | 88.1801 |  | 25874.5561
2017-09-05 | 5:30 | 1.884 | 0 | 0 | 1.5 | 87.7381 | 0 | 25744.8604
2017-09-05 | 5:32 |  |  |  |  | 87.3497 |  | 25630.8956
2017-09-05 | 5:34 |  |  |  |  | 86.9776 |  | 25521.7129
2017-09-05 | 5:36 |  |  |  |  | 86.5652 |  | 25400.7144
2017-09-05 | 5:38 |  |  |  |  | 86.1011 |  | 25264.5219
2017-09-05 | 5:40 |  |  |  |  | 85.6796 |  | 25140.8391
2017-09-05 | 5:42 |  |  |  |  | 85.2432 |  | 25012.7954
2017-09-05 | 5:44 |  |  |  |  | 84.8045 |  | 24884.0712
2017-09-05 | 5:45 | 1.8989 | 0 | 0 | 1.5 | 84.5911 | 0 | 24821.453
2017-09-05 | 5:46 |  |  |  |  | 84.3967 |  | 24764.4116
2017-09-05 | 5:48 |  |  |  |  | 83.961 |  | 24636.5648
2017-09-05 | 5:50 |  |  |  |  | 83.5686 |  | 24521.4205
2017-09-05 | 5:52 |  |  |  |  | 83.1774 |  | 24406.6119
2017-09-05 | 5:54 |  |  |  |  | 82.8161 |  | 24300.6102
2017-09-05 | 5:56 |  |  |  |  | 82.4795 |  | 24201.8463
2017-09-05 | 5:58 |  |  |  |  | 82.1386 |  | 24101.8041
2017-09-05 | 6:00 | 1.8669 | 0 | 0 | 1.5 | 81.8106 | 0 | 24005.5607
2017-09-05 | 6:02 |  |  |  |  | 81.5002 |  | 23914.4934
2017-09-05 | 6:04 |  |  |  |  | 81.1901 |  | 23823.4842
2017-09-05 | 6:06 |  |  |  |  | 80.972 |  | 23759.5027
2017-09-05 | 6:08 |  |  |  |  | 80.7364 |  | 23690.3633
2017-09-05 | 6:10 |  |  |  |  | 80.5077 |  | 23623.2544
2017-09-05 | 6:12 |  |  |  |  | 80.2927 |  | 23560.1796
2017-09-05 | 6:14 |  |  |  |  | 80.0941 |  | 23501.8865
2017-09-05 | 6:15 | 1.8037 | 0 | 0 | 1.5 | 80.0164 | 0 | 23479.0921
2017-09-05 | 6:16 |  |  |  |  | 79.9255 |  | 23452.4317
2017-09-05 | 6:18 |  |  |  |  | 79.7383 |  | 23397.4855
2017-09-05 | 6:20 |  |  |  |  | 79.5857 |  | 23352.7276
2017-09-05 | 6:22 |  |  |  |  | 79.4553 |  | 23314.4505
2017-09-05 | 6:24 |  |  |  |  | 79.3127 |  | 23272.6049
2017-09-05 | 6:26 |  |  |  |  | 79.1786 |  | 23233.2512
2017-09-05 | 6:28 |  |  |  |  | 79.0576 |  | 23197.7548
2017-09-05 | 6:30 | 1.7889 | 0 | 0 | 1.5 | 78.9398 | 0 | 23163.1804
2017-09-05 | 6:32 |  |  |  |  | 78.8106 |  | 23125.2818
2017-09-05 | 6:34 |  |  |  |  | 78.6948 |  | 23091.3142
2017-09-05 | 6:36 |  |  |  |  | 78.5567 |  | 23050.7717
2017-09-05 | 6:38 |  |  |  |  | 78.4274 |  | 23012.8396
2017-09-05 | 6:40 |  |  |  |  | 78.2847 |  | 22970.9583
2017-09-05 | 6:42 |  |  |  |  | 78.1709 |  | 22937.5773
2017-09-05 | 6:44 |  |  |  |  | 78.0589 |  | 22904.7224
2017-09-05 | 6:45 | 1.7834 | 0 | 0 | 1.5 | 78.0136 | 0 | 22891.4245
2017-09-05 | 6:46 |  |  |  |  | 77.9512 |  | 22873.0987
2017-09-05 | 6:48 |  |  |  |  | 77.8296 |  | 22837.4342
2017-09-05 | 6:50 |  |  |  |  | 77.7136 |  | 22803.3839
2017-09-05 | 6:52 |  |  |  |  | 77.6182 |  | 22775.4072
2017-09-05 | 6:54 |  |  |  |  | 77.5282 |  | 22748.9907
2017-09-05 | 6:56 |  |  |  |  | 77.4422 |  | 22723.7673
2017-09-05 | 6:58 |  |  |  |  | 77.368 |  | 22701.9896
2017-09-05 | 7:00 | 1.7725 | 0 | 0 | 1.5 | 77.292 | 0 | 22679.6744
2017-09-05 | 7:02 |  |  |  |  | 77.2159 |  | 22657.3413
2017-09-05 | 7:04 |  |  |  |  | 77.1669 |  | 22642.96
2017-09-05 | 7:06 |  |  |  |  | 77.0669 |  | 22613.6242
2017-09-05 | 7:08 |  |  |  |  | 77.0256 |  | 22601.4994
2017-09-05 | 7:10 |  |  |  |  | 76.9777 |  | 22587.4697
2017-09-05 | 7:12 |  |  |  |  | 76.9344 |  | 22574.754
2017-09-05 | 7:14 |  |  |  |  | 76.8753 |  | 22557.4221
2017-09-05 | 7:15 | 1.7132 | 0 | 0 | 1.5 | 76.9295 | 0 | 22573.3057
2017-09-05 | 7:16 |  |  |  |  | 76.9565 |  | 22581.2441
2017-09-05 | 7:18 |  |  |  |  | 77.0237 |  | 22600.9399
2017-09-05 | 7:20 |  |  |  |  | 77.0367 |  | 22604.7568
2017-09-05 | 7:22 |  |  |  |  | 77.0278 |  | 22602.1512
2017-09-05 | 7:24 |  |  |  |  | 76.9978 |  | 22593.3418
2017-09-05 | 7:26 |  |  |  |  | 76.9936 |  | 22592.1241
2017-09-05 | 7:28 |  |  |  |  | 76.9771 |  | 22587.2729
2017-09-05 | 7:30 | 1.7538 | 0 | 0 | 1.5 | 76.9447 | 0 | 22577.7696
2017-09-05 | 7:32 |  |  |  |  | 76.9378 |  | 22575.7435
2017-09-05 | 7:34 |  |  |  |  | 76.9514 |  | 22579.7285
2017-09-05 | 7:36 |  |  |  |  | 76.9323 |  | 22574.1496
2017-09-05 | 7:38 |  |  |  |  | 76.8909 |  | 22561.9778
2017-09-05 | 7:40 |  |  |  |  | 76.897 |  | 22563.7777
2017-09-05 | 7:42 |  |  |  |  | 76.9028 |  | 22565.4702
2017-09-05 | 7:44 |  |  |  |  | 76.9259 |  | 22572.2534
2017-09-05 | 7:45 | 1.7429 | 0 | 0 | 1.5 | 76.9341 | 0 | 22574.6554
2017-09-05 | 7:46 |  |  |  |  | 76.9325 |  | 22574.1898
2017-09-05 | 7:48 |  |  |  |  | 76.9443 |  | 22577.6531
2017-09-05 | 7:50 |  |  |  |  | 76.9538 |  | 22580.4424
2017-09-05 | 7:52 |  |  |  |  | 76.9424 |  | 22577.0956
2017-09-05 | 7:54 |  |  |  |  | 76.9216 |  | 22570.9975
2017-09-05 | 7:56 |  |  |  |  | 76.967 |  | 22584.3154
2017-09-05 | 7:58 |  |  |  |  | 76.9694 |  | 22585.0272
2017-09-05 | 8:00 | 1.7397 | 0 | 0 | 1.5 | 76.9577 | 0 | 22581.5754
2017-09-05 | 8:02 |  |  |  |  | 76.9803 |  | 22588.2221
2017-09-05 | 8:04 |  |  |  |  | 76.9854 |  | 22589.7286
2017-09-05 | 8:06 |  |  |  |  | 76.9985 |  | 22593.5499
2017-09-05 | 8:08 |  |  |  |  | 77.0231 |  | 22600.7764
2017-09-05 | 8:10 |  |  |  |  | 77.0587 |  | 22611.2378
2017-09-05 | 8:12 |  |  |  |  | 77.0821 |  | 22618.104
2017-09-05 | 8:14 |  |  |  |  | 77.1041 |  | 22624.5603
2017-09-05 | 8:15 | 1.7031 | 0 | 0 | 1.5 | 77.1599 | 0 | 22640.9139
2017-09-05 | 8:16 |  |  |  |  | 77.1738 |  | 22644.9882
2017-09-05 | 8:18 |  |  |  |  | 77.2369 |  | 22663.5021
2017-09-05 | 8:20 |  |  |  |  | 77.2801 |  | 22676.1844
2017-09-05 | 8:22 |  |  |  |  | 77.3433 |  | 22694.7361
2017-09-05 | 8:24 |  |  |  |  | 77.395 |  | 22709.892
2017-09-05 | 8:26 |  |  |  |  | 77.4891 |  | 22737.5153
2017-09-05 | 8:28 |  |  |  |  | 77.5243 |  | 22747.8446
2017-09-05 | 8:30 | 1.739 | 0 | 0 | 1.5 | 77.5089 | 0 | 22743.3381
2017-09-05 | 8:32 |  |  |  |  | 77.5246 |  | 22747.9429
2017-09-05 | 8:34 |  |  |  |  | 77.5828 |  | 22765.0064
2017-09-05 | 8:36 |  |  |  |  | 77.599 |  | 22769.7499
2017-09-05 | 8:38 |  |  |  |  | 77.6427 |  | 22782.5956
2017-09-05 | 8:40 |  |  |  |  | 77.7392 |  | 22810.8948
2017-09-05 | 8:42 |  |  |  |  | 77.7892 |  | 22825.5627
2017-09-05 | 8:44 |  |  |  |  | 77.7634 |  | 22817.9957
2017-09-05 | 8:45 | 1.7468 | 0 | 0 | 1.5 | 77.8028 | 0 | 22829.5498
2017-09-05 | 8:46 |  |  |  |  | 77.8168 |  | 22833.6801
2017-09-05 | 8:48 |  |  |  |  | 77.8094 |  | 22831.4885
2017-09-05 | 8:50 |  |  |  |  | 77.7966 |  | 22827.7587
2017-09-05 | 8:52 |  |  |  |  | 77.8286 |  | 22837.1455
2017-09-05 | 8:54 |  |  |  |  | 77.8623 |  | 22847.0202
2017-09-05 | 8:56 |  |  |  |  | 77.8353 |  | 22839.1044
2017-09-05 | 8:58 |  |  |  |  | 77.8813 |  | 22852.6127
2017-09-05 | 9:00 | 1.7358 | 0 | 0 | 1.5 | 77.9307 | 0 | 22867.0878
2017-09-05 | 9:02 |  |  |  |  | 77.9387 |  | 22869.4429
2017-09-05 | 9:04 |  |  |  |  | 77.9765 |  | 22880.5289
2017-09-05 | 9:06 |  |  |  |  | 78.0081 |  | 22889.8059
2017-09-05 | 9:08 |  |  |  |  | 78.0598 |  | 22904.9618
2017-09-05 | 9:10 |  |  |  |  | 78.1309 |  | 22925.8422
2017-09-05 | 9:12 |  |  |  |  | 78.1877 |  | 22942.516
2017-09-05 | 9:14 |  |  |  |  | 78.2471 |  | 22959.9486
2017-09-05 | 9:15 | 1.7202 | 0 | 0 | 1.5 | 78.3038 | 0 | 22976.5707
2017-09-05 | 9:16 |  |  |  |  | 78.3127 |  | 22979.1787
2017-09-05 | 9:18 |  |  |  |  | 78.319 |  | 22981.0279
2017-09-05 | 9:20 |  |  |  |  | 78.4114 |  | 23008.1383
2017-09-05 | 9:22 |  |  |  |  | 78.4304 |  | 23013.717
2017-09-05 | 9:24 |  |  |  |  | 78.4684 |  | 23024.8726
2017-09-05 | 9:26 |  |  |  |  | 78.5702 |  | 23054.7366
2017-09-05 | 9:28 |  |  |  |  | 78.5983 |  | 23062.9972
2017-09-05 | 9:30 | 1.7093 | 0 | 0 | 1.5 | 78.679 | 0 | 23086.6757
2017-09-05 | 9:32 |  |  |  |  | 78.7793 |  | 23116.1077
2017-09-05 | 9:34 |  |  |  |  | 78.8953 |  | 23150.1425
2017-09-05 | 9:36 |  |  |  |  | 79.0579 |  | 23197.8511
2017-09-05 | 9:38 |  |  |  |  | 79.1976 |  | 23238.8322
2017-09-05 | 9:40 |  |  |  |  | 79.299 |  | 23268.5999
2017-09-05 | 9:42 |  |  |  |  | 79.3521 |  | 23284.1657
2017-09-05 | 9:44 |  |  |  |  | 79.382 |  | 23292.9548
2017-09-05 | 9:45 | 1.7429 | 0 | 0 | 1.5 | 79.3784 | 0 | 23291.8914
2017-09-05 | 9:46 |  |  |  |  | 79.4117 |  | 23301.6588
2017-09-05 | 9:48 |  |  |  |  | 79.4709 |  | 23319.0241
2017-09-05 | 9:50 |  |  |  |  | 79.6502 |  | 23371.6353
2017-09-05 | 9:52 |  |  |  |  | 79.8096 |  | 23418.4149
2017-09-05 | 9:54 |  |  |  |  | 79.958 |  | 23461.9685
2017-09-05 | 9:56 |  |  |  |  | 80.0034 |  | 23475.2843
2017-09-05 | 9:58 |  |  |  |  | 80.0853 |  | 23499.321
2017-09-05 | 10:00 | 1.7304 | 0 | 0 | 1.5 | 80.1579 | 0 | 23520.6242
2017-09-05 | 10:02 |  |  |  |  | 80.2065 |  | 23534.889
2017-09-05 | 10:04 |  |  |  |  | 80.2846 |  | 23557.8019
2017-09-05 | 10:06 |  |  |  |  | 80.4008 |  | 23591.8837
2017-09-05 | 10:08 |  |  |  |  | 80.5524 |  | 23636.3886
2017-09-05 | 10:10 |  |  |  |  | 80.6481 |  | 23664.4506
2017-09-05 | 10:12 |  |  |  |  | 80.7164 |  | 23684.4979
2017-09-05 | 10:14 |  |  |  |  | 80.7269 |  | 23687.5763
2017-09-05 | 10:15 | 1.7351 | 0 | 0 | 1.5 | 80.7541 | 0 | 23695.5502
2017-09-05 | 10:16 |  |  |  |  | 80.7356 |  | 23690.1171
2017-09-05 | 10:18 |  |  |  |  | 80.8052 |  | 23710.5609
2017-09-05 | 10:20 |  |  |  |  | 80.923 |  | 23745.1194
2017-09-05 | 10:22 |  |  |  |  | 81.019 |  | 23773.2997
2017-09-05 | 10:24 |  |  |  |  | 81.1053 |  | 23798.6035
2017-09-05 | 10:26 |  |  |  |  | 81.0717 |  | 23788.749
2017-09-05 | 10:28 |  |  |  |  | 81.0899 |  | 23794.1061
2017-09-05 | 10:30 | 1.721 | 0 | 0 | 1.5 | 81.1146 | 0 | 23801.3327
2017-09-05 | 10:32 |  |  |  |  | 81.2748 |  | 23848.3584
2017-09-05 | 10:34 |  |  |  |  | 81.4353 |  | 23895.4446
2017-09-05 | 10:36 |  |  |  |  | 81.5384 |  | 23925.6868
2017-09-05 | 10:38 |  |  |  |  | 81.5711 |  | 23935.2776
2017-09-05 | 10:40 |  |  |  |  | 81.6416 |  | 23955.9739
2017-09-05 | 10:42 |  |  |  |  | 81.6332 |  | 23953.5138
2017-09-05 | 10:44 |  |  |  |  | 81.5318 |  | 23923.7573
2017-09-05 | 10:45 | 1.7475 | 0 | 0 | 1.5 | 81.5516 | 0 | 23929.5777
2017-09-05 | 10:46 |  |  |  |  | 81.5931 |  | 23941.7606
2017-09-05 | 10:48 |  |  |  |  | 81.6811 |  | 23967.5614
2017-09-05 | 10:50 |  |  |  |  | 81.7705 |  | 23993.7943
2017-09-05 | 10:52 |  |  |  |  | 81.7974 |  | 24001.6969
2017-09-05 | 10:54 |  |  |  |  | 81.8764 |  | 24024.8604
2017-09-05 | 10:56 |  |  |  |  | 81.9488 |  | 24046.1214
2017-09-05 | 10:58 |  |  |  |  | 81.9274 |  | 24039.8529
2017-09-05 | 11:00 | 1.7522 | 0 | 0 | 1.5 | 81.9949 | 0 | 24059.634
2017-09-05 | 11:02 |  |  |  |  | 82.0965 |  | 24089.4555
2017-09-05 | 11:04 |  |  |  |  | 82.2703 |  | 24140.4481
2017-09-05 | 11:06 |  |  |  |  | 82.3987 |  | 24178.1363
2017-09-05 | 11:08 |  |  |  |  | 82.5099 |  | 24210.7518
2017-09-05 | 11:10 |  |  |  |  | 82.5954 |  | 24235.8631
2017-09-05 | 11:12 |  |  |  |  | 82.6133 |  | 24241.0926
2017-09-05 | 11:14 |  |  |  |  | 82.696 |  | 24265.3668
2017-09-05 | 11:15 | 1.707 | 0 | 0 | 1.5 | 82.7766 | 0 | 24289.0318
2017-09-05 | 11:16 |  |  |  |  | 82.8626 |  | 24314.2505
2017-09-05 | 11:18 |  |  |  |  | 83.0175 |  | 24359.6959
2017-09-05 | 11:20 |  |  |  |  | 83.0486 |  | 24368.8429
2017-09-05 | 11:22 |  |  |  |  | 83.0629 |  | 24373.034
2017-09-05 | 11:24 |  |  |  |  | 83.058 |  | 24371.6032
2017-09-05 | 11:26 |  |  |  |  | 83.1237 |  | 24390.8694
2017-09-05 | 11:28 |  |  |  |  | 83.2928 |  | 24440.4741
2017-09-05 | 11:30 | 1.7382 | 0 | 0 | 1.5 | 83.3882 | 0 | 24468.4778
2017-09-05 | 11:32 |  |  |  |  | 83.5189 |  | 24506.8198
2017-09-05 | 11:34 |  |  |  |  | 83.5995 |  | 24530.4827
2017-09-05 | 11:36 |  |  |  |  | 83.7274 |  | 24567.9985
2017-09-05 | 11:38 |  |  |  |  | 83.8153 |  | 24593.7926
2017-09-05 | 11:40 |  |  |  |  | 83.8095 |  | 24592.1001
2017-09-05 | 11:42 |  |  |  |  | 83.8317 |  | 24598.6169
2017-09-05 | 11:44 |  |  |  |  | 83.9408 |  | 24630.6414
2017-09-05 | 11:45 | 1.7202 | 0 | 0 | 1.5 | 83.9586 | 0 | 24635.8485
2017-09-05 | 11:46 |  |  |  |  | 84.0394 |  | 24659.5537
2017-09-05 | 11:48 |  |  |  |  | 84.1896 |  | 24703.6358
2017-09-05 | 11:50 |  |  |  |  | 84.3195 |  | 24741.7537
2017-09-05 | 11:52 |  |  |  |  | 84.4438 |  | 24778.2198
2017-09-05 | 11:54 |  |  |  |  | 84.6052 |  | 24825.5924
2017-09-05 | 11:56 |  |  |  |  | 84.5838 |  | 24819.3018
2017-09-05 | 11:58 |  |  |  |  | 84.5254 |  | 24802.1647
2017-09-05 | 12:00 | 1.7522 | 0 | 0 | 1.5 | 84.5212 | 0 | 24800.9467
2017-09-05 | 12:02 |  |  |  |  | 84.5853 |  | 24819.7294
2017-09-05 | 12:04 |  |  |  |  | 84.7902 |  | 24879.8781
2017-09-05 | 12:06 |  |  |  |  | 84.9711 |  | 24932.9417
2017-09-05 | 12:08 |  |  |  |  | 85.1535 |  | 24986.4731
2017-09-05 | 12:10 |  |  |  |  | 85.254 |  | 25015.9632
2017-09-05 | 12:12 |  |  |  |  | 85.2979 |  | 25028.8468
2017-09-05 | 12:14 |  |  |  |  | 85.3865 |  | 25054.8334
2017-09-05 | 12:15 | 1.6836 | 0 | 0 | 1.5 | 85.5043 | 0 | 25089.3964
2017-09-05 | 12:16 |  |  |  |  | 85.6084 |  | 25119.959
2017-09-05 | 12:18 |  |  |  |  | 85.7101 |  | 25149.7963
2017-09-05 | 12:20 |  |  |  |  | 85.7014 |  | 25147.2306
2017-09-05 | 12:22 |  |  |  |  | 85.7733 |  | 25168.3257
2017-09-05 | 12:24 |  |  |  |  | 85.8972 |  | 25204.6977
2017-09-05 | 12:26 |  |  |  |  | 86.0635 |  | 25253.4808
2017-09-05 | 12:28 |  |  |  |  | 86.1931 |  | 25291.5138
2017-09-05 | 12:30 | 1.7561 | 0 | 0 | 1.5 | 86.1688 | 0 | 25284.3747
2017-09-05 | 12:32 |  |  |  |  | 85.983 |  | 25229.8826
2017-09-05 | 12:34 |  |  |  |  | 85.6987 |  | 25146.4539
2017-09-05 | 12:36 |  |  |  |  | 85.4224 |  | 25065.3619
2017-09-05 | 12:38 |  |  |  |  | 85.1997 |  | 25000.0239
2017-09-05 | 12:40 |  |  |  |  | 84.8418 |  | 24895.0117
2017-09-05 | 12:42 |  |  |  |  | 84.4617 |  | 24783.4648
2017-09-05 | 12:44 |  |  |  |  | 84.0951 |  | 24675.903
2017-09-05 | 12:45 | 1.8279 | 0 | 0 | 1.5 | 83.9554 | 0 | 24634.9104
2017-09-05 | 12:46 |  |  |  |  | 83.8477 |  | 24603.2979
2017-09-05 | 12:48 |  |  |  |  | 83.7678 |  | 24579.8588
2017-09-05 | 12:50 |  |  |  |  | 83.6856 |  | 24555.7349
2017-09-05 | 12:52 |  |  |  |  | 83.6492 |  | 24545.072
2017-09-05 | 12:54 |  |  |  |  | 83.6804 |  | 24554.2349
2017-09-05 | 12:56 |  |  |  |  | 83.7041 |  | 24561.1862
2017-09-05 | 12:58 |  |  |  |  | 83.6885 |  | 24556.6058
2017-09-05 | 13:00 | 1.7156 | 0 | 0 | 1.5 | 83.8094 | 0 | 24592.0599
2017-09-05 | 13:02 |  |  |  |  | 84.0098 |  | 24650.87
2017-09-05 | 13:04 |  |  |  |  | 84.2015 |  | 24707.1326
2017-09-05 | 13:06 |  |  |  |  | 84.3684 |  | 24756.1126
2017-09-05 | 13:08 |  |  |  |  | 84.6203 |  | 24830.0272
2017-09-05 | 13:10 |  |  |  |  | 84.8478 |  | 24896.7714
2017-09-05 | 13:12 |  |  |  |  | 85.0128 |  | 24945.1739
2017-09-05 | 13:14 |  |  |  |  | 85.1073 |  | 24972.9155
2017-09-05 | 13:15 | 1.721 | 0 | 0 | 1.5 | 85.1476 | 0 | 24984.7269
2017-09-05 | 13:16 |  |  |  |  | 85.2314 |  | 25009.3367
2017-09-05 | 13:18 |  |  |  |  | 85.44 |  | 25070.5401
2017-09-05 | 13:20 |  |  |  |  | 85.6689 |  | 25137.7073
2017-09-05 | 13:22 |  |  |  |  | 85.9378 |  | 25216.6006
2017-09-05 | 13:24 |  |  |  |  | 86.1024 |  | 25264.9092
2017-09-05 | 13:26 |  |  |  |  | 86.1125 |  | 25267.8778
2017-09-05 | 13:28 |  |  |  |  | 85.9796 |  | 25228.8618
2017-09-05 | 13:30 | 1.7733 | 0 | 0 | 1.5 | 85.877 | 0 | 25198.7739
2017-09-05 | 13:32 |  |  |  |  | 85.754 |  | 25162.6687
2017-09-05 | 13:34 |  |  |  |  | 85.503 |  | 25089.0293
2017-09-05 | 13:36 |  |  |  |  | 85.1363 |  | 24981.4205
2017-09-05 | 13:38 |  |  |  |  | 84.716 |  | 24858.0846
2017-09-05 | 13:40 |  |  |  |  | 84.4478 |  | 24779.3926
2017-09-05 | 13:42 |  |  |  |  | 84.1809 |  | 24701.0724
2017-09-05 | 13:44 |  |  |  |  | 83.9053 |  | 24620.2179
2017-09-05 | 13:45 | 1.7959 | 0 | 0 | 1.5 | 83.8538 | 0 | 24605.1025
2017-09-05 | 13:46 |  |  |  |  | 83.7931 |  | 24587.2779
2017-09-05 | 13:48 |  |  |  |  | 83.6472 |  | 24544.479
2017-09-05 | 13:50 |  |  |  |  | 83.6031 |  | 24531.5259
2017-09-05 | 13:52 |  |  |  |  | 83.6526 |  | 24546.0638
2017-09-05 | 13:54 |  |  |  |  | 83.7635 |  | 24578.5965
2017-09-05 | 13:56 |  |  |  |  | 83.9512 |  | 24633.6769
2017-09-05 | 13:58 |  |  |  |  | 84.157 |  | 24694.0788
2017-09-05 | 14:00 | 1.6641 | 0 | 0 | 1.5 | 84.3573 | 0 | 24752.8532
2017-09-05 | 14:02 |  |  |  |  | 84.6122 |  | 24827.6431
2017-09-05 | 14:04 |  |  |  |  | 84.8781 |  | 24905.6455
2017-09-05 | 14:06 |  |  |  |  | 85.0934 |  | 24968.8234
2017-09-05 | 14:08 |  |  |  |  | 85.3202 |  | 25035.3973
2017-09-05 | 14:10 |  |  |  |  | 85.6239 |  | 25124.5013
2017-09-05 | 14:12 |  |  |  |  | 85.9623 |  | 25223.8025
2017-09-05 | 14:14 |  |  |  |  | 86.1017 |  | 25264.6988
2017-09-05 | 14:15 | 1.721 | 0 | 0 | 1.5 | 86.1426 | 0 | 25276.7138
2017-09-05 | 14:16 |  |  |  |  | 86.1027 |  | 25264.9788
2017-09-05 | 14:18 |  |  |  |  | 85.9584 |  | 25222.6473
2017-09-05 | 14:20 |  |  |  |  | 85.7344 |  | 25156.9287
2017-09-05 | 14:22 |  |  |  |  | 85.4702 |  | 25079.4075
2017-09-05 | 14:24 |  |  |  |  | 85.1411 |  | 24982.822
2017-09-05 | 14:26 |  |  |  |  | 84.9187 |  | 24917.5643
2017-09-05 | 14:28 |  |  |  |  | 84.6397 |  | 24835.7089
2017-09-05 | 14:30 | 1.7928 | 0 | 0 | 1.5 | 84.4021 | 0 | 24765.9964
2017-09-05 | 14:32 |  |  |  |  | 84.2598 |  | 24724.2383
2017-09-05 | 14:34 |  |  |  |  | 84.2769 |  | 24729.253
2017-09-05 | 14:36 |  |  |  |  | 84.3144 |  | 24740.2671
2017-09-05 | 14:38 |  |  |  |  | 84.4109 |  | 24768.571
2017-09-05 | 14:40 |  |  |  |  | 84.504 |  | 24795.8962
2017-09-05 | 14:42 |  |  |  |  | 84.623 |  | 24830.8154
2017-09-05 | 14:44 |  |  |  |  | 84.6291 |  | 24832.6018
2017-09-05 | 14:45 | 1.7195 | 0 | 0 | 1.5 | 84.7226 | 0 | 24860.0324
2017-09-05 | 14:46 |  |  |  |  | 84.8691 |  | 24903.0062
2017-09-05 | 14:48 |  |  |  |  | 85.2167 |  | 25005.0228
2017-09-05 | 14:50 |  |  |  |  | 85.5645 |  | 25107.0576
2017-09-05 | 14:52 |  |  |  |  | 85.8998 |  | 25205.47
2017-09-05 | 14:54 |  |  |  |  | 86.1848 |  | 25289.0757
2017-09-05 | 14:56 |  |  |  |  | 86.5636 |  | 25400.2464
2017-09-05 | 14:58 |  |  |  |  | 86.9011 |  | 25499.2612
2017-09-05 | 15:00 | 1.7062 | 0 | 0 | 1.5 | 87.0455 | 0 | 25541.6262
2017-09-05 | 15:02 |  |  |  |  | 87.198 |  | 25586.3931
2017-09-05 | 15:04 |  |  |  |  | 87.0955 |  | 25556.3052
2017-09-05 | 15:06 |  |  |  |  | 86.903 |  | 25499.8343
2017-09-05 | 15:08 |  |  |  |  | 86.7438 |  | 25453.104
2017-09-05 | 15:10 |  |  |  |  | 86.4936 |  | 25379.7043
2017-09-05 | 15:12 |  |  |  |  | 86.2435 |  | 25306.307
2017-09-05 | 15:14 |  |  |  |  | 85.897 |  | 25204.6305
2017-09-05 | 15:15 | 1.8747 | 0 | 0 | 1.5 | 85.6724 | 0 | 25138.7326
2017-09-05 | 15:16 |  |  |  |  | 85.5081 |  | 25090.5091
2017-09-05 | 15:18 |  |  |  |  | 85.1447 |  | 24983.8786
2017-09-05 | 15:20 |  |  |  |  | 84.8948 |  | 24910.5728
2017-09-05 | 15:22 |  |  |  |  | 84.6928 |  | 24851.2747
2017-09-05 | 15:24 |  |  |  |  | 84.4456 |  | 24778.7436
2017-09-05 | 15:26 |  |  |  |  | 84.2876 |  | 24732.3848
2017-09-05 | 15:28 |  |  |  |  | 84.2647 |  | 24725.6799
2017-09-05 | 15:30 | 1.7405 | 0 | 0 | 1.5 | 84.3532 | 0 | 24751.6264
2017-09-05 | 15:32 |  |  |  |  | 84.4613 |  | 24783.3486
2017-09-05 | 15:34 |  |  |  |  | 84.6885 |  | 24850.03
2017-09-05 | 15:36 |  |  |  |  | 84.8875 |  | 24908.4237
2017-09-05 | 15:38 |  |  |  |  | 85.1764 |  | 24993.1779
2017-09-05 | 15:40 |  |  |  |  | 85.5157 |  | 25092.75
2017-09-05 | 15:42 |  |  |  |  | 85.7675 |  | 25166.6312
2017-09-05 | 15:44 |  |  |  |  | 86.0513 |  | 25249.9144
2017-09-05 | 15:45 | 1.6586 | 0 | 0 | 1.5 | 86.1838 | 0 | 25288.7802
2017-09-05 | 15:46 |  |  |  |  | 86.3591 |  | 25340.232
2017-09-05 | 15:48 |  |  |  |  | 86.7171 |  | 25445.2619
2017-09-05 | 15:50 |  |  |  |  | 86.9992 |  | 25528.0463
2017-09-05 | 15:52 |  |  |  |  | 87.282 |  | 25611.034
2017-09-05 | 15:54 |  |  |  |  | 87.3695 |  | 25636.7184
2017-09-05 | 15:56 |  |  |  |  | 87.2527 |  | 25602.4354
2017-09-05 | 15:58 |  |  |  |  | 86.9042 |  | 25500.1612
2017-09-05 | 16:00 | 1.806 | 0 | 0 | 1.5 | 86.7751 | 0 | 25462.3051
2017-09-05 | 16:02 |  |  |  |  | 86.5879 |  | 25407.37
2017-09-05 | 16:04 |  |  |  |  | 86.4451 |  | 25365.4484
2017-09-05 | 16:06 |  |  |  |  | 86.14 |  | 25275.928
2017-09-05 | 16:08 |  |  |  |  | 85.7261 |  | 25154.4727
2017-09-05 | 16:10 |  |  |  |  | 85.467 |  | 25078.4673
2017-09-05 | 16:12 |  |  |  |  | 85.2325 |  | 25009.6366
2017-09-05 | 16:14 |  |  |  |  | 84.9162 |  | 24916.8343
2017-09-05 | 16:15 | 1.8209 | 0 | 0 | 1.5 | 84.8333 | 0 | 24892.5111
2017-09-05 | 16:16 |  |  |  |  | 84.7078 |  | 24855.6802
2017-09-05 | 16:18 |  |  |  |  | 84.4919 |  | 24792.3255
2017-09-05 | 16:20 |  |  |  |  | 84.4611 |  | 24783.297
2017-09-05 | 16:22 |  |  |  |  | 84.5229 |  | 24801.4215
2017-09-05 | 16:24 |  |  |  |  | 84.6627 |  | 24842.4586
2017-09-05 | 16:26 |  |  |  |  | 84.7669 |  | 24873.0257
2017-09-05 | 16:28 |  |  |  |  | 84.9239 |  | 24919.1022
2017-09-05 | 16:30 | 1.6773 | 0 | 0 | 1.5 | 85.137 | 0 | 24981.6174
2017-09-05 | 16:32 |  |  |  |  | 85.356 |  | 25045.89
2017-09-05 | 16:34 |  |  |  |  | 85.6323 |  | 25126.9705
2017-09-05 | 16:36 |  |  |  |  | 85.8332 |  | 25185.915
2017-09-05 | 16:38 |  |  |  |  | 86.1026 |  | 25264.9562
2017-09-05 | 16:40 |  |  |  |  | 86.3199 |  | 25328.7205
2017-09-05 | 16:42 |  |  |  |  | 86.5704 |  | 25402.2232
2017-09-05 | 16:44 |  |  |  |  | 86.6443 |  | 25423.9117
2017-09-05 | 16:45 | 1.7507 | 0 | 0 | 1.5 | 86.6599 | 0 | 25428.4942
2017-09-05 | 16:46 |  |  |  |  | 86.5372 |  | 25392.4805
2017-09-05 | 16:48 |  |  |  |  | 86.3754 |  | 25345.0182
2017-09-05 | 16:50 |  |  |  |  | 86.2574 |  | 25310.3971
2017-09-05 | 16:52 |  |  |  |  | 86.1226 |  | 25270.8215
2017-09-05 | 16:54 |  |  |  |  | 85.8235 |  | 25183.0676
2017-09-05 | 16:56 |  |  |  |  | 85.4425 |  | 25071.2654
2017-09-05 | 16:58 |  |  |  |  | 85.0812 |  | 24965.2661
2017-09-05 | 17:00 | 1.8552 | 0 | 0 | 1.5 | 84.7899 | 0 | 24879.7687
2017-09-05 | 17:02 |  |  |  |  | 84.5911 |  | 24821.4374
2017-09-05 | 17:04 |  |  |  |  | 84.344 |  | 24748.9377
2017-09-05 | 17:06 |  |  |  |  | 83.9376 |  | 24629.6763
2017-09-05 | 17:08 |  |  |  |  | 83.7348 |  | 24570.1698
2017-09-05 | 17:10 |  |  |  |  | 83.6067 |  | 24532.5869
2017-09-05 | 17:12 |  |  |  |  | 83.6206 |  | 24536.6861
2017-09-05 | 17:14 |  |  |  |  | 83.713 |  | 24563.774
2017-09-05 | 17:15 | 1.7015 | 0 | 0 | 1.5 | 83.7728 | 0 | 24581.3275
2017-09-05 | 17:16 |  |  |  |  | 83.8508 |  | 24604.2205
2017-09-05 | 17:18 |  |  |  |  | 84.0871 |  | 24673.5611
2017-09-05 | 17:20 |  |  |  |  | 84.0644 |  | 24666.8989
2017-09-05 | 17:22 |  |  |  |  | 84.0801 |  | 24671.4995
2017-09-05 | 17:24 |  |  |  |  | 84.1245 |  | 24684.5442
2017-09-05 | 17:26 |  |  |  |  | 84.1611 |  | 24695.2675
2017-09-05 | 17:28 |  |  |  |  | 84.1184 |  | 24682.7466
2017-09-05 | 17:30 | 1.7561 | 0 | 0 | 1.5 | 84.0942 | 0 | 24675.6454
2017-09-05 | 17:32 |  |  |  |  | 84.1412 |  | 24689.4224
2017-09-05 | 17:34 |  |  |  |  | 84.3591 |  | 24753.3702
2017-09-05 | 17:36 |  |  |  |  | 84.478 |  | 24788.2445
2017-09-05 | 17:38 |  |  |  |  | 84.6366 |  | 24834.789
2017-09-05 | 17:40 |  |  |  |  | 84.7012 |  | 24853.7618
2017-09-05 | 17:42 |  |  |  |  | 84.8333 |  | 24892.5246
2017-09-05 | 17:44 |  |  |  |  | 84.9331 |  | 24921.8044
2017-09-05 | 17:45 | 1.7273 | 0 | 0 | 1.5 | 84.9829 | 0 | 24936.4183
2017-09-05 | 17:46 |  |  |  |  | 85.0033 |  | 24942.3846
2017-09-05 | 17:48 |  |  |  |  | 85.0625 |  | 24959.7588
2017-09-05 | 17:50 |  |  |  |  | 84.9992 |  | 24941.1959
2017-09-05 | 17:52 |  |  |  |  | 84.9594 |  | 24929.503
2017-09-05 | 17:54 |  |  |  |  | 85.0042 |  | 24942.6621
2017-09-05 | 17:56 |  |  |  |  | 84.9971 |  | 24940.58
2017-09-05 | 17:58 |  |  |  |  | 84.9566 |  | 24928.6814
2017-09-05 | 18:00 | 1.7249 | 0 | 0 | 1.5 | 84.9581 | 0 | 24929.136
2017-09-05 | 18:02 |  |  |  |  | 84.8511 |  | 24897.7338
2017-09-05 | 18:04 |  |  |  |  | 84.7317 |  | 24862.7099
2017-09-05 | 18:06 |  |  |  |  | 84.6885 |  | 24850.0209
2017-09-05 | 18:08 |  |  |  |  | 84.6972 |  | 24852.5819
2017-09-05 | 18:10 |  |  |  |  | 84.6772 |  | 24846.6966
2017-09-05 | 18:12 |  |  |  |  | 84.6321 |  | 24833.4906
2017-09-05 | 18:14 |  |  |  |  | 84.5544 |  | 24810.6695
2017-09-05 | 18:15 | 1.7897 | 0 | 0 | 1.5 | 84.4799 | 0 | 24788.804
2017-09-05 | 18:16 |  |  |  |  | 84.4449 |  | 24778.5399
2017-09-05 | 18:18 |  |  |  |  | 84.3607 |  | 24753.8359
2017-09-05 | 18:20 |  |  |  |  | 84.3085 |  | 24738.5368
2017-09-05 | 18:22 |  |  |  |  | 84.1392 |  | 24688.8538
2017-09-05 | 18:24 |  |  |  |  | 83.9789 |  | 24641.7943
2017-09-05 | 18:26 |  |  |  |  | 83.8788 |  | 24612.4362
2017-09-05 | 18:28 |  |  |  |  | 83.8636 |  | 24607.979
2017-09-05 | 18:30 | 1.7748 | 0 | 0 | 1.5 | 83.8011 | 0 | 24589.6329
2017-09-05 | 18:32 |  |  |  |  | 83.7583 |  | 24577.0786
2017-09-05 | 18:34 |  |  |  |  | 83.6944 |  | 24558.3385
2017-09-05 | 18:36 |  |  |  |  | 83.5828 |  | 24525.5798
2017-09-05 | 18:38 |  |  |  |  | 83.3993 |  | 24471.7486
2017-09-05 | 18:40 |  |  |  |  | 83.2468 |  | 24427.0016
2017-09-05 | 18:42 |  |  |  |  | 83.1536 |  | 24399.6541
2017-09-05 | 18:44 |  |  |  |  | 83.1451 |  | 24397.1555
2017-09-05 | 18:45 | 1.7546 | 0 | 0 | 1.5 | 83.1172 | 0 | 24388.9621
2017-09-05 | 18:46 |  |  |  |  | 83.1268 |  | 24391.7761
2017-09-05 | 18:48 |  |  |  |  | 83.052 |  | 24369.8192
2017-09-05 | 18:50 |  |  |  |  | 83.0287 |  | 24362.9911
2017-09-05 | 18:52 |  |  |  |  | 82.8661 |  | 24315.2737
2017-09-05 | 18:54 |  |  |  |  | 82.716 |  | 24271.2298
2017-09-05 | 18:56 |  |  |  |  | 82.5778 |  | 24230.6783
2017-09-05 | 18:58 |  |  |  |  | 82.4563 |  | 24195.0384
2017-09-05 | 19:00 | 1.753 | 0 | 0 | 1.5 | 82.4351 | 0 | 24188.8262
2017-09-05 | 19:02 |  |  |  |  | 82.3965 |  | 24177.4873
2017-09-05 | 19:04 |  |  |  |  | 82.3799 |  | 24172.6158
2017-09-05 | 19:06 |  |  |  |  | 82.2569 |  | 24136.5194
2017-09-05 | 19:08 |  |  |  |  | 82.1277 |  | 24098.616
2017-09-05 | 19:10 |  |  |  |  | 82.0123 |  | 24064.7382
2017-09-05 | 19:12 |  |  |  |  | 81.8671 |  | 24022.1474
2017-09-05 | 19:14 |  |  |  |  | 81.7803 |  | 23996.6666
2017-09-05 | 19:15 | 1.7577 | 0 | 0 | 1.5 | 81.7788 | 0 | 23996.2456
2017-09-05 | 19:16 |  |  |  |  | 81.7294 |  | 23981.7323
2017-09-05 | 19:18 |  |  |  |  | 81.7639 |  | 23991.8714
2017-09-05 | 19:20 |  |  |  |  | 81.6789 |  | 23966.9323
2017-09-05 | 19:22 |  |  |  |  | 81.6127 |  | 23947.505
2017-09-05 | 19:24 |  |  |  |  | 81.5191 |  | 23920.0275
2017-09-05 | 19:26 |  |  |  |  | 81.3786 |  | 23878.8134
2017-09-05 | 19:28 |  |  |  |  | 81.2695 |  | 23846.8071
2017-09-05 | 19:30 | 1.7772 | 0 | 0 | 1.5 | 81.1886 | 0 | 23823.0546
2017-09-05 | 19:32 |  |  |  |  | 81.1183 |  | 23802.4272
2017-09-05 | 19:34 |  |  |  |  | 81.1047 |  | 23798.438
2017-09-05 | 19:36 |  |  |  |  | 81.0359 |  | 23778.2583
2017-09-05 | 19:38 |  |  |  |  | 80.9409 |  | 23750.3803
2017-09-05 | 19:40 |  |  |  |  | 80.8123 |  | 23712.636
2017-09-05 | 19:42 |  |  |  |  | 80.7249 |  | 23686.9918
2017-09-05 | 19:44 |  |  |  |  | 80.6211 |  | 23656.5412
2017-09-05 | 19:45 | 1.7694 | 0 | 0 | 1.5 | 80.5486 | 0 | 23635.2694
2017-09-05 | 19:46 |  |  |  |  | 80.5562 |  | 23637.4878
2017-09-05 | 19:48 |  |  |  |  | 80.5845 |  | 23645.7868
2017-09-05 | 19:50 |  |  |  |  | 80.5762 |  | 23643.3689
2017-09-05 | 19:52 |  |  |  |  | 80.532 |  | 23630.3912
2017-09-05 | 19:54 |  |  |  |  | 80.4053 |  | 23593.2111
2017-09-05 | 19:56 |  |  |  |  | 80.2462 |  | 23546.5234
2017-09-05 | 19:58 |  |  |  |  | 80.1489 |  | 23517.969
2017-09-05 | 20:00 | 1.7936 | 0 | 0 | 1.5 | 80.0503 | 0 | 23489.0499
2017-09-05 | 20:02 |  |  |  |  | 79.9779 |  | 23467.798
2017-09-05 | 20:04 |  |  |  |  | 79.9686 |  | 23465.0779
2017-09-05 | 20:06 |  |  |  |  | 80.1666 |  | 23523.1718
2017-09-05 | 20:08 |  |  |  |  | 80.1885 |  | 23529.5856
2017-09-05 | 20:10 |  |  |  |  | 80.127 |  | 23511.5597
2017-09-05 | 20:12 |  |  |  |  | 80.0666 |  | 23493.8204
2017-09-05 | 20:14 |  |  |  |  | 79.9702 |  | 23465.548
2017-09-05 | 20:15 | 1.7858 | 0 | 0 | 1.5 | 79.9121 | 0 | 23448.5007
2017-09-05 | 20:16 |  |  |  |  | 79.8557 |  | 23431.9522
2017-09-05 | 20:18 |  |  |  |  | 79.7905 |  | 23412.8159
2017-09-05 | 20:20 |  |  |  |  | 79.7022 |  | 23386.9121
2017-09-05 | 20:22 |  |  |  |  | 79.6741 |  | 23378.665
2017-09-05 | 20:24 |  |  |  |  | 79.6878 |  | 23382.6811
2017-09-05 | 20:26 |  |  |  |  | 79.6796 |  | 23380.2633
2017-09-05 | 20:28 |  |  |  |  | 79.6007 |  | 23357.1332
2017-09-05 | 20:30 | 1.7873 | 0 | 0 | 1.5 | 79.4546 | 0 | 23314.2556
2017-09-05 | 20:32 |  |  |  |  | 79.3679 |  | 23288.8019
2017-09-05 | 20:34 |  |  |  |  | 79.2417 |  | 23251.7785
2017-09-05 | 20:36 |  |  |  |  | 79.1782 |  | 23233.1573
2017-09-05 | 20:38 |  |  |  |  | 79.0686 |  | 23200.9808
2017-09-05 | 20:40 |  |  |  |  | 78.9813 |  | 23175.3656
2017-09-05 | 20:42 |  |  |  |  | 78.8945 |  | 23149.894
2017-09-05 | 20:44 |  |  |  |  | 78.8436 |  | 23134.9731
2017-09-05 | 20:45 | 1.728 | 0 | 0 | 1.5 | 78.8212 | 0 | 23128.3824
2017-09-05 | 20:46 |  |  |  |  | 78.8828 |  | 23146.4529
2017-09-05 | 20:48 |  |  |  |  | 78.9083 |  | 23153.955
2017-09-05 | 20:50 |  |  |  |  | 78.8448 |  | 23135.3112
2017-09-05 | 20:52 |  |  |  |  | 78.7413 |  | 23104.9413
2017-09-05 | 20:54 |  |  |  |  | 78.6585 |  | 23080.6648
2017-09-05 | 20:56 |  |  |  |  | 78.5637 |  | 23052.8404
2017-09-05 | 20:58 |  |  |  |  | 78.4793 |  | 23028.0759
2017-09-05 | 21:00 | 1.7663 | 0 | 0 | 1.5 | 78.4391 | 0 | 23016.2827
2017-09-05 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-05 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 5:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-06 | 5:04 |  |  |  |  | 100 |  | 29342.8571
2017-09-06 | 5:06 |  |  |  |  | 99.8 |  | 29284.1656
2017-09-06 | 5:08 |  |  |  |  | 99.2836 |  | 29132.6517
2017-09-06 | 5:10 |  |  |  |  | 98.8383 |  | 29001.9753
2017-09-06 | 5:12 |  |  |  |  | 98.5003 |  | 28902.8082
2017-09-06 | 5:14 |  |  |  |  | 98.2211 |  | 28820.8636
2017-09-06 | 5:15 | 1.8817 | 0 | 0 | 1.5 | 98.0015 | 0 | 28756.4366
2017-09-06 | 5:16 |  |  |  |  | 97.8422 |  | 28709.704
2017-09-06 | 5:18 |  |  |  |  | 97.6288 |  | 28647.0679
2017-09-06 | 5:20 |  |  |  |  | 97.2988 |  | 28550.2494
2017-09-06 | 5:22 |  |  |  |  | 96.9236 |  | 28440.1532
2017-09-06 | 5:24 |  |  |  |  | 96.4094 |  | 28289.2617
2017-09-06 | 5:26 |  |  |  |  | 95.6953 |  | 28079.7208
2017-09-06 | 5:28 |  |  |  |  | 94.7745 |  | 27809.5321
2017-09-06 | 5:30 | 2.0705 | 0 | 0 | 1.5 | 93.8015 | 0 | 27524.0284
2017-09-06 | 5:32 |  |  |  |  | 92.9781 |  | 27282.4255
2017-09-06 | 5:34 |  |  |  |  | 92.1857 |  | 27049.9271
2017-09-06 | 5:36 |  |  |  |  | 91.4346 |  | 26829.5355
2017-09-06 | 5:38 |  |  |  |  | 90.7994 |  | 26643.1362
2017-09-06 | 5:40 |  |  |  |  | 90.1422 |  | 26450.2981
2017-09-06 | 5:42 |  |  |  |  | 89.553 |  | 26277.3959
2017-09-06 | 5:44 |  |  |  |  | 89.0039 |  | 26116.289
2017-09-06 | 5:45 | 1.9316 | 0 | 0 | 1.5 | 88.7624 | 0 | 26045.4257
2017-09-06 | 5:46 |  |  |  |  | 88.4998 |  | 25968.3772
2017-09-06 | 5:48 |  |  |  |  | 87.9576 |  | 25809.2805
2017-09-06 | 5:50 |  |  |  |  | 87.4931 |  | 25672.9874
2017-09-06 | 5:52 |  |  |  |  | 87.0381 |  | 25539.4612
2017-09-06 | 5:54 |  |  |  |  | 86.5617 |  | 25399.6733
2017-09-06 | 5:56 |  |  |  |  | 86.1836 |  | 25288.7289
2017-09-06 | 5:58 |  |  |  |  | 85.7581 |  | 25163.8753
2017-09-06 | 6:00 | 1.8809 | 0 | 0 | 1.5 | 85.3557 | 0 | 25045.8049
2017-09-06 | 6:02 |  |  |  |  | 84.9569 |  | 24928.7935
2017-09-06 | 6:04 |  |  |  |  | 84.5753 |  | 24816.8077
2017-09-06 | 6:06 |  |  |  |  | 84.2404 |  | 24718.5499
2017-09-06 | 6:08 |  |  |  |  | 83.907 |  | 24620.7082
2017-09-06 | 6:10 |  |  |  |  | 83.5609 |  | 24519.1617
2017-09-06 | 6:12 |  |  |  |  | 83.3078 |  | 24444.8934
2017-09-06 | 6:14 |  |  |  |  | 83.0401 |  | 24366.3447
2017-09-06 | 6:15 | 1.8177 | 0 | 0 | 1.5 | 82.957 | 0 | 24341.9519
2017-09-06 | 6:16 |  |  |  |  | 82.8377 |  | 24306.9456
2017-09-06 | 6:18 |  |  |  |  | 82.6003 |  | 24237.2801
2017-09-06 | 6:20 |  |  |  |  | 82.4267 |  | 24186.3547
2017-09-06 | 6:22 |  |  |  |  | 82.2068 |  | 24121.8292
2017-09-06 | 6:24 |  |  |  |  | 81.9845 |  | 24056.5982
2017-09-06 | 6:26 |  |  |  |  | 81.8038 |  | 24003.5663
2017-09-06 | 6:28 |  |  |  |  | 81.628 |  | 23951.9824
2017-09-06 | 6:30 | 1.7936 | 0 | 0 | 1.5 | 81.4345 | 0 | 23895.2184
2017-09-06 | 6:32 |  |  |  |  | 81.2793 |  | 23849.6636
2017-09-06 | 6:34 |  |  |  |  | 81.1533 |  | 23812.6895
2017-09-06 | 6:36 |  |  |  |  | 80.8942 |  | 23736.6616
2017-09-06 | 6:38 |  |  |  |  | 80.7044 |  | 23680.9833
2017-09-06 | 6:40 |  |  |  |  | 80.604 |  | 23651.5086
2017-09-06 | 6:42 |  |  |  |  | 80.4429 |  | 23604.2435
2017-09-06 | 6:44 |  |  |  |  | 80.3143 |  | 23566.5218
2017-09-06 | 6:45 | 1.8131 | 0 | 0 | 1.5 | 80.214 | 0 | 23537.0718
2017-09-06 | 6:46 |  |  |  |  | 80.1575 |  | 23520.499
2017-09-06 | 6:48 |  |  |  |  | 80.0788 |  | 23497.4091
2017-09-06 | 6:50 |  |  |  |  | 79.9718 |  | 23466.0116
2017-09-06 | 6:52 |  |  |  |  | 79.8084 |  | 23418.0633
2017-09-06 | 6:54 |  |  |  |  | 79.7579 |  | 23403.2613
2017-09-06 | 6:56 |  |  |  |  | 79.6536 |  | 23372.6362
2017-09-06 | 6:58 |  |  |  |  | 79.5095 |  | 23330.3452
2017-09-06 | 7:00 | 1.7889 | 0 | 0 | 1.5 | 79.4655 | 0 | 23317.4505
2017-09-06 | 7:02 |  |  |  |  | 79.3747 |  | 23290.801
2017-09-06 | 7:04 |  |  |  |  | 79.2847 |  | 23264.3936
2017-09-06 | 7:06 |  |  |  |  | 79.1836 |  | 23234.7221
2017-09-06 | 7:08 |  |  |  |  | 79.0595 |  | 23198.3167
2017-09-06 | 7:10 |  |  |  |  | 78.8956 |  | 23150.2118
2017-09-06 | 7:12 |  |  |  |  | 78.7788 |  | 23115.9399
2017-09-06 | 7:14 |  |  |  |  | 78.6291 |  | 23072.0348
2017-09-06 | 7:15 | 1.8084 | 0 | 0 | 1.5 | 78.5463 | 0 | 23047.716
2017-09-06 | 7:16 |  |  |  |  | 78.5158 |  | 23038.7679
2017-09-06 | 7:18 |  |  |  |  | 78.4118 |  | 23008.2636
2017-09-06 | 7:20 |  |  |  |  | 78.3911 |  | 23002.1812
2017-09-06 | 7:22 |  |  |  |  | 78.3991 |  | 23004.5274
2017-09-06 | 7:24 |  |  |  |  | 78.4511 |  | 23019.793
2017-09-06 | 7:26 |  |  |  |  | 78.3787 |  | 22998.5523
2017-09-06 | 7:28 |  |  |  |  | 78.3668 |  | 22995.0643
2017-09-06 | 7:30 | 1.785 | 0 | 0 | 1.5 | 78.3181 | 0 | 22980.7638
2017-09-06 | 7:32 |  |  |  |  | 78.2938 |  | 22973.6311
2017-09-06 | 7:34 |  |  |  |  | 78.2468 |  | 22959.8544
2017-09-06 | 7:36 |  |  |  |  | 78.2103 |  | 22949.1222
2017-09-06 | 7:38 |  |  |  |  | 78.1897 |  | 22943.0823
2017-09-06 | 7:40 |  |  |  |  | 78.2406 |  | 22958.0231
2017-09-06 | 7:42 |  |  |  |  | 78.2853 |  | 22971.1329
2017-09-06 | 7:44 |  |  |  |  | 78.2939 |  | 22973.6737
2017-09-06 | 7:45 | 1.7312 | 0 | 0 | 1.5 | 78.3201 | 0 | 22981.3571
2017-09-06 | 7:46 |  |  |  |  | 78.2932 |  | 22973.4477
2017-09-06 | 7:48 |  |  |  |  | 78.3399 |  | 22987.1708
2017-09-06 | 7:50 |  |  |  |  | 78.3445 |  | 22988.5074
2017-09-06 | 7:52 |  |  |  |  | 78.3723 |  | 22996.665
2017-09-06 | 7:54 |  |  |  |  | 78.3392 |  | 22986.9716
2017-09-06 | 7:56 |  |  |  |  | 78.3128 |  | 22979.2124
2017-09-06 | 7:58 |  |  |  |  | 78.3288 |  | 22983.9135
2017-09-06 | 8:00 | 1.7405 | 0 | 0 | 1.5 | 78.3599 | 0 | 22993.0385
2017-09-06 | 8:02 |  |  |  |  | 78.4057 |  | 23006.4816
2017-09-06 | 8:04 |  |  |  |  | 78.4566 |  | 23021.4092
2017-09-06 | 8:06 |  |  |  |  | 78.4353 |  | 23015.1677
2017-09-06 | 8:08 |  |  |  |  | 78.5816 |  | 23058.0723
2017-09-06 | 8:10 |  |  |  |  | 78.6918 |  | 23090.4321
2017-09-06 | 8:12 |  |  |  |  | 78.8387 |  | 23133.5136
2017-09-06 | 8:14 |  |  |  |  | 78.9973 |  | 23180.0669
2017-09-06 | 8:15 | 1.6906 | 0 | 0 | 1.5 | 79.0899 | 0 | 23207.2311
2017-09-06 | 8:16 |  |  |  |  | 79.1255 |  | 23217.6901
2017-09-06 | 8:18 |  |  |  |  | 79.2889 |  | 23265.6204
2017-09-06 | 8:20 |  |  |  |  | 79.3802 |  | 23292.4331
2017-09-06 | 8:22 |  |  |  |  | 79.5149 |  | 23331.9368
2017-09-06 | 8:24 |  |  |  |  | 79.5984 |  | 23356.4548
2017-09-06 | 8:26 |  |  |  |  | 79.6013 |  | 23357.2966
2017-09-06 | 8:28 |  |  |  |  | 79.6388 |  | 23368.2999
2017-09-06 | 8:30 | 1.7748 | 0 | 0 | 1.5 | 79.6011 | 0 | 23357.2318
2017-09-06 | 8:32 |  |  |  |  | 79.6488 |  | 23371.228
2017-09-06 | 8:34 |  |  |  |  | 79.6622 |  | 23375.1726
2017-09-06 | 8:36 |  |  |  |  | 79.6221 |  | 23363.3926
2017-09-06 | 8:38 |  |  |  |  | 79.6513 |  | 23371.9601
2017-09-06 | 8:40 |  |  |  |  | 79.731 |  | 23395.3543
2017-09-06 | 8:42 |  |  |  |  | 79.8084 |  | 23418.0657
2017-09-06 | 8:44 |  |  |  |  | 79.9213 |  | 23451.1894
2017-09-06 | 8:45 | 1.7132 | 0 | 0 | 1.5 | 79.9845 | 0 | 23469.7434
2017-09-06 | 8:46 |  |  |  |  | 80.0117 |  | 23477.7312
2017-09-06 | 8:48 |  |  |  |  | 80.049 |  | 23488.6602
2017-09-06 | 8:50 |  |  |  |  | 80.0511 |  | 23489.2758
2017-09-06 | 8:52 |  |  |  |  | 79.9969 |  | 23473.3858
2017-09-06 | 8:54 |  |  |  |  | 79.9898 |  | 23471.2948
2017-09-06 | 8:56 |  |  |  |  | 80.0102 |  | 23477.2655
2017-09-06 | 8:58 |  |  |  |  | 80.0444 |  | 23487.3104
2017-09-06 | 9:00 | 1.7312 | 0 | 0 | 1.5 | 80.0883 | 0 | 23500.1963
2017-09-06 | 9:02 |  |  |  |  | 80.0636 |  | 23492.9542
2017-09-06 | 9:04 |  |  |  |  | 80.0767 |  | 23496.8022
2017-09-06 | 9:06 |  |  |  |  | 80.0913 |  | 23501.0693
2017-09-06 | 9:08 |  |  |  |  | 80.1047 |  | 23505.0182
2017-09-06 | 9:10 |  |  |  |  | 80.083 |  | 23498.6359
2017-09-06 | 9:12 |  |  |  |  | 80.0597 |  | 23491.8101
2017-09-06 | 9:14 |  |  |  |  | 80.1074 |  | 23505.7906
2017-09-06 | 9:15 | 1.7296 | 0 | 0 | 1.5 | 80.1402 | 0 | 23515.4282
2017-09-06 | 9:16 |  |  |  |  | 80.2169 |  | 23537.918
2017-09-06 | 9:18 |  |  |  |  | 80.3413 |  | 23574.4308
2017-09-06 | 9:20 |  |  |  |  | 80.4406 |  | 23603.5583
2017-09-06 | 9:22 |  |  |  |  | 80.3962 |  | 23590.5562
2017-09-06 | 9:24 |  |  |  |  | 80.3244 |  | 23569.4833
2017-09-06 | 9:26 |  |  |  |  | 80.3294 |  | 23570.9519
2017-09-06 | 9:28 |  |  |  |  | 80.3583 |  | 23579.4097
2017-09-06 | 9:30 | 1.746 | 0 | 0 | 1.5 | 80.3651 | 0 | 23581.4224
2017-09-06 | 9:32 |  |  |  |  | 80.415 |  | 23596.0565
2017-09-06 | 9:34 |  |  |  |  | 80.3994 |  | 23591.4852
2017-09-06 | 9:36 |  |  |  |  | 80.4828 |  | 23615.9519
2017-09-06 | 9:38 |  |  |  |  | 80.6109 |  | 23653.5483
2017-09-06 | 9:40 |  |  |  |  | 80.6881 |  | 23676.2036
2017-09-06 | 9:42 |  |  |  |  | 80.7576 |  | 23696.5734
2017-09-06 | 9:44 |  |  |  |  | 80.7552 |  | 23695.8704
2017-09-06 | 9:45 | 1.76 | 0 | 0 | 1.5 | 80.7498 | 0 | 23694.2899
2017-09-06 | 9:46 |  |  |  |  | 80.7861 |  | 23704.9484
2017-09-06 | 9:48 |  |  |  |  | 80.7732 |  | 23701.1785
2017-09-06 | 9:50 |  |  |  |  | 80.7501 |  | 23694.375
2017-09-06 | 9:52 |  |  |  |  | 80.8282 |  | 23717.2924
2017-09-06 | 9:54 |  |  |  |  | 80.9798 |  | 23761.7841
2017-09-06 | 9:56 |  |  |  |  | 81.0705 |  | 23788.3951
2017-09-06 | 9:58 |  |  |  |  | 81.1034 |  | 23798.0439
2017-09-06 | 10:00 | 1.7475 | 0 | 0 | 1.5 | 81.1413 | 0 | 23809.1746
2017-09-06 | 10:02 |  |  |  |  | 81.1914 |  | 23823.8739
2017-09-06 | 10:04 |  |  |  |  | 81.2478 |  | 23840.4156
2017-09-06 | 10:06 |  |  |  |  | 81.379 |  | 23878.9275
2017-09-06 | 10:08 |  |  |  |  | 81.5112 |  | 23917.7285
2017-09-06 | 10:10 |  |  |  |  | 81.6784 |  | 23966.7621
2017-09-06 | 10:12 |  |  |  |  | 81.7695 |  | 23993.5055
2017-09-06 | 10:14 |  |  |  |  | 81.7897 |  | 23999.4404
2017-09-06 | 10:15 | 1.7538 | 0 | 0 | 1.5 | 81.7706 | 0 | 23993.8391
2017-09-06 | 10:16 |  |  |  |  | 81.7404 |  | 23984.9761
2017-09-06 | 10:18 |  |  |  |  | 81.7689 |  | 23993.3242
2017-09-06 | 10:20 |  |  |  |  | 81.7705 |  | 23993.8122
2017-09-06 | 10:22 |  |  |  |  | 81.8793 |  | 24025.7202
2017-09-06 | 10:24 |  |  |  |  | 81.944 |  | 24044.7041
2017-09-06 | 10:26 |  |  |  |  | 82.0572 |  | 24077.9284
2017-09-06 | 10:28 |  |  |  |  | 82.0082 |  | 24063.5361
2017-09-06 | 10:30 | 1.76 | 0 | 0 | 1.5 | 81.9561 | 0 | 24048.266
2017-09-06 | 10:32 |  |  |  |  | 81.9677 |  | 24051.6686
2017-09-06 | 10:34 |  |  |  |  | 82.0066 |  | 24063.0927
2017-09-06 | 10:36 |  |  |  |  | 82.1637 |  | 24109.1627
2017-09-06 | 10:38 |  |  |  |  | 82.2724 |  | 24141.0795
2017-09-06 | 10:40 |  |  |  |  | 82.3539 |  | 24164.9863
2017-09-06 | 10:42 |  |  |  |  | 82.3907 |  | 24175.7725
2017-09-06 | 10:44 |  |  |  |  | 82.4129 |  | 24182.3092
2017-09-06 | 10:45 | 1.753 | 0 | 0 | 1.5 | 82.3639 | 0 | 24167.9077
2017-09-06 | 10:46 |  |  |  |  | 82.4028 |  | 24179.3476
2017-09-06 | 10:48 |  |  |  |  | 82.4907 |  | 24205.1283
2017-09-06 | 10:50 |  |  |  |  | 82.5937 |  | 24235.3637
2017-09-06 | 10:52 |  |  |  |  | 82.7232 |  | 24273.3566
2017-09-06 | 10:54 |  |  |  |  | 82.8045 |  | 24297.212
2017-09-06 | 10:56 |  |  |  |  | 82.7592 |  | 24283.9053
2017-09-06 | 10:58 |  |  |  |  | 82.7059 |  | 24268.2882
2017-09-06 | 11:00 | 1.7663 | 0 | 0 | 1.5 | 82.6818 | 0 | 24261.2116
2017-09-06 | 11:02 |  |  |  |  | 82.7159 |  | 24271.2028
2017-09-06 | 11:04 |  |  |  |  | 82.8662 |  | 24315.296
2017-09-06 | 11:06 |  |  |  |  | 82.9504 |  | 24340.0244
2017-09-06 | 11:08 |  |  |  |  | 83.0318 |  | 24363.9022
2017-09-06 | 11:10 |  |  |  |  | 83.0544 |  | 24370.5422
2017-09-06 | 11:12 |  |  |  |  | 83.0529 |  | 24370.0944
2017-09-06 | 11:14 |  |  |  |  | 83.0678 |  | 24374.4756
2017-09-06 | 11:15 | 1.7382 | 0 | 0 | 1.5 | 83.1108 | 0 | 24387.0839
2017-09-06 | 11:16 |  |  |  |  | 83.1432 |  | 24396.6004
2017-09-06 | 11:18 |  |  |  |  | 83.2691 |  | 24433.5207
2017-09-06 | 11:20 |  |  |  |  | 83.3751 |  | 24464.6227
2017-09-06 | 11:22 |  |  |  |  | 83.4165 |  | 24476.7856
2017-09-06 | 11:24 |  |  |  |  | 83.5218 |  | 24507.6772
2017-09-06 | 11:26 |  |  |  |  | 83.4895 |  | 24498.2188
2017-09-06 | 11:28 |  |  |  |  | 83.5099 |  | 24504.205
2017-09-06 | 11:30 | 1.7273 | 0 | 0 | 1.5 | 83.5572 | 0 | 24518.0557
2017-09-06 | 11:32 |  |  |  |  | 83.6977 |  | 24559.2901
2017-09-06 | 11:34 |  |  |  |  | 83.8402 |  | 24601.1242
2017-09-06 | 11:36 |  |  |  |  | 83.9611 |  | 24636.5759
2017-09-06 | 11:38 |  |  |  |  | 83.9784 |  | 24641.6646
2017-09-06 | 11:40 |  |  |  |  | 83.9258 |  | 24626.2311
2017-09-06 | 11:42 |  |  |  |  | 83.9907 |  | 24645.2688
2017-09-06 | 11:44 |  |  |  |  | 84.1035 |  | 24678.3567
2017-09-06 | 11:45 | 1.6992 | 0 | 0 | 1.5 | 84.2067 | 0 | 24708.6505
2017-09-06 | 11:46 |  |  |  |  | 84.3217 |  | 24742.3895
2017-09-06 | 11:48 |  |  |  |  | 84.5297 |  | 24803.4206
2017-09-06 | 11:50 |  |  |  |  | 84.7154 |  | 24857.9056
2017-09-06 | 11:52 |  |  |  |  | 84.7833 |  | 24877.8499
2017-09-06 | 11:54 |  |  |  |  | 84.7757 |  | 24875.607
2017-09-06 | 11:56 |  |  |  |  | 84.7707 |  | 24874.1583
2017-09-06 | 11:58 |  |  |  |  | 84.9442 |  | 24925.0638
2017-09-06 | 12:00 | 1.6961 | 0 | 0 | 1.5 | 85.1276 | 0 | 24978.8818
2017-09-06 | 12:02 |  |  |  |  | 85.2622 |  | 25018.3541
2017-09-06 | 12:04 |  |  |  |  | 85.3815 |  | 25053.3672
2017-09-06 | 12:06 |  |  |  |  | 85.4615 |  | 25076.8464
2017-09-06 | 12:08 |  |  |  |  | 85.4974 |  | 25087.3929
2017-09-06 | 12:10 |  |  |  |  | 85.5556 |  | 25104.454
2017-09-06 | 12:12 |  |  |  |  | 85.4921 |  | 25085.8324
2017-09-06 | 12:14 |  |  |  |  | 85.4032 |  | 25059.7451
2017-09-06 | 12:15 | 1.7834 | 0 | 0 | 1.5 | 85.3395 | 0 | 25041.0567
2017-09-06 | 12:16 |  |  |  |  | 85.3644 |  | 25048.3592
2017-09-06 | 12:18 |  |  |  |  | 85.4063 |  | 25060.6407
2017-09-06 | 12:20 |  |  |  |  | 85.5096 |  | 25090.9703
2017-09-06 | 12:22 |  |  |  |  | 85.538 |  | 25099.287
2017-09-06 | 12:24 |  |  |  |  | 85.5956 |  | 25116.207
2017-09-06 | 12:26 |  |  |  |  | 85.6156 |  | 25122.052
2017-09-06 | 12:28 |  |  |  |  | 85.5679 |  | 25108.0693
2017-09-06 | 12:30 | 1.7842 | 0 | 0 | 1.5 | 85.4859 | 0 | 25084.0035
2017-09-06 | 12:32 |  |  |  |  | 85.4591 |  | 25076.1501
2017-09-06 | 12:34 |  |  |  |  | 85.4832 |  | 25083.2244
2017-09-06 | 12:36 |  |  |  |  | 85.5333 |  | 25097.9058
2017-09-06 | 12:38 |  |  |  |  | 85.4916 |  | 25085.6781
2017-09-06 | 12:40 |  |  |  |  | 85.4489 |  | 25073.1572
2017-09-06 | 12:42 |  |  |  |  | 85.3162 |  | 25034.2039
2017-09-06 | 12:44 |  |  |  |  | 85.3131 |  | 25033.3151
2017-09-06 | 12:45 | 1.7335 | 0 | 0 | 1.5 | 85.3567 | 0 | 25046.0825
2017-09-06 | 12:46 |  |  |  |  | 85.4151 |  | 25063.2331
2017-09-06 | 12:48 |  |  |  |  | 85.4185 |  | 25064.2428
2017-09-06 | 12:50 |  |  |  |  | 85.4625 |  | 25077.1463
2017-09-06 | 12:52 |  |  |  |  | 85.4675 |  | 25078.5926
2017-09-06 | 12:54 |  |  |  |  | 85.4618 |  | 25076.9383
2017-09-06 | 12:56 |  |  |  |  | 85.4612 |  | 25076.7569
2017-09-06 | 12:58 |  |  |  |  | 85.4224 |  | 25065.3619
2017-09-06 | 13:00 | 1.7624 | 0 | 0 | 1.5 | 85.4128 | 0 | 25062.5547
2017-09-06 | 13:02 |  |  |  |  | 85.4484 |  | 25073.0025
2017-09-06 | 13:04 |  |  |  |  | 85.4291 |  | 25067.3364
2017-09-06 | 13:06 |  |  |  |  | 85.3306 |  | 25038.424
2017-09-06 | 13:08 |  |  |  |  | 85.2593 |  | 25017.5258
2017-09-06 | 13:10 |  |  |  |  | 85.2782 |  | 25023.0733
2017-09-06 | 13:12 |  |  |  |  | 85.3171 |  | 25034.4704
2017-09-06 | 13:14 |  |  |  |  | 85.3234 |  | 25036.3375
2017-09-06 | 13:15 | 1.7507 | 0 | 0 | 1.5 | 85.3394 | 0 | 25041.0097
2017-09-06 | 13:16 |  |  |  |  | 85.2935 |  | 25027.5416
2017-09-06 | 13:18 |  |  |  |  | 85.1661 |  | 24990.1671
2017-09-06 | 13:20 |  |  |  |  | 85.0611 |  | 24959.3491
2017-09-06 | 13:22 |  |  |  |  | 84.9991 |  | 24941.1733
2017-09-06 | 13:24 |  |  |  |  | 85.0618 |  | 24959.5686
2017-09-06 | 13:26 |  |  |  |  | 85.1551 |  | 24986.932
2017-09-06 | 13:28 |  |  |  |  | 85.234 |  | 25010.1023
2017-09-06 | 13:30 | 1.7452 | 0 | 0 | 1.5 | 85.2762 | 0 | 25022.4712
2017-09-06 | 13:32 |  |  |  |  | 85.2479 |  | 25014.1745
2017-09-06 | 13:34 |  |  |  |  | 85.1779 |  | 24993.6257
2017-09-06 | 13:36 |  |  |  |  | 85.2738 |  | 25021.7772
2017-09-06 | 13:38 |  |  |  |  | 85.3951 |  | 25057.3678
2017-09-06 | 13:40 |  |  |  |  | 85.5113 |  | 25091.4448
2017-09-06 | 13:42 |  |  |  |  | 85.5676 |  | 25107.9731
2017-09-06 | 13:44 |  |  |  |  | 85.5568 |  | 25104.7964
2017-09-06 | 13:45 | 1.7756 | 0 | 0 | 1.5 | 85.5089 | 0 | 25090.7532
2017-09-06 | 13:46 |  |  |  |  | 85.4399 |  | 25070.5043
2017-09-06 | 13:48 |  |  |  |  | 85.405 |  | 25060.2713
2017-09-06 | 13:50 |  |  |  |  | 85.5347 |  | 25098.3178
2017-09-06 | 13:52 |  |  |  |  | 85.6692 |  | 25137.7789
2017-09-06 | 13:54 |  |  |  |  | 85.785 |  | 25171.78
2017-09-06 | 13:56 |  |  |  |  | 85.8821 |  | 25200.2537
2017-09-06 | 13:58 |  |  |  |  | 85.9807 |  | 25229.2045
2017-09-06 | 14:00 | 1.7179 | 0 | 0 | 1.5 | 86.0578 | 0 | 25251.822
2017-09-06 | 14:02 |  |  |  |  | 86.1382 |  | 25275.4222
2017-09-06 | 14:04 |  |  |  |  | 86.2915 |  | 25320.3772
2017-09-06 | 14:06 |  |  |  |  | 86.4103 |  | 25355.2603
2017-09-06 | 14:08 |  |  |  |  | 86.5138 |  | 25385.6146
2017-09-06 | 14:10 |  |  |  |  | 86.5472 |  | 25395.4333
2017-09-06 | 14:12 |  |  |  |  | 86.6571 |  | 25427.6658
2017-09-06 | 14:14 |  |  |  |  | 86.6491 |  | 25425.3131
2017-09-06 | 14:15 | 1.7538 | 0 | 0 | 1.5 | 86.6296 | 0 | 25419.6021
2017-09-06 | 14:16 |  |  |  |  | 86.5724 |  | 25402.8098
2017-09-06 | 14:18 |  |  |  |  | 86.5991 |  | 25410.6496
2017-09-06 | 14:20 |  |  |  |  | 86.7073 |  | 25442.4097
2017-09-06 | 14:22 |  |  |  |  | 86.7502 |  | 25454.9867
2017-09-06 | 14:24 |  |  |  |  | 86.8095 |  | 25472.3993
2017-09-06 | 14:26 |  |  |  |  | 86.8817 |  | 25493.5728
2017-09-06 | 14:28 |  |  |  |  | 87.0023 |  | 25528.9641
2017-09-06 | 14:30 | 1.7265 | 0 | 0 | 1.5 | 87.0415 | 0 | 25540.473
2017-09-06 | 14:32 |  |  |  |  | 87.1344 |  | 25567.7269
2017-09-06 | 14:34 |  |  |  |  | 87.1925 |  | 25584.7833
2017-09-06 | 14:36 |  |  |  |  | 87.198 |  | 25586.3931
2017-09-06 | 14:38 |  |  |  |  | 87.2485 |  | 25601.2018
2017-09-06 | 14:40 |  |  |  |  | 87.2682 |  | 25606.9686
2017-09-06 | 14:42 |  |  |  |  | 87.3119 |  | 25619.7964
2017-09-06 | 14:44 |  |  |  |  | 87.3785 |  | 25639.3423
2017-09-06 | 14:45 | 1.7241 | 0 | 0 | 1.5 | 87.4198 | 0 | 25651.467
2017-09-06 | 14:46 |  |  |  |  | 87.5068 |  | 25676.988
2017-09-06 | 14:48 |  |  |  |  | 87.6207 |  | 25710.425
2017-09-06 | 14:50 |  |  |  |  | 87.7602 |  | 25751.3481
2017-09-06 | 14:52 |  |  |  |  | 87.8174 |  | 25768.1248
2017-09-06 | 14:54 |  |  |  |  | 87.9534 |  | 25808.0473
2017-09-06 | 14:56 |  |  |  |  | 88.0666 |  | 25841.2625
2017-09-06 | 14:58 |  |  |  |  | 88.137 |  | 25861.9119
2017-09-06 | 15:00 | 1.7873 | 0 | 0 | 1.5 | 88.0593 | 0 | 25839.1087
2017-09-06 | 15:02 |  |  |  |  | 87.9245 |  | 25799.5648
2017-09-06 | 15:04 |  |  |  |  | 87.823 |  | 25769.7701
2017-09-06 | 15:06 |  |  |  |  | 87.6181 |  | 25709.6548
2017-09-06 | 15:08 |  |  |  |  | 87.3665 |  | 25635.8208
2017-09-06 | 15:10 |  |  |  |  | 86.9686 |  | 25519.0847
2017-09-06 | 15:12 |  |  |  |  | 86.5277 |  | 25389.6868
2017-09-06 | 15:14 |  |  |  |  | 86.1375 |  | 25275.1959
2017-09-06 | 15:15 | 1.8271 | 0 | 0 | 1.5 | 86.0535 | 0 | 25250.5614
2017-09-06 | 15:16 |  |  |  |  | 85.9359 |  | 25216.0545
2017-09-06 | 15:18 |  |  |  |  | 85.7603 |  | 25164.52
2017-09-06 | 15:20 |  |  |  |  | 85.6314 |  | 25126.6997
2017-09-06 | 15:22 |  |  |  |  | 85.4897 |  | 25085.1252
2017-09-06 | 15:24 |  |  |  |  | 85.2949 |  | 25027.956
2017-09-06 | 15:26 |  |  |  |  | 85.2085 |  | 25002.5985
2017-09-06 | 15:28 |  |  |  |  | 85.2366 |  | 25010.8567
2017-09-06 | 15:30 | 1.7288 | 0 | 0 | 1.5 | 85.2927 | 0 | 25027.3022
2017-09-06 | 15:32 |  |  |  |  | 85.3716 |  | 25050.459
2017-09-06 | 15:34 |  |  |  |  | 85.4094 |  | 25061.5673
2017-09-06 | 15:36 |  |  |  |  | 85.4953 |  | 25086.7772
2017-09-06 | 15:38 |  |  |  |  | 85.5619 |  | 25106.292
2017-09-06 | 15:40 |  |  |  |  | 85.7237 |  | 25153.7831
2017-09-06 | 15:42 |  |  |  |  | 85.934 |  | 25215.4768
2017-09-06 | 15:44 |  |  |  |  | 86.0051 |  | 25236.3571
2017-09-06 | 15:45 | 1.721 | 0 | 0 | 1.5 | 86.0476 | 0 | 25248.8176
2017-09-06 | 15:46 |  |  |  |  | 86.0386 |  | 25246.1938
2017-09-06 | 15:48 |  |  |  |  | 86.1458 |  | 25277.6428
2017-09-06 | 15:50 |  |  |  |  | 86.275 |  | 25315.5438
2017-09-06 | 15:52 |  |  |  |  | 86.4463 |  | 25365.8246
2017-09-06 | 15:54 |  |  |  |  | 86.616 |  | 25415.5971
2017-09-06 | 15:56 |  |  |  |  | 86.7518 |  | 25455.4635
2017-09-06 | 15:58 |  |  |  |  | 86.8774 |  | 25492.3234
2017-09-06 | 16:00 | 1.7046 | 0 | 0 | 1.5 | 87.0174 | 0 | 25533.4011
2017-09-06 | 16:02 |  |  |  |  | 87.1611 |  | 25575.5488
2017-09-06 | 16:04 |  |  |  |  | 87.2665 |  | 25606.4897
2017-09-06 | 16:06 |  |  |  |  | 87.355 |  | 25632.4605
2017-09-06 | 16:08 |  |  |  |  | 87.4428 |  | 25658.2144
2017-09-06 | 16:10 |  |  |  |  | 87.5217 |  | 25681.3601
2017-09-06 | 16:12 |  |  |  |  | 87.5384 |  | 25686.2539
2017-09-06 | 16:14 |  |  |  |  | 87.5763 |  | 25697.3868
2017-09-06 | 16:15 | 1.8177 | 0 | 0 | 1.5 | 87.424 | 0 | 25652.705
2017-09-06 | 16:16 |  |  |  |  | 87.4072 |  | 25647.7731
2017-09-06 | 16:18 |  |  |  |  | 87.4193 |  | 25651.3238
2017-09-06 | 16:20 |  |  |  |  | 87.4472 |  | 25659.5017
2017-09-06 | 16:22 |  |  |  |  | 87.5595 |  | 25692.4505
2017-09-06 | 16:24 |  |  |  |  | 87.592 |  | 25701.994
2017-09-06 | 16:26 |  |  |  |  | 87.6368 |  | 25715.1487
2017-09-06 | 16:28 |  |  |  |  | 87.709 |  | 25736.3377
2017-09-06 | 16:30 | 1.7436 | 0 | 0 | 1.5 | 87.6983 | 0 | 25733.1901
2017-09-06 | 16:32 |  |  |  |  | 87.6945 |  | 25732.0619
2017-09-06 | 16:34 |  |  |  |  | 87.7251 |  | 25741.0455
2017-09-06 | 16:36 |  |  |  |  | 87.722 |  | 25740.1546
2017-09-06 | 16:38 |  |  |  |  | 87.7151 |  | 25738.1241
2017-09-06 | 16:40 |  |  |  |  | 87.7698 |  | 25754.1732
2017-09-06 | 16:42 |  |  |  |  | 87.8722 |  | 25784.2232
2017-09-06 | 16:44 |  |  |  |  | 87.8936 |  | 25790.4958
2017-09-06 | 16:45 | 1.7499 | 0 | 0 | 1.5 | 87.8918 | 0 | 25789.9765
2017-09-06 | 16:46 |  |  |  |  | 87.8683 |  | 25783.0835
2017-09-06 | 16:48 |  |  |  |  | 87.8377 |  | 25774.102
2017-09-06 | 16:50 |  |  |  |  | 87.8388 |  | 25774.411
2017-09-06 | 16:52 |  |  |  |  | 87.8317 |  | 25772.3335
2017-09-06 | 16:54 |  |  |  |  | 87.9633 |  | 25810.9328
2017-09-06 | 16:56 |  |  |  |  | 87.992 |  | 25819.368
2017-09-06 | 16:58 |  |  |  |  | 88.014 |  | 25825.8223
2017-09-06 | 17:00 | 1.7873 | 0 | 0 | 1.5 | 87.932 | 0 | 25801.7588
2017-09-06 | 17:02 |  |  |  |  | 87.8682 |  | 25783.0366
2017-09-06 | 17:04 |  |  |  |  | 87.8452 |  | 25776.2868
2017-09-06 | 17:06 |  |  |  |  | 87.8214 |  | 25769.3203
2017-09-06 | 17:08 |  |  |  |  | 87.8234 |  | 25769.8842
2017-09-06 | 17:10 |  |  |  |  | 87.8379 |  | 25774.1422
2017-09-06 | 17:12 |  |  |  |  | 87.7507 |  | 25748.5675
2017-09-06 | 17:14 |  |  |  |  | 87.7883 |  | 25759.5864
2017-09-06 | 17:15 | 1.7709 | 0 | 0 | 1.5 | 87.729 | 0 | 25742.194
2017-09-06 | 17:16 |  |  |  |  | 87.7114 |  | 25737.0452
2017-09-06 | 17:18 |  |  |  |  | 87.6657 |  | 25723.6085
2017-09-06 | 17:20 |  |  |  |  | 87.4415 |  | 25657.8247
2017-09-06 | 17:22 |  |  |  |  | 87.3755 |  | 25638.4714
2017-09-06 | 17:24 |  |  |  |  | 87.2007 |  | 25587.1877
2017-09-06 | 17:26 |  |  |  |  | 87.0338 |  | 25538.203
2017-09-06 | 17:28 |  |  |  |  | 86.8653 |  | 25488.753
2017-09-06 | 17:30 | 1.7834 | 0 | 0 | 1.5 | 86.7263 | 0 | 25447.9887
2017-09-06 | 17:32 |  |  |  |  | 86.4887 |  | 25378.2469
2017-09-06 | 17:34 |  |  |  |  | 86.2894 |  | 25319.7727
2017-09-06 | 17:36 |  |  |  |  | 86.0394 |  | 25246.4176
2017-09-06 | 17:38 |  |  |  |  | 85.9369 |  | 25216.3456
2017-09-06 | 17:40 |  |  |  |  | 85.8772 |  | 25198.83
2017-09-06 | 17:42 |  |  |  |  | 85.7327 |  | 25156.4316
2017-09-06 | 17:44 |  |  |  |  | 85.6526 |  | 25132.9209
2017-09-06 | 17:45 | 1.7811 | 0 | 0 | 1.5 | 85.6098 | 0 | 25120.371
2017-09-06 | 17:46 |  |  |  |  | 85.5535 |  | 25103.8384
2017-09-06 | 17:48 |  |  |  |  | 85.4233 |  | 25065.6395
2017-09-06 | 17:50 |  |  |  |  | 85.2507 |  | 25014.985
2017-09-06 | 17:52 |  |  |  |  | 85.08 |  | 24964.8899
2017-09-06 | 17:54 |  |  |  |  | 85.0458 |  | 24954.8764
2017-09-06 | 17:56 |  |  |  |  | 84.957 |  | 24928.8091
2017-09-06 | 17:58 |  |  |  |  | 84.8951 |  | 24910.6579
2017-09-06 | 18:00 | 1.7748 | 0 | 0 | 1.5 | 84.8525 | 0 | 24898.1549
2017-09-06 | 18:02 |  |  |  |  | 84.832 |  | 24892.1261
2017-09-06 | 18:04 |  |  |  |  | 84.7463 |  | 24866.9925
2017-09-06 | 18:06 |  |  |  |  | 84.6492 |  | 24838.4962
2017-09-06 | 18:08 |  |  |  |  | 84.4556 |  | 24781.6987
2017-09-06 | 18:10 |  |  |  |  | 84.3153 |  | 24740.5292
2017-09-06 | 18:12 |  |  |  |  | 84.2768 |  | 24729.2351
2017-09-06 | 18:14 |  |  |  |  | 84.2447 |  | 24719.7879
2017-09-06 | 18:15 | 1.7787 | 0 | 0 | 1.5 | 84.2048 | 0 | 24708.0974
2017-09-06 | 18:16 |  |  |  |  | 84.1801 |  | 24700.833
2017-09-06 | 18:18 |  |  |  |  | 84.0851 |  | 24672.9702
2017-09-06 | 18:20 |  |  |  |  | 83.9321 |  | 24628.0712
2017-09-06 | 18:22 |  |  |  |  | 83.7206 |  | 24566.0284
2017-09-06 | 18:24 |  |  |  |  | 83.5633 |  | 24519.8512
2017-09-06 | 18:26 |  |  |  |  | 83.4233 |  | 24478.7712
2017-09-06 | 18:28 |  |  |  |  | 83.4139 |  | 24476.0177
2017-09-06 | 18:30 | 1.7826 | 0 | 0 | 1.5 | 83.3165 | 0 | 24447.443
2017-09-06 | 18:32 |  |  |  |  | 83.2235 |  | 24420.1536
2017-09-06 | 18:34 |  |  |  |  | 82.984 |  | 24349.8748
2017-09-06 | 18:36 |  |  |  |  | 82.8136 |  | 24299.8646
2017-09-06 | 18:38 |  |  |  |  | 82.6471 |  | 24251.0258
2017-09-06 | 18:40 |  |  |  |  | 82.5089 |  | 24210.4763
2017-09-06 | 18:42 |  |  |  |  | 82.4336 |  | 24188.3738
2017-09-06 | 18:44 |  |  |  |  | 82.3561 |  | 24165.6425
2017-09-06 | 18:45 | 1.7928 | 0 | 0 | 1.5 | 82.2835 | 0 | 24144.3346
2017-09-06 | 18:46 |  |  |  |  | 82.2505 |  | 24134.6455
2017-09-06 | 18:48 |  |  |  |  | 82.0624 |  | 24079.4598
2017-09-06 | 18:50 |  |  |  |  | 81.8993 |  | 24031.5967
2017-09-06 | 18:52 |  |  |  |  | 81.7868 |  | 23998.5962
2017-09-06 | 18:54 |  |  |  |  | 81.7145 |  | 23977.3713
2017-09-06 | 18:56 |  |  |  |  | 81.6805 |  | 23967.3892
2017-09-06 | 18:58 |  |  |  |  | 81.5975 |  | 23943.0323
2017-09-06 | 19:00 | 1.7967 | 0 | 0 | 1.5 | 81.4612 | 0 | 23903.0471
2017-09-06 | 19:02 |  |  |  |  | 81.334 |  | 23865.708
2017-09-06 | 19:04 |  |  |  |  | 81.204 |  | 23827.5611
2017-09-06 | 19:06 |  |  |  |  | 81.1175 |  | 23802.1789
2017-09-06 | 19:08 |  |  |  |  | 81.0716 |  | 23788.7379
2017-09-06 | 19:10 |  |  |  |  | 81.0535 |  | 23783.3986
2017-09-06 | 19:12 |  |  |  |  | 81.0291 |  | 23776.2504
2017-09-06 | 19:14 |  |  |  |  | 80.8828 |  | 23733.3371
2017-09-06 | 19:15 | 1.767 | 0 | 0 | 1.5 | 80.8594 | 0 | 23726.4485
2017-09-06 | 19:16 |  |  |  |  | 80.7716 |  | 23700.6882
2017-09-06 | 19:18 |  |  |  |  | 80.6804 |  | 23673.9225
2017-09-06 | 19:20 |  |  |  |  | 80.6232 |  | 23657.1616
2017-09-06 | 19:22 |  |  |  |  | 80.655 |  | 23666.4788
2017-09-06 | 19:24 |  |  |  |  | 80.6319 |  | 23659.7067
2017-09-06 | 19:26 |  |  |  |  | 80.5651 |  | 23640.1004
2017-09-06 | 19:28 |  |  |  |  | 80.4382 |  | 23602.869
2017-09-06 | 19:30 | 1.7873 | 0 | 0 | 1.5 | 80.3567 | 0 | 23578.962
2017-09-06 | 19:32 |  |  |  |  | 80.2865 |  | 23558.3392
2017-09-06 | 19:34 |  |  |  |  | 80.2436 |  | 23545.769
2017-09-06 | 19:36 |  |  |  |  | 80.2647 |  | 23551.9501
2017-09-06 | 19:38 |  |  |  |  | 80.2503 |  | 23547.7391
2017-09-06 | 19:40 |  |  |  |  | 80.2139 |  | 23537.0404
2017-09-06 | 19:42 |  |  |  |  | 80.1055 |  | 23505.2445
2017-09-06 | 19:44 |  |  |  |  | 80.0292 |  | 23482.8465
2017-09-06 | 19:45 | 1.7686 | 0 | 0 | 1.5 | 79.9617 | 0 | 23463.0521
2017-09-06 | 19:46 |  |  |  |  | 79.9944 |  | 23472.6493
2017-09-06 | 19:48 |  |  |  |  | 79.9086 |  | 23447.4663
2017-09-06 | 19:50 |  |  |  |  | 79.8979 |  | 23444.3322
2017-09-06 | 19:52 |  |  |  |  | 79.9277 |  | 23453.0741
2017-09-06 | 19:54 |  |  |  |  | 79.9228 |  | 23451.6236
2017-09-06 | 19:56 |  |  |  |  | 79.9201 |  | 23450.8378
2017-09-06 | 19:58 |  |  |  |  | 79.8347 |  | 23425.7846
2017-09-06 | 20:00 | 1.7858 | 0 | 0 | 1.5 | 79.8115 | 0 | 23418.9791
2017-09-06 | 20:02 |  |  |  |  | 79.696 |  | 23385.0966
2017-09-06 | 20:04 |  |  |  |  | 79.6729 |  | 23378.309
2017-09-06 | 20:06 |  |  |  |  | 79.6015 |  | 23357.3483
2017-09-06 | 20:08 |  |  |  |  | 79.6618 |  | 23375.0537
2017-09-06 | 20:10 |  |  |  |  | 79.6862 |  | 23382.2178
2017-09-06 | 20:12 |  |  |  |  | 79.6706 |  | 23377.6306
2017-09-06 | 20:14 |  |  |  |  | 79.6174 |  | 23362.0226
2017-09-06 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 79.5999 | 0 | 23356.8779
2017-09-06 | 20:16 |  |  |  |  | 79.58 |  | 23351.0372
2017-09-06 | 20:18 |  |  |  |  | 79.5156 |  | 23332.136
2017-09-06 | 20:20 |  |  |  |  | 79.4584 |  | 23315.3548
2017-09-06 | 20:22 |  |  |  |  | 79.4555 |  | 23314.5153
2017-09-06 | 20:24 |  |  |  |  | 79.5224 |  | 23334.1398
2017-09-06 | 20:26 |  |  |  |  | 79.5583 |  | 23344.666
2017-09-06 | 20:28 |  |  |  |  | 79.5531 |  | 23343.166
2017-09-06 | 20:30 | 1.7811 | 0 | 0 | 1.5 | 79.4805 | 0 | 23321.8358
2017-09-06 | 20:32 |  |  |  |  | 79.4163 |  | 23302.9974
2017-09-06 | 20:34 |  |  |  |  | 79.3626 |  | 23287.2414
2017-09-06 | 20:36 |  |  |  |  | 79.3 |  | 23268.8957
2017-09-06 | 20:38 |  |  |  |  | 79.2286 |  | 23247.9481
2017-09-06 | 20:40 |  |  |  |  | 79.1951 |  | 23238.1092
2017-09-06 | 20:42 |  |  |  |  | 79.1354 |  | 23220.5982
2017-09-06 | 20:44 |  |  |  |  | 79.1536 |  | 23225.9307
2017-09-06 | 20:45 | 1.7421 | 0 | 0 | 1.5 | 79.1859 | 0 | 23235.3938
2017-09-06 | 20:46 |  |  |  |  | 79.2151 |  | 23243.959
2017-09-06 | 20:48 |  |  |  |  | 79.2421 |  | 23251.9106
2017-09-06 | 20:50 |  |  |  |  | 79.1698 |  | 23230.6722
2017-09-06 | 20:52 |  |  |  |  | 79.1255 |  | 23217.6857
2017-09-06 | 20:54 |  |  |  |  | 79.066 |  | 23200.2173
2017-09-06 | 20:56 |  |  |  |  | 79.0404 |  | 23192.7243
2017-09-06 | 20:58 |  |  |  |  | 78.9785 |  | 23174.5464
2017-09-06 | 21:00 | 1.7795 | 0 | 0 | 1.5 | 78.9225 | 0 | 23158.1188
2017-09-06 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-06 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:45 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 5:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 5:02 |  |  |  |  | 69.625 |  | 20429.9643
2017-09-07 | 5:04 |  |  |  |  | 99.9912 |  | 29340.2647
2017-09-07 | 5:06 |  |  |  |  | 99.817 |  | 29289.1533
2017-09-07 | 5:08 |  |  |  |  | 99.2427 |  | 29120.6478
2017-09-07 | 5:10 |  |  |  |  | 98.7928 |  | 28988.6372
2017-09-07 | 5:12 |  |  |  |  | 98.4516 |  | 28888.5076
2017-09-07 | 5:14 |  |  |  |  | 98.1123 |  | 28788.9623
2017-09-07 | 5:15 | 1.8762 | 0 | 0 | 1.5 | 97.8966 | 0 | 28725.6727
2017-09-07 | 5:16 |  |  |  |  | 97.6543 |  | 28654.5585
2017-09-07 | 5:18 |  |  |  |  | 97.2741 |  | 28542.987
2017-09-07 | 5:20 |  |  |  |  | 96.9426 |  | 28445.7298
2017-09-07 | 5:22 |  |  |  |  | 96.6908 |  | 28371.8445
2017-09-07 | 5:24 |  |  |  |  | 96.3023 |  | 28257.8528
2017-09-07 | 5:26 |  |  |  |  | 95.7124 |  | 28084.7557
2017-09-07 | 5:28 |  |  |  |  | 95.0901 |  | 27902.1419
2017-09-07 | 5:30 | 1.9948 | 0 | 0 | 1.5 | 94.2686 | 0 | 27661.0986
2017-09-07 | 5:32 |  |  |  |  | 93.594 |  | 27463.1678
2017-09-07 | 5:34 |  |  |  |  | 92.7543 |  | 27216.7491
2017-09-07 | 5:36 |  |  |  |  | 91.9641 |  | 26984.8798
2017-09-07 | 5:38 |  |  |  |  | 91.2124 |  | 26764.3339
2017-09-07 | 5:40 |  |  |  |  | 90.4953 |  | 26553.9089
2017-09-07 | 5:42 |  |  |  |  | 89.799 |  | 26349.6046
2017-09-07 | 5:44 |  |  |  |  | 89.159 |  | 26161.7971
2017-09-07 | 5:45 | 1.9457 | 0 | 0 | 1.5 | 88.8885 | 0 | 26082.4267
2017-09-07 | 5:46 |  |  |  |  | 88.5816 |  | 25992.3668
2017-09-07 | 5:48 |  |  |  |  | 88.0382 |  | 25832.9347
2017-09-07 | 5:50 |  |  |  |  | 87.5356 |  | 25685.4434
2017-09-07 | 5:52 |  |  |  |  | 87.0928 |  | 25555.5215
2017-09-07 | 5:54 |  |  |  |  | 86.6823 |  | 25435.0579
2017-09-07 | 5:56 |  |  |  |  | 86.2791 |  | 25316.746
2017-09-07 | 5:58 |  |  |  |  | 85.8907 |  | 25202.7836
2017-09-07 | 6:00 | 1.8521 | 0 | 0 | 1.5 | 85.5543 | 0 | 25104.0845
2017-09-07 | 6:02 |  |  |  |  | 85.1812 |  | 24994.5861
2017-09-07 | 6:04 |  |  |  |  | 84.8745 |  | 24904.5957
2017-09-07 | 6:06 |  |  |  |  | 84.5298 |  | 24803.452
2017-09-07 | 6:08 |  |  |  |  | 84.2309 |  | 24715.7491
2017-09-07 | 6:10 |  |  |  |  | 83.9462 |  | 24632.2262
2017-09-07 | 6:12 |  |  |  |  | 83.6874 |  | 24556.2745
2017-09-07 | 6:14 |  |  |  |  | 83.4055 |  | 24473.5641
2017-09-07 | 6:15 | 1.8482 | 0 | 0 | 1.5 | 83.2555 | 0 | 24429.5404
2017-09-07 | 6:16 |  |  |  |  | 83.1323 |  | 24393.3812
2017-09-07 | 6:18 |  |  |  |  | 82.8553 |  | 24312.1015
2017-09-07 | 6:20 |  |  |  |  | 82.6403 |  | 24249.0131
2017-09-07 | 6:22 |  |  |  |  | 82.3966 |  | 24177.5251
2017-09-07 | 6:24 |  |  |  |  | 82.141 |  | 24102.518
2017-09-07 | 6:26 |  |  |  |  | 81.9641 |  | 24050.6231
2017-09-07 | 6:28 |  |  |  |  | 81.7568 |  | 23989.7939
2017-09-07 | 6:30 | 1.8333 | 0 | 0 | 1.5 | 81.5724 | 0 | 23935.6693
2017-09-07 | 6:32 |  |  |  |  | 81.3907 |  | 23882.3439
2017-09-07 | 6:34 |  |  |  |  | 81.2081 |  | 23828.79
2017-09-07 | 6:36 |  |  |  |  | 81.086 |  | 23792.9553
2017-09-07 | 6:38 |  |  |  |  | 80.9542 |  | 23754.2644
2017-09-07 | 6:40 |  |  |  |  | 80.7841 |  | 23704.3507
2017-09-07 | 6:42 |  |  |  |  | 80.6878 |  | 23676.1074
2017-09-07 | 6:44 |  |  |  |  | 80.5629 |  | 23639.4693
2017-09-07 | 6:45 | 1.7709 | 0 | 0 | 1.5 | 80.5065 | 0 | 23622.9005
2017-09-07 | 6:46 |  |  |  |  | 80.4251 |  | 23599.0116
2017-09-07 | 6:48 |  |  |  |  | 80.3052 |  | 23563.8307
2017-09-07 | 6:50 |  |  |  |  | 80.183 |  | 23527.9849
2017-09-07 | 6:52 |  |  |  |  | 80.1121 |  | 23507.172
2017-09-07 | 6:54 |  |  |  |  | 80.0374 |  | 23485.2643
2017-09-07 | 6:56 |  |  |  |  | 79.8965 |  | 23443.9091
2017-09-07 | 6:58 |  |  |  |  | 79.8326 |  | 23425.1667
2017-09-07 | 7:00 | 1.7912 | 0 | 0 | 1.5 | 79.7394 | 0 | 23397.8259
2017-09-07 | 7:02 |  |  |  |  | 79.6547 |  | 23372.9651
2017-09-07 | 7:04 |  |  |  |  | 79.5867 |  | 23353.0005
2017-09-07 | 7:06 |  |  |  |  | 79.4723 |  | 23319.4449
2017-09-07 | 7:08 |  |  |  |  | 79.3802 |  | 23292.4196
2017-09-07 | 7:10 |  |  |  |  | 79.3202 |  | 23274.8012
2017-09-07 | 7:12 |  |  |  |  | 79.2655 |  | 23258.7589
2017-09-07 | 7:14 |  |  |  |  | 79.2452 |  | 23252.7926
2017-09-07 | 7:15 | 1.7795 | 0 | 0 | 1.5 | 79.1785 | 0 | 23233.24
2017-09-07 | 7:16 |  |  |  |  | 79.1889 |  | 23236.2981
2017-09-07 | 7:18 |  |  |  |  | 79.1423 |  | 23222.5974
2017-09-07 | 7:20 |  |  |  |  | 79.0751 |  | 23202.8857
2017-09-07 | 7:22 |  |  |  |  | 79.0972 |  | 23209.3869
2017-09-07 | 7:24 |  |  |  |  | 78.9929 |  | 23178.7885
2017-09-07 | 7:26 |  |  |  |  | 78.9252 |  | 23158.9069
2017-09-07 | 7:28 |  |  |  |  | 78.9261 |  | 23159.171
2017-09-07 | 7:30 | 1.7639 | 0 | 0 | 1.5 | 78.9005 | 0 | 23151.649
2017-09-07 | 7:32 |  |  |  |  | 78.8777 |  | 23144.9755
2017-09-07 | 7:34 |  |  |  |  | 78.8395 |  | 23133.7666
2017-09-07 | 7:36 |  |  |  |  | 78.8714 |  | 23143.1108
2017-09-07 | 7:38 |  |  |  |  | 78.8209 |  | 23128.2973
2017-09-07 | 7:40 |  |  |  |  | 78.8357 |  | 23132.638
2017-09-07 | 7:42 |  |  |  |  | 78.8741 |  | 23143.9077
2017-09-07 | 7:44 |  |  |  |  | 78.8724 |  | 23143.4083
2017-09-07 | 7:45 | 1.7569 | 0 | 0 | 1.5 | 78.8359 | 0 | 23132.7076
2017-09-07 | 7:46 |  |  |  |  | 78.8667 |  | 23141.754
2017-09-07 | 7:48 |  |  |  |  | 78.8546 |  | 23138.1967
2017-09-07 | 7:50 |  |  |  |  | 78.8787 |  | 23145.2555
2017-09-07 | 7:52 |  |  |  |  | 78.8426 |  | 23134.6618
2017-09-07 | 7:54 |  |  |  |  | 78.8663 |  | 23141.6175
2017-09-07 | 7:56 |  |  |  |  | 78.8439 |  | 23135.0424
2017-09-07 | 7:58 |  |  |  |  | 78.8511 |  | 23137.1559
2017-09-07 | 8:00 | 1.7631 | 0 | 0 | 1.5 | 78.8262 | 0 | 23129.8534
2017-09-07 | 8:02 |  |  |  |  | 78.8447 |  | 23135.3021
2017-09-07 | 8:04 |  |  |  |  | 78.9184 |  | 23156.9122
2017-09-07 | 8:06 |  |  |  |  | 78.9254 |  | 23158.965
2017-09-07 | 8:08 |  |  |  |  | 78.9685 |  | 23171.6001
2017-09-07 | 8:10 |  |  |  |  | 79.0232 |  | 23187.6582
2017-09-07 | 8:12 |  |  |  |  | 79.1644 |  | 23229.0874
2017-09-07 | 8:14 |  |  |  |  | 79.2409 |  | 23251.5435
2017-09-07 | 8:15 | 1.7062 | 0 | 0 | 1.5 | 79.3258 | 0 | 23276.4421
2017-09-07 | 8:16 |  |  |  |  | 79.3617 |  | 23286.9976
2017-09-07 | 8:18 |  |  |  |  | 79.5089 |  | 23330.1774
2017-09-07 | 8:20 |  |  |  |  | 79.6669 |  | 23376.5382
2017-09-07 | 8:22 |  |  |  |  | 79.8345 |  | 23425.7377
2017-09-07 | 8:24 |  |  |  |  | 79.9405 |  | 23456.8217
2017-09-07 | 8:26 |  |  |  |  | 79.9515 |  | 23460.0453
2017-09-07 | 8:28 |  |  |  |  | 80.026 |  | 23481.9219
2017-09-07 | 8:30 | 1.721 | 0 | 0 | 1.5 | 80.0846 | 0 | 23499.1104
2017-09-07 | 8:32 |  |  |  |  | 80.1318 |  | 23512.9658
2017-09-07 | 8:34 |  |  |  |  | 80.2058 |  | 23534.6742
2017-09-07 | 8:36 |  |  |  |  | 80.2534 |  | 23548.6546
2017-09-07 | 8:38 |  |  |  |  | 80.2715 |  | 23553.9381
2017-09-07 | 8:40 |  |  |  |  | 80.3043 |  | 23563.5889
2017-09-07 | 8:42 |  |  |  |  | 80.3995 |  | 23591.5054
2017-09-07 | 8:44 |  |  |  |  | 80.5366 |  | 23631.7254
2017-09-07 | 8:45 | 1.7187 | 0 | 0 | 1.5 | 80.562 | 0 | 23639.2005
2017-09-07 | 8:46 |  |  |  |  | 80.6247 |  | 23657.6002
2017-09-07 | 8:48 |  |  |  |  | 80.7731 |  | 23701.1336
2017-09-07 | 8:50 |  |  |  |  | 80.8238 |  | 23716.0254
2017-09-07 | 8:52 |  |  |  |  | 80.7869 |  | 23705.1835
2017-09-07 | 8:54 |  |  |  |  | 80.8165 |  | 23713.8672
2017-09-07 | 8:56 |  |  |  |  | 80.8288 |  | 23717.4828
2017-09-07 | 8:58 |  |  |  |  | 80.8492 |  | 23723.4556
2017-09-07 | 9:00 | 1.7413 | 0 | 0 | 1.5 | 80.8544 | 0 | 23724.9981
2017-09-07 | 9:02 |  |  |  |  | 80.8871 |  | 23734.5997
2017-09-07 | 9:04 |  |  |  |  | 81.0499 |  | 23782.3687
2017-09-07 | 9:06 |  |  |  |  | 81.1367 |  | 23807.8157
2017-09-07 | 9:08 |  |  |  |  | 81.1922 |  | 23824.0978
2017-09-07 | 9:10 |  |  |  |  | 81.1769 |  | 23819.6203
2017-09-07 | 9:12 |  |  |  |  | 81.1986 |  | 23825.9915
2017-09-07 | 9:14 |  |  |  |  | 81.2117 |  | 23829.8422
2017-09-07 | 9:15 | 1.7468 | 0 | 0 | 1.5 | 81.2159 | 0 | 23831.0758
2017-09-07 | 9:16 |  |  |  |  | 81.2726 |  | 23847.6979
2017-09-07 | 9:18 |  |  |  |  | 81.3421 |  | 23868.0991
2017-09-07 | 9:20 |  |  |  |  | 81.5505 |  | 23929.2397
2017-09-07 | 9:22 |  |  |  |  | 81.7403 |  | 23984.9515
2017-09-07 | 9:24 |  |  |  |  | 81.8327 |  | 24012.0599
2017-09-07 | 9:26 |  |  |  |  | 81.8337 |  | 24012.3574
2017-09-07 | 9:28 |  |  |  |  | 81.8722 |  | 24023.645
2017-09-07 | 9:30 | 1.7507 | 0 | 0 | 1.5 | 81.8829 | 0 | 24026.797
2017-09-07 | 9:32 |  |  |  |  | 81.9089 |  | 24034.3974
2017-09-07 | 9:34 |  |  |  |  | 81.9384 |  | 24043.0589
2017-09-07 | 9:36 |  |  |  |  | 82.1077 |  | 24092.7375
2017-09-07 | 9:38 |  |  |  |  | 82.1266 |  | 24098.278
2017-09-07 | 9:40 |  |  |  |  | 82.1831 |  | 24114.8825
2017-09-07 | 9:42 |  |  |  |  | 82.0622 |  | 24079.4038
2017-09-07 | 9:44 |  |  |  |  | 82.0181 |  | 24066.4395
2017-09-07 | 9:45 | 1.7616 | 0 | 0 | 1.5 | 81.9724 | 0 | 24053.0568
2017-09-07 | 9:46 |  |  |  |  | 81.9319 |  | 24041.1739
2017-09-07 | 9:48 |  |  |  |  | 81.9341 |  | 24041.8097
2017-09-07 | 9:50 |  |  |  |  | 82.0121 |  | 24064.6977
2017-09-07 | 9:52 |  |  |  |  | 82.1063 |  | 24092.339
2017-09-07 | 9:54 |  |  |  |  | 82.1069 |  | 24092.5045
2017-09-07 | 9:56 |  |  |  |  | 82.0658 |  | 24080.4537
2017-09-07 | 9:58 |  |  |  |  | 81.9995 |  | 24060.9885
2017-09-07 | 10:00 | 1.7709 | 0 | 0 | 1.5 | 81.943 | 0 | 24044.4245
2017-09-07 | 10:02 |  |  |  |  | 81.9637 |  | 24050.4958
2017-09-07 | 10:04 |  |  |  |  | 82.0823 |  | 24085.2914
2017-09-07 | 10:06 |  |  |  |  | 82.2633 |  | 24138.4111
2017-09-07 | 10:08 |  |  |  |  | 82.3874 |  | 24174.8053
2017-09-07 | 10:10 |  |  |  |  | 82.3827 |  | 24173.4465
2017-09-07 | 10:12 |  |  |  |  | 82.3095 |  | 24151.9684
2017-09-07 | 10:14 |  |  |  |  | 82.3245 |  | 24156.3584
2017-09-07 | 10:15 | 1.7436 | 0 | 0 | 1.5 | 82.3581 | 0 | 24166.2132
2017-09-07 | 10:16 |  |  |  |  | 82.4297 |  | 24187.2435
2017-09-07 | 10:18 |  |  |  |  | 82.5299 |  | 24216.6192
2017-09-07 | 10:20 |  |  |  |  | 82.636 |  | 24247.7728
2017-09-07 | 10:22 |  |  |  |  | 82.7023 |  | 24267.2069
2017-09-07 | 10:24 |  |  |  |  | 82.6892 |  | 24263.363
2017-09-07 | 10:26 |  |  |  |  | 82.6288 |  | 24245.6639
2017-09-07 | 10:28 |  |  |  |  | 82.5605 |  | 24225.6234
2017-09-07 | 10:30 | 1.7327 | 0 | 0 | 1.5 | 82.6196 | 0 | 24242.9395
2017-09-07 | 10:32 |  |  |  |  | 82.7653 |  | 24285.7073
2017-09-07 | 10:34 |  |  |  |  | 82.8999 |  | 24325.1931
2017-09-07 | 10:36 |  |  |  |  | 82.9023 |  | 24325.8961
2017-09-07 | 10:38 |  |  |  |  | 82.8995 |  | 24325.0745
2017-09-07 | 10:40 |  |  |  |  | 82.8864 |  | 24321.2465
2017-09-07 | 10:42 |  |  |  |  | 82.8994 |  | 24325.0499
2017-09-07 | 10:44 |  |  |  |  | 83.0038 |  | 24355.6909
2017-09-07 | 10:45 | 1.739 | 0 | 0 | 1.5 | 83.0037 | 0 | 24355.6595
2017-09-07 | 10:46 |  |  |  |  | 83.0685 |  | 24374.6637
2017-09-07 | 10:48 |  |  |  |  | 83.1206 |  | 24389.9695
2017-09-07 | 10:50 |  |  |  |  | 83.1044 |  | 24385.2189
2017-09-07 | 10:52 |  |  |  |  | 83.139 |  | 24395.3557
2017-09-07 | 10:54 |  |  |  |  | 83.219 |  | 24418.8329
2017-09-07 | 10:56 |  |  |  |  | 83.2968 |  | 24441.6651
2017-09-07 | 10:58 |  |  |  |  | 83.4099 |  | 24474.8513
2017-09-07 | 11:00 | 1.7163 | 0 | 0 | 1.5 | 83.5547 | 0 | 24517.3327
2017-09-07 | 11:02 |  |  |  |  | 83.622 |  | 24537.0866
2017-09-07 | 11:04 |  |  |  |  | 83.5335 |  | 24511.1159
2017-09-07 | 11:06 |  |  |  |  | 83.537 |  | 24512.1344
2017-09-07 | 11:08 |  |  |  |  | 83.5743 |  | 24523.0792
2017-09-07 | 11:10 |  |  |  |  | 83.6396 |  | 24542.258
2017-09-07 | 11:12 |  |  |  |  | 83.7045 |  | 24561.2892
2017-09-07 | 11:14 |  |  |  |  | 83.7765 |  | 24582.4067
2017-09-07 | 11:15 | 1.7374 | 0 | 0 | 1.5 | 83.7757 | 0 | 24582.1828
2017-09-07 | 11:16 |  |  |  |  | 83.7478 |  | 24573.9914
2017-09-07 | 11:18 |  |  |  |  | 83.7022 |  | 24560.6287
2017-09-07 | 11:20 |  |  |  |  | 83.7365 |  | 24570.6692
2017-09-07 | 11:22 |  |  |  |  | 83.7771 |  | 24582.6036
2017-09-07 | 11:24 |  |  |  |  | 83.8824 |  | 24613.4995
2017-09-07 | 11:26 |  |  |  |  | 83.9516 |  | 24633.8069
2017-09-07 | 11:28 |  |  |  |  | 83.9928 |  | 24645.9002
2017-09-07 | 11:30 | 1.7748 | 0 | 0 | 1.5 | 83.9445 | 0 | 24631.7135
2017-09-07 | 11:32 |  |  |  |  | 83.9063 |  | 24620.5157
2017-09-07 | 11:34 |  |  |  |  | 83.9538 |  | 24634.4515
2017-09-07 | 11:36 |  |  |  |  | 84.032 |  | 24657.3756
2017-09-07 | 11:38 |  |  |  |  | 84.0422 |  | 24660.3844
2017-09-07 | 11:40 |  |  |  |  | 83.9995 |  | 24647.8389
2017-09-07 | 11:42 |  |  |  |  | 84.069 |  | 24668.2533
2017-09-07 | 11:44 |  |  |  |  | 84.0839 |  | 24672.6166
2017-09-07 | 11:45 | 1.7452 | 0 | 0 | 1.5 | 84.0756 | 0 | 24670.1964
2017-09-07 | 11:46 |  |  |  |  | 84.0079 |  | 24650.3058
2017-09-07 | 11:48 |  |  |  |  | 83.9723 |  | 24639.8758
2017-09-07 | 11:50 |  |  |  |  | 84.013 |  | 24651.8058
2017-09-07 | 11:52 |  |  |  |  | 84.0538 |  | 24663.7961
2017-09-07 | 11:54 |  |  |  |  | 84.1 |  | 24677.3558
2017-09-07 | 11:56 |  |  |  |  | 84.1519 |  | 24692.5653
2017-09-07 | 11:58 |  |  |  |  | 84.1832 |  | 24701.7529
2017-09-07 | 12:00 | 1.7296 | 0 | 0 | 1.5 | 84.2481 | 0 | 24720.7996
2017-09-07 | 12:02 |  |  |  |  | 84.2786 |  | 24729.7565
2017-09-07 | 12:04 |  |  |  |  | 84.3126 |  | 24739.7322
2017-09-07 | 12:06 |  |  |  |  | 84.2133 |  | 24710.5892
2017-09-07 | 12:08 |  |  |  |  | 84.2412 |  | 24718.7826
2017-09-07 | 12:10 |  |  |  |  | 84.3824 |  | 24760.2206
2017-09-07 | 12:12 |  |  |  |  | 84.4993 |  | 24794.5174
2017-09-07 | 12:14 |  |  |  |  | 84.5306 |  | 24803.6914
2017-09-07 | 12:15 | 1.7616 | 0 | 0 | 1.5 | 84.5049 | 0 | 24796.138
2017-09-07 | 12:16 |  |  |  |  | 84.5217 |  | 24801.0788
2017-09-07 | 12:18 |  |  |  |  | 84.5117 |  | 24798.1462
2017-09-07 | 12:20 |  |  |  |  | 84.5076 |  | 24796.9396
2017-09-07 | 12:22 |  |  |  |  | 84.5586 |  | 24811.9209
2017-09-07 | 12:24 |  |  |  |  | 84.537 |  | 24805.5785
2017-09-07 | 12:26 |  |  |  |  | 84.4479 |  | 24779.4173
2017-09-07 | 12:28 |  |  |  |  | 84.4892 |  | 24791.5532
2017-09-07 | 12:30 | 1.6929 | 0 | 0 | 1.5 | 84.6267 | 0 | 24831.9011
2017-09-07 | 12:32 |  |  |  |  | 84.6581 |  | 24841.093
2017-09-07 | 12:34 |  |  |  |  | 84.6534 |  | 24839.7119
2017-09-07 | 12:36 |  |  |  |  | 84.6168 |  | 24828.9862
2017-09-07 | 12:38 |  |  |  |  | 84.5476 |  | 24808.6771
2017-09-07 | 12:40 |  |  |  |  | 84.4082 |  | 24767.7828
2017-09-07 | 12:42 |  |  |  |  | 84.2873 |  | 24732.2976
2017-09-07 | 12:44 |  |  |  |  | 84.3922 |  | 24763.0707
2017-09-07 | 12:45 | 1.7179 | 0 | 0 | 1.5 | 84.4553 | 0 | 24781.6092
2017-09-07 | 12:46 |  |  |  |  | 84.5604 |  | 24812.4312
2017-09-07 | 12:48 |  |  |  |  | 84.7573 |  | 24870.2228
2017-09-07 | 12:50 |  |  |  |  | 84.9451 |  | 24925.3079
2017-09-07 | 12:52 |  |  |  |  | 85.0816 |  | 24965.3644
2017-09-07 | 12:54 |  |  |  |  | 85.1868 |  | 24996.2472
2017-09-07 | 12:56 |  |  |  |  | 85.2118 |  | 25003.5788
2017-09-07 | 12:58 |  |  |  |  | 85.2217 |  | 25006.4779
2017-09-07 | 13:00 | 1.7304 | 0 | 0 | 1.5 | 85.3216 | 0 | 25035.8025
2017-09-07 | 13:02 |  |  |  |  | 85.1989 |  | 24999.8021
2017-09-07 | 13:04 |  |  |  |  | 85.1107 |  | 24973.9073
2017-09-07 | 13:06 |  |  |  |  | 85.1749 |  | 24992.7369
2017-09-07 | 13:08 |  |  |  |  | 85.2746 |  | 25022.0143
2017-09-07 | 13:10 |  |  |  |  | 85.4507 |  | 25073.6809
2017-09-07 | 13:12 |  |  |  |  | 85.4403 |  | 25070.6387
2017-09-07 | 13:14 |  |  |  |  | 85.5445 |  | 25101.1966
2017-09-07 | 13:15 | 1.7179 | 0 | 0 | 1.5 | 85.5724 | 0 | 25109.3856
2017-09-07 | 13:16 |  |  |  |  | 85.6049 |  | 25118.9159
2017-09-07 | 13:18 |  |  |  |  | 85.6198 |  | 25123.3035
2017-09-07 | 13:20 |  |  |  |  | 85.6811 |  | 25141.2801
2017-09-07 | 13:22 |  |  |  |  | 85.8932 |  | 25203.5222
2017-09-07 | 13:24 |  |  |  |  | 85.9624 |  | 25223.836
2017-09-07 | 13:26 |  |  |  |  | 85.9984 |  | 25234.3982
2017-09-07 | 13:28 |  |  |  |  | 86.0465 |  | 25248.513
2017-09-07 | 13:30 | 1.7436 | 0 | 0 | 1.5 | 86.0809 | 0 | 25258.6005
2017-09-07 | 13:32 |  |  |  |  | 86.1088 |  | 25266.7942
2017-09-07 | 13:34 |  |  |  |  | 86.0449 |  | 25248.0318
2017-09-07 | 13:36 |  |  |  |  | 85.9496 |  | 25220.0727
2017-09-07 | 13:38 |  |  |  |  | 86.0736 |  | 25256.4494
2017-09-07 | 13:40 |  |  |  |  | 86.1416 |  | 25276.4116
2017-09-07 | 13:42 |  |  |  |  | 86.2751 |  | 25315.5749
2017-09-07 | 13:44 |  |  |  |  | 86.379 |  | 25346.0592
2017-09-07 | 13:45 | 1.7195 | 0 | 0 | 1.5 | 86.44 | 0 | 25363.9731
2017-09-07 | 13:46 |  |  |  |  | 86.5195 |  | 25387.3071
2017-09-07 | 13:48 |  |  |  |  | 86.5917 |  | 25408.4826
2017-09-07 | 13:50 |  |  |  |  | 86.7378 |  | 25451.349
2017-09-07 | 13:52 |  |  |  |  | 86.8863 |  | 25494.9226
2017-09-07 | 13:54 |  |  |  |  | 87.0079 |  | 25530.5938
2017-09-07 | 13:56 |  |  |  |  | 87.1293 |  | 25566.2178
2017-09-07 | 13:58 |  |  |  |  | 87.2387 |  | 25598.3342
2017-09-07 | 14:00 | 1.7241 | 0 | 0 | 1.5 | 87.2968 | 0 | 25615.3659
2017-09-07 | 14:02 |  |  |  |  | 87.5014 |  | 25675.4164
2017-09-07 | 14:04 |  |  |  |  | 87.5177 |  | 25680.1981
2017-09-07 | 14:06 |  |  |  |  | 87.5877 |  | 25700.7313
2017-09-07 | 14:08 |  |  |  |  | 87.5742 |  | 25696.7645
2017-09-07 | 14:10 |  |  |  |  | 87.6035 |  | 25705.3655
2017-09-07 | 14:12 |  |  |  |  | 87.6029 |  | 25705.1841
2017-09-07 | 14:14 |  |  |  |  | 87.6513 |  | 25719.4066
2017-09-07 | 14:15 | 1.739 | 0 | 0 | 1.5 | 87.6963 | 0 | 25732.5901
2017-09-07 | 14:16 |  |  |  |  | 87.695 |  | 25732.2051
2017-09-07 | 14:18 |  |  |  |  | 87.6087 |  | 25706.8901
2017-09-07 | 14:20 |  |  |  |  | 87.5806 |  | 25698.6518
2017-09-07 | 14:22 |  |  |  |  | 87.544 |  | 25687.9194
2017-09-07 | 14:24 |  |  |  |  | 87.5144 |  | 25679.211
2017-09-07 | 14:26 |  |  |  |  | 87.6027 |  | 25705.1483
2017-09-07 | 14:28 |  |  |  |  | 87.5579 |  | 25691.9892
2017-09-07 | 14:30 | 1.746 | 0 | 0 | 1.5 | 87.5543 | 0 | 25690.9349
2017-09-07 | 14:32 |  |  |  |  | 87.4172 |  | 25650.7059
2017-09-07 | 14:34 |  |  |  |  | 87.3226 |  | 25622.9373
2017-09-07 | 14:36 |  |  |  |  | 87.2947 |  | 25614.7638
2017-09-07 | 14:38 |  |  |  |  | 87.4048 |  | 25647.0703
2017-09-07 | 14:40 |  |  |  |  | 87.5134 |  | 25678.9378
2017-09-07 | 14:42 |  |  |  |  | 87.5887 |  | 25701.0248
2017-09-07 | 14:44 |  |  |  |  | 87.7314 |  | 25742.9038
2017-09-07 | 14:45 | 1.7444 | 0 | 0 | 1.5 | 87.7287 | 0 | 25742.1136
2017-09-07 | 14:46 |  |  |  |  | 87.8165 |  | 25767.8652
2017-09-07 | 14:48 |  |  |  |  | 87.9443 |  | 25805.3562
2017-09-07 | 14:50 |  |  |  |  | 88.0361 |  | 25832.2965
2017-09-07 | 14:52 |  |  |  |  | 88.0845 |  | 25846.5078
2017-09-07 | 14:54 |  |  |  |  | 87.935 |  | 25802.6294
2017-09-07 | 14:56 |  |  |  |  | 87.7593 |  | 25751.0995
2017-09-07 | 14:58 |  |  |  |  | 87.5313 |  | 25684.174
2017-09-07 | 15:00 | 1.8739 | 0 | 0 | 1.5 | 87.186 | 0 | 25582.8669
2017-09-07 | 15:02 |  |  |  |  | 86.8397 |  | 25481.2421
2017-09-07 | 15:04 |  |  |  |  | 86.5392 |  | 25393.0647
2017-09-07 | 15:06 |  |  |  |  | 86.366 |  | 25342.2444
2017-09-07 | 15:08 |  |  |  |  | 86.1274 |  | 25272.2273
2017-09-07 | 15:10 |  |  |  |  | 85.9253 |  | 25212.9269
2017-09-07 | 15:12 |  |  |  |  | 85.857 |  | 25192.8907
2017-09-07 | 15:14 |  |  |  |  | 85.943 |  | 25218.1341
2017-09-07 | 15:15 | 1.7148 | 0 | 0 | 1.5 | 86.0492 | 0 | 25249.2809
2017-09-07 | 15:16 |  |  |  |  | 86.07 |  | 25255.4103
2017-09-07 | 15:18 |  |  |  |  | 86.1661 |  | 25283.5842
2017-09-07 | 15:20 |  |  |  |  | 86.2634 |  | 25312.1588
2017-09-07 | 15:22 |  |  |  |  | 86.3373 |  | 25333.8338
2017-09-07 | 15:24 |  |  |  |  | 86.4486 |  | 25366.476
2017-09-07 | 15:26 |  |  |  |  | 86.5458 |  | 25395.0193
2017-09-07 | 15:28 |  |  |  |  | 86.6686 |  | 25431.0306
2017-09-07 | 15:30 | 1.707 | 0 | 0 | 1.5 | 86.7884 | 0 | 25466.2094
2017-09-07 | 15:32 |  |  |  |  | 86.9414 |  | 25511.0814
2017-09-07 | 15:34 |  |  |  |  | 87.0387 |  | 25539.6537
2017-09-07 | 15:36 |  |  |  |  | 87.1111 |  | 25560.8853
2017-09-07 | 15:38 |  |  |  |  | 87.2899 |  | 25613.3512
2017-09-07 | 15:40 |  |  |  |  | 87.4411 |  | 25657.7308
2017-09-07 | 15:42 |  |  |  |  | 87.595 |  | 25702.8672
2017-09-07 | 15:44 |  |  |  |  | 87.7181 |  | 25738.9927
2017-09-07 | 15:45 | 1.7226 | 0 | 0 | 1.5 | 87.7654 | 0 | 25752.8839
2017-09-07 | 15:46 |  |  |  |  | 87.8394 |  | 25774.6034
2017-09-07 | 15:48 |  |  |  |  | 87.9693 |  | 25812.7013
2017-09-07 | 15:50 |  |  |  |  | 87.8222 |  | 25769.5574
2017-09-07 | 15:52 |  |  |  |  | 87.674 |  | 25726.0531
2017-09-07 | 15:54 |  |  |  |  | 87.3272 |  | 25624.3005
2017-09-07 | 15:56 |  |  |  |  | 87.1242 |  | 25564.7225
2017-09-07 | 15:58 |  |  |  |  | 86.8723 |  | 25490.8058
2017-09-07 | 16:00 | 1.8341 | 0 | 0 | 1.5 | 86.633 | 0 | 25420.6027
2017-09-07 | 16:02 |  |  |  |  | 86.2399 |  | 25305.2392
2017-09-07 | 16:04 |  |  |  |  | 85.8134 |  | 25180.099
2017-09-07 | 16:06 |  |  |  |  | 85.6089 |  | 25120.0887
2017-09-07 | 16:08 |  |  |  |  | 85.4159 |  | 25063.4658
2017-09-07 | 16:10 |  |  |  |  | 85.2797 |  | 25023.4897
2017-09-07 | 16:12 |  |  |  |  | 85.1758 |  | 24993.001
2017-09-07 | 16:14 |  |  |  |  | 85.1437 |  | 24983.5808
2017-09-07 | 16:15 | 1.7405 | 0 | 0 | 1.5 | 85.1656 | 0 | 24990.0124
2017-09-07 | 16:16 |  |  |  |  | 85.2006 |  | 25000.288
2017-09-07 | 16:18 |  |  |  |  | 85.2226 |  | 25006.7487
2017-09-07 | 16:20 |  |  |  |  | 85.2726 |  | 25021.4099
2017-09-07 | 16:22 |  |  |  |  | 85.2999 |  | 25029.4266
2017-09-07 | 16:24 |  |  |  |  | 85.3056 |  | 25031.0945
2017-09-07 | 16:26 |  |  |  |  | 85.3256 |  | 25036.9689
2017-09-07 | 16:28 |  |  |  |  | 85.374 |  | 25051.1597
2017-09-07 | 16:30 | 1.7452 | 0 | 0 | 1.5 | 85.401 | 0 | 25059.0893
2017-09-07 | 16:32 |  |  |  |  | 85.46 |  | 25076.4078
2017-09-07 | 16:34 |  |  |  |  | 85.5719 |  | 25109.2515
2017-09-07 | 16:36 |  |  |  |  | 85.7106 |  | 25149.9507
2017-09-07 | 16:38 |  |  |  |  | 85.8096 |  | 25178.9819
2017-09-07 | 16:40 |  |  |  |  | 85.9738 |  | 25227.1828
2017-09-07 | 16:42 |  |  |  |  | 86.033 |  | 25244.5374
2017-09-07 | 16:44 |  |  |  |  | 86.046 |  | 25248.3408
2017-09-07 | 16:45 | 1.7195 | 0 | 0 | 1.5 | 86.0721 | 0 | 25256.0239
2017-09-07 | 16:46 |  |  |  |  | 86.1089 |  | 25266.8165
2017-09-07 | 16:48 |  |  |  |  | 86.2525 |  | 25308.9352
2017-09-07 | 16:50 |  |  |  |  | 86.3599 |  | 25340.4715
2017-09-07 | 16:52 |  |  |  |  | 86.4316 |  | 25361.4971
2017-09-07 | 16:54 |  |  |  |  | 86.4842 |  | 25376.9329
2017-09-07 | 16:56 |  |  |  |  | 86.5026 |  | 25382.3481
2017-09-07 | 16:58 |  |  |  |  | 86.5113 |  | 25384.8825
2017-09-07 | 17:00 | 1.7436 | 0 | 0 | 1.5 | 86.5188 | 0 | 25387.0943
2017-09-07 | 17:02 |  |  |  |  | 86.4151 |  | 25356.6593
2017-09-07 | 17:04 |  |  |  |  | 86.4032 |  | 25353.1649
2017-09-07 | 17:06 |  |  |  |  | 86.4423 |  | 25364.6447
2017-09-07 | 17:08 |  |  |  |  | 86.4677 |  | 25372.1063
2017-09-07 | 17:10 |  |  |  |  | 86.5303 |  | 25390.4702
2017-09-07 | 17:12 |  |  |  |  | 86.5807 |  | 25405.259
2017-09-07 | 17:14 |  |  |  |  | 86.589 |  | 25407.6924
2017-09-07 | 17:15 | 1.7397 | 0 | 0 | 1.5 | 86.6403 | 0 | 25422.7474
2017-09-07 | 17:16 |  |  |  |  | 86.663 |  | 25429.3941
2017-09-07 | 17:18 |  |  |  |  | 86.6728 |  | 25432.282
2017-09-07 | 17:20 |  |  |  |  | 86.5576 |  | 25398.46
2017-09-07 | 17:22 |  |  |  |  | 86.5095 |  | 25384.3719
2017-09-07 | 17:24 |  |  |  |  | 86.5195 |  | 25387.2868
2017-09-07 | 17:26 |  |  |  |  | 86.4494 |  | 25366.7357
2017-09-07 | 17:28 |  |  |  |  | 86.3913 |  | 25349.6678
2017-09-07 | 17:30 | 1.7904 | 0 | 0 | 1.5 | 86.3205 | 0 | 25328.8998
2017-09-07 | 17:32 |  |  |  |  | 86.32 |  | 25328.761
2017-09-07 | 17:34 |  |  |  |  | 86.2791 |  | 25316.7393
2017-09-07 | 17:36 |  |  |  |  | 86.2412 |  | 25305.6174
2017-09-07 | 17:38 |  |  |  |  | 86.2074 |  | 25295.7045
2017-09-07 | 17:40 |  |  |  |  | 86.1568 |  | 25280.8664
2017-09-07 | 17:42 |  |  |  |  | 86.0224 |  | 25241.4367
2017-09-07 | 17:44 |  |  |  |  | 85.8708 |  | 25196.9315
2017-09-07 | 17:45 | 1.8201 | 0 | 0 | 1.5 | 85.7485 | 0 | 25161.0701
2017-09-07 | 17:46 |  |  |  |  | 85.7769 |  | 25169.4026
2017-09-07 | 17:48 |  |  |  |  | 85.7255 |  | 25154.3207
2017-09-07 | 17:50 |  |  |  |  | 85.6201 |  | 25123.3751
2017-09-07 | 17:52 |  |  |  |  | 85.6024 |  | 25118.177
2017-09-07 | 17:54 |  |  |  |  | 85.4899 |  | 25085.1901
2017-09-07 | 17:56 |  |  |  |  | 85.4021 |  | 25059.4162
2017-09-07 | 17:58 |  |  |  |  | 85.251 |  | 25015.0768
2017-09-07 | 18:00 | 1.8365 | 0 | 0 | 1.5 | 84.987 | 0 | 24937.614
2017-09-07 | 18:02 |  |  |  |  | 84.7075 |  | 24855.6066
2017-09-07 | 18:04 |  |  |  |  | 84.5606 |  | 24812.4873
2017-09-07 | 18:06 |  |  |  |  | 84.4634 |  | 24783.9642
2017-09-07 | 18:08 |  |  |  |  | 84.2725 |  | 24727.9701
2017-09-07 | 18:10 |  |  |  |  | 84.2669 |  | 24726.3225
2017-09-07 | 18:12 |  |  |  |  | 84.1237 |  | 24684.3003
2017-09-07 | 18:14 |  |  |  |  | 83.9896 |  | 24644.951
2017-09-07 | 18:15 | 1.806 | 0 | 0 | 1.5 | 83.866 | 0 | 24608.6685
2017-09-07 | 18:16 |  |  |  |  | 83.8122 |  | 24592.8836
2017-09-07 | 18:18 |  |  |  |  | 83.6936 |  | 24558.1035
2017-09-07 | 18:20 |  |  |  |  | 83.6663 |  | 24550.0934
2017-09-07 | 18:22 |  |  |  |  | 83.6116 |  | 24534.0221
2017-09-07 | 18:24 |  |  |  |  | 83.5556 |  | 24517.5989
2017-09-07 | 18:26 |  |  |  |  | 83.4818 |  | 24495.9306
2017-09-07 | 18:28 |  |  |  |  | 83.3535 |  | 24458.2917
2017-09-07 | 18:30 | 1.8014 | 0 | 0 | 1.5 | 83.1656 | 0 | 24403.1664
2017-09-07 | 18:32 |  |  |  |  | 82.9874 |  | 24350.8842
2017-09-07 | 18:34 |  |  |  |  | 82.8626 |  | 24314.2617
2017-09-07 | 18:36 |  |  |  |  | 82.9219 |  | 24331.6564
2017-09-07 | 18:38 |  |  |  |  | 82.9012 |  | 24325.5871
2017-09-07 | 18:40 |  |  |  |  | 82.8447 |  | 24308.9896
2017-09-07 | 18:42 |  |  |  |  | 82.8023 |  | 24296.5603
2017-09-07 | 18:44 |  |  |  |  | 82.7257 |  | 24274.0772
2017-09-07 | 18:45 | 1.7881 | 0 | 0 | 1.5 | 82.6889 | 0 | 24263.2735
2017-09-07 | 18:46 |  |  |  |  | 82.6985 |  | 24266.0919
2017-09-07 | 18:48 |  |  |  |  | 82.6767 |  | 24259.7162
2017-09-07 | 18:50 |  |  |  |  | 82.6852 |  | 24262.2033
2017-09-07 | 18:52 |  |  |  |  | 82.6759 |  | 24259.4721
2017-09-07 | 18:54 |  |  |  |  | 82.6018 |  | 24237.7144
2017-09-07 | 18:56 |  |  |  |  | 82.3858 |  | 24174.3485
2017-09-07 | 18:58 |  |  |  |  | 82.1658 |  | 24109.8074
2017-09-07 | 19:00 | 1.8006 | 0 | 0 | 1.5 | 82.0053 | 0 | 24062.7121
2017-09-07 | 19:02 |  |  |  |  | 81.8767 |  | 24024.9725
2017-09-07 | 19:04 |  |  |  |  | 81.7935 |  | 24000.5595
2017-09-07 | 19:06 |  |  |  |  | 81.7727 |  | 23994.4524
2017-09-07 | 19:08 |  |  |  |  | 81.6505 |  | 23958.591
2017-09-07 | 19:10 |  |  |  |  | 81.4451 |  | 23898.3258
2017-09-07 | 19:12 |  |  |  |  | 81.2591 |  | 23843.7534
2017-09-07 | 19:14 |  |  |  |  | 81.1016 |  | 23797.5269
2017-09-07 | 19:15 | 1.7889 | 0 | 0 | 1.5 | 81.0748 | 0 | 23789.6645
2017-09-07 | 19:16 |  |  |  |  | 81.0586 |  | 23784.9162
2017-09-07 | 19:18 |  |  |  |  | 81.0447 |  | 23780.8194
2017-09-07 | 19:20 |  |  |  |  | 80.9993 |  | 23767.515
2017-09-07 | 19:22 |  |  |  |  | 80.9204 |  | 23744.3448
2017-09-07 | 19:24 |  |  |  |  | 80.7986 |  | 23708.6222
2017-09-07 | 19:26 |  |  |  |  | 80.6967 |  | 23678.7153
2017-09-07 | 19:28 |  |  |  |  | 80.5231 |  | 23627.7855
2017-09-07 | 19:30 | 1.7803 | 0 | 0 | 1.5 | 80.5303 | 0 | 23629.8853
2017-09-07 | 19:32 |  |  |  |  | 80.5372 |  | 23631.9246
2017-09-07 | 19:34 |  |  |  |  | 80.4789 |  | 23614.8189
2017-09-07 | 19:36 |  |  |  |  | 80.3597 |  | 23579.8305
2017-09-07 | 19:38 |  |  |  |  | 80.2402 |  | 23544.7684
2017-09-07 | 19:40 |  |  |  |  | 80.1189 |  | 23509.1711
2017-09-07 | 19:42 |  |  |  |  | 80.0862 |  | 23499.5851
2017-09-07 | 19:44 |  |  |  |  | 80.0989 |  | 23503.2991
2017-09-07 | 19:45 | 1.746 | 0 | 0 | 1.5 | 80.11 | 0 | 23506.5517
2017-09-07 | 19:46 |  |  |  |  | 80.1111 |  | 23506.8742
2017-09-07 | 19:48 |  |  |  |  | 80.0539 |  | 23490.093
2017-09-07 | 19:50 |  |  |  |  | 79.9273 |  | 23452.9579
2017-09-07 | 19:52 |  |  |  |  | 79.8066 |  | 23417.5328
2017-09-07 | 19:54 |  |  |  |  | 79.7003 |  | 23386.3481
2017-09-07 | 19:56 |  |  |  |  | 79.5843 |  | 23352.3066
2017-09-07 | 19:58 |  |  |  |  | 79.5282 |  | 23335.8479
2017-09-07 | 20:00 | 1.7678 | 0 | 0 | 1.5 | 79.4915 | 0 | 23325.0664
2017-09-07 | 20:02 |  |  |  |  | 79.5117 |  | 23331.0078
2017-09-07 | 20:04 |  |  |  |  | 79.4927 |  | 23325.4335
2017-09-07 | 20:06 |  |  |  |  | 79.4221 |  | 23304.7145
2017-09-07 | 20:08 |  |  |  |  | 79.3121 |  | 23272.4236
2017-09-07 | 20:10 |  |  |  |  | 79.2192 |  | 23245.1679
2017-09-07 | 20:12 |  |  |  |  | 79.1469 |  | 23223.9653
2017-09-07 | 20:14 |  |  |  |  | 79.0575 |  | 23197.7278
2017-09-07 | 20:15 | 1.7561 | 0 | 0 | 1.5 | 79.0342 | 0 | 23190.8886
2017-09-07 | 20:16 |  |  |  |  | 78.9975 |  | 23180.1183
2017-09-07 | 20:18 |  |  |  |  | 79.0711 |  | 23201.7217
2017-09-07 | 20:20 |  |  |  |  | 79.0832 |  | 23205.2587
2017-09-07 | 20:22 |  |  |  |  | 79.0193 |  | 23186.5276
2017-09-07 | 20:24 |  |  |  |  | 78.9069 |  | 23153.534
2017-09-07 | 20:26 |  |  |  |  | 78.8226 |  | 23128.81
2017-09-07 | 20:28 |  |  |  |  | 78.761 |  | 23110.7304
2017-09-07 | 20:30 | 1.785 | 0 | 0 | 1.5 | 78.6598 | 0 | 23081.0275
2017-09-07 | 20:32 |  |  |  |  | 78.5838 |  | 23058.7304
2017-09-07 | 20:34 |  |  |  |  | 78.4888 |  | 23030.8609
2017-09-07 | 20:36 |  |  |  |  | 78.4721 |  | 23025.9471
2017-09-07 | 20:38 |  |  |  |  | 78.4517 |  | 23019.9676
2017-09-07 | 20:40 |  |  |  |  | 78.3954 |  | 23003.4549
2017-09-07 | 20:42 |  |  |  |  | 78.2639 |  | 22964.8579
2017-09-07 | 20:44 |  |  |  |  | 78.2092 |  | 22948.82
2017-09-07 | 20:45 | 1.7655 | 0 | 0 | 1.5 | 78.1878 | 0 | 22942.5204
2017-09-07 | 20:46 |  |  |  |  | 78.1496 |  | 22931.3179
2017-09-07 | 20:48 |  |  |  |  | 78.0836 |  | 22911.9601
2017-09-07 | 20:50 |  |  |  |  | 78.0036 |  | 22888.4852
2017-09-07 | 20:52 |  |  |  |  | 77.8978 |  | 22857.4325
2017-09-07 | 20:54 |  |  |  |  | 77.864 |  | 22847.5331
2017-09-07 | 20:56 |  |  |  |  | 77.828 |  | 22836.9732
2017-09-07 | 20:58 |  |  |  |  | 77.8463 |  | 22842.3213
2017-09-07 | 21:00 | 1.7382 | 0 | 0 | 1.5 | 77.8949 | 0 | 22856.5795
2017-09-07 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-07 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-07 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-08 | 5:04 |  |  |  |  | 99.9807 |  | 29337.1934
2017-09-08 | 5:06 |  |  |  |  | 99.5849 |  | 29221.0684
2017-09-08 | 5:08 |  |  |  |  | 98.8304 |  | 28999.6628
2017-09-08 | 5:10 |  |  |  |  | 98.1774 |  | 28808.0671
2017-09-08 | 5:12 |  |  |  |  | 97.6793 |  | 28661.8969
2017-09-08 | 5:14 |  |  |  |  | 97.2626 |  | 28539.6225
2017-09-08 | 5:15 | 1.8614 | 0 | 0 | 1.5 | 97.0419 | 0 | 28474.8775
2017-09-08 | 5:16 |  |  |  |  | 96.8012 |  | 28404.2314
2017-09-08 | 5:18 |  |  |  |  | 96.5385 |  | 28327.1647
2017-09-08 | 5:20 |  |  |  |  | 96.2263 |  | 28235.5578
2017-09-08 | 5:22 |  |  |  |  | 95.9272 |  | 28147.7948
2017-09-08 | 5:24 |  |  |  |  | 95.6852 |  | 28076.7748
2017-09-08 | 5:26 |  |  |  |  | 95.3264 |  | 27971.4762
2017-09-08 | 5:28 |  |  |  |  | 94.8522 |  | 27832.3511
2017-09-08 | 5:30 | 1.909 | 0 | 0 | 1.5 | 94.3765 | 0 | 27692.7601
2017-09-08 | 5:32 |  |  |  |  | 93.8786 |  | 27546.6749
2017-09-08 | 5:34 |  |  |  |  | 93.2166 |  | 27352.4223
2017-09-08 | 5:36 |  |  |  |  | 92.5089 |  | 27144.7441
2017-09-08 | 5:38 |  |  |  |  | 91.6707 |  | 26898.8137
2017-09-08 | 5:40 |  |  |  |  | 90.9357 |  | 26683.1302
2017-09-08 | 5:42 |  |  |  |  | 90.187 |  | 26463.437
2017-09-08 | 5:44 |  |  |  |  | 89.4803 |  | 26256.0657
2017-09-08 | 5:45 | 1.9706 | 0 | 0 | 1.5 | 89.1653 | 0 | 26163.6396
2017-09-08 | 5:46 |  |  |  |  | 88.8267 |  | 26064.2779
2017-09-08 | 5:48 |  |  |  |  | 88.2426 |  | 25892.9089
2017-09-08 | 5:50 |  |  |  |  | 87.6764 |  | 25726.774
2017-09-08 | 5:52 |  |  |  |  | 87.1657 |  | 25576.9212
2017-09-08 | 5:54 |  |  |  |  | 86.6313 |  | 25420.0857
2017-09-08 | 5:56 |  |  |  |  | 86.1562 |  | 25280.6898
2017-09-08 | 5:58 |  |  |  |  | 85.7522 |  | 25162.1447
2017-09-08 | 6:00 | 1.8996 | 0 | 0 | 1.5 | 85.2825 | 0 | 25024.3292
2017-09-08 | 6:02 |  |  |  |  | 84.9187 |  | 24917.5843
2017-09-08 | 6:04 |  |  |  |  | 84.5726 |  | 24816.0043
2017-09-08 | 6:06 |  |  |  |  | 84.1581 |  | 24694.3831
2017-09-08 | 6:08 |  |  |  |  | 83.8219 |  | 24595.7336
2017-09-08 | 6:10 |  |  |  |  | 83.4265 |  | 24479.707
2017-09-08 | 6:12 |  |  |  |  | 83.1531 |  | 24399.4927
2017-09-08 | 6:14 |  |  |  |  | 82.8245 |  | 24303.0727
2017-09-08 | 6:15 | 1.8326 | 0 | 0 | 1.5 | 82.7004 | 0 | 24266.6517
2017-09-08 | 6:16 |  |  |  |  | 82.552 |  | 24223.1228
2017-09-08 | 6:18 |  |  |  |  | 82.3042 |  | 24150.4059
2017-09-08 | 6:20 |  |  |  |  | 82.0383 |  | 24072.39
2017-09-08 | 6:22 |  |  |  |  | 81.8036 |  | 24003.5079
2017-09-08 | 6:24 |  |  |  |  | 81.5753 |  | 23936.5267
2017-09-08 | 6:26 |  |  |  |  | 81.3919 |  | 23882.7042
2017-09-08 | 6:28 |  |  |  |  | 81.2436 |  | 23839.1841
2017-09-08 | 6:30 | 1.7811 | 0 | 0 | 1.5 | 81.0691 | 0 | 23787.9879
2017-09-08 | 6:32 |  |  |  |  | 80.9128 |  | 23742.1352
2017-09-08 | 6:34 |  |  |  |  | 80.7249 |  | 23686.9941
2017-09-08 | 6:36 |  |  |  |  | 80.5397 |  | 23632.6432
2017-09-08 | 6:38 |  |  |  |  | 80.4394 |  | 23603.2314
2017-09-08 | 6:40 |  |  |  |  | 80.2627 |  | 23551.3726
2017-09-08 | 6:42 |  |  |  |  | 80.1336 |  | 23513.4919
2017-09-08 | 6:44 |  |  |  |  | 80.0055 |  | 23475.8999
2017-09-08 | 6:45 | 1.806 | 0 | 0 | 1.5 | 79.9377 | 0 | 23455.9978
2017-09-08 | 6:46 |  |  |  |  | 79.8918 |  | 23442.5391
2017-09-08 | 6:48 |  |  |  |  | 79.7472 |  | 23400.0958
2017-09-08 | 6:50 |  |  |  |  | 79.6375 |  | 23367.9035
2017-09-08 | 6:52 |  |  |  |  | 79.5881 |  | 23353.4081
2017-09-08 | 6:54 |  |  |  |  | 79.4457 |  | 23311.652
2017-09-08 | 6:56 |  |  |  |  | 79.3623 |  | 23287.1654
2017-09-08 | 6:58 |  |  |  |  | 79.2401 |  | 23251.324
2017-09-08 | 7:00 | 1.767 | 0 | 0 | 1.5 | 79.1758 | 0 | 23232.4454
2017-09-08 | 7:02 |  |  |  |  | 79.0596 |  | 23198.3367
2017-09-08 | 7:04 |  |  |  |  | 78.9862 |  | 23176.8096
2017-09-08 | 7:06 |  |  |  |  | 78.9049 |  | 23152.9632
2017-09-08 | 7:08 |  |  |  |  | 78.8667 |  | 23141.7317
2017-09-08 | 7:10 |  |  |  |  | 78.7718 |  | 23113.907
2017-09-08 | 7:12 |  |  |  |  | 78.7446 |  | 23105.9263
2017-09-08 | 7:14 |  |  |  |  | 78.6601 |  | 23081.1105
2017-09-08 | 7:15 | 1.7811 | 0 | 0 | 1.5 | 78.6464 | 0 | 23077.1122
2017-09-08 | 7:16 |  |  |  |  | 78.6408 |  | 23075.4599
2017-09-08 | 7:18 |  |  |  |  | 78.5624 |  | 23052.4642
2017-09-08 | 7:20 |  |  |  |  | 78.5243 |  | 23041.2799
2017-09-08 | 7:22 |  |  |  |  | 78.4947 |  | 23032.5982
2017-09-08 | 7:24 |  |  |  |  | 78.4369 |  | 23015.6155
2017-09-08 | 7:26 |  |  |  |  | 78.3896 |  | 23001.7401
2017-09-08 | 7:28 |  |  |  |  | 78.3007 |  | 22975.6752
2017-09-08 | 7:30 | 1.7733 | 0 | 0 | 1.5 | 78.2869 | 0 | 22971.603
2017-09-08 | 7:32 |  |  |  |  | 78.2416 |  | 22958.3321
2017-09-08 | 7:34 |  |  |  |  | 78.2755 |  | 22968.2608
2017-09-08 | 7:36 |  |  |  |  | 78.2549 |  | 22962.2094
2017-09-08 | 7:38 |  |  |  |  | 78.2564 |  | 22962.6572
2017-09-08 | 7:40 |  |  |  |  | 78.2674 |  | 22965.8788
2017-09-08 | 7:42 |  |  |  |  | 78.2793 |  | 22969.3934
2017-09-08 | 7:44 |  |  |  |  | 78.2542 |  | 22962.0328
2017-09-08 | 7:45 | 1.7522 | 0 | 0 | 1.5 | 78.2666 | 0 | 22965.6616
2017-09-08 | 7:46 |  |  |  |  | 78.2839 |  | 22970.7368
2017-09-08 | 7:48 |  |  |  |  | 78.2779 |  | 22968.9659
2017-09-08 | 7:50 |  |  |  |  | 78.2926 |  | 22973.282
2017-09-08 | 7:52 |  |  |  |  | 78.3369 |  | 22986.2753
2017-09-08 | 7:54 |  |  |  |  | 78.3286 |  | 22983.8598
2017-09-08 | 7:56 |  |  |  |  | 78.3245 |  | 22982.642
2017-09-08 | 7:58 |  |  |  |  | 78.3645 |  | 22994.395
2017-09-08 | 8:00 | 1.7694 | 0 | 0 | 1.5 | 78.3442 | 0 | 22988.4334
2017-09-08 | 8:02 |  |  |  |  | 78.3196 |  | 22981.2227
2017-09-08 | 8:04 |  |  |  |  | 78.3279 |  | 22983.6538
2017-09-08 | 8:06 |  |  |  |  | 78.3523 |  | 22990.8131
2017-09-08 | 8:08 |  |  |  |  | 78.3091 |  | 22978.14
2017-09-08 | 8:10 |  |  |  |  | 78.2671 |  | 22965.796
2017-09-08 | 8:12 |  |  |  |  | 78.2625 |  | 22964.455
2017-09-08 | 8:14 |  |  |  |  | 78.2781 |  | 22969.0196
2017-09-08 | 8:15 | 1.7444 | 0 | 0 | 1.5 | 78.2819 | 0 | 22970.1502
2017-09-08 | 8:16 |  |  |  |  | 78.247 |  | 22959.9104
2017-09-08 | 8:18 |  |  |  |  | 78.2609 |  | 22963.9982
2017-09-08 | 8:20 |  |  |  |  | 78.1965 |  | 22945.0993
2017-09-08 | 8:22 |  |  |  |  | 78.1829 |  | 22941.092
2017-09-08 | 8:24 |  |  |  |  | 78.1965 |  | 22945.0902
2017-09-08 | 8:26 |  |  |  |  | 78.1703 |  | 22937.3915
2017-09-08 | 8:28 |  |  |  |  | 78.1767 |  | 22939.2809
2017-09-08 | 8:30 | 1.7429 | 0 | 0 | 1.5 | 78.1486 | 0 | 22931.0359
2017-09-08 | 8:32 |  |  |  |  | 78.1187 |  | 22922.2492
2017-09-08 | 8:34 |  |  |  |  | 78.1108 |  | 22919.9454
2017-09-08 | 8:36 |  |  |  |  | 78.1817 |  | 22940.7451
2017-09-08 | 8:38 |  |  |  |  | 78.2526 |  | 22961.5401
2017-09-08 | 8:40 |  |  |  |  | 78.3138 |  | 22979.5167
2017-09-08 | 8:42 |  |  |  |  | 78.3138 |  | 22979.5147
2017-09-08 | 8:44 |  |  |  |  | 78.318 |  | 22980.7347
2017-09-08 | 8:45 | 1.7405 | 0 | 0 | 1.5 | 78.3511 | 0 | 22990.4481
2017-09-08 | 8:46 |  |  |  |  | 78.3529 |  | 22990.9766
2017-09-08 | 8:48 |  |  |  |  | 78.4178 |  | 23010.0189
2017-09-08 | 8:50 |  |  |  |  | 78.4359 |  | 23015.3402
2017-09-08 | 8:52 |  |  |  |  | 78.4452 |  | 23018.0715
2017-09-08 | 8:54 |  |  |  |  | 78.4431 |  | 23017.4512
2017-09-08 | 8:56 |  |  |  |  | 78.4544 |  | 23020.7511
2017-09-08 | 8:58 |  |  |  |  | 78.5205 |  | 23040.1446
2017-09-08 | 9:00 | 1.7421 | 0 | 0 | 1.5 | 78.5362 | 0 | 23044.7653
2017-09-08 | 9:02 |  |  |  |  | 78.5231 |  | 23040.9125
2017-09-08 | 9:04 |  |  |  |  | 78.6778 |  | 23086.3086
2017-09-08 | 9:06 |  |  |  |  | 78.7935 |  | 23120.2515
2017-09-08 | 9:08 |  |  |  |  | 78.8641 |  | 23140.9705
2017-09-08 | 9:10 |  |  |  |  | 78.8872 |  | 23147.7628
2017-09-08 | 9:12 |  |  |  |  | 78.9352 |  | 23161.8395
2017-09-08 | 9:14 |  |  |  |  | 78.907 |  | 23153.5677
2017-09-08 | 9:15 | 1.7491 | 0 | 0 | 1.5 | 78.939 | 0 | 23162.9521
2017-09-08 | 9:16 |  |  |  |  | 78.9732 |  | 23172.9815
2017-09-08 | 9:18 |  |  |  |  | 79.0975 |  | 23209.4808
2017-09-08 | 9:20 |  |  |  |  | 79.0813 |  | 23204.7102
2017-09-08 | 9:22 |  |  |  |  | 79.0877 |  | 23206.602
2017-09-08 | 9:24 |  |  |  |  | 79.1758 |  | 23232.4387
2017-09-08 | 9:26 |  |  |  |  | 79.2366 |  | 23250.29
2017-09-08 | 9:28 |  |  |  |  | 79.3171 |  | 23273.908
2017-09-08 | 9:30 | 1.7522 | 0 | 0 | 1.5 | 79.3537 | 0 | 23284.6513
2017-09-08 | 9:32 |  |  |  |  | 79.3393 |  | 23280.4292
2017-09-08 | 9:34 |  |  |  |  | 79.297 |  | 23268.018
2017-09-08 | 9:36 |  |  |  |  | 79.3408 |  | 23280.8435
2017-09-08 | 9:38 |  |  |  |  | 79.3878 |  | 23294.647
2017-09-08 | 9:40 |  |  |  |  | 79.4087 |  | 23300.7811
2017-09-08 | 9:42 |  |  |  |  | 79.4717 |  | 23319.2592
2017-09-08 | 9:44 |  |  |  |  | 79.5765 |  | 23350.012
2017-09-08 | 9:45 | 1.7101 | 0 | 0 | 1.5 | 79.6479 | 0 | 23370.9771
2017-09-08 | 9:46 |  |  |  |  | 79.6681 |  | 23376.8985
2017-09-08 | 9:48 |  |  |  |  | 79.7319 |  | 23395.616
2017-09-08 | 9:50 |  |  |  |  | 79.6835 |  | 23381.4118
2017-09-08 | 9:52 |  |  |  |  | 79.5708 |  | 23348.3397
2017-09-08 | 9:54 |  |  |  |  | 79.4607 |  | 23316.0288
2017-09-08 | 9:56 |  |  |  |  | 79.4814 |  | 23322.1046
2017-09-08 | 9:58 |  |  |  |  | 79.4632 |  | 23316.7856
2017-09-08 | 10:00 | 1.7265 | 0 | 0 | 1.5 | 79.4528 | 0 | 23313.7275
2017-09-08 | 10:02 |  |  |  |  | 79.5385 |  | 23338.8746
2017-09-08 | 10:04 |  |  |  |  | 79.6995 |  | 23386.1198
2017-09-08 | 10:06 |  |  |  |  | 79.8139 |  | 23419.6663
2017-09-08 | 10:08 |  |  |  |  | 79.798 |  | 23415.0234
2017-09-08 | 10:10 |  |  |  |  | 79.7504 |  | 23401.0518
2017-09-08 | 10:12 |  |  |  |  | 79.7714 |  | 23407.1947
2017-09-08 | 10:14 |  |  |  |  | 79.8205 |  | 23421.6253
2017-09-08 | 10:15 | 1.7491 | 0 | 0 | 1.5 | 79.8173 | 0 | 23420.6848
2017-09-08 | 10:16 |  |  |  |  | 79.8438 |  | 23428.451
2017-09-08 | 10:18 |  |  |  |  | 79.9264 |  | 23452.6756
2017-09-08 | 10:20 |  |  |  |  | 80.0317 |  | 23483.5739
2017-09-08 | 10:22 |  |  |  |  | 80.0744 |  | 23496.115
2017-09-08 | 10:24 |  |  |  |  | 80.0036 |  | 23475.3468
2017-09-08 | 10:26 |  |  |  |  | 79.9784 |  | 23467.957
2017-09-08 | 10:28 |  |  |  |  | 79.9774 |  | 23467.6616
2017-09-08 | 10:30 | 1.7312 | 0 | 0 | 1.5 | 80.0082 | 0 | 23476.6833
2017-09-08 | 10:32 |  |  |  |  | 80.1166 |  | 23508.486
2017-09-08 | 10:34 |  |  |  |  | 80.2551 |  | 23549.1429
2017-09-08 | 10:36 |  |  |  |  | 80.3259 |  | 23569.9112
2017-09-08 | 10:38 |  |  |  |  | 80.3221 |  | 23568.8073
2017-09-08 | 10:40 |  |  |  |  | 80.2978 |  | 23561.6594
2017-09-08 | 10:42 |  |  |  |  | 80.3783 |  | 23585.2909
2017-09-08 | 10:44 |  |  |  |  | 80.4973 |  | 23620.2098
2017-09-08 | 10:45 | 1.6844 | 0 | 0 | 1.5 | 80.5941 | 0 | 23648.6163
2017-09-08 | 10:46 |  |  |  |  | 80.7041 |  | 23680.8847
2017-09-08 | 10:48 |  |  |  |  | 80.8368 |  | 23719.822
2017-09-08 | 10:50 |  |  |  |  | 80.8911 |  | 23735.7661
2017-09-08 | 10:52 |  |  |  |  | 80.8299 |  | 23717.8118
2017-09-08 | 10:54 |  |  |  |  | 80.8146 |  | 23713.3076
2017-09-08 | 10:56 |  |  |  |  | 80.924 |  | 23745.4102
2017-09-08 | 10:58 |  |  |  |  | 81.1709 |  | 23817.8674
2017-09-08 | 11:00 | 1.7015 | 0 | 0 | 1.5 | 81.29 | 0 | 23852.8133
2017-09-08 | 11:02 |  |  |  |  | 81.4501 |  | 23899.7786
2017-09-08 | 11:04 |  |  |  |  | 81.4999 |  | 23914.4063
2017-09-08 | 11:06 |  |  |  |  | 81.5337 |  | 23924.3057
2017-09-08 | 11:08 |  |  |  |  | 81.5972 |  | 23942.9472
2017-09-08 | 11:10 |  |  |  |  | 81.7606 |  | 23990.8996
2017-09-08 | 11:12 |  |  |  |  | 81.9019 |  | 24032.3534
2017-09-08 | 11:14 |  |  |  |  | 81.9154 |  | 24036.3314
2017-09-08 | 11:15 | 1.7772 | 0 | 0 | 1.5 | 81.8735 | 0 | 24024.0165
2017-09-08 | 11:16 |  |  |  |  | 81.8268 |  | 24010.3316
2017-09-08 | 11:18 |  |  |  |  | 81.781 |  | 23996.877
2017-09-08 | 11:20 |  |  |  |  | 81.8075 |  | 24004.6476
2017-09-08 | 11:22 |  |  |  |  | 81.8863 |  | 24027.773
2017-09-08 | 11:24 |  |  |  |  | 81.8759 |  | 24024.7395
2017-09-08 | 11:26 |  |  |  |  | 81.8875 |  | 24028.138
2017-09-08 | 11:28 |  |  |  |  | 81.8737 |  | 24024.0726
2017-09-08 | 11:30 | 1.7569 | 0 | 0 | 1.5 | 81.8379 | 0 | 24013.5798
2017-09-08 | 11:32 |  |  |  |  | 81.8625 |  | 24020.7838
2017-09-08 | 11:34 |  |  |  |  | 81.9486 |  | 24046.0721
2017-09-08 | 11:36 |  |  |  |  | 82.0364 |  | 24071.8348
2017-09-08 | 11:38 |  |  |  |  | 82.0546 |  | 24077.1764
2017-09-08 | 11:40 |  |  |  |  | 82.1237 |  | 24097.4341
2017-09-08 | 11:42 |  |  |  |  | 81.9894 |  | 24058.0445
2017-09-08 | 11:44 |  |  |  |  | 81.9529 |  | 24047.3347
2017-09-08 | 11:45 | 1.7756 | 0 | 0 | 1.5 | 81.9195 | 0 | 24037.5136
2017-09-08 | 11:46 |  |  |  |  | 81.9098 |  | 24034.6882
2017-09-08 | 11:48 |  |  |  |  | 81.9273 |  | 24039.815
2017-09-08 | 11:50 |  |  |  |  | 82.0415 |  | 24073.3058
2017-09-08 | 11:52 |  |  |  |  | 82.1886 |  | 24116.4764
2017-09-08 | 11:54 |  |  |  |  | 82.1648 |  | 24109.4961
2017-09-08 | 11:56 |  |  |  |  | 82.0965 |  | 24089.4643
2017-09-08 | 11:58 |  |  |  |  | 82.063 |  | 24079.6388
2017-09-08 | 12:00 | 1.7538 | 0 | 0 | 1.5 | 82.0572 | 0 | 24077.9217
2017-09-08 | 12:02 |  |  |  |  | 82.128 |  | 24098.6991
2017-09-08 | 12:04 |  |  |  |  | 82.2332 |  | 24129.5795
2017-09-08 | 12:06 |  |  |  |  | 82.3085 |  | 24151.6753
2017-09-08 | 12:08 |  |  |  |  | 82.2347 |  | 24130.0249
2017-09-08 | 12:10 |  |  |  |  | 82.1754 |  | 24112.6079
2017-09-08 | 12:12 |  |  |  |  | 82.1282 |  | 24098.746
2017-09-08 | 12:14 |  |  |  |  | 82.1913 |  | 24117.2778
2017-09-08 | 12:15 | 1.7226 | 0 | 0 | 1.5 | 82.2073 | 0 | 24121.9568
2017-09-08 | 12:16 |  |  |  |  | 82.1665 |  | 24109.9955
2017-09-08 | 12:18 |  |  |  |  | 82.177 |  | 24113.0712
2017-09-08 | 12:20 |  |  |  |  | 82.1665 |  | 24109.9931
2017-09-08 | 12:22 |  |  |  |  | 82.0993 |  | 24090.2859
2017-09-08 | 12:24 |  |  |  |  | 82.0014 |  | 24061.5569
2017-09-08 | 12:26 |  |  |  |  | 81.9006 |  | 24031.9884
2017-09-08 | 12:28 |  |  |  |  | 81.8283 |  | 24010.7524
2017-09-08 | 12:30 | 1.739 | 0 | 0 | 1.5 | 81.8487 | 0 | 24016.7589
2017-09-08 | 12:32 |  |  |  |  | 81.8575 |  | 24019.3422
2017-09-08 | 12:34 |  |  |  |  | 81.866 |  | 24021.8272
2017-09-08 | 12:36 |  |  |  |  | 81.7784 |  | 23996.127
2017-09-08 | 12:38 |  |  |  |  | 81.6766 |  | 23966.2519
2017-09-08 | 12:40 |  |  |  |  | 81.6877 |  | 23969.5045
2017-09-08 | 12:42 |  |  |  |  | 81.6967 |  | 23972.1486
2017-09-08 | 12:44 |  |  |  |  | 81.7678 |  | 23992.9996
2017-09-08 | 12:45 | 1.7148 | 0 | 0 | 1.5 | 81.7771 | 0 | 23995.7488
2017-09-08 | 12:46 |  |  |  |  | 81.8156 |  | 24007.0384
2017-09-08 | 12:48 |  |  |  |  | 81.8186 |  | 24007.9205
2017-09-08 | 12:50 |  |  |  |  | 81.6666 |  | 23963.3191
2017-09-08 | 12:52 |  |  |  |  | 81.6387 |  | 23955.1391
2017-09-08 | 12:54 |  |  |  |  | 81.6817 |  | 23967.7563
2017-09-08 | 12:56 |  |  |  |  | 81.7697 |  | 23993.5727
2017-09-08 | 12:58 |  |  |  |  | 81.9044 |  | 24033.1011
2017-09-08 | 13:00 | 1.7358 | 0 | 0 | 1.5 | 81.9124 | 0 | 24035.4362
2017-09-08 | 13:02 |  |  |  |  | 81.957 |  | 24048.5257
2017-09-08 | 13:04 |  |  |  |  | 81.8999 |  | 24031.7645
2017-09-08 | 13:06 |  |  |  |  | 81.8864 |  | 24027.8
2017-09-08 | 13:08 |  |  |  |  | 81.9831 |  | 24056.191
2017-09-08 | 13:10 |  |  |  |  | 82.0185 |  | 24066.5672
2017-09-08 | 13:12 |  |  |  |  | 82.0715 |  | 24082.1371
2017-09-08 | 13:14 |  |  |  |  | 82.1833 |  | 24114.9227
2017-09-08 | 13:15 | 1.7234 | 0 | 0 | 1.5 | 82.236 | 0 | 24130.3987
2017-09-08 | 13:16 |  |  |  |  | 82.3058 |  | 24150.8692
2017-09-08 | 13:18 |  |  |  |  | 82.3272 |  | 24157.1553
2017-09-08 | 13:20 |  |  |  |  | 82.2856 |  | 24144.9458
2017-09-08 | 13:22 |  |  |  |  | 82.2419 |  | 24132.127
2017-09-08 | 13:24 |  |  |  |  | 82.2868 |  | 24145.3061
2017-09-08 | 13:26 |  |  |  |  | 82.2805 |  | 24143.4549
2017-09-08 | 13:28 |  |  |  |  | 82.3928 |  | 24176.3969
2017-09-08 | 13:30 | 1.7499 | 0 | 0 | 1.5 | 82.4179 | 0 | 24183.7532
2017-09-08 | 13:32 |  |  |  |  | 82.5222 |  | 24214.3739
2017-09-08 | 13:34 |  |  |  |  | 82.4665 |  | 24198.0249
2017-09-08 | 13:36 |  |  |  |  | 82.4007 |  | 24178.7273
2017-09-08 | 13:38 |  |  |  |  | 82.489 |  | 24204.62
2017-09-08 | 13:40 |  |  |  |  | 82.6901 |  | 24263.6406
2017-09-08 | 13:42 |  |  |  |  | 82.9044 |  | 24326.5117
2017-09-08 | 13:44 |  |  |  |  | 83.0449 |  | 24367.7417
2017-09-08 | 13:45 | 1.714 | 0 | 0 | 1.5 | 83.0585 | 0 | 24371.7511
2017-09-08 | 13:46 |  |  |  |  | 83.0708 |  | 24375.3441
2017-09-08 | 13:48 |  |  |  |  | 83.1305 |  | 24392.8618
2017-09-08 | 13:50 |  |  |  |  | 83.1993 |  | 24413.057
2017-09-08 | 13:52 |  |  |  |  | 83.3542 |  | 24458.5091
2017-09-08 | 13:54 |  |  |  |  | 83.4868 |  | 24497.4039
2017-09-08 | 13:56 |  |  |  |  | 83.6461 |  | 24544.1542
2017-09-08 | 13:58 |  |  |  |  | 83.7929 |  | 24587.24
2017-09-08 | 14:00 | 1.707 | 0 | 0 | 1.5 | 83.8891 | 0 | 24615.4517
2017-09-08 | 14:02 |  |  |  |  | 83.9458 |  | 24632.083
2017-09-08 | 14:04 |  |  |  |  | 83.8321 |  | 24598.7198
2017-09-08 | 14:06 |  |  |  |  | 83.8297 |  | 24598.0235
2017-09-08 | 14:08 |  |  |  |  | 83.9727 |  | 24639.9991
2017-09-08 | 14:10 |  |  |  |  | 84.0816 |  | 24671.9382
2017-09-08 | 14:12 |  |  |  |  | 84.2309 |  | 24715.7447
2017-09-08 | 14:14 |  |  |  |  | 84.3362 |  | 24746.6431
2017-09-08 | 14:15 | 1.746 | 0 | 0 | 1.5 | 84.3347 | 0 | 24746.2132
2017-09-08 | 14:16 |  |  |  |  | 84.346 |  | 24749.5154
2017-09-08 | 14:18 |  |  |  |  | 84.3539 |  | 24751.8435
2017-09-08 | 14:20 |  |  |  |  | 84.4279 |  | 24773.5631
2017-09-08 | 14:22 |  |  |  |  | 84.4558 |  | 24781.7321
2017-09-08 | 14:24 |  |  |  |  | 84.4383 |  | 24776.6191
2017-09-08 | 14:26 |  |  |  |  | 84.3856 |  | 24761.134
2017-09-08 | 14:28 |  |  |  |  | 84.3143 |  | 24740.2381
2017-09-08 | 14:30 | 1.76 | 0 | 0 | 1.5 | 84.2568 | 0 | 24723.3495
2017-09-08 | 14:32 |  |  |  |  | 84.2615 |  | 24724.7219
2017-09-08 | 14:34 |  |  |  |  | 84.239 |  | 24718.1244
2017-09-08 | 14:36 |  |  |  |  | 84.1595 |  | 24694.8042
2017-09-08 | 14:38 |  |  |  |  | 84.006 |  | 24649.7617
2017-09-08 | 14:40 |  |  |  |  | 84.0122 |  | 24651.5684
2017-09-08 | 14:42 |  |  |  |  | 84.0739 |  | 24669.6726
2017-09-08 | 14:44 |  |  |  |  | 84.1041 |  | 24678.5468
2017-09-08 | 14:45 | 1.7468 | 0 | 0 | 1.5 | 84.092 | 0 | 24675.0007
2017-09-08 | 14:46 |  |  |  |  | 84.1143 |  | 24681.5401
2017-09-08 | 14:48 |  |  |  |  | 84.063 |  | 24666.4781
2017-09-08 | 14:50 |  |  |  |  | 84.0681 |  | 24667.969
2017-09-08 | 14:52 |  |  |  |  | 84.0522 |  | 24663.3193
2017-09-08 | 14:54 |  |  |  |  | 84.0542 |  | 24663.8947
2017-09-08 | 14:56 |  |  |  |  | 84.0905 |  | 24674.5485
2017-09-08 | 14:58 |  |  |  |  | 84.0481 |  | 24662.1127
2017-09-08 | 15:00 | 1.7569 | 0 | 0 | 1.5 | 83.9806 | 0 | 24642.2937
2017-09-08 | 15:02 |  |  |  |  | 84.0615 |  | 24666.0438
2017-09-08 | 15:04 |  |  |  |  | 84.1483 |  | 24691.5067
2017-09-08 | 15:06 |  |  |  |  | 84.3407 |  | 24747.9729
2017-09-08 | 15:08 |  |  |  |  | 84.5578 |  | 24811.6724
2017-09-08 | 15:10 |  |  |  |  | 84.7099 |  | 24856.2938
2017-09-08 | 15:12 |  |  |  |  | 84.964 |  | 24930.8778
2017-09-08 | 15:14 |  |  |  |  | 85.1984 |  | 24999.6501
2017-09-08 | 15:15 | 1.6961 | 0 | 0 | 1.5 | 85.263 | 0 | 25018.5871
2017-09-08 | 15:16 |  |  |  |  | 85.2855 |  | 25025.2112
2017-09-08 | 15:18 |  |  |  |  | 85.3374 |  | 25040.4208
2017-09-08 | 15:20 |  |  |  |  | 85.4953 |  | 25086.7549
2017-09-08 | 15:22 |  |  |  |  | 85.6449 |  | 25130.6645
2017-09-08 | 15:24 |  |  |  |  | 85.7387 |  | 25158.1734
2017-09-08 | 15:26 |  |  |  |  | 85.8149 |  | 25180.5511
2017-09-08 | 15:28 |  |  |  |  | 85.9214 |  | 25211.803
2017-09-08 | 15:30 | 1.7039 | 0 | 0 | 1.5 | 86.0481 | 0 | 25248.9831
2017-09-08 | 15:32 |  |  |  |  | 86.1212 |  | 25270.4186
2017-09-08 | 15:34 |  |  |  |  | 86.1551 |  | 25280.3785
2017-09-08 | 15:36 |  |  |  |  | 86.2928 |  | 25320.7821
2017-09-08 | 15:38 |  |  |  |  | 86.3673 |  | 25342.6317
2017-09-08 | 15:40 |  |  |  |  | 86.4948 |  | 25380.0491
2017-09-08 | 15:42 |  |  |  |  | 86.5874 |  | 25407.2133
2017-09-08 | 15:44 |  |  |  |  | 86.6109 |  | 25414.0995
2017-09-08 | 15:45 | 1.7717 | 0 | 0 | 1.5 | 86.5881 | 0 | 25407.4348
2017-09-08 | 15:46 |  |  |  |  | 86.527 |  | 25389.4919
2017-09-08 | 15:48 |  |  |  |  | 86.438 |  | 25363.3665
2017-09-08 | 15:50 |  |  |  |  | 86.5076 |  | 25383.8147
2017-09-08 | 15:52 |  |  |  |  | 86.6328 |  | 25420.5402
2017-09-08 | 15:54 |  |  |  |  | 86.762 |  | 25458.4544
2017-09-08 | 15:56 |  |  |  |  | 86.8317 |  | 25478.9161
2017-09-08 | 15:58 |  |  |  |  | 86.8787 |  | 25492.6884
2017-09-08 | 16:00 | 1.7085 | 0 | 0 | 1.5 | 86.9293 | 0 | 25507.5333
2017-09-08 | 16:02 |  |  |  |  | 87.0248 |  | 25535.5525
2017-09-08 | 16:04 |  |  |  |  | 87.092 |  | 25555.2753
2017-09-08 | 16:06 |  |  |  |  | 87.1421 |  | 25569.9722
2017-09-08 | 16:08 |  |  |  |  | 87.2208 |  | 25593.0753
2017-09-08 | 16:10 |  |  |  |  | 87.2291 |  | 25595.5023
2017-09-08 | 16:12 |  |  |  |  | 87.1788 |  | 25580.7449
2017-09-08 | 16:14 |  |  |  |  | 87.0926 |  | 25555.4455
2017-09-08 | 16:15 | 1.7858 | 0 | 0 | 1.5 | 87.029 | 0 | 25536.8016
2017-09-08 | 16:16 |  |  |  |  | 86.834 |  | 25479.581
2017-09-08 | 16:18 |  |  |  |  | 86.5188 |  | 25387.0987
2017-09-08 | 16:20 |  |  |  |  | 86.1972 |  | 25292.716
2017-09-08 | 16:22 |  |  |  |  | 86.0006 |  | 25235.0273
2017-09-08 | 16:24 |  |  |  |  | 85.8689 |  | 25196.3898
2017-09-08 | 16:26 |  |  |  |  | 85.7369 |  | 25157.6652
2017-09-08 | 16:28 |  |  |  |  | 85.5788 |  | 25111.2706
2017-09-08 | 16:30 | 1.8045 | 0 | 0 | 1.5 | 85.4343 | 0 | 25068.8543
2017-09-08 | 16:32 |  |  |  |  | 85.1659 |  | 24990.1087
2017-09-08 | 16:34 |  |  |  |  | 84.9796 |  | 24935.4514
2017-09-08 | 16:36 |  |  |  |  | 84.8344 |  | 24892.8403
2017-09-08 | 16:38 |  |  |  |  | 84.8172 |  | 24887.7851
2017-09-08 | 16:40 |  |  |  |  | 84.7971 |  | 24881.8887
2017-09-08 | 16:42 |  |  |  |  | 84.7789 |  | 24876.5559
2017-09-08 | 16:44 |  |  |  |  | 84.7371 |  | 24864.2724
2017-09-08 | 16:45 | 1.7663 | 0 | 0 | 1.5 | 84.6753 | 0 | 24846.1412
2017-09-08 | 16:46 |  |  |  |  | 84.6498 |  | 24838.662
2017-09-08 | 16:48 |  |  |  |  | 84.5086 |  | 24797.2395
2017-09-08 | 16:50 |  |  |  |  | 84.3863 |  | 24761.34
2017-09-08 | 16:52 |  |  |  |  | 84.2558 |  | 24723.0675
2017-09-08 | 16:54 |  |  |  |  | 84.3373 |  | 24746.9743
2017-09-08 | 16:56 |  |  |  |  | 84.3259 |  | 24743.641
2017-09-08 | 16:58 |  |  |  |  | 84.2507 |  | 24721.5564
2017-09-08 | 17:00 | 1.7709 | 0 | 0 | 1.5 | 84.1815 | 0 | 24701.2514
2017-09-08 | 17:02 |  |  |  |  | 84.0975 |  | 24676.6172
2017-09-08 | 17:04 |  |  |  |  | 83.975 |  | 24640.6572
2017-09-08 | 17:06 |  |  |  |  | 83.8085 |  | 24591.8134
2017-09-08 | 17:08 |  |  |  |  | 83.6314 |  | 24539.8425
2017-09-08 | 17:10 |  |  |  |  | 83.5991 |  | 24530.3706
2017-09-08 | 17:12 |  |  |  |  | 83.4976 |  | 24500.5918
2017-09-08 | 17:14 |  |  |  |  | 83.4352 |  | 24482.268
2017-09-08 | 17:15 | 1.7834 | 0 | 0 | 1.5 | 83.3398 | 0 | 24454.2688
2017-09-08 | 17:16 |  |  |  |  | 83.2704 |  | 24433.9104
2017-09-08 | 17:18 |  |  |  |  | 83.1031 |  | 24384.8227
2017-09-08 | 17:20 |  |  |  |  | 82.9565 |  | 24341.8108
2017-09-08 | 17:22 |  |  |  |  | 82.7651 |  | 24285.6559
2017-09-08 | 17:24 |  |  |  |  | 82.5623 |  | 24226.1292
2017-09-08 | 17:26 |  |  |  |  | 82.3305 |  | 24158.1113
2017-09-08 | 17:28 |  |  |  |  | 82.2557 |  | 24136.1857
2017-09-08 | 17:30 | 1.7647 | 0 | 0 | 1.5 | 82.1734 | 0 | 24112.0237
2017-09-08 | 17:32 |  |  |  |  | 82.1177 |  | 24095.6791
2017-09-08 | 17:34 |  |  |  |  | 82.0175 |  | 24066.2673
2017-09-08 | 17:36 |  |  |  |  | 81.9026 |  | 24032.5682
2017-09-08 | 17:38 |  |  |  |  | 81.7538 |  | 23988.8984
2017-09-08 | 17:40 |  |  |  |  | 81.5727 |  | 23935.7497
2017-09-08 | 17:42 |  |  |  |  | 81.4928 |  | 23912.3264
2017-09-08 | 17:44 |  |  |  |  | 81.4497 |  | 23899.6823
2017-09-08 | 17:45 | 1.7717 | 0 | 0 | 1.5 | 81.419 | 0 | 23890.6582
2017-09-08 | 17:46 |  |  |  |  | 81.385 |  | 23880.6984
2017-09-08 | 17:48 |  |  |  |  | 81.32 |  | 23861.6091
2017-09-08 | 17:50 |  |  |  |  | 81.1624 |  | 23815.36
2017-09-08 | 17:52 |  |  |  |  | 81.0338 |  | 23777.6272
2017-09-08 | 17:54 |  |  |  |  | 80.9885 |  | 23764.3451
2017-09-08 | 17:56 |  |  |  |  | 80.9036 |  | 23739.4219
2017-09-08 | 17:58 |  |  |  |  | 80.8462 |  | 23722.5891
2017-09-08 | 18:00 | 1.7881 | 0 | 0 | 1.5 | 80.7326 | 0 | 23689.253
2017-09-08 | 18:02 |  |  |  |  | 80.5704 |  | 23641.6474
2017-09-08 | 18:04 |  |  |  |  | 80.3904 |  | 23588.8323
2017-09-08 | 18:06 |  |  |  |  | 80.2149 |  | 23537.3494
2017-09-08 | 18:08 |  |  |  |  | 80.1816 |  | 23527.5844
2017-09-08 | 18:10 |  |  |  |  | 80.0956 |  | 23502.3475
2017-09-08 | 18:12 |  |  |  |  | 79.9902 |  | 23471.4113
2017-09-08 | 18:14 |  |  |  |  | 79.8604 |  | 23433.3334
2017-09-08 | 18:15 | 1.8084 | 0 | 0 | 1.5 | 79.7635 | 0 | 23404.9022
2017-09-08 | 18:16 |  |  |  |  | 79.6847 |  | 23381.7788
2017-09-08 | 18:18 |  |  |  |  | 79.5166 |  | 23332.4382
2017-09-08 | 18:20 |  |  |  |  | 79.4222 |  | 23304.7301
2017-09-08 | 18:22 |  |  |  |  | 79.3812 |  | 23292.7262
2017-09-08 | 18:24 |  |  |  |  | 79.3367 |  | 23279.666
2017-09-08 | 18:26 |  |  |  |  | 79.282 |  | 23263.6011
2017-09-08 | 18:28 |  |  |  |  | 79.1115 |  | 23213.5733
2017-09-08 | 18:30 | 1.7928 | 0 | 0 | 1.5 | 78.9913 | 0 | 23178.3028
2017-09-08 | 18:32 |  |  |  |  | 78.8705 |  | 23142.8646
2017-09-08 | 18:34 |  |  |  |  | 78.7841 |  | 23117.5182
2017-09-08 | 18:36 |  |  |  |  | 78.7902 |  | 23119.3023
2017-09-08 | 18:38 |  |  |  |  | 78.7991 |  | 23121.9217
2017-09-08 | 18:40 |  |  |  |  | 78.7538 |  | 23108.6036
2017-09-08 | 18:42 |  |  |  |  | 78.6369 |  | 23074.3226
2017-09-08 | 18:44 |  |  |  |  | 78.5394 |  | 23045.6922
2017-09-08 | 18:45 | 1.7975 | 0 | 0 | 1.5 | 78.4378 | 0 | 23015.8954
2017-09-08 | 18:46 |  |  |  |  | 78.3702 |  | 22996.0629
2017-09-08 | 18:48 |  |  |  |  | 78.261 |  | 22964.0161
2017-09-08 | 18:50 |  |  |  |  | 78.2514 |  | 22961.1886
2017-09-08 | 18:52 |  |  |  |  | 78.2236 |  | 22953.0533
2017-09-08 | 18:54 |  |  |  |  | 78.1874 |  | 22942.4194
2017-09-08 | 18:56 |  |  |  |  | 78.107 |  | 22918.8372
2017-09-08 | 18:58 |  |  |  |  | 78.017 |  | 22892.423
2017-09-08 | 19:00 | 1.7741 | 0 | 0 | 1.5 | 77.9207 | 0 | 22864.1597
2017-09-08 | 19:02 |  |  |  |  | 77.8368 |  | 22839.5454
2017-09-08 | 19:04 |  |  |  |  | 77.7217 |  | 22805.7659
2017-09-08 | 19:06 |  |  |  |  | 77.6976 |  | 22798.6984
2017-09-08 | 19:08 |  |  |  |  | 77.6927 |  | 22797.2545
2017-09-08 | 19:10 |  |  |  |  | 77.7561 |  | 22815.869
2017-09-08 | 19:12 |  |  |  |  | 77.724 |  | 22806.4464
2017-09-08 | 19:14 |  |  |  |  | 77.617 |  | 22775.0401
2017-09-08 | 19:15 | 1.7858 | 0 | 0 | 1.5 | 77.5788 | 0 | 22763.842
2017-09-08 | 19:16 |  |  |  |  | 77.5373 |  | 22751.6457
2017-09-08 | 19:18 |  |  |  |  | 77.4132 |  | 22715.2494
2017-09-08 | 19:20 |  |  |  |  | 77.3208 |  | 22688.1366
2017-09-08 | 19:22 |  |  |  |  | 77.2456 |  | 22666.052
2017-09-08 | 19:24 |  |  |  |  | 77.1361 |  | 22633.938
2017-09-08 | 19:26 |  |  |  |  | 77.0769 |  | 22616.5526
2017-09-08 | 19:28 |  |  |  |  | 77.0925 |  | 22621.1486
2017-09-08 | 19:30 | 1.7561 | 0 | 0 | 1.5 | 77.1031 | 0 | 22624.2513
2017-09-08 | 19:32 |  |  |  |  | 77.0836 |  | 22618.5248
2017-09-08 | 19:34 |  |  |  |  | 76.9707 |  | 22585.3899
2017-09-08 | 19:36 |  |  |  |  | 76.9189 |  | 22570.1915
2017-09-08 | 19:38 |  |  |  |  | 76.8604 |  | 22553.0365
2017-09-08 | 19:40 |  |  |  |  | 76.8436 |  | 22548.1183
2017-09-08 | 19:42 |  |  |  |  | 76.7378 |  | 22517.0566
2017-09-08 | 19:44 |  |  |  |  | 76.6882 |  | 22502.5072
2017-09-08 | 19:45 | 1.7655 | 0 | 0 | 1.5 | 76.682 | 0 | 22500.6962
2017-09-08 | 19:46 |  |  |  |  | 76.629 |  | 22485.1395
2017-09-08 | 19:48 |  |  |  |  | 76.5986 |  | 22476.2184
2017-09-08 | 19:50 |  |  |  |  | 76.673 |  | 22498.0612
2017-09-08 | 19:52 |  |  |  |  | 76.7163 |  | 22510.7523
2017-09-08 | 19:54 |  |  |  |  | 76.7874 |  | 22531.6191
2017-09-08 | 19:56 |  |  |  |  | 76.7614 |  | 22523.9985
2017-09-08 | 19:58 |  |  |  |  | 76.742 |  | 22518.2878
2017-09-08 | 20:00 | 1.7546 | 0 | 0 | 1.5 | 76.7168 | 0 | 22510.9025
2017-09-08 | 20:02 |  |  |  |  | 76.6451 |  | 22489.8654
2017-09-08 | 20:04 |  |  |  |  | 76.6345 |  | 22486.758
2017-09-08 | 20:06 |  |  |  |  | 76.5621 |  | 22465.5109
2017-09-08 | 20:08 |  |  |  |  | 76.5281 |  | 22455.5419
2017-09-08 | 20:10 |  |  |  |  | 76.4497 |  | 22432.526
2017-09-08 | 20:12 |  |  |  |  | 76.4832 |  | 22442.3494
2017-09-08 | 20:14 |  |  |  |  | 76.5103 |  | 22450.2969
2017-09-08 | 20:15 | 1.7397 | 0 | 0 | 1.5 | 76.5358 | 0 | 22457.7761
2017-09-08 | 20:16 |  |  |  |  | 76.5158 |  | 22451.931
2017-09-08 | 20:18 |  |  |  |  | 76.4717 |  | 22438.9826
2017-09-08 | 20:20 |  |  |  |  | 76.3923 |  | 22415.6978
2017-09-08 | 20:22 |  |  |  |  | 76.3666 |  | 22408.1467
2017-09-08 | 20:24 |  |  |  |  | 76.2993 |  | 22388.4016
2017-09-08 | 20:26 |  |  |  |  | 76.3558 |  | 22404.9633
2017-09-08 | 20:28 |  |  |  |  | 76.4504 |  | 22432.7275
2017-09-08 | 20:30 | 1.7234 | 0 | 0 | 1.5 | 76.5533 | 0 | 22462.9228
2017-09-08 | 20:32 |  |  |  |  | 76.5619 |  | 22465.4504
2017-09-08 | 20:34 |  |  |  |  | 76.5646 |  | 22466.2518
2017-09-08 | 20:36 |  |  |  |  | 76.6124 |  | 22480.2548
2017-09-08 | 20:38 |  |  |  |  | 76.7387 |  | 22517.323
2017-09-08 | 20:40 |  |  |  |  | 76.8142 |  | 22539.4681
2017-09-08 | 20:42 |  |  |  |  | 76.7736 |  | 22527.5739
2017-09-08 | 20:44 |  |  |  |  | 76.7096 |  | 22508.7957
2017-09-08 | 20:45 | 1.7733 | 0 | 0 | 1.5 | 76.6919 | 0 | 22503.5885
2017-09-08 | 20:46 |  |  |  |  | 76.64 |  | 22488.3566
2017-09-08 | 20:48 |  |  |  |  | 76.5978 |  | 22475.9945
2017-09-08 | 20:50 |  |  |  |  | 76.5468 |  | 22461.0067
2017-09-08 | 20:52 |  |  |  |  | 76.5179 |  | 22452.531
2017-09-08 | 20:54 |  |  |  |  | 76.4731 |  | 22439.3854
2017-09-08 | 20:56 |  |  |  |  | 76.4504 |  | 22432.7208
2017-09-08 | 20:58 |  |  |  |  | 76.3756 |  | 22410.7929
2017-09-08 | 21:00 | 1.7585 | 0 | 0 | 1.5 | 76.3722 | 0 | 22409.7923
2017-09-08 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-08 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-08 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 5:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 5:02 |  |  |  |  | 69.625 |  | 20429.9643
2017-09-09 | 5:04 |  |  |  |  | 99.964 |  | 29332.3016
2017-09-09 | 5:06 |  |  |  |  | 98.7728 |  | 28982.7739
2017-09-09 | 5:08 |  |  |  |  | 97.1961 |  | 28520.101
2017-09-09 | 5:10 |  |  |  |  | 95.9238 |  | 28146.7695
2017-09-09 | 5:12 |  |  |  |  | 94.9468 |  | 27860.0904
2017-09-09 | 5:14 |  |  |  |  | 94.1953 |  | 27639.6005
2017-09-09 | 5:15 | 1.955 | 0 | 0 | 1.5 | 93.8966 | 0 | 27551.9584
2017-09-09 | 5:16 |  |  |  |  | 93.4851 |  | 27431.2014
2017-09-09 | 5:18 |  |  |  |  | 92.8261 |  | 27237.8196
2017-09-09 | 5:20 |  |  |  |  | 92.269 |  | 27074.3465
2017-09-09 | 5:22 |  |  |  |  | 91.7668 |  | 26926.9966
2017-09-09 | 5:24 |  |  |  |  | 91.2014 |  | 26761.0833
2017-09-09 | 5:26 |  |  |  |  | 90.6461 |  | 26598.17
2017-09-09 | 5:28 |  |  |  |  | 89.9272 |  | 26387.2122
2017-09-09 | 5:30 | 1.9644 | 0 | 0 | 1.5 | 89.2832 | 0 | 26198.2339
2017-09-09 | 5:32 |  |  |  |  | 88.7095 |  | 26029.8983
2017-09-09 | 5:34 |  |  |  |  | 88.1084 |  | 25853.5082
2017-09-09 | 5:36 |  |  |  |  | 87.5267 |  | 25682.8378
2017-09-09 | 5:38 |  |  |  |  | 86.9276 |  | 25507.0295
2017-09-09 | 5:40 |  |  |  |  | 86.4372 |  | 25363.1538
2017-09-09 | 5:42 |  |  |  |  | 85.9255 |  | 25212.9964
2017-09-09 | 5:44 |  |  |  |  | 85.3897 |  | 25055.7739
2017-09-09 | 5:45 | 1.895 | 0 | 0 | 1.5 | 85.1752 | 0 | 24992.8331
2017-09-09 | 5:46 |  |  |  |  | 84.9058 |  | 24913.792
2017-09-09 | 5:48 |  |  |  |  | 84.46 |  | 24782.9724
2017-09-09 | 5:50 |  |  |  |  | 84.0633 |  | 24666.5699
2017-09-09 | 5:52 |  |  |  |  | 83.6775 |  | 24553.3822
2017-09-09 | 5:54 |  |  |  |  | 83.2945 |  | 24440.9891
2017-09-09 | 5:56 |  |  |  |  | 82.9089 |  | 24327.8392
2017-09-09 | 5:58 |  |  |  |  | 82.5854 |  | 24232.9013
2017-09-09 | 6:00 | 1.845 | 0 | 0 | 1.5 | 82.2837 | 0 | 24144.3815
2017-09-09 | 6:02 |  |  |  |  | 82.0036 |  | 24062.2086
2017-09-09 | 6:04 |  |  |  |  | 81.7712 |  | 23994.0114
2017-09-09 | 6:06 |  |  |  |  | 81.5431 |  | 23927.0636
2017-09-09 | 6:08 |  |  |  |  | 81.2407 |  | 23838.3537
2017-09-09 | 6:10 |  |  |  |  | 80.9156 |  | 23742.9589
2017-09-09 | 6:12 |  |  |  |  | 80.6702 |  | 23670.9316
2017-09-09 | 6:14 |  |  |  |  | 80.4152 |  | 23596.1217
2017-09-09 | 6:15 | 1.8419 | 0 | 0 | 1.5 | 80.2856 | 0 | 23558.1021
2017-09-09 | 6:16 |  |  |  |  | 80.1766 |  | 23526.109
2017-09-09 | 6:18 |  |  |  |  | 79.9732 |  | 23466.4256
2017-09-09 | 6:20 |  |  |  |  | 79.7835 |  | 23410.7631
2017-09-09 | 6:22 |  |  |  |  | 79.6005 |  | 23357.0616
2017-09-09 | 6:24 |  |  |  |  | 79.354 |  | 23284.7344
2017-09-09 | 6:26 |  |  |  |  | 79.1228 |  | 23216.9022
2017-09-09 | 6:28 |  |  |  |  | 78.9362 |  | 23162.1261
2017-09-09 | 6:30 | 1.8123 | 0 | 0 | 1.5 | 78.7422 | 0 | 23105.2256
2017-09-09 | 6:32 |  |  |  |  | 78.5938 |  | 23061.6653
2017-09-09 | 6:34 |  |  |  |  | 78.4145 |  | 23009.0606
2017-09-09 | 6:36 |  |  |  |  | 78.3073 |  | 22977.5871
2017-09-09 | 6:38 |  |  |  |  | 78.2906 |  | 22972.6933
2017-09-09 | 6:40 |  |  |  |  | 78.3403 |  | 22987.2894
2017-09-09 | 6:42 |  |  |  |  | 78.2577 |  | 22963.0469
2017-09-09 | 6:44 |  |  |  |  | 78.2207 |  | 22952.1935
2017-09-09 | 6:45 | 1.7631 | 0 | 0 | 1.5 | 78.1901 | 0 | 22943.2032
2017-09-09 | 6:46 |  |  |  |  | 78.1409 |  | 22928.7592
2017-09-09 | 6:48 |  |  |  |  | 78.0166 |  | 22892.3065
2017-09-09 | 6:50 |  |  |  |  | 77.9403 |  | 22869.9109
2017-09-09 | 6:52 |  |  |  |  | 77.8251 |  | 22836.1091
2017-09-09 | 6:54 |  |  |  |  | 77.7374 |  | 22810.3687
2017-09-09 | 6:56 |  |  |  |  | 77.7289 |  | 22807.8725
2017-09-09 | 6:58 |  |  |  |  | 77.7653 |  | 22818.5644
2017-09-09 | 7:00 | 1.7195 | 0 | 0 | 1.5 | 77.8628 | 0 | 22847.159
2017-09-09 | 7:02 |  |  |  |  | 77.7964 |  | 22827.6894
2017-09-09 | 7:04 |  |  |  |  | 77.7595 |  | 22816.8608
2017-09-09 | 7:06 |  |  |  |  | 77.6851 |  | 22795.0314
2017-09-09 | 7:08 |  |  |  |  | 77.5978 |  | 22769.421
2017-09-09 | 7:10 |  |  |  |  | 77.5054 |  | 22742.2903
2017-09-09 | 7:12 |  |  |  |  | 77.4343 |  | 22721.4214
2017-09-09 | 7:14 |  |  |  |  | 77.3837 |  | 22706.6012
2017-09-09 | 7:15 | 1.7569 | 0 | 0 | 1.5 | 77.3624 | 0 | 22700.3285
2017-09-09 | 7:16 |  |  |  |  | 77.4242 |  | 22718.4774
2017-09-09 | 7:18 |  |  |  |  | 77.4775 |  | 22734.108
2017-09-09 | 7:20 |  |  |  |  | 77.5786 |  | 22763.766
2017-09-09 | 7:22 |  |  |  |  | 77.5115 |  | 22744.0878
2017-09-09 | 7:24 |  |  |  |  | 77.501 |  | 22740.9963
2017-09-09 | 7:26 |  |  |  |  | 77.4893 |  | 22737.5643
2017-09-09 | 7:28 |  |  |  |  | 77.4531 |  | 22726.9554
2017-09-09 | 7:30 | 1.7522 | 0 | 0 | 1.5 | 77.3879 | 0 | 22707.8212
2017-09-09 | 7:32 |  |  |  |  | 77.3097 |  | 22684.8839
2017-09-09 | 7:34 |  |  |  |  | 77.1689 |  | 22643.5554
2017-09-09 | 7:36 |  |  |  |  | 77.1724 |  | 22644.5965
2017-09-09 | 7:38 |  |  |  |  | 77.2311 |  | 22661.8143
2017-09-09 | 7:40 |  |  |  |  | 77.3157 |  | 22686.6433
2017-09-09 | 7:42 |  |  |  |  | 77.2756 |  | 22674.8748
2017-09-09 | 7:44 |  |  |  |  | 77.2854 |  | 22677.7313
2017-09-09 | 7:45 | 1.7553 | 0 | 0 | 1.5 | 77.2769 | 0 | 22675.2554
2017-09-09 | 7:46 |  |  |  |  | 77.225 |  | 22660.012
2017-09-09 | 7:48 |  |  |  |  | 77.1878 |  | 22649.0918
2017-09-09 | 7:50 |  |  |  |  | 77.1454 |  | 22636.6648
2017-09-09 | 7:52 |  |  |  |  | 77.227 |  | 22660.5942
2017-09-09 | 7:54 |  |  |  |  | 77.3152 |  | 22686.4799
2017-09-09 | 7:56 |  |  |  |  | 77.321 |  | 22688.2038
2017-09-09 | 7:58 |  |  |  |  | 77.306 |  | 22683.7891
2017-09-09 | 8:00 | 1.7592 | 0 | 0 | 1.5 | 77.2601 | 0 | 22670.3346
2017-09-09 | 8:02 |  |  |  |  | 77.2089 |  | 22655.2861
2017-09-09 | 8:04 |  |  |  |  | 77.1323 |  | 22632.8256
2017-09-09 | 8:06 |  |  |  |  | 77.1963 |  | 22651.6059
2017-09-09 | 8:08 |  |  |  |  | 77.2097 |  | 22655.5258
2017-09-09 | 8:10 |  |  |  |  | 77.306 |  | 22683.7844
2017-09-09 | 8:12 |  |  |  |  | 77.2576 |  | 22669.5846
2017-09-09 | 8:14 |  |  |  |  | 77.2411 |  | 22664.7401
2017-09-09 | 8:15 | 1.76 | 0 | 0 | 1.5 | 77.2392 | 0 | 22664.2028
2017-09-09 | 8:16 |  |  |  |  | 77.2085 |  | 22655.1878
2017-09-09 | 8:18 |  |  |  |  | 77.1897 |  | 22649.6581
2017-09-09 | 8:20 |  |  |  |  | 77.1235 |  | 22630.2466
2017-09-09 | 8:22 |  |  |  |  | 77.0312 |  | 22603.1605
2017-09-09 | 8:24 |  |  |  |  | 76.9851 |  | 22589.6323
2017-09-09 | 8:26 |  |  |  |  | 77.0402 |  | 22605.8002
2017-09-09 | 8:28 |  |  |  |  | 77.0522 |  | 22609.3082
2017-09-09 | 8:30 | 1.7148 | 0 | 0 | 1.5 | 77.1399 | 0 | 22635.0463
2017-09-09 | 8:32 |  |  |  |  | 77.0495 |  | 22608.5268
2017-09-09 | 8:34 |  |  |  |  | 77.0226 |  | 22600.6288
2017-09-09 | 8:36 |  |  |  |  | 77.0066 |  | 22595.9343
2017-09-09 | 8:38 |  |  |  |  | 76.9948 |  | 22592.4821
2017-09-09 | 8:40 |  |  |  |  | 76.9011 |  | 22564.9711
2017-09-09 | 8:42 |  |  |  |  | 77.0176 |  | 22599.1737
2017-09-09 | 8:44 |  |  |  |  | 77.0951 |  | 22621.9142
2017-09-09 | 8:45 | 1.7187 | 0 | 0 | 1.5 | 77.1621 | 0 | 22641.5698
2017-09-09 | 8:46 |  |  |  |  | 77.1619 |  | 22641.4958
2017-09-09 | 8:48 |  |  |  |  | 77.13 |  | 22632.1495
2017-09-09 | 8:50 |  |  |  |  | 77.1499 |  | 22637.9767
2017-09-09 | 8:52 |  |  |  |  | 77.1453 |  | 22636.6402
2017-09-09 | 8:54 |  |  |  |  | 77.0769 |  | 22616.5793
2017-09-09 | 8:56 |  |  |  |  | 77.0837 |  | 22618.5562
2017-09-09 | 8:58 |  |  |  |  | 77.0038 |  | 22595.1262
2017-09-09 | 9:00 | 1.7912 | 0 | 0 | 1.5 | 76.878 | 0 | 22558.2035
2017-09-09 | 9:02 |  |  |  |  | 76.9511 |  | 22579.6478
2017-09-09 | 9:04 |  |  |  |  | 76.9696 |  | 22585.0721
2017-09-09 | 9:06 |  |  |  |  | 76.9214 |  | 22570.9506
2017-09-09 | 9:08 |  |  |  |  | 76.9474 |  | 22578.5642
2017-09-09 | 9:10 |  |  |  |  | 76.9496 |  | 22579.2
2017-09-09 | 9:12 |  |  |  |  | 76.9494 |  | 22579.1396
2017-09-09 | 9:14 |  |  |  |  | 76.9353 |  | 22575.0049
2017-09-09 | 9:15 | 1.753 | 0 | 0 | 1.5 | 76.9362 | 0 | 22575.2666
2017-09-09 | 9:16 |  |  |  |  | 76.9482 |  | 22578.8083
2017-09-09 | 9:18 |  |  |  |  | 76.8881 |  | 22561.1785
2017-09-09 | 9:20 |  |  |  |  | 76.8254 |  | 22542.7812
2017-09-09 | 9:22 |  |  |  |  | 76.94 |  | 22576.3884
2017-09-09 | 9:24 |  |  |  |  | 77.0379 |  | 22605.1127
2017-09-09 | 9:26 |  |  |  |  | 77.04 |  | 22605.7462
2017-09-09 | 9:28 |  |  |  |  | 77.0768 |  | 22616.5391
2017-09-09 | 9:30 | 1.7468 | 0 | 0 | 1.5 | 77.0904 | 0 | 22620.5127
2017-09-09 | 9:32 |  |  |  |  | 77.0844 |  | 22618.751
2017-09-09 | 9:34 |  |  |  |  | 77.0765 |  | 22616.4608
2017-09-09 | 9:36 |  |  |  |  | 77.0372 |  | 22604.9158
2017-09-09 | 9:38 |  |  |  |  | 77.0594 |  | 22611.4437
2017-09-09 | 9:40 |  |  |  |  | 77.049 |  | 22608.3677
2017-09-09 | 9:42 |  |  |  |  | 77.0399 |  | 22605.6949
2017-09-09 | 9:44 |  |  |  |  | 77.0124 |  | 22597.6356
2017-09-09 | 9:45 | 1.76 | 0 | 0 | 1.5 | 76.9967 | 0 | 22593.0261
2017-09-09 | 9:46 |  |  |  |  | 77.0761 |  | 22616.3173
2017-09-09 | 9:48 |  |  |  |  | 77.1552 |  | 22639.5504
2017-09-09 | 9:50 |  |  |  |  | 77.3259 |  | 22689.6207
2017-09-09 | 9:52 |  |  |  |  | 77.3631 |  | 22700.5345
2017-09-09 | 9:54 |  |  |  |  | 77.3784 |  | 22705.0296
2017-09-09 | 9:56 |  |  |  |  | 77.3904 |  | 22708.5557
2017-09-09 | 9:58 |  |  |  |  | 77.4035 |  | 22712.3861
2017-09-09 | 10:00 | 1.7327 | 0 | 0 | 1.5 | 77.4193 | 0 | 22717.0223
2017-09-09 | 10:02 |  |  |  |  | 77.4297 |  | 22720.0871
2017-09-09 | 10:04 |  |  |  |  | 77.399 |  | 22711.083
2017-09-09 | 10:06 |  |  |  |  | 77.4056 |  | 22713.0152
2017-09-09 | 10:08 |  |  |  |  | 77.4514 |  | 22726.4405
2017-09-09 | 10:10 |  |  |  |  | 77.4396 |  | 22722.9839
2017-09-09 | 10:12 |  |  |  |  | 77.4879 |  | 22737.1594
2017-09-09 | 10:14 |  |  |  |  | 77.4813 |  | 22735.2386
2017-09-09 | 10:15 | 1.7366 | 0 | 0 | 1.5 | 77.5162 | 0 | 22745.4581
2017-09-09 | 10:16 |  |  |  |  | 77.5393 |  | 22752.2366
2017-09-09 | 10:18 |  |  |  |  | 77.5562 |  | 22757.1956
2017-09-09 | 10:20 |  |  |  |  | 77.6181 |  | 22775.3802
2017-09-09 | 10:22 |  |  |  |  | 77.6627 |  | 22788.463
2017-09-09 | 10:24 |  |  |  |  | 77.6984 |  | 22798.9179
2017-09-09 | 10:26 |  |  |  |  | 77.6925 |  | 22797.2031
2017-09-09 | 10:28 |  |  |  |  | 77.6625 |  | 22788.4049
2017-09-09 | 10:30 | 1.7647 | 0 | 0 | 1.5 | 77.6301 | 0 | 22778.9017
2017-09-09 | 10:32 |  |  |  |  | 77.6265 |  | 22777.8183
2017-09-09 | 10:34 |  |  |  |  | 77.6097 |  | 22772.8908
2017-09-09 | 10:36 |  |  |  |  | 77.5544 |  | 22756.6648
2017-09-09 | 10:38 |  |  |  |  | 77.5351 |  | 22751.0257
2017-09-09 | 10:40 |  |  |  |  | 77.4716 |  | 22732.3753
2017-09-09 | 10:42 |  |  |  |  | 77.4563 |  | 22727.8956
2017-09-09 | 10:44 |  |  |  |  | 77.4627 |  | 22729.7559
2017-09-09 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 77.4904 | 0 | 22737.898
2017-09-09 | 10:46 |  |  |  |  | 77.4785 |  | 22734.417
2017-09-09 | 10:48 |  |  |  |  | 77.4745 |  | 22733.228
2017-09-09 | 10:50 |  |  |  |  | 77.4766 |  | 22733.8504
2017-09-09 | 10:52 |  |  |  |  | 77.5122 |  | 22744.2985
2017-09-09 | 10:54 |  |  |  |  | 77.4932 |  | 22738.7196
2017-09-09 | 10:56 |  |  |  |  | 77.4993 |  | 22740.4948
2017-09-09 | 10:58 |  |  |  |  | 77.5211 |  | 22746.8974
2017-09-09 | 11:00 | 1.753 | 0 | 0 | 1.5 | 77.5856 | 0 | 22765.8412
2017-09-09 | 11:02 |  |  |  |  | 77.6165 |  | 22774.8879
2017-09-09 | 11:04 |  |  |  |  | 77.6256 |  | 22777.5607
2017-09-09 | 11:06 |  |  |  |  | 77.5905 |  | 22767.2672
2017-09-09 | 11:08 |  |  |  |  | 77.5814 |  | 22764.592
2017-09-09 | 11:10 |  |  |  |  | 77.5529 |  | 22756.2237
2017-09-09 | 11:12 |  |  |  |  | 77.5681 |  | 22760.6877
2017-09-09 | 11:14 |  |  |  |  | 77.64 |  | 22781.794
2017-09-09 | 11:15 | 1.7296 | 0 | 0 | 1.5 | 77.6437 | 0 | 22782.8685
2017-09-09 | 11:16 |  |  |  |  | 77.6067 |  | 22772.0199
2017-09-09 | 11:18 |  |  |  |  | 77.6642 |  | 22788.8953
2017-09-09 | 11:20 |  |  |  |  | 77.7194 |  | 22805.0875
2017-09-09 | 11:22 |  |  |  |  | 77.7679 |  | 22819.3279
2017-09-09 | 11:24 |  |  |  |  | 77.8079 |  | 22831.0653
2017-09-09 | 11:26 |  |  |  |  | 77.8323 |  | 22838.2112
2017-09-09 | 11:28 |  |  |  |  | 77.8513 |  | 22843.801
2017-09-09 | 11:30 | 1.7483 | 0 | 0 | 1.5 | 77.8772 | 0 | 22851.4058
2017-09-09 | 11:32 |  |  |  |  | 77.9347 |  | 22868.2633
2017-09-09 | 11:34 |  |  |  |  | 77.9652 |  | 22877.209
2017-09-09 | 11:36 |  |  |  |  | 77.9521 |  | 22873.381
2017-09-09 | 11:38 |  |  |  |  | 77.9304 |  | 22866.9963
2017-09-09 | 11:40 |  |  |  |  | 77.9617 |  | 22876.197
2017-09-09 | 11:42 |  |  |  |  | 77.9845 |  | 22882.8795
2017-09-09 | 11:44 |  |  |  |  | 77.9814 |  | 22881.9661
2017-09-09 | 11:45 | 1.7522 | 0 | 0 | 1.5 | 77.9694 | 0 | 22878.4359
2017-09-09 | 11:46 |  |  |  |  | 77.9674 |  | 22877.8605
2017-09-09 | 11:48 |  |  |  |  | 78.009 |  | 22890.0568
2017-09-09 | 11:50 |  |  |  |  | 78.0371 |  | 22898.3086
2017-09-09 | 11:52 |  |  |  |  | 78.0404 |  | 22899.2936
2017-09-09 | 11:54 |  |  |  |  | 78.0573 |  | 22904.2567
2017-09-09 | 11:56 |  |  |  |  | 78.0447 |  | 22900.5519
2017-09-09 | 11:58 |  |  |  |  | 78.048 |  | 22901.5099
2017-09-09 | 12:00 | 1.7319 | 0 | 0 | 1.5 | 78.0861 | 0 | 22912.6922
2017-09-09 | 12:02 |  |  |  |  | 78.0799 |  | 22910.8855
2017-09-09 | 12:04 |  |  |  |  | 78.094 |  | 22915.0091
2017-09-09 | 12:06 |  |  |  |  | 78.0661 |  | 22906.8133
2017-09-09 | 12:08 |  |  |  |  | 78.0974 |  | 22916.0053
2017-09-09 | 12:10 |  |  |  |  | 78.0613 |  | 22905.4275
2017-09-09 | 12:12 |  |  |  |  | 77.9785 |  | 22881.1178
2017-09-09 | 12:14 |  |  |  |  | 77.8984 |  | 22857.6027
2017-09-09 | 12:15 | 1.7709 | 0 | 0 | 1.5 | 77.8905 | 0 | 22855.2855
2017-09-09 | 12:16 |  |  |  |  | 77.8748 |  | 22850.6852
2017-09-09 | 12:18 |  |  |  |  | 77.7946 |  | 22827.1677
2017-09-09 | 12:20 |  |  |  |  | 77.7646 |  | 22818.354
2017-09-09 | 12:22 |  |  |  |  | 77.818 |  | 22834.0205
2017-09-09 | 12:24 |  |  |  |  | 77.8805 |  | 22852.3776
2017-09-09 | 12:26 |  |  |  |  | 77.922 |  | 22864.547
2017-09-09 | 12:28 |  |  |  |  | 78.0004 |  | 22887.5339
2017-09-09 | 12:30 | 1.7514 | 0 | 0 | 1.5 | 78.0181 | 0 | 22892.7431
2017-09-09 | 12:32 |  |  |  |  | 78.0249 |  | 22894.749
2017-09-09 | 12:34 |  |  |  |  | 78.0162 |  | 22892.1856
2017-09-09 | 12:36 |  |  |  |  | 78.025 |  | 22894.7669
2017-09-09 | 12:38 |  |  |  |  | 78.0346 |  | 22897.5877
2017-09-09 | 12:40 |  |  |  |  | 78.0457 |  | 22900.8248
2017-09-09 | 12:42 |  |  |  |  | 78.0204 |  | 22893.4013
2017-09-09 | 12:44 |  |  |  |  | 78.0659 |  | 22906.7684
2017-09-09 | 12:45 | 1.7319 | 0 | 0 | 1.5 | 78.0917 | 0 | 22914.3242
2017-09-09 | 12:46 |  |  |  |  | 78.1179 |  | 22922.0364
2017-09-09 | 12:48 |  |  |  |  | 78.1252 |  | 22924.172
2017-09-09 | 12:50 |  |  |  |  | 78.1285 |  | 22925.1391
2017-09-09 | 12:52 |  |  |  |  | 78.1823 |  | 22940.9086
2017-09-09 | 12:54 |  |  |  |  | 78.2436 |  | 22958.9075
2017-09-09 | 12:56 |  |  |  |  | 78.2535 |  | 22961.8177
2017-09-09 | 12:58 |  |  |  |  | 78.2609 |  | 22963.9847
2017-09-09 | 13:00 | 1.7592 | 0 | 0 | 1.5 | 78.2571 | 0 | 22962.8676
2017-09-09 | 13:02 |  |  |  |  | 78.266 |  | 22965.4668
2017-09-09 | 13:04 |  |  |  |  | 78.2732 |  | 22967.6026
2017-09-09 | 13:06 |  |  |  |  | 78.2429 |  | 22958.6903
2017-09-09 | 13:08 |  |  |  |  | 78.2199 |  | 22951.9518
2017-09-09 | 13:10 |  |  |  |  | 78.2467 |  | 22959.803
2017-09-09 | 13:12 |  |  |  |  | 78.2411 |  | 22958.1845
2017-09-09 | 13:14 |  |  |  |  | 78.2703 |  | 22966.7406
2017-09-09 | 13:15 | 1.7475 | 0 | 0 | 1.5 | 78.2493 | 0 | 22960.5709
2017-09-09 | 13:16 |  |  |  |  | 78.261 |  | 22964.0073
2017-09-09 | 13:18 |  |  |  |  | 78.2639 |  | 22964.8735
2017-09-09 | 13:20 |  |  |  |  | 78.3185 |  | 22980.8979
2017-09-09 | 13:22 |  |  |  |  | 78.3554 |  | 22991.7222
2017-09-09 | 13:24 |  |  |  |  | 78.3266 |  | 22983.2755
2017-09-09 | 13:26 |  |  |  |  | 78.3722 |  | 22996.6403
2017-09-09 | 13:28 |  |  |  |  | 78.3525 |  | 22990.8668
2017-09-09 | 13:30 | 1.7429 | 0 | 0 | 1.5 | 78.3381 | 0 | 22986.6426
2017-09-09 | 13:32 |  |  |  |  | 78.3668 |  | 22995.0623
2017-09-09 | 13:34 |  |  |  |  | 78.3217 |  | 22981.8204
2017-09-09 | 13:36 |  |  |  |  | 78.2498 |  | 22960.7408
2017-09-09 | 13:38 |  |  |  |  | 78.1635 |  | 22935.3901
2017-09-09 | 13:40 |  |  |  |  | 78.0676 |  | 22907.2611
2017-09-09 | 13:42 |  |  |  |  | 78.0165 |  | 22892.2707
2017-09-09 | 13:44 |  |  |  |  | 77.9069 |  | 22860.1233
2017-09-09 | 13:45 | 1.7655 | 0 | 0 | 1.5 | 77.9104 | 0 | 22861.1421
2017-09-09 | 13:46 |  |  |  |  | 77.8833 |  | 22853.1767
2017-09-09 | 13:48 |  |  |  |  | 77.8281 |  | 22837.0023
2017-09-09 | 13:50 |  |  |  |  | 77.8162 |  | 22833.4964
2017-09-09 | 13:52 |  |  |  |  | 77.8351 |  | 22839.0281
2017-09-09 | 13:54 |  |  |  |  | 77.8996 |  | 22857.9563
2017-09-09 | 13:56 |  |  |  |  | 77.9249 |  | 22865.3977
2017-09-09 | 13:58 |  |  |  |  | 77.9479 |  | 22872.1362
2017-09-09 | 14:00 | 1.7382 | 0 | 0 | 1.5 | 77.9643 | 0 | 22876.9649
2017-09-09 | 14:02 |  |  |  |  | 77.9224 |  | 22864.6568
2017-09-09 | 14:04 |  |  |  |  | 77.8689 |  | 22848.9569
2017-09-09 | 14:06 |  |  |  |  | 77.7997 |  | 22828.661
2017-09-09 | 14:08 |  |  |  |  | 77.7386 |  | 22810.7357
2017-09-09 | 14:10 |  |  |  |  | 77.7018 |  | 22799.9161
2017-09-09 | 14:12 |  |  |  |  | 77.6441 |  | 22782.9894
2017-09-09 | 14:14 |  |  |  |  | 77.6193 |  | 22775.7162
2017-09-09 | 14:15 | 1.753 | 0 | 0 | 1.5 | 77.6433 | 0 | 22782.7523
2017-09-09 | 14:16 |  |  |  |  | 77.6599 |  | 22787.6414
2017-09-09 | 14:18 |  |  |  |  | 77.7151 |  | 22803.8384
2017-09-09 | 14:20 |  |  |  |  | 77.7722 |  | 22820.5993
2017-09-09 | 14:22 |  |  |  |  | 77.7772 |  | 22822.0635
2017-09-09 | 14:24 |  |  |  |  | 77.8396 |  | 22840.3535
2017-09-09 | 14:26 |  |  |  |  | 77.8649 |  | 22847.7837
2017-09-09 | 14:28 |  |  |  |  | 77.9019 |  | 22858.6503
2017-09-09 | 14:30 | 1.7514 | 0 | 0 | 1.5 | 77.9072 | 0 | 22860.1928
2017-09-09 | 14:32 |  |  |  |  | 77.9347 |  | 22868.2542
2017-09-09 | 14:34 |  |  |  |  | 77.9338 |  | 22867.9924
2017-09-09 | 14:36 |  |  |  |  | 77.9477 |  | 22872.0735
2017-09-09 | 14:38 |  |  |  |  | 77.9652 |  | 22877.2246
2017-09-09 | 14:40 |  |  |  |  | 77.9733 |  | 22879.5843
2017-09-09 | 14:42 |  |  |  |  | 77.9949 |  | 22885.9397
2017-09-09 | 14:44 |  |  |  |  | 78.0162 |  | 22892.1677
2017-09-09 | 14:45 | 1.7195 | 0 | 0 | 1.5 | 78.0626 | 0 | 22905.8037
2017-09-09 | 14:46 |  |  |  |  | 78.0651 |  | 22906.5314
2017-09-09 | 14:48 |  |  |  |  | 78.0655 |  | 22906.6611
2017-09-09 | 14:50 |  |  |  |  | 78.1076 |  | 22919.003
2017-09-09 | 14:52 |  |  |  |  | 78.0985 |  | 22916.3389
2017-09-09 | 14:54 |  |  |  |  | 78.1176 |  | 22921.929
2017-09-09 | 14:56 |  |  |  |  | 78.1201 |  | 22922.6834
2017-09-09 | 14:58 |  |  |  |  | 78.129 |  | 22925.2712
2017-09-09 | 15:00 | 1.7553 | 0 | 0 | 1.5 | 78.0928 | 0 | 22914.6576
2017-09-09 | 15:02 |  |  |  |  | 78.0709 |  | 22908.2215
2017-09-09 | 15:04 |  |  |  |  | 78.0402 |  | 22899.2265
2017-09-09 | 15:06 |  |  |  |  | 78.0286 |  | 22895.8236
2017-09-09 | 15:08 |  |  |  |  | 78.0213 |  | 22893.6812
2017-09-09 | 15:10 |  |  |  |  | 78.0001 |  | 22887.4576
2017-09-09 | 15:12 |  |  |  |  | 77.9005 |  | 22858.2251
2017-09-09 | 15:14 |  |  |  |  | 77.8586 |  | 22845.9369
2017-09-09 | 15:15 | 1.7608 | 0 | 0 | 1.5 | 77.883 | 0 | 22853.0895
2017-09-09 | 15:16 |  |  |  |  | 77.8549 |  | 22844.8398
2017-09-09 | 15:18 |  |  |  |  | 77.8232 |  | 22835.5539
2017-09-09 | 15:20 |  |  |  |  | 77.8137 |  | 22832.7511
2017-09-09 | 15:22 |  |  |  |  | 77.7963 |  | 22827.6692
2017-09-09 | 15:24 |  |  |  |  | 77.7477 |  | 22813.3998
2017-09-09 | 15:26 |  |  |  |  | 77.726 |  | 22807.0242
2017-09-09 | 15:28 |  |  |  |  | 77.7108 |  | 22802.5555
2017-09-09 | 15:30 | 1.7639 | 0 | 0 | 1.5 | 77.67 | 0 | 22790.5945
2017-09-09 | 15:32 |  |  |  |  | 77.6675 |  | 22789.8712
2017-09-09 | 15:34 |  |  |  |  | 77.6443 |  | 22783.0657
2017-09-09 | 15:36 |  |  |  |  | 77.6134 |  | 22774.0011
2017-09-09 | 15:38 |  |  |  |  | 77.6187 |  | 22775.5302
2017-09-09 | 15:40 |  |  |  |  | 77.6103 |  | 22773.0701
2017-09-09 | 15:42 |  |  |  |  | 77.5608 |  | 22758.5544
2017-09-09 | 15:44 |  |  |  |  | 77.5257 |  | 22748.2498
2017-09-09 | 15:45 | 1.7538 | 0 | 0 | 1.5 | 77.5216 | 0 | 22747.0609
2017-09-09 | 15:46 |  |  |  |  | 77.5253 |  | 22748.1468
2017-09-09 | 15:48 |  |  |  |  | 77.5022 |  | 22741.3657
2017-09-09 | 15:50 |  |  |  |  | 77.4457 |  | 22724.7838
2017-09-09 | 15:52 |  |  |  |  | 77.4173 |  | 22716.4583
2017-09-09 | 15:54 |  |  |  |  | 77.3797 |  | 22705.4216
2017-09-09 | 15:56 |  |  |  |  | 77.3523 |  | 22697.3711
2017-09-09 | 15:58 |  |  |  |  | 77.3455 |  | 22695.381
2017-09-09 | 16:00 | 1.7429 | 0 | 0 | 1.5 | 77.3429 | 0 | 22694.631
2017-09-09 | 16:02 |  |  |  |  | 77.3191 |  | 22687.6395
2017-09-09 | 16:04 |  |  |  |  | 77.3186 |  | 22687.494
2017-09-09 | 16:06 |  |  |  |  | 77.297 |  | 22681.1339
2017-09-09 | 16:08 |  |  |  |  | 77.2915 |  | 22679.5265
2017-09-09 | 16:10 |  |  |  |  | 77.3013 |  | 22682.4235
2017-09-09 | 16:12 |  |  |  |  | 77.2595 |  | 22670.1421
2017-09-09 | 16:14 |  |  |  |  | 77.2636 |  | 22671.3352
2017-09-09 | 16:15 | 1.753 | 0 | 0 | 1.5 | 77.2694 | 0 | 22673.0455
2017-09-09 | 16:16 |  |  |  |  | 77.2872 |  | 22678.2865
2017-09-09 | 16:18 |  |  |  |  | 77.2569 |  | 22669.3897
2017-09-09 | 16:20 |  |  |  |  | 77.2378 |  | 22663.7685
2017-09-09 | 16:22 |  |  |  |  | 77.188 |  | 22649.1722
2017-09-09 | 16:24 |  |  |  |  | 77.1089 |  | 22625.9594
2017-09-09 | 16:26 |  |  |  |  | 77.0652 |  | 22613.1183
2017-09-09 | 16:28 |  |  |  |  | 76.9652 |  | 22583.7872
2017-09-09 | 16:30 | 1.7717 | 0 | 0 | 1.5 | 76.8864 | 0 | 22560.6771
2017-09-09 | 16:32 |  |  |  |  | 76.7961 |  | 22534.1802
2017-09-09 | 16:34 |  |  |  |  | 76.7297 |  | 22514.688
2017-09-09 | 16:36 |  |  |  |  | 76.7138 |  | 22510.007
2017-09-09 | 16:38 |  |  |  |  | 76.6671 |  | 22496.3062
2017-09-09 | 16:40 |  |  |  |  | 76.6364 |  | 22487.3223
2017-09-09 | 16:42 |  |  |  |  | 76.6113 |  | 22479.9346
2017-09-09 | 16:44 |  |  |  |  | 76.6524 |  | 22492.0101
2017-09-09 | 16:45 | 1.7452 | 0 | 0 | 1.5 | 76.6851 | 0 | 22501.6052
2017-09-09 | 16:46 |  |  |  |  | 76.6818 |  | 22500.6334
2017-09-09 | 16:48 |  |  |  |  | 76.7424 |  | 22518.4107
2017-09-09 | 16:50 |  |  |  |  | 76.7652 |  | 22525.1
2017-09-09 | 16:52 |  |  |  |  | 76.793 |  | 22533.26
2017-09-09 | 16:54 |  |  |  |  | 76.8313 |  | 22544.5004
2017-09-09 | 16:56 |  |  |  |  | 76.8211 |  | 22541.505
2017-09-09 | 16:58 |  |  |  |  | 76.8566 |  | 22551.915
2017-09-09 | 17:00 | 1.7491 | 0 | 0 | 1.5 | 76.8917 | 0 | 22562.2331
2017-09-09 | 17:02 |  |  |  |  | 76.9052 |  | 22566.1753
2017-09-09 | 17:04 |  |  |  |  | 76.916 |  | 22569.3408
2017-09-09 | 17:06 |  |  |  |  | 76.8975 |  | 22563.9368
2017-09-09 | 17:08 |  |  |  |  | 76.8925 |  | 22562.4435
2017-09-09 | 17:10 |  |  |  |  | 76.9593 |  | 22582.0498
2017-09-09 | 17:12 |  |  |  |  | 76.968 |  | 22584.6109
2017-09-09 | 17:14 |  |  |  |  | 76.9844 |  | 22589.4128
2017-09-09 | 17:15 | 1.7553 | 0 | 0 | 1.5 | 76.9831 | 0 | 22589.0279
2017-09-09 | 17:16 |  |  |  |  | 76.9956 |  | 22592.7083
2017-09-09 | 17:18 |  |  |  |  | 76.9778 |  | 22587.4721
2017-09-09 | 17:20 |  |  |  |  | 76.9656 |  | 22583.9102
2017-09-09 | 17:22 |  |  |  |  | 76.9665 |  | 22584.1698
2017-09-09 | 17:24 |  |  |  |  | 76.892 |  | 22562.3138
2017-09-09 | 17:26 |  |  |  |  | 76.8655 |  | 22554.5388
2017-09-09 | 17:28 |  |  |  |  | 76.8207 |  | 22541.3976
2017-09-09 | 17:30 | 1.7717 | 0 | 0 | 1.5 | 76.7589 | 0 | 22523.2509
2017-09-09 | 17:32 |  |  |  |  | 76.7686 |  | 22526.0962
2017-09-09 | 17:34 |  |  |  |  | 76.6975 |  | 22505.2364
2017-09-09 | 17:36 |  |  |  |  | 76.6414 |  | 22488.7797
2017-09-09 | 17:38 |  |  |  |  | 76.6132 |  | 22480.5056
2017-09-09 | 17:40 |  |  |  |  | 76.5894 |  | 22473.5253
2017-09-09 | 17:42 |  |  |  |  | 76.556 |  | 22463.7177
2017-09-09 | 17:44 |  |  |  |  | 76.5216 |  | 22453.6191
2017-09-09 | 17:45 | 1.7553 | 0 | 0 | 1.5 | 76.5552 | 0 | 22463.4827
2017-09-09 | 17:46 |  |  |  |  | 76.5355 |  | 22457.7112
2017-09-09 | 17:48 |  |  |  |  | 76.549 |  | 22461.6737
2017-09-09 | 17:50 |  |  |  |  | 76.5193 |  | 22452.9518
2017-09-09 | 17:52 |  |  |  |  | 76.4512 |  | 22432.967
2017-09-09 | 17:54 |  |  |  |  | 76.427 |  | 22425.8569
2017-09-09 | 17:56 |  |  |  |  | 76.4558 |  | 22434.3171
2017-09-09 | 17:58 |  |  |  |  | 76.556 |  | 22463.7086
2017-09-09 | 18:00 | 1.7046 | 0 | 0 | 1.5 | 76.6877 | 0 | 22502.3573
2017-09-09 | 18:02 |  |  |  |  | 76.6753 |  | 22498.7105
2017-09-09 | 18:04 |  |  |  |  | 76.6788 |  | 22499.7537
2017-09-09 | 18:06 |  |  |  |  | 76.6557 |  | 22492.984
2017-09-09 | 18:08 |  |  |  |  | 76.6485 |  | 22490.8596
2017-09-09 | 18:10 |  |  |  |  | 76.5613 |  | 22465.2667
2017-09-09 | 18:12 |  |  |  |  | 76.5501 |  | 22461.9982
2017-09-09 | 18:14 |  |  |  |  | 76.516 |  | 22451.987
2017-09-09 | 18:15 | 1.7507 | 0 | 0 | 1.5 | 76.5216 | 0 | 22453.6123
2017-09-09 | 18:16 |  |  |  |  | 76.5101 |  | 22450.2587
2017-09-09 | 18:18 |  |  |  |  | 76.5026 |  | 22448.0624
2017-09-09 | 18:20 |  |  |  |  | 76.4455 |  | 22431.2859
2017-09-09 | 18:22 |  |  |  |  | 76.5715 |  | 22468.2556
2017-09-09 | 18:24 |  |  |  |  | 76.655 |  | 22492.7578
2017-09-09 | 18:26 |  |  |  |  | 76.6783 |  | 22499.6149
2017-09-09 | 18:28 |  |  |  |  | 76.7043 |  | 22507.2355
2017-09-09 | 18:30 | 1.7491 | 0 | 0 | 1.5 | 76.6844 | 0 | 22501.3925
2017-09-09 | 18:32 |  |  |  |  | 76.7032 |  | 22506.913
2017-09-09 | 18:34 |  |  |  |  | 76.6754 |  | 22498.7419
2017-09-09 | 18:36 |  |  |  |  | 76.6295 |  | 22485.2941
2017-09-09 | 18:38 |  |  |  |  | 76.5935 |  | 22474.7274
2017-09-09 | 18:40 |  |  |  |  | 76.536 |  | 22457.8477
2017-09-09 | 18:42 |  |  |  |  | 76.5046 |  | 22448.6378
2017-09-09 | 18:44 |  |  |  |  | 76.4362 |  | 22428.5635
2017-09-09 | 18:45 | 1.7678 | 0 | 0 | 1.5 | 76.4201 | 0 | 22423.849
2017-09-09 | 18:46 |  |  |  |  | 76.4467 |  | 22431.6351
2017-09-09 | 18:48 |  |  |  |  | 76.5447 |  | 22460.3976
2017-09-09 | 18:50 |  |  |  |  | 76.6126 |  | 22480.3196
2017-09-09 | 18:52 |  |  |  |  | 76.5441 |  | 22460.2321
2017-09-09 | 18:54 |  |  |  |  | 76.5282 |  | 22455.5598
2017-09-09 | 18:56 |  |  |  |  | 76.4629 |  | 22436.4036
2017-09-09 | 18:58 |  |  |  |  | 76.4473 |  | 22431.8097
2017-09-09 | 19:00 | 1.7592 | 0 | 0 | 1.5 | 76.4031 | 0 | 22418.8633
2017-09-09 | 19:02 |  |  |  |  | 76.3337 |  | 22398.4891
2017-09-09 | 19:04 |  |  |  |  | 76.2813 |  | 22383.1161
2017-09-09 | 19:06 |  |  |  |  | 76.3324 |  | 22398.1197
2017-09-09 | 19:08 |  |  |  |  | 76.37 |  | 22409.1497
2017-09-09 | 19:10 |  |  |  |  | 76.4885 |  | 22443.9098
2017-09-09 | 19:12 |  |  |  |  | 76.4879 |  | 22443.7329
2017-09-09 | 19:14 |  |  |  |  | 76.4986 |  | 22446.8693
2017-09-09 | 19:15 | 1.753 | 0 | 0 | 1.5 | 76.4857 | 0 | 22443.0771
2017-09-09 | 19:16 |  |  |  |  | 76.461 |  | 22435.8438
2017-09-09 | 19:18 |  |  |  |  | 76.4294 |  | 22426.5755
2017-09-09 | 19:20 |  |  |  |  | 76.4146 |  | 22422.2416
2017-09-09 | 19:22 |  |  |  |  | 76.3359 |  | 22399.1226
2017-09-09 | 19:24 |  |  |  |  | 76.3027 |  | 22389.3843
2017-09-09 | 19:26 |  |  |  |  | 76.3268 |  | 22396.4677
2017-09-09 | 19:28 |  |  |  |  | 76.4245 |  | 22425.1451
2017-09-09 | 19:30 | 1.728 | 0 | 0 | 1.5 | 76.5084 | 0 | 22449.7414
2017-09-09 | 19:32 |  |  |  |  | 76.4763 |  | 22440.3367
2017-09-09 | 19:34 |  |  |  |  | 76.4287 |  | 22426.3742
2017-09-09 | 19:36 |  |  |  |  | 76.4543 |  | 22433.8828
2017-09-09 | 19:38 |  |  |  |  | 76.3857 |  | 22413.7392
2017-09-09 | 19:40 |  |  |  |  | 76.378 |  | 22411.4959
2017-09-09 | 19:42 |  |  |  |  | 76.4003 |  | 22418.0306
2017-09-09 | 19:44 |  |  |  |  | 76.34 |  | 22400.3471
2017-09-09 | 19:45 | 1.7733 | 0 | 0 | 1.5 | 76.3081 | 0 | 22390.9762
2017-09-09 | 19:46 |  |  |  |  | 76.3292 |  | 22397.1549
2017-09-09 | 19:48 |  |  |  |  | 76.3744 |  | 22410.4235
2017-09-09 | 19:50 |  |  |  |  | 76.4537 |  | 22433.7035
2017-09-09 | 19:52 |  |  |  |  | 76.4045 |  | 22419.273
2017-09-09 | 19:54 |  |  |  |  | 76.3633 |  | 22407.1796
2017-09-09 | 19:56 |  |  |  |  | 76.2977 |  | 22387.9383
2017-09-09 | 19:58 |  |  |  |  | 76.2744 |  | 22381.0923
2017-09-09 | 20:00 | 1.7709 | 0 | 0 | 1.5 | 76.2049 | 0 | 22360.7046
2017-09-09 | 20:02 |  |  |  |  | 76.3169 |  | 22393.5639
2017-09-09 | 20:04 |  |  |  |  | 76.3746 |  | 22410.4795
2017-09-09 | 20:06 |  |  |  |  | 76.4044 |  | 22419.2328
2017-09-09 | 20:08 |  |  |  |  | 76.3979 |  | 22417.3164
2017-09-09 | 20:10 |  |  |  |  | 76.3975 |  | 22417.2157
2017-09-09 | 20:12 |  |  |  |  | 76.3422 |  | 22400.9921
2017-09-09 | 20:14 |  |  |  |  | 76.3325 |  | 22398.1467
2017-09-09 | 20:15 | 1.7663 | 0 | 0 | 1.5 | 76.2955 | 0 | 22387.2755
2017-09-09 | 20:16 |  |  |  |  | 76.2806 |  | 22382.9057
2017-09-09 | 20:18 |  |  |  |  | 76.2342 |  | 22369.3036
2017-09-09 | 20:20 |  |  |  |  | 76.2113 |  | 22362.5808
2017-09-09 | 20:22 |  |  |  |  | 76.3204 |  | 22394.5871
2017-09-09 | 20:24 |  |  |  |  | 76.3888 |  | 22414.6479
2017-09-09 | 20:26 |  |  |  |  | 76.3942 |  | 22416.2375
2017-09-09 | 20:28 |  |  |  |  | 76.3604 |  | 22406.3155
2017-09-09 | 20:30 | 1.76 | 0 | 0 | 1.5 | 76.3415 | 0 | 22400.7837
2017-09-09 | 20:32 |  |  |  |  | 76.3245 |  | 22395.8004
2017-09-09 | 20:34 |  |  |  |  | 76.3128 |  | 22392.353
2017-09-09 | 20:36 |  |  |  |  | 76.3426 |  | 22401.0971
2017-09-09 | 20:38 |  |  |  |  | 76.3832 |  | 22413.0071
2017-09-09 | 20:40 |  |  |  |  | 76.4838 |  | 22442.5465
2017-09-09 | 20:42 |  |  |  |  | 76.4327 |  | 22427.5383
2017-09-09 | 20:44 |  |  |  |  | 76.3897 |  | 22414.9279
2017-09-09 | 20:45 | 1.7631 | 0 | 0 | 1.5 | 76.3649 | 0 | 22407.6432
2017-09-09 | 20:46 |  |  |  |  | 76.3318 |  | 22397.9228
2017-09-09 | 20:48 |  |  |  |  | 76.2806 |  | 22382.9192
2017-09-09 | 20:50 |  |  |  |  | 76.2444 |  | 22372.2989
2017-09-09 | 20:52 |  |  |  |  | 76.3004 |  | 22388.7083
2017-09-09 | 20:54 |  |  |  |  | 76.3716 |  | 22409.6086
2017-09-09 | 20:56 |  |  |  |  | 76.3778 |  | 22411.4264
2017-09-09 | 20:58 |  |  |  |  | 76.3157 |  | 22393.208
2017-09-09 | 21:00 | 1.7764 | 0 | 0 | 1.5 | 76.2433 | 0 | 22371.9585
2017-09-09 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-09 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-10 | 5:04 |  |  |  |  | 99.8427 |  | 29296.6865
2017-09-10 | 5:06 |  |  |  |  | 98.2374 |  | 28825.6611
2017-09-10 | 5:08 |  |  |  |  | 96.0106 |  | 28172.2614
2017-09-10 | 5:10 |  |  |  |  | 94.3716 |  | 27691.3296
2017-09-10 | 5:12 |  |  |  |  | 92.7628 |  | 27219.2453
2017-09-10 | 5:14 |  |  |  |  | 91.4146 |  | 26823.6678
2017-09-10 | 5:15 | 2.1664 | 0 | 0 | 1.5 | 90.8551 | 0 | 26659.4895
2017-09-10 | 5:16 |  |  |  |  | 90.3354 |  | 26506.9794
2017-09-10 | 5:18 |  |  |  |  | 89.3323 |  | 26212.6533
2017-09-10 | 5:20 |  |  |  |  | 88.3491 |  | 25924.1385
2017-09-10 | 5:22 |  |  |  |  | 87.5463 |  | 25688.5799
2017-09-10 | 5:24 |  |  |  |  | 86.7326 |  | 25449.8132
2017-09-10 | 5:26 |  |  |  |  | 86.0422 |  | 25247.2483
2017-09-10 | 5:28 |  |  |  |  | 85.3516 |  | 25044.5937
2017-09-10 | 5:30 | 1.9464 | 0 | 0 | 1.5 | 84.7838 | 0 | 24877.9999
2017-09-10 | 5:32 |  |  |  |  | 84.2599 |  | 24724.2674
2017-09-10 | 5:34 |  |  |  |  | 83.6951 |  | 24558.5377
2017-09-10 | 5:36 |  |  |  |  | 83.1695 |  | 24404.3014
2017-09-10 | 5:38 |  |  |  |  | 82.7511 |  | 24281.53
2017-09-10 | 5:40 |  |  |  |  | 82.3109 |  | 24152.3625
2017-09-10 | 5:42 |  |  |  |  | 81.8902 |  | 24028.9215
2017-09-10 | 5:44 |  |  |  |  | 81.5427 |  | 23926.9518
2017-09-10 | 5:45 | 1.8661 | 0 | 0 | 1.5 | 81.3372 | 0 | 23866.6619
2017-09-10 | 5:46 |  |  |  |  | 81.151 |  | 23812.0358
2017-09-10 | 5:48 |  |  |  |  | 80.7525 |  | 23695.1027
2017-09-10 | 5:50 |  |  |  |  | 80.4035 |  | 23592.6718
2017-09-10 | 5:52 |  |  |  |  | 80.0483 |  | 23488.4498
2017-09-10 | 5:54 |  |  |  |  | 79.7663 |  | 23405.7194
2017-09-10 | 5:56 |  |  |  |  | 79.5139 |  | 23331.6639
2017-09-10 | 5:58 |  |  |  |  | 79.3924 |  | 23296.0082
2017-09-10 | 6:00 | 1.7858 | 0 | 0 | 1.5 | 79.2802 | 0 | 23263.0793
2017-09-10 | 6:02 |  |  |  |  | 79.2213 |  | 23245.8034
2017-09-10 | 6:04 |  |  |  |  | 79.1841 |  | 23234.8765
2017-09-10 | 6:06 |  |  |  |  | 79.0834 |  | 23205.3147
2017-09-10 | 6:08 |  |  |  |  | 79.0166 |  | 23185.7351
2017-09-10 | 6:10 |  |  |  |  | 78.9934 |  | 23178.9117
2017-09-10 | 6:12 |  |  |  |  | 78.8466 |  | 23135.8596
2017-09-10 | 6:14 |  |  |  |  | 78.7353 |  | 23103.1884
2017-09-10 | 6:15 | 1.8029 | 0 | 0 | 1.5 | 78.673 | 0 | 23084.9004
2017-09-10 | 6:16 |  |  |  |  | 78.5463 |  | 23047.7406
2017-09-10 | 6:18 |  |  |  |  | 78.3556 |  | 22991.7668
2017-09-10 | 6:20 |  |  |  |  | 78.1723 |  | 22938.0004
2017-09-10 | 6:22 |  |  |  |  | 78.1324 |  | 22926.2741
2017-09-10 | 6:24 |  |  |  |  | 78.0694 |  | 22907.8051
2017-09-10 | 6:26 |  |  |  |  | 78.0233 |  | 22894.279
2017-09-10 | 6:28 |  |  |  |  | 78.033 |  | 22897.122
2017-09-10 | 6:30 | 1.7351 | 0 | 0 | 1.5 | 78.1109 | 0 | 22919.9633
2017-09-10 | 6:32 |  |  |  |  | 78.0285 |  | 22895.781
2017-09-10 | 6:34 |  |  |  |  | 78.0115 |  | 22890.7933
2017-09-10 | 6:36 |  |  |  |  | 77.9619 |  | 22876.2486
2017-09-10 | 6:38 |  |  |  |  | 77.9093 |  | 22860.8219
2017-09-10 | 6:40 |  |  |  |  | 77.7822 |  | 22823.5187
2017-09-10 | 6:42 |  |  |  |  | 77.6435 |  | 22782.8283
2017-09-10 | 6:44 |  |  |  |  | 77.4819 |  | 22735.3997
2017-09-10 | 6:45 | 1.8248 | 0 | 0 | 1.5 | 77.3975 | 0 | 22710.642
2017-09-10 | 6:46 |  |  |  |  | 77.3631 |  | 22700.5545
2017-09-10 | 6:48 |  |  |  |  | 77.3435 |  | 22694.781
2017-09-10 | 6:50 |  |  |  |  | 77.35 |  | 22696.7085
2017-09-10 | 6:52 |  |  |  |  | 77.3486 |  | 22696.2965
2017-09-10 | 6:54 |  |  |  |  | 77.3948 |  | 22709.8318
2017-09-10 | 6:56 |  |  |  |  | 77.4286 |  | 22719.7738
2017-09-10 | 6:58 |  |  |  |  | 77.3655 |  | 22701.2373
2017-09-10 | 7:00 | 1.7936 | 0 | 0 | 1.5 | 77.2511 | 0 | 22667.6884
2017-09-10 | 7:02 |  |  |  |  | 77.1919 |  | 22650.3163
2017-09-10 | 7:04 |  |  |  |  | 77.1368 |  | 22634.1507
2017-09-10 | 7:06 |  |  |  |  | 77.105 |  | 22624.8021
2017-09-10 | 7:08 |  |  |  |  | 77.1908 |  | 22649.9985
2017-09-10 | 7:10 |  |  |  |  | 77.158 |  | 22640.3564
2017-09-10 | 7:12 |  |  |  |  | 77.0064 |  | 22595.8894
2017-09-10 | 7:14 |  |  |  |  | 76.8828 |  | 22559.6049
2017-09-10 | 7:15 | 1.7897 | 0 | 0 | 1.5 | 76.8555 | 0 | 22551.5905
2017-09-10 | 7:16 |  |  |  |  | 76.7659 |  | 22525.2972
2017-09-10 | 7:18 |  |  |  |  | 76.6488 |  | 22490.9467
2017-09-10 | 7:20 |  |  |  |  | 76.4543 |  | 22433.8649
2017-09-10 | 7:22 |  |  |  |  | 76.4603 |  | 22435.6266
2017-09-10 | 7:24 |  |  |  |  | 76.4437 |  | 22430.7531
2017-09-10 | 7:26 |  |  |  |  | 76.4325 |  | 22427.4711
2017-09-10 | 7:28 |  |  |  |  | 76.4608 |  | 22435.7901
2017-09-10 | 7:30 | 1.7132 | 0 | 0 | 1.5 | 76.4952 | 0 | 22445.882
2017-09-10 | 7:32 |  |  |  |  | 76.4267 |  | 22425.7786
2017-09-10 | 7:34 |  |  |  |  | 76.3365 |  | 22399.3151
2017-09-10 | 7:36 |  |  |  |  | 76.2359 |  | 22369.7824
2017-09-10 | 7:38 |  |  |  |  | 76.1674 |  | 22349.6858
2017-09-10 | 7:40 |  |  |  |  | 76.1316 |  | 22339.1998
2017-09-10 | 7:42 |  |  |  |  | 76.1412 |  | 22341.9983
2017-09-10 | 7:44 |  |  |  |  | 76.1976 |  | 22358.5532
2017-09-10 | 7:45 | 1.7195 | 0 | 0 | 1.5 | 76.2284 | 0 | 22367.6043
2017-09-10 | 7:46 |  |  |  |  | 76.2277 |  | 22367.3916
2017-09-10 | 7:48 |  |  |  |  | 76.3055 |  | 22390.2218
2017-09-10 | 7:50 |  |  |  |  | 76.445 |  | 22431.1424
2017-09-10 | 7:52 |  |  |  |  | 76.4363 |  | 22428.5928
2017-09-10 | 7:54 |  |  |  |  | 76.4404 |  | 22429.8062
2017-09-10 | 7:56 |  |  |  |  | 76.4266 |  | 22425.734
2017-09-10 | 7:58 |  |  |  |  | 76.458 |  | 22434.9597
2017-09-10 | 8:00 | 1.7522 | 0 | 0 | 1.5 | 76.4402 | 0 | 22429.7501
2017-09-10 | 8:02 |  |  |  |  | 76.5529 |  | 22462.8066
2017-09-10 | 8:04 |  |  |  |  | 76.6361 |  | 22487.226
2017-09-10 | 8:06 |  |  |  |  | 76.6659 |  | 22495.9749
2017-09-10 | 8:08 |  |  |  |  | 76.6395 |  | 22488.2222
2017-09-10 | 8:10 |  |  |  |  | 76.5897 |  | 22473.5948
2017-09-10 | 8:12 |  |  |  |  | 76.5466 |  | 22460.9686
2017-09-10 | 8:14 |  |  |  |  | 76.5445 |  | 22460.3462
2017-09-10 | 8:15 | 1.7577 | 0 | 0 | 1.5 | 76.5533 | 0 | 22462.9252
2017-09-10 | 8:16 |  |  |  |  | 76.6156 |  | 22481.2175
2017-09-10 | 8:18 |  |  |  |  | 76.738 |  | 22517.1079
2017-09-10 | 8:20 |  |  |  |  | 76.8563 |  | 22551.8343
2017-09-10 | 8:22 |  |  |  |  | 76.9602 |  | 22582.3342
2017-09-10 | 8:24 |  |  |  |  | 77.0728 |  | 22615.3549
2017-09-10 | 8:26 |  |  |  |  | 77.1371 |  | 22634.2223
2017-09-10 | 8:28 |  |  |  |  | 77.1037 |  | 22624.4236
2017-09-10 | 8:30 | 1.7608 | 0 | 0 | 1.5 | 77.0307 | 0 | 22602.9951
2017-09-10 | 8:32 |  |  |  |  | 77.0389 |  | 22605.4241
2017-09-10 | 8:34 |  |  |  |  | 76.9928 |  | 22591.8776
2017-09-10 | 8:36 |  |  |  |  | 77.0457 |  | 22607.3962
2017-09-10 | 8:38 |  |  |  |  | 77.1238 |  | 22630.3226
2017-09-10 | 8:40 |  |  |  |  | 77.2696 |  | 22673.1127
2017-09-10 | 8:42 |  |  |  |  | 77.3056 |  | 22683.6659
2017-09-10 | 8:44 |  |  |  |  | 77.3131 |  | 22685.8643
2017-09-10 | 8:45 | 1.7546 | 0 | 0 | 1.5 | 77.2806 | 0 | 22676.3431
2017-09-10 | 8:46 |  |  |  |  | 77.2859 |  | 22677.9012
2017-09-10 | 8:48 |  |  |  |  | 77.2633 |  | 22671.2504
2017-09-10 | 8:50 |  |  |  |  | 77.2624 |  | 22670.9907
2017-09-10 | 8:52 |  |  |  |  | 77.2856 |  | 22677.8141
2017-09-10 | 8:54 |  |  |  |  | 77.3993 |  | 22711.1772
2017-09-10 | 8:56 |  |  |  |  | 77.4908 |  | 22738.0233
2017-09-10 | 8:58 |  |  |  |  | 77.4805 |  | 22734.9833
2017-09-10 | 9:00 | 1.7522 | 0 | 0 | 1.5 | 77.4717 | 0 | 22732.402
2017-09-10 | 9:02 |  |  |  |  | 77.4335 |  | 22721.211
2017-09-10 | 9:04 |  |  |  |  | 77.3957 |  | 22710.1158
2017-09-10 | 9:06 |  |  |  |  | 77.449 |  | 22725.76
2017-09-10 | 9:08 |  |  |  |  | 77.5429 |  | 22753.2936
2017-09-10 | 9:10 |  |  |  |  | 77.6447 |  | 22783.1843
2017-09-10 | 9:12 |  |  |  |  | 77.7166 |  | 22804.275
2017-09-10 | 9:14 |  |  |  |  | 77.6684 |  | 22790.1288
2017-09-10 | 9:15 | 1.7475 | 0 | 0 | 1.5 | 77.6924 | 0 | 22797.1606
2017-09-10 | 9:16 |  |  |  |  | 77.6868 |  | 22795.5262
2017-09-10 | 9:18 |  |  |  |  | 77.6981 |  | 22798.8372
2017-09-10 | 9:20 |  |  |  |  | 77.6613 |  | 22788.0446
2017-09-10 | 9:22 |  |  |  |  | 77.7407 |  | 22811.3469
2017-09-10 | 9:24 |  |  |  |  | 77.7983 |  | 22828.2467
2017-09-10 | 9:26 |  |  |  |  | 77.8728 |  | 22850.1141
2017-09-10 | 9:28 |  |  |  |  | 77.8993 |  | 22857.8935
2017-09-10 | 9:30 | 1.753 | 0 | 0 | 1.5 | 77.8981 | 0 | 22857.5197
2017-09-10 | 9:32 |  |  |  |  | 77.8658 |  | 22848.0613
2017-09-10 | 9:34 |  |  |  |  | 77.8401 |  | 22840.4991
2017-09-10 | 9:36 |  |  |  |  | 77.7793 |  | 22822.6724
2017-09-10 | 9:38 |  |  |  |  | 77.7198 |  | 22805.2084
2017-09-10 | 9:40 |  |  |  |  | 77.6323 |  | 22779.5352
2017-09-10 | 9:42 |  |  |  |  | 77.7157 |  | 22804.0109
2017-09-10 | 9:44 |  |  |  |  | 77.7325 |  | 22808.9382
2017-09-10 | 9:45 | 1.7335 | 0 | 0 | 1.5 | 77.8236 | 0 | 22835.6546
2017-09-10 | 9:46 |  |  |  |  | 77.7911 |  | 22826.1334
2017-09-10 | 9:48 |  |  |  |  | 77.7317 |  | 22808.6964
2017-09-10 | 9:50 |  |  |  |  | 77.7644 |  | 22818.2868
2017-09-10 | 9:52 |  |  |  |  | 77.69 |  | 22796.4531
2017-09-10 | 9:54 |  |  |  |  | 77.6872 |  | 22795.6494
2017-09-10 | 9:56 |  |  |  |  | 77.595 |  | 22768.6014
2017-09-10 | 9:58 |  |  |  |  | 77.5751 |  | 22762.7496
2017-09-10 | 10:00 | 1.7725 | 0 | 0 | 1.5 | 77.5072 | 0 | 22742.8387
2017-09-10 | 10:02 |  |  |  |  | 77.5226 |  | 22747.3499
2017-09-10 | 10:04 |  |  |  |  | 77.6239 |  | 22777.0751
2017-09-10 | 10:06 |  |  |  |  | 77.7021 |  | 22800.0238
2017-09-10 | 10:08 |  |  |  |  | 77.6974 |  | 22798.6403
2017-09-10 | 10:10 |  |  |  |  | 77.7387 |  | 22810.7425
2017-09-10 | 10:12 |  |  |  |  | 77.7586 |  | 22816.5923
2017-09-10 | 10:14 |  |  |  |  | 77.7718 |  | 22820.4784
2017-09-10 | 10:15 | 1.746 | 0 | 0 | 1.5 | 77.7592 | 0 | 22816.7713
2017-09-10 | 10:16 |  |  |  |  | 77.7127 |  | 22803.1198
2017-09-10 | 10:18 |  |  |  |  | 77.7112 |  | 22802.6943
2017-09-10 | 10:20 |  |  |  |  | 77.682 |  | 22794.1045
2017-09-10 | 10:22 |  |  |  |  | 77.7723 |  | 22820.6061
2017-09-10 | 10:24 |  |  |  |  | 77.8528 |  | 22844.2241
2017-09-10 | 10:26 |  |  |  |  | 77.9706 |  | 22878.7874
2017-09-10 | 10:28 |  |  |  |  | 78.0043 |  | 22888.6888
2017-09-10 | 10:30 | 1.7507 | 0 | 0 | 1.5 | 78.0198 | 0 | 22893.2291
2017-09-10 | 10:32 |  |  |  |  | 78.0169 |  | 22892.3761
2017-09-10 | 10:34 |  |  |  |  | 77.9919 |  | 22885.0398
2017-09-10 | 10:36 |  |  |  |  | 78.0171 |  | 22892.4477
2017-09-10 | 10:38 |  |  |  |  | 77.9705 |  | 22878.7581
2017-09-10 | 10:40 |  |  |  |  | 77.9521 |  | 22873.3607
2017-09-10 | 10:42 |  |  |  |  | 77.9611 |  | 22876.0001
2017-09-10 | 10:44 |  |  |  |  | 77.9459 |  | 22871.5652
2017-09-10 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 77.9247 | 0 | 22865.3372
2017-09-10 | 10:46 |  |  |  |  | 77.8859 |  | 22853.949
2017-09-10 | 10:48 |  |  |  |  | 77.8831 |  | 22853.1162
2017-09-10 | 10:50 |  |  |  |  | 77.8465 |  | 22842.402
2017-09-10 | 10:52 |  |  |  |  | 77.7989 |  | 22828.4236
2017-09-10 | 10:54 |  |  |  |  | 77.7945 |  | 22827.1275
2017-09-10 | 10:56 |  |  |  |  | 77.8292 |  | 22837.3248
2017-09-10 | 10:58 |  |  |  |  | 77.9046 |  | 22859.4273
2017-09-10 | 11:00 | 1.7039 | 0 | 0 | 1.5 | 78.0179 | 0 | 22892.6806
2017-09-10 | 11:02 |  |  |  |  | 78.0391 |  | 22898.8952
2017-09-10 | 11:04 |  |  |  |  | 78.0869 |  | 22912.9384
2017-09-10 | 11:06 |  |  |  |  | 78.125 |  | 22924.1139
2017-09-10 | 11:08 |  |  |  |  | 78.1639 |  | 22935.5312
2017-09-10 | 11:10 |  |  |  |  | 78.1557 |  | 22933.1245
2017-09-10 | 11:12 |  |  |  |  | 78.1187 |  | 22922.2445
2017-09-10 | 11:14 |  |  |  |  | 78.1035 |  | 22917.7964
2017-09-10 | 11:15 | 1.7499 | 0 | 0 | 1.5 | 78.1478 | 0 | 22930.7829
2017-09-10 | 11:16 |  |  |  |  | 78.1341 |  | 22926.7867
2017-09-10 | 11:18 |  |  |  |  | 78.1179 |  | 22922.0094
2017-09-10 | 11:20 |  |  |  |  | 78.114 |  | 22920.8812
2017-09-10 | 11:22 |  |  |  |  | 78.1026 |  | 22917.5411
2017-09-10 | 11:24 |  |  |  |  | 78.1074 |  | 22918.929
2017-09-10 | 11:26 |  |  |  |  | 78.0318 |  | 22896.7661
2017-09-10 | 11:28 |  |  |  |  | 78.0005 |  | 22887.5853
2017-09-10 | 11:30 | 1.7522 | 0 | 0 | 1.5 | 77.9613 | 0 | 22876.0673
2017-09-10 | 11:32 |  |  |  |  | 77.9959 |  | 22886.222
2017-09-10 | 11:34 |  |  |  |  | 77.9688 |  | 22878.2613
2017-09-10 | 11:36 |  |  |  |  | 77.9456 |  | 22871.4622
2017-09-10 | 11:38 |  |  |  |  | 77.919 |  | 22863.6694
2017-09-10 | 11:40 |  |  |  |  | 77.9098 |  | 22860.9651
2017-09-10 | 11:42 |  |  |  |  | 77.9298 |  | 22866.8281
2017-09-10 | 11:44 |  |  |  |  | 77.9408 |  | 22870.0453
2017-09-10 | 11:45 | 1.7499 | 0 | 0 | 1.5 | 77.9119 | 0 | 22861.5831
2017-09-10 | 11:46 |  |  |  |  | 77.8969 |  | 22857.1682
2017-09-10 | 11:48 |  |  |  |  | 77.8756 |  | 22850.9357
2017-09-10 | 11:50 |  |  |  |  | 77.7686 |  | 22819.5204
2017-09-10 | 11:52 |  |  |  |  | 77.7923 |  | 22826.4738
2017-09-10 | 11:54 |  |  |  |  | 77.7885 |  | 22825.3813
2017-09-10 | 11:56 |  |  |  |  | 77.7789 |  | 22822.5559
2017-09-10 | 11:58 |  |  |  |  | 77.7958 |  | 22827.5058
2017-09-10 | 12:00 | 1.7405 | 0 | 0 | 1.5 | 77.7818 | 0 | 22823.3934
2017-09-10 | 12:02 |  |  |  |  | 77.7719 |  | 22820.4831
2017-09-10 | 12:04 |  |  |  |  | 77.7154 |  | 22803.9258
2017-09-10 | 12:06 |  |  |  |  | 77.6986 |  | 22798.9827
2017-09-10 | 12:08 |  |  |  |  | 77.7084 |  | 22801.8504
2017-09-10 | 12:10 |  |  |  |  | 77.7007 |  | 22799.5984
2017-09-10 | 12:12 |  |  |  |  | 77.6809 |  | 22793.809
2017-09-10 | 12:14 |  |  |  |  | 77.6781 |  | 22792.9807
2017-09-10 | 12:15 | 1.7577 | 0 | 0 | 1.5 | 77.6782 | 0 | 22793.0033
2017-09-10 | 12:16 |  |  |  |  | 77.6763 |  | 22792.4457
2017-09-10 | 12:18 |  |  |  |  | 77.6431 |  | 22782.7165
2017-09-10 | 12:20 |  |  |  |  | 77.5965 |  | 22769.0448
2017-09-10 | 12:22 |  |  |  |  | 77.587 |  | 22766.2443
2017-09-10 | 12:24 |  |  |  |  | 77.5721 |  | 22761.8676
2017-09-10 | 12:26 |  |  |  |  | 77.5095 |  | 22743.5104
2017-09-10 | 12:28 |  |  |  |  | 77.5092 |  | 22743.4141
2017-09-10 | 12:30 | 1.7538 | 0 | 0 | 1.5 | 77.5236 | 0 | 22747.6275
2017-09-10 | 12:32 |  |  |  |  | 77.5305 |  | 22749.6577
2017-09-10 | 12:34 |  |  |  |  | 77.5368 |  | 22751.5025
2017-09-10 | 12:36 |  |  |  |  | 77.4553 |  | 22727.5889
2017-09-10 | 12:38 |  |  |  |  | 77.4153 |  | 22715.8559
2017-09-10 | 12:40 |  |  |  |  | 77.3889 |  | 22708.1214
2017-09-10 | 12:42 |  |  |  |  | 77.3837 |  | 22706.5968
2017-09-10 | 12:44 |  |  |  |  | 77.3805 |  | 22705.6499
2017-09-10 | 12:45 | 1.7351 | 0 | 0 | 1.5 | 77.3915 | 0 | 22708.8914
2017-09-10 | 12:46 |  |  |  |  | 77.3633 |  | 22700.6149
2017-09-10 | 12:48 |  |  |  |  | 77.2959 |  | 22680.8161
2017-09-10 | 12:50 |  |  |  |  | 77.3065 |  | 22683.9458
2017-09-10 | 12:52 |  |  |  |  | 77.3279 |  | 22690.2164
2017-09-10 | 12:54 |  |  |  |  | 77.3048 |  | 22683.4464
2017-09-10 | 12:56 |  |  |  |  | 77.3122 |  | 22685.609
2017-09-10 | 12:58 |  |  |  |  | 77.2682 |  | 22672.6896
2017-09-10 | 13:00 | 1.7631 | 0 | 0 | 1.5 | 77.243 | 0 | 22665.3155
2017-09-10 | 13:02 |  |  |  |  | 77.2264 |  | 22660.4284
2017-09-10 | 13:04 |  |  |  |  | 77.2132 |  | 22656.5733
2017-09-10 | 13:06 |  |  |  |  | 77.203 |  | 22653.5557
2017-09-10 | 13:08 |  |  |  |  | 77.2055 |  | 22654.3125
2017-09-10 | 13:10 |  |  |  |  | 77.179 |  | 22646.5173
2017-09-10 | 13:12 |  |  |  |  | 77.1537 |  | 22639.1141
2017-09-10 | 13:14 |  |  |  |  | 77.1711 |  | 22644.2203
2017-09-10 | 13:15 | 1.7491 | 0 | 0 | 1.5 | 77.1795 | 0 | 22646.6672
2017-09-10 | 13:16 |  |  |  |  | 77.1842 |  | 22648.0598
2017-09-10 | 13:18 |  |  |  |  | 77.172 |  | 22644.4712
2017-09-10 | 13:20 |  |  |  |  | 77.1462 |  | 22636.8954
2017-09-10 | 13:22 |  |  |  |  | 77.1506 |  | 22638.176
2017-09-10 | 13:24 |  |  |  |  | 77.1114 |  | 22626.6982
2017-09-10 | 13:26 |  |  |  |  | 77.1344 |  | 22633.4433
2017-09-10 | 13:28 |  |  |  |  | 77.0953 |  | 22621.9746
2017-09-10 | 13:30 | 1.7592 | 0 | 0 | 1.5 | 77.0754 | 0 | 22616.1248
2017-09-10 | 13:32 |  |  |  |  | 77.0712 |  | 22614.8801
2017-09-10 | 13:34 |  |  |  |  | 77.0481 |  | 22608.106
2017-09-10 | 13:36 |  |  |  |  | 77.0507 |  | 22608.8806
2017-09-10 | 13:38 |  |  |  |  | 77.0716 |  | 22615.0121
2017-09-10 | 13:40 |  |  |  |  | 77.0568 |  | 22610.6535
2017-09-10 | 13:42 |  |  |  |  | 77.0532 |  | 22609.6171
2017-09-10 | 13:44 |  |  |  |  | 77.0367 |  | 22604.7547
2017-09-10 | 13:45 | 1.7569 | 0 | 0 | 1.5 | 77.0527 | 0 | 22609.476
2017-09-10 | 13:46 |  |  |  |  | 77.0326 |  | 22603.5526
2017-09-10 | 13:48 |  |  |  |  | 77.0188 |  | 22599.5182
2017-09-10 | 13:50 |  |  |  |  | 77.0075 |  | 22596.2028
2017-09-10 | 13:52 |  |  |  |  | 77.0064 |  | 22595.8738
2017-09-10 | 13:54 |  |  |  |  | 77.0326 |  | 22603.5593
2017-09-10 | 13:56 |  |  |  |  | 77.0386 |  | 22605.3322
2017-09-10 | 13:58 |  |  |  |  | 77.0607 |  | 22611.8088
2017-09-10 | 14:00 | 1.7304 | 0 | 0 | 1.5 | 77.054 | 0 | 22609.8363
2017-09-10 | 14:02 |  |  |  |  | 77.0686 |  | 22614.1189
2017-09-10 | 14:04 |  |  |  |  | 77.0579 |  | 22610.9828
2017-09-10 | 14:06 |  |  |  |  | 77.05 |  | 22608.6656
2017-09-10 | 14:08 |  |  |  |  | 77.0892 |  | 22620.1835
2017-09-10 | 14:10 |  |  |  |  | 77.0682 |  | 22614.0159
2017-09-10 | 14:12 |  |  |  |  | 77.0774 |  | 22616.7249
2017-09-10 | 14:14 |  |  |  |  | 77.0784 |  | 22616.9913
2017-09-10 | 14:15 | 1.753 | 0 | 0 | 1.5 | 77.0666 | 0 | 22613.5438
2017-09-10 | 14:16 |  |  |  |  | 77.062 |  | 22612.1802
2017-09-10 | 14:18 |  |  |  |  | 77.0739 |  | 22615.6905
2017-09-10 | 14:20 |  |  |  |  | 77.0875 |  | 22619.6688
2017-09-10 | 14:22 |  |  |  |  | 77.084 |  | 22618.6568
2017-09-10 | 14:24 |  |  |  |  | 77.069 |  | 22614.2445
2017-09-10 | 14:26 |  |  |  |  | 77.0961 |  | 22622.1961
2017-09-10 | 14:28 |  |  |  |  | 77.041 |  | 22606.0238
2017-09-10 | 14:30 | 1.7647 | 0 | 0 | 1.5 | 77.0016 | 0 | 22594.4836
2017-09-10 | 14:32 |  |  |  |  | 76.9996 |  | 22593.8903
2017-09-10 | 14:34 |  |  |  |  | 77.0477 |  | 22607.9872
2017-09-10 | 14:36 |  |  |  |  | 76.9976 |  | 22593.2881
2017-09-10 | 14:38 |  |  |  |  | 76.9784 |  | 22587.669
2017-09-10 | 14:40 |  |  |  |  | 76.9524 |  | 22580.044
2017-09-10 | 14:42 |  |  |  |  | 76.9189 |  | 22570.1894
2017-09-10 | 14:44 |  |  |  |  | 76.8787 |  | 22558.4183
2017-09-10 | 14:45 | 1.7491 | 0 | 0 | 1.5 | 76.8689 | 0 | 22555.535
2017-09-10 | 14:46 |  |  |  |  | 76.8384 |  | 22546.5913
2017-09-10 | 14:48 |  |  |  |  | 76.8763 |  | 22557.7111
2017-09-10 | 14:50 |  |  |  |  | 76.9218 |  | 22571.0512
2017-09-10 | 14:52 |  |  |  |  | 76.9497 |  | 22579.2449
2017-09-10 | 14:54 |  |  |  |  | 76.9385 |  | 22575.9606
2017-09-10 | 14:56 |  |  |  |  | 76.9748 |  | 22586.6168
2017-09-10 | 14:58 |  |  |  |  | 76.9761 |  | 22586.9862
2017-09-10 | 15:00 | 1.7616 | 0 | 0 | 1.5 | 76.9575 | 0 | 22581.517
2017-09-10 | 15:02 |  |  |  |  | 76.9753 |  | 22586.7646
2017-09-10 | 15:04 |  |  |  |  | 76.9779 |  | 22587.5055
2017-09-10 | 15:06 |  |  |  |  | 76.9518 |  | 22579.8471
2017-09-10 | 15:08 |  |  |  |  | 76.9416 |  | 22576.872
2017-09-10 | 15:10 |  |  |  |  | 77.0103 |  | 22597.0311
2017-09-10 | 15:12 |  |  |  |  | 76.9767 |  | 22587.1496
2017-09-10 | 15:14 |  |  |  |  | 76.9944 |  | 22592.3545
2017-09-10 | 15:15 | 1.7631 | 0 | 0 | 1.5 | 76.9464 | 0 | 22578.2711
2017-09-10 | 15:16 |  |  |  |  | 76.9306 |  | 22573.6234
2017-09-10 | 15:18 |  |  |  |  | 76.9158 |  | 22569.3074
2017-09-10 | 15:20 |  |  |  |  | 76.8709 |  | 22556.1169
2017-09-10 | 15:22 |  |  |  |  | 76.8642 |  | 22554.1448
2017-09-10 | 15:24 |  |  |  |  | 76.8053 |  | 22536.8621
2017-09-10 | 15:26 |  |  |  |  | 76.7238 |  | 22512.9486
2017-09-10 | 15:28 |  |  |  |  | 76.6721 |  | 22497.7883
2017-09-10 | 15:30 | 1.7585 | 0 | 0 | 1.5 | 76.6299 | 0 | 22485.388
2017-09-10 | 15:32 |  |  |  |  | 76.5761 |  | 22469.6165
2017-09-10 | 15:34 |  |  |  |  | 76.547 |  | 22461.0648
2017-09-10 | 15:36 |  |  |  |  | 76.5147 |  | 22451.5906
2017-09-10 | 15:38 |  |  |  |  | 76.4458 |  | 22431.3754
2017-09-10 | 15:40 |  |  |  |  | 76.4334 |  | 22427.7287
2017-09-10 | 15:42 |  |  |  |  | 76.4142 |  | 22422.0984
2017-09-10 | 15:44 |  |  |  |  | 76.4164 |  | 22422.7475
2017-09-10 | 15:45 | 1.7468 | 0 | 0 | 1.5 | 76.4528 | 0 | 22433.4283
2017-09-10 | 15:46 |  |  |  |  | 76.4847 |  | 22442.8062
2017-09-10 | 15:48 |  |  |  |  | 76.5262 |  | 22454.9756
2017-09-10 | 15:50 |  |  |  |  | 76.5374 |  | 22458.2485
2017-09-10 | 15:52 |  |  |  |  | 76.5772 |  | 22469.941
2017-09-10 | 15:54 |  |  |  |  | 76.5669 |  | 22466.919
2017-09-10 | 15:56 |  |  |  |  | 76.5355 |  | 22457.7136
2017-09-10 | 15:58 |  |  |  |  | 76.5357 |  | 22457.7605
2017-09-10 | 16:00 | 1.7569 | 0 | 0 | 1.5 | 76.5462 | 0 | 22460.8521
2017-09-10 | 16:02 |  |  |  |  | 76.5599 |  | 22464.8706
2017-09-10 | 16:04 |  |  |  |  | 76.5682 |  | 22467.304
2017-09-10 | 16:06 |  |  |  |  | 76.5762 |  | 22469.6591
2017-09-10 | 16:08 |  |  |  |  | 76.6125 |  | 22480.2997
2017-09-10 | 16:10 |  |  |  |  | 76.6169 |  | 22481.5734
2017-09-10 | 16:12 |  |  |  |  | 76.6168 |  | 22481.5643
2017-09-10 | 16:14 |  |  |  |  | 76.6071 |  | 22478.699
2017-09-10 | 16:15 | 1.76 | 0 | 0 | 1.5 | 76.5901 | 0 | 22473.709
2017-09-10 | 16:16 |  |  |  |  | 76.5979 |  | 22476.008
2017-09-10 | 16:18 |  |  |  |  | 76.5815 |  | 22471.2037
2017-09-10 | 16:20 |  |  |  |  | 76.5664 |  | 22466.7556
2017-09-10 | 16:22 |  |  |  |  | 76.5017 |  | 22447.7804
2017-09-10 | 16:24 |  |  |  |  | 76.4862 |  | 22443.2426
2017-09-10 | 16:26 |  |  |  |  | 76.5123 |  | 22450.8831
2017-09-10 | 16:28 |  |  |  |  | 76.5013 |  | 22447.6639
2017-09-10 | 16:30 | 1.7592 | 0 | 0 | 1.5 | 76.441 | 0 | 22429.9764
2017-09-10 | 16:32 |  |  |  |  | 76.4484 |  | 22432.1501
2017-09-10 | 16:34 |  |  |  |  | 76.446 |  | 22431.4359
2017-09-10 | 16:36 |  |  |  |  | 76.4506 |  | 22432.7836
2017-09-10 | 16:38 |  |  |  |  | 76.4718 |  | 22439.0116
2017-09-10 | 16:40 |  |  |  |  | 76.4812 |  | 22441.7719
2017-09-10 | 16:42 |  |  |  |  | 76.4725 |  | 22439.2153
2017-09-10 | 16:44 |  |  |  |  | 76.4172 |  | 22422.9892
2017-09-10 | 16:45 | 1.753 | 0 | 0 | 1.5 | 76.4121 | 0 | 22421.4872
2017-09-10 | 16:46 |  |  |  |  | 76.3689 |  | 22408.8096
2017-09-10 | 16:48 |  |  |  |  | 76.3362 |  | 22399.2189
2017-09-10 | 16:50 |  |  |  |  | 76.3041 |  | 22389.7943
2017-09-10 | 16:52 |  |  |  |  | 76.2565 |  | 22375.8271
2017-09-10 | 16:54 |  |  |  |  | 76.1724 |  | 22351.1635
2017-09-10 | 16:56 |  |  |  |  | 76.2157 |  | 22363.8657
2017-09-10 | 16:58 |  |  |  |  | 76.3386 |  | 22399.9175
2017-09-10 | 17:00 | 1.7117 | 0 | 0 | 1.5 | 76.4688 | 0 | 22438.1431
2017-09-10 | 17:02 |  |  |  |  | 76.5368 |  | 22458.0962
2017-09-10 | 17:04 |  |  |  |  | 76.5713 |  | 22468.2195
2017-09-10 | 17:06 |  |  |  |  | 76.5776 |  | 22470.0531
2017-09-10 | 17:08 |  |  |  |  | 76.5837 |  | 22471.8507
2017-09-10 | 17:10 |  |  |  |  | 76.5748 |  | 22469.2315
2017-09-10 | 17:12 |  |  |  |  | 76.5468 |  | 22461.0246
2017-09-10 | 17:14 |  |  |  |  | 76.563 |  | 22465.7861
2017-09-10 | 17:15 | 1.7538 | 0 | 0 | 1.5 | 76.5479 | 0 | 22461.3333
2017-09-10 | 17:16 |  |  |  |  | 76.5059 |  | 22449.0073
2017-09-10 | 17:18 |  |  |  |  | 76.4304 |  | 22426.8534
2017-09-10 | 17:20 |  |  |  |  | 76.3932 |  | 22415.9376
2017-09-10 | 17:22 |  |  |  |  | 76.3345 |  | 22398.7198
2017-09-10 | 17:24 |  |  |  |  | 76.3096 |  | 22391.4061
2017-09-10 | 17:26 |  |  |  |  | 76.2794 |  | 22382.5653
2017-09-10 | 17:28 |  |  |  |  | 76.2702 |  | 22379.8544
2017-09-10 | 17:30 | 1.7546 | 0 | 0 | 1.5 | 76.2371 | 0 | 22370.1519
2017-09-10 | 17:32 |  |  |  |  | 76.2396 |  | 22370.884
2017-09-10 | 17:34 |  |  |  |  | 76.1761 |  | 22352.2468
2017-09-10 | 17:36 |  |  |  |  | 76.1731 |  | 22351.3715
2017-09-10 | 17:38 |  |  |  |  | 76.2672 |  | 22378.9835
2017-09-10 | 17:40 |  |  |  |  | 76.3716 |  | 22409.5954
2017-09-10 | 17:42 |  |  |  |  | 76.3289 |  | 22397.0675
2017-09-10 | 17:44 |  |  |  |  | 76.3376 |  | 22399.6332
2017-09-10 | 17:45 | 1.7624 | 0 | 0 | 1.5 | 76.3186 | 0 | 22394.0475
2017-09-10 | 17:46 |  |  |  |  | 76.3163 |  | 22393.3917
2017-09-10 | 17:48 |  |  |  |  | 76.3123 |  | 22392.203
2017-09-10 | 17:50 |  |  |  |  | 76.2747 |  | 22381.1886
2017-09-10 | 17:52 |  |  |  |  | 76.1758 |  | 22352.1462
2017-09-10 | 17:54 |  |  |  |  | 76.0556 |  | 22316.8846
2017-09-10 | 17:56 |  |  |  |  | 76.0638 |  | 22319.2869
2017-09-10 | 17:58 |  |  |  |  | 76.1645 |  | 22348.8351
2017-09-10 | 18:00 | 1.7132 | 0 | 0 | 1.5 | 76.2001 | 0 | 22359.2921
2017-09-10 | 18:02 |  |  |  |  | 76.2361 |  | 22369.8429
2017-09-10 | 18:04 |  |  |  |  | 76.179 |  | 22353.1066
2017-09-10 | 18:06 |  |  |  |  | 76.1259 |  | 22337.5208
2017-09-10 | 18:08 |  |  |  |  | 76.0467 |  | 22314.2654
2017-09-10 | 18:10 |  |  |  |  | 75.8978 |  | 22270.5707
2017-09-10 | 18:12 |  |  |  |  | 75.7775 |  | 22235.2736
2017-09-10 | 18:14 |  |  |  |  | 75.6839 |  | 22207.8116
2017-09-10 | 18:15 | 1.7686 | 0 | 0 | 1.5 | 75.6568 | 0 | 22199.8597
2017-09-10 | 18:16 |  |  |  |  | 75.62 |  | 22189.0583
2017-09-10 | 18:18 |  |  |  |  | 75.7211 |  | 22218.7363
2017-09-10 | 18:20 |  |  |  |  | 75.7988 |  | 22241.5263
2017-09-10 | 18:22 |  |  |  |  | 75.7407 |  | 22224.4763
2017-09-10 | 18:24 |  |  |  |  | 75.7438 |  | 22225.4053
2017-09-10 | 18:26 |  |  |  |  | 75.7103 |  | 22215.5596
2017-09-10 | 18:28 |  |  |  |  | 75.6986 |  | 22212.1233
2017-09-10 | 18:30 | 1.7873 | 0 | 0 | 1.5 | 75.6512 | 0 | 22198.2344
2017-09-10 | 18:32 |  |  |  |  | 75.6154 |  | 22187.7082
2017-09-10 | 18:34 |  |  |  |  | 75.6194 |  | 22188.8837
2017-09-10 | 18:36 |  |  |  |  | 75.6787 |  | 22206.2961
2017-09-10 | 18:38 |  |  |  |  | 75.7592 |  | 22229.9209
2017-09-10 | 18:40 |  |  |  |  | 75.8562 |  | 22258.3834
2017-09-10 | 18:42 |  |  |  |  | 75.7719 |  | 22233.6483
2017-09-10 | 18:44 |  |  |  |  | 75.7052 |  | 22214.071
2017-09-10 | 18:45 | 1.7858 | 0 | 0 | 1.5 | 75.6722 | 0 | 22204.3976
2017-09-10 | 18:46 |  |  |  |  | 75.6632 |  | 22201.7315
2017-09-10 | 18:48 |  |  |  |  | 75.635 |  | 22193.4618
2017-09-10 | 18:50 |  |  |  |  | 75.5668 |  | 22173.4456
2017-09-10 | 18:52 |  |  |  |  | 75.6457 |  | 22196.6205
2017-09-10 | 18:54 |  |  |  |  | 75.7874 |  | 22238.1973
2017-09-10 | 18:56 |  |  |  |  | 75.8599 |  | 22259.4759
2017-09-10 | 18:58 |  |  |  |  | 75.8637 |  | 22260.5707
2017-09-10 | 19:00 | 1.7678 | 0 | 0 | 1.5 | 75.8293 | 0 | 22250.492
2017-09-10 | 19:02 |  |  |  |  | 75.8285 |  | 22250.2569
2017-09-10 | 19:04 |  |  |  |  | 75.8096 |  | 22244.6962
2017-09-10 | 19:06 |  |  |  |  | 75.8146 |  | 22246.1668
2017-09-10 | 19:08 |  |  |  |  | 75.9005 |  | 22271.3768
2017-09-10 | 19:10 |  |  |  |  | 76.0489 |  | 22314.926
2017-09-10 | 19:12 |  |  |  |  | 75.9574 |  | 22288.0705
2017-09-10 | 19:14 |  |  |  |  | 75.8864 |  | 22267.2465
2017-09-10 | 19:15 | 1.7702 | 0 | 0 | 1.5 | 75.8728 | 0 | 22263.2391
2017-09-10 | 19:16 |  |  |  |  | 75.842 |  | 22254.215
2017-09-10 | 19:18 |  |  |  |  | 75.771 |  | 22233.3684
2017-09-10 | 19:20 |  |  |  |  | 75.7229 |  | 22219.2536
2017-09-10 | 19:22 |  |  |  |  | 75.7739 |  | 22234.2146
2017-09-10 | 19:24 |  |  |  |  | 75.8791 |  | 22265.0883
2017-09-10 | 19:26 |  |  |  |  | 75.9583 |  | 22288.3214
2017-09-10 | 19:28 |  |  |  |  | 75.87 |  | 22262.4354
2017-09-10 | 19:30 | 1.7592 | 0 | 0 | 1.5 | 75.849 | 0 | 22256.2702
2017-09-10 | 19:32 |  |  |  |  | 75.7967 |  | 22240.9174
2017-09-10 | 19:34 |  |  |  |  | 75.7286 |  | 22220.9481
2017-09-10 | 19:36 |  |  |  |  | 75.718 |  | 22217.8275
2017-09-10 | 19:38 |  |  |  |  | 75.7696 |  | 22232.952
2017-09-10 | 19:40 |  |  |  |  | 75.8649 |  | 22260.9377
2017-09-10 | 19:42 |  |  |  |  | 75.7858 |  | 22237.707
2017-09-10 | 19:44 |  |  |  |  | 75.6974 |  | 22211.7808
2017-09-10 | 19:45 | 1.7678 | 0 | 0 | 1.5 | 75.6568 | 0 | 22199.8553
2017-09-10 | 19:46 |  |  |  |  | 75.613 |  | 22187.0254
2017-09-10 | 19:48 |  |  |  |  | 75.5604 |  | 22171.5697
2017-09-10 | 19:50 |  |  |  |  | 75.503 |  | 22154.7415
2017-09-10 | 19:52 |  |  |  |  | 75.663 |  | 22201.6889
2017-09-10 | 19:54 |  |  |  |  | 75.7499 |  | 22227.1852
2017-09-10 | 19:56 |  |  |  |  | 75.8515 |  | 22256.9955
2017-09-10 | 19:58 |  |  |  |  | 75.7517 |  | 22227.7067
2017-09-10 | 20:00 | 1.7585 | 0 | 0 | 1.5 | 75.7226 | 0 | 22219.182
2017-09-10 | 20:02 |  |  |  |  | 75.6803 |  | 22206.7526
2017-09-10 | 20:04 |  |  |  |  | 75.6379 |  | 22194.3101
2017-09-10 | 20:06 |  |  |  |  | 75.6858 |  | 22208.3891
2017-09-10 | 20:08 |  |  |  |  | 75.7958 |  | 22240.6642
2017-09-10 | 20:10 |  |  |  |  | 75.9477 |  | 22285.2275
2017-09-10 | 20:12 |  |  |  |  | 75.9229 |  | 22277.954
2017-09-10 | 20:14 |  |  |  |  | 75.8795 |  | 22265.2115
2017-09-10 | 20:15 | 1.7725 | 0 | 0 | 1.5 | 75.8711 | 0 | 22262.7555
2017-09-10 | 20:16 |  |  |  |  | 75.861 |  | 22259.7714
2017-09-10 | 20:18 |  |  |  |  | 75.818 |  | 22247.1765
2017-09-10 | 20:20 |  |  |  |  | 75.7681 |  | 22232.5268
2017-09-10 | 20:22 |  |  |  |  | 75.8536 |  | 22257.6
2017-09-10 | 20:24 |  |  |  |  | 76.0036 |  | 22301.6257
2017-09-10 | 20:26 |  |  |  |  | 76.1051 |  | 22331.3982
2017-09-10 | 20:28 |  |  |  |  | 76.0046 |  | 22301.9326
2017-09-10 | 20:30 | 1.7647 | 0 | 0 | 1.5 | 75.9568 | 0 | 22287.905
2017-09-10 | 20:32 |  |  |  |  | 75.8908 |  | 22268.5358
2017-09-10 | 20:34 |  |  |  |  | 75.8358 |  | 22252.3837
2017-09-10 | 20:36 |  |  |  |  | 75.8716 |  | 22262.8876
2017-09-10 | 20:38 |  |  |  |  | 75.9456 |  | 22284.6074
2017-09-10 | 20:40 |  |  |  |  | 76.0635 |  | 22319.195
2017-09-10 | 20:42 |  |  |  |  | 76.0024 |  | 22301.2877
2017-09-10 | 20:44 |  |  |  |  | 75.939 |  | 22282.6708
2017-09-10 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 75.9374 | 0 | 22282.1896
2017-09-10 | 20:46 |  |  |  |  | 75.9075 |  | 22273.4407
2017-09-10 | 20:48 |  |  |  |  | 75.8212 |  | 22248.1146
2017-09-10 | 20:50 |  |  |  |  | 75.7614 |  | 22230.5544
2017-09-10 | 20:52 |  |  |  |  | 75.8623 |  | 22260.1543
2017-09-10 | 20:54 |  |  |  |  | 75.9151 |  | 22275.6505
2017-09-10 | 20:56 |  |  |  |  | 76.0209 |  | 22306.7009
2017-09-10 | 20:58 |  |  |  |  | 75.921 |  | 22277.39
2017-09-10 | 21:00 | 1.7694 | 0 | 0 | 1.5 | 75.8909 | 0 | 22268.5651
2017-09-10 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-10 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-10 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 5:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-11 | 5:04 |  |  |  |  | 98.8063 |  | 28992.5929
2017-09-11 | 5:06 |  |  |  |  | 96.1049 |  | 28199.9091
2017-09-11 | 5:08 |  |  |  |  | 93.464 |  | 27425.0027
2017-09-11 | 5:10 |  |  |  |  | 91.2811 |  | 26784.4866
2017-09-11 | 5:12 |  |  |  |  | 89.3231 |  | 26209.9443
2017-09-11 | 5:14 |  |  |  |  | 87.6622 |  | 25722.59
2017-09-11 | 5:15 | 2.2514 | 0 | 0 | 1.5 | 86.9232 | 0 | 25505.7378
2017-09-11 | 5:16 |  |  |  |  | 86.241 |  | 25305.586
2017-09-11 | 5:18 |  |  |  |  | 85.0113 |  | 24944.7373
2017-09-11 | 5:20 |  |  |  |  | 83.9769 |  | 24641.2347
2017-09-11 | 5:22 |  |  |  |  | 83.0977 |  | 24383.2288
2017-09-11 | 5:24 |  |  |  |  | 82.409 |  | 24181.1496
2017-09-11 | 5:26 |  |  |  |  | 81.7457 |  | 23986.5207
2017-09-11 | 5:28 |  |  |  |  | 81.0661 |  | 23787.1126
2017-09-11 | 5:30 | 1.9441 | 0 | 0 | 1.5 | 80.4804 | 0 | 23615.2532
2017-09-11 | 5:32 |  |  |  |  | 80.1068 |  | 23505.616
2017-09-11 | 5:34 |  |  |  |  | 79.7648 |  | 23405.276
2017-09-11 | 5:36 |  |  |  |  | 79.5117 |  | 23330.9922
2017-09-11 | 5:38 |  |  |  |  | 79.1156 |  | 23214.7731
2017-09-11 | 5:40 |  |  |  |  | 78.7844 |  | 23117.5942
2017-09-11 | 5:42 |  |  |  |  | 78.6079 |  | 23065.7932
2017-09-11 | 5:44 |  |  |  |  | 78.524 |  | 23041.1881
2017-09-11 | 5:45 | 1.778 | 0 | 0 | 1.5 | 78.4881 | 0 | 23030.637
2017-09-11 | 5:46 |  |  |  |  | 78.4807 |  | 23028.47
2017-09-11 | 5:48 |  |  |  |  | 78.4352 |  | 23015.1184
2017-09-11 | 5:50 |  |  |  |  | 78.4189 |  | 23010.3411
2017-09-11 | 5:52 |  |  |  |  | 78.4123 |  | 23008.4227
2017-09-11 | 5:54 |  |  |  |  | 78.4678 |  | 23024.6933
2017-09-11 | 5:56 |  |  |  |  | 78.5411 |  | 23046.216
2017-09-11 | 5:58 |  |  |  |  | 78.5566 |  | 23050.7427
2017-09-11 | 6:00 | 1.7351 | 0 | 0 | 1.5 | 78.6395 | 0 | 23075.0726
2017-09-11 | 6:02 |  |  |  |  | 78.7249 |  | 23100.1279
2017-09-11 | 6:04 |  |  |  |  | 78.7983 |  | 23121.6708
2017-09-11 | 6:06 |  |  |  |  | 78.8746 |  | 23144.0688
2017-09-11 | 6:08 |  |  |  |  | 78.9516 |  | 23166.6593
2017-09-11 | 6:10 |  |  |  |  | 79.0229 |  | 23187.5755
2017-09-11 | 6:12 |  |  |  |  | 79.0794 |  | 23204.1595
2017-09-11 | 6:14 |  |  |  |  | 79.1878 |  | 23235.9645
2017-09-11 | 6:15 | 1.7109 | 0 | 0 | 1.5 | 79.2087 | 0 | 23242.1074
2017-09-11 | 6:16 |  |  |  |  | 79.2623 |  | 23257.8164
2017-09-11 | 6:18 |  |  |  |  | 79.3397 |  | 23280.5301
2017-09-11 | 6:20 |  |  |  |  | 79.4158 |  | 23302.8653
2017-09-11 | 6:22 |  |  |  |  | 79.4763 |  | 23320.6225
2017-09-11 | 6:24 |  |  |  |  | 79.5512 |  | 23342.6088
2017-09-11 | 6:26 |  |  |  |  | 79.5913 |  | 23354.3729
2017-09-11 | 6:28 |  |  |  |  | 79.6077 |  | 23359.186
2017-09-11 | 6:30 | 1.7397 | 0 | 0 | 1.5 | 79.674 | 0 | 23378.6201
2017-09-11 | 6:32 |  |  |  |  | 79.7386 |  | 23397.5706
2017-09-11 | 6:34 |  |  |  |  | 79.741 |  | 23398.3003
2017-09-11 | 6:36 |  |  |  |  | 79.813 |  | 23419.409
2017-09-11 | 6:38 |  |  |  |  | 79.8087 |  | 23418.1552
2017-09-11 | 6:40 |  |  |  |  | 79.8251 |  | 23422.9774
2017-09-11 | 6:42 |  |  |  |  | 79.8774 |  | 23438.3146
2017-09-11 | 6:44 |  |  |  |  | 79.8882 |  | 23441.471
2017-09-11 | 6:45 | 1.7491 | 0 | 0 | 1.5 | 79.8487 | 0 | 23429.895
2017-09-11 | 6:46 |  |  |  |  | 79.898 |  | 23444.3478
2017-09-11 | 6:48 |  |  |  |  | 79.8895 |  | 23441.8583
2017-09-11 | 6:50 |  |  |  |  | 79.8914 |  | 23442.4068
2017-09-11 | 6:52 |  |  |  |  | 79.9418 |  | 23457.2047
2017-09-11 | 6:54 |  |  |  |  | 79.9722 |  | 23466.1214
2017-09-11 | 6:56 |  |  |  |  | 79.9785 |  | 23467.9817
2017-09-11 | 6:58 |  |  |  |  | 79.9795 |  | 23468.2569
2017-09-11 | 7:00 | 1.7546 | 0 | 0 | 1.5 | 80.0368 | 0 | 23485.0918
2017-09-11 | 7:02 |  |  |  |  | 80.0634 |  | 23492.887
2017-09-11 | 7:04 |  |  |  |  | 80.098 |  | 23503.0326
2017-09-11 | 7:06 |  |  |  |  | 80.1132 |  | 23507.5144
2017-09-11 | 7:08 |  |  |  |  | 80.1166 |  | 23508.513
2017-09-11 | 7:10 |  |  |  |  | 80.1349 |  | 23513.8725
2017-09-11 | 7:12 |  |  |  |  | 80.161 |  | 23521.5242
2017-09-11 | 7:14 |  |  |  |  | 80.1626 |  | 23521.9855
2017-09-11 | 7:15 | 1.7561 | 0 | 0 | 1.5 | 80.1576 | 0 | 23520.5213
2017-09-11 | 7:16 |  |  |  |  | 80.1669 |  | 23523.2457
2017-09-11 | 7:18 |  |  |  |  | 80.2103 |  | 23535.9949
2017-09-11 | 7:20 |  |  |  |  | 80.1992 |  | 23532.7264
2017-09-11 | 7:22 |  |  |  |  | 80.2328 |  | 23542.588
2017-09-11 | 7:24 |  |  |  |  | 80.2362 |  | 23543.5842
2017-09-11 | 7:26 |  |  |  |  | 80.2412 |  | 23545.0751
2017-09-11 | 7:28 |  |  |  |  | 80.3013 |  | 23562.6822
2017-09-11 | 7:30 | 1.7507 | 0 | 0 | 1.5 | 80.2984 | 0 | 23561.8495
2017-09-11 | 7:32 |  |  |  |  | 80.1765 |  | 23526.0776
2017-09-11 | 7:34 |  |  |  |  | 80.017 |  | 23479.2781
2017-09-11 | 7:36 |  |  |  |  | 79.8802 |  | 23439.1227
2017-09-11 | 7:38 |  |  |  |  | 79.7816 |  | 23410.2056
2017-09-11 | 7:40 |  |  |  |  | 79.6803 |  | 23380.4649
2017-09-11 | 7:42 |  |  |  |  | 79.5584 |  | 23344.7109
2017-09-11 | 7:44 |  |  |  |  | 79.4592 |  | 23315.5855
2017-09-11 | 7:45 | 1.7795 | 0 | 0 | 1.5 | 79.3999 | 0 | 23298.211
2017-09-11 | 7:46 |  |  |  |  | 79.3742 |  | 23290.6578
2017-09-11 | 7:48 |  |  |  |  | 79.4128 |  | 23301.9721
2017-09-11 | 7:50 |  |  |  |  | 79.4374 |  | 23309.2142
2017-09-11 | 7:52 |  |  |  |  | 79.3357 |  | 23279.357
2017-09-11 | 7:54 |  |  |  |  | 79.2328 |  | 23249.1817
2017-09-11 | 7:56 |  |  |  |  | 79.0907 |  | 23207.4594
2017-09-11 | 7:58 |  |  |  |  | 78.9714 |  | 23172.4756
2017-09-11 | 8:00 | 1.7897 | 0 | 0 | 1.5 | 78.8446 | 0 | 23135.271
2017-09-11 | 8:02 |  |  |  |  | 78.8011 |  | 23122.4992
2017-09-11 | 8:04 |  |  |  |  | 78.8546 |  | 23138.2035
2017-09-11 | 8:06 |  |  |  |  | 78.8793 |  | 23145.4277
2017-09-11 | 8:08 |  |  |  |  | 78.7959 |  | 23120.9566
2017-09-11 | 8:10 |  |  |  |  | 78.7111 |  | 23096.0715
2017-09-11 | 8:12 |  |  |  |  | 78.7452 |  | 23106.1053
2017-09-11 | 8:14 |  |  |  |  | 78.7163 |  | 23097.6094
2017-09-11 | 8:15 | 1.7608 | 0 | 0 | 1.5 | 78.7286 | 0 | 23101.2115
2017-09-11 | 8:16 |  |  |  |  | 78.765 |  | 23111.8967
2017-09-11 | 8:18 |  |  |  |  | 78.8277 |  | 23130.2853
2017-09-11 | 8:20 |  |  |  |  | 79.0005 |  | 23181.005
2017-09-11 | 8:22 |  |  |  |  | 79.0309 |  | 23189.915
2017-09-11 | 8:24 |  |  |  |  | 79.0155 |  | 23185.4106
2017-09-11 | 8:26 |  |  |  |  | 78.9948 |  | 23179.3193
2017-09-11 | 8:28 |  |  |  |  | 78.9567 |  | 23168.1526
2017-09-11 | 8:30 | 1.7709 | 0 | 0 | 1.5 | 78.9426 | 0 | 23164.0111
2017-09-11 | 8:32 |  |  |  |  | 78.9853 |  | 23176.5543
2017-09-11 | 8:34 |  |  |  |  | 78.9183 |  | 23156.8697
2017-09-11 | 8:36 |  |  |  |  | 78.9757 |  | 23173.7359
2017-09-11 | 8:38 |  |  |  |  | 79.0637 |  | 23199.5568
2017-09-11 | 8:40 |  |  |  |  | 79.2162 |  | 23244.3058
2017-09-11 | 8:42 |  |  |  |  | 79.2009 |  | 23239.8061
2017-09-11 | 8:44 |  |  |  |  | 79.2497 |  | 23254.1224
2017-09-11 | 8:45 | 1.7507 | 0 | 0 | 1.5 | 79.3138 | 0 | 23272.9365
2017-09-11 | 8:46 |  |  |  |  | 79.3244 |  | 23276.0348
2017-09-11 | 8:48 |  |  |  |  | 79.4057 |  | 23299.9058
2017-09-11 | 8:50 |  |  |  |  | 79.4537 |  | 23313.9713
2017-09-11 | 8:52 |  |  |  |  | 79.4709 |  | 23319.0444
2017-09-11 | 8:54 |  |  |  |  | 79.462 |  | 23316.4297
2017-09-11 | 8:56 |  |  |  |  | 79.4889 |  | 23324.3053
2017-09-11 | 8:58 |  |  |  |  | 79.4599 |  | 23315.7958
2017-09-11 | 9:00 | 1.7616 | 0 | 0 | 1.5 | 79.4279 | 0 | 23306.4182
2017-09-11 | 9:02 |  |  |  |  | 79.4769 |  | 23320.8061
2017-09-11 | 9:04 |  |  |  |  | 79.6405 |  | 23368.8078
2017-09-11 | 9:06 |  |  |  |  | 79.811 |  | 23418.8336
2017-09-11 | 9:08 |  |  |  |  | 79.8949 |  | 23443.4343
2017-09-11 | 9:10 |  |  |  |  | 79.951 |  | 23459.8954
2017-09-11 | 9:12 |  |  |  |  | 79.9755 |  | 23467.0882
2017-09-11 | 9:14 |  |  |  |  | 80.0193 |  | 23479.963
2017-09-11 | 9:15 | 1.739 | 0 | 0 | 1.5 | 80.027 | 0 | 23482.2106
2017-09-11 | 9:16 |  |  |  |  | 79.9995 |  | 23474.1314
2017-09-11 | 9:18 |  |  |  |  | 79.9995 |  | 23474.1425
2017-09-11 | 9:20 |  |  |  |  | 79.9814 |  | 23468.8344
2017-09-11 | 9:22 |  |  |  |  | 79.9699 |  | 23465.4406
2017-09-11 | 9:24 |  |  |  |  | 79.9858 |  | 23470.1196
2017-09-11 | 9:26 |  |  |  |  | 79.9203 |  | 23450.8983
2017-09-11 | 9:28 |  |  |  |  | 79.8718 |  | 23436.6579
2017-09-11 | 9:30 | 1.7585 | 0 | 0 | 1.5 | 79.8724 | 0 | 23436.8483
2017-09-11 | 9:32 |  |  |  |  | 79.8481 |  | 23429.7069
2017-09-11 | 9:34 |  |  |  |  | 79.7842 |  | 23410.9647
2017-09-11 | 9:36 |  |  |  |  | 79.719 |  | 23391.8396
2017-09-11 | 9:38 |  |  |  |  | 79.6427 |  | 23369.4548
2017-09-11 | 9:40 |  |  |  |  | 79.5848 |  | 23352.4545
2017-09-11 | 9:42 |  |  |  |  | 79.4849 |  | 23323.1389
2017-09-11 | 9:44 |  |  |  |  | 79.4747 |  | 23320.1568
2017-09-11 | 9:45 | 1.76 | 0 | 0 | 1.5 | 79.4128 | 0 | 23301.9968
2017-09-11 | 9:46 |  |  |  |  | 79.4274 |  | 23306.275
2017-09-11 | 9:48 |  |  |  |  | 79.3524 |  | 23284.262
2017-09-11 | 9:50 |  |  |  |  | 79.3561 |  | 23285.3341
2017-09-11 | 9:52 |  |  |  |  | 79.2797 |  | 23262.9362
2017-09-11 | 9:54 |  |  |  |  | 79.2605 |  | 23257.2859
2017-09-11 | 9:56 |  |  |  |  | 79.2126 |  | 23243.2336
2017-09-11 | 9:58 |  |  |  |  | 79.1852 |  | 23235.2124
2017-09-11 | 10:00 | 1.7686 | 0 | 0 | 1.5 | 79.1649 | 0 | 23229.2462
2017-09-11 | 10:02 |  |  |  |  | 79.1457 |  | 23223.5959
2017-09-11 | 10:04 |  |  |  |  | 79.1082 |  | 23212.6173
2017-09-11 | 10:06 |  |  |  |  | 79.1136 |  | 23214.2
2017-09-11 | 10:08 |  |  |  |  | 79.1218 |  | 23216.6044
2017-09-11 | 10:10 |  |  |  |  | 79.1603 |  | 23227.8829
2017-09-11 | 10:12 |  |  |  |  | 79.1939 |  | 23237.7667
2017-09-11 | 10:14 |  |  |  |  | 79.2362 |  | 23250.1623
2017-09-11 | 10:15 | 1.7397 | 0 | 0 | 1.5 | 79.2877 | 0 | 23265.2622
2017-09-11 | 10:16 |  |  |  |  | 79.2818 |  | 23263.5474
2017-09-11 | 10:18 |  |  |  |  | 79.316 |  | 23273.5923
2017-09-11 | 10:20 |  |  |  |  | 79.3425 |  | 23281.3696
2017-09-11 | 10:22 |  |  |  |  | 79.3923 |  | 23295.9657
2017-09-11 | 10:24 |  |  |  |  | 79.4439 |  | 23311.106
2017-09-11 | 10:26 |  |  |  |  | 79.5188 |  | 23333.0808
2017-09-11 | 10:28 |  |  |  |  | 79.5786 |  | 23350.6434
2017-09-11 | 10:30 | 1.76 | 0 | 0 | 1.5 | 79.5339 | 0 | 23337.5201
2017-09-11 | 10:32 |  |  |  |  | 79.4844 |  | 23322.9822
2017-09-11 | 10:34 |  |  |  |  | 79.4806 |  | 23321.8807
2017-09-11 | 10:36 |  |  |  |  | 79.4439 |  | 23311.106
2017-09-11 | 10:38 |  |  |  |  | 79.4504 |  | 23313.0268
2017-09-11 | 10:40 |  |  |  |  | 79.4332 |  | 23307.9786
2017-09-11 | 10:42 |  |  |  |  | 79.4175 |  | 23303.3533
2017-09-11 | 10:44 |  |  |  |  | 79.4433 |  | 23310.9267
2017-09-11 | 10:45 | 1.746 | 0 | 0 | 1.5 | 79.4432 | 0 | 23310.8956
2017-09-11 | 10:46 |  |  |  |  | 79.4113 |  | 23301.5558
2017-09-11 | 10:48 |  |  |  |  | 79.3888 |  | 23294.9448
2017-09-11 | 10:50 |  |  |  |  | 79.4027 |  | 23299.0326
2017-09-11 | 10:52 |  |  |  |  | 79.424 |  | 23305.272
2017-09-11 | 10:54 |  |  |  |  | 79.4062 |  | 23300.0558
2017-09-11 | 10:56 |  |  |  |  | 79.3876 |  | 23294.598
2017-09-11 | 10:58 |  |  |  |  | 79.4445 |  | 23311.2715
2017-09-11 | 11:00 | 1.7483 | 0 | 0 | 1.5 | 79.4526 | 0 | 23313.6691
2017-09-11 | 11:02 |  |  |  |  | 79.5958 |  | 23355.6737
2017-09-11 | 11:04 |  |  |  |  | 79.8355 |  | 23426.0129
2017-09-11 | 11:06 |  |  |  |  | 79.9844 |  | 23469.7032
2017-09-11 | 11:08 |  |  |  |  | 80.0856 |  | 23499.4126
2017-09-11 | 11:10 |  |  |  |  | 80.1514 |  | 23518.7214
2017-09-11 | 11:12 |  |  |  |  | 80.2723 |  | 23554.1978
2017-09-11 | 11:14 |  |  |  |  | 80.3033 |  | 23563.2911
2017-09-11 | 11:15 | 1.7358 | 0 | 0 | 1.5 | 80.3435 | 0 | 23575.0802
2017-09-11 | 11:16 |  |  |  |  | 80.3846 |  | 23587.1466
2017-09-11 | 11:18 |  |  |  |  | 80.3781 |  | 23585.2393
2017-09-11 | 11:20 |  |  |  |  | 80.4802 |  | 23615.1951
2017-09-11 | 11:22 |  |  |  |  | 80.5669 |  | 23640.6354
2017-09-11 | 11:24 |  |  |  |  | 80.6385 |  | 23661.6434
2017-09-11 | 11:26 |  |  |  |  | 80.7842 |  | 23704.3953
2017-09-11 | 11:28 |  |  |  |  | 80.8819 |  | 23733.0504
2017-09-11 | 11:30 | 1.739 | 0 | 0 | 1.5 | 80.881 | 0 | 23732.7819
2017-09-11 | 11:32 |  |  |  |  | 80.9671 |  | 23758.0746
2017-09-11 | 11:34 |  |  |  |  | 80.9669 |  | 23758.003
2017-09-11 | 11:36 |  |  |  |  | 80.9905 |  | 23764.9385
2017-09-11 | 11:38 |  |  |  |  | 81.0333 |  | 23777.4995
2017-09-11 | 11:40 |  |  |  |  | 81.1518 |  | 23812.2529
2017-09-11 | 11:42 |  |  |  |  | 81.3112 |  | 23859.0345
2017-09-11 | 11:44 |  |  |  |  | 81.4023 |  | 23885.7577
2017-09-11 | 11:45 | 1.7312 | 0 | 0 | 1.5 | 81.4268 | 0 | 23892.9417
2017-09-11 | 11:46 |  |  |  |  | 81.495 |  | 23912.96
2017-09-11 | 11:48 |  |  |  |  | 81.5289 |  | 23922.9154
2017-09-11 | 11:50 |  |  |  |  | 81.6546 |  | 23959.8044
2017-09-11 | 11:52 |  |  |  |  | 81.6867 |  | 23969.2158
2017-09-11 | 11:54 |  |  |  |  | 81.749 |  | 23987.4791
2017-09-11 | 11:56 |  |  |  |  | 81.8579 |  | 24019.4361
2017-09-11 | 11:58 |  |  |  |  | 81.9278 |  | 24039.9582
2017-09-11 | 12:00 | 1.689 | 0 | 0 | 1.5 | 82.1346 | 0 | 24100.631
2017-09-11 | 12:02 |  |  |  |  | 82.2603 |  | 24137.5132
2017-09-11 | 12:04 |  |  |  |  | 82.3251 |  | 24156.5286
2017-09-11 | 12:06 |  |  |  |  | 82.3224 |  | 24155.7495
2017-09-11 | 12:08 |  |  |  |  | 82.3341 |  | 24159.168
2017-09-11 | 12:10 |  |  |  |  | 82.3699 |  | 24169.6877
2017-09-11 | 12:12 |  |  |  |  | 82.3945 |  | 24176.8872
2017-09-11 | 12:14 |  |  |  |  | 82.4661 |  | 24197.9219
2017-09-11 | 12:15 | 1.7109 | 0 | 0 | 1.5 | 82.5791 | 0 | 24231.0656
2017-09-11 | 12:16 |  |  |  |  | 82.5963 |  | 24236.1093
2017-09-11 | 12:18 |  |  |  |  | 82.722 |  | 24273.0118
2017-09-11 | 12:20 |  |  |  |  | 82.7813 |  | 24290.4109
2017-09-11 | 12:22 |  |  |  |  | 82.759 |  | 24283.8604
2017-09-11 | 12:24 |  |  |  |  | 82.7118 |  | 24269.9939
2017-09-11 | 12:26 |  |  |  |  | 82.6575 |  | 24254.0792
2017-09-11 | 12:28 |  |  |  |  | 82.6155 |  | 24241.7599
2017-09-11 | 12:30 | 1.7351 | 0 | 0 | 1.5 | 82.7258 | 0 | 24274.1019
2017-09-11 | 12:32 |  |  |  |  | 82.7611 |  | 24284.4784
2017-09-11 | 12:34 |  |  |  |  | 82.7893 |  | 24292.7569
2017-09-11 | 12:36 |  |  |  |  | 82.7615 |  | 24284.5746
2017-09-11 | 12:38 |  |  |  |  | 82.6472 |  | 24251.0616
2017-09-11 | 12:40 |  |  |  |  | 82.6117 |  | 24240.6449
2017-09-11 | 12:42 |  |  |  |  | 82.55 |  | 24222.5271
2017-09-11 | 12:44 |  |  |  |  | 82.6316 |  | 24246.4656
2017-09-11 | 12:45 | 1.7 | 0 | 0 | 1.5 | 82.6614 | 0 | 24255.2186
2017-09-11 | 12:46 |  |  |  |  | 82.6839 |  | 24261.814
2017-09-11 | 12:48 |  |  |  |  | 82.7422 |  | 24278.9173
2017-09-11 | 12:50 |  |  |  |  | 82.7658 |  | 24285.8619
2017-09-11 | 12:52 |  |  |  |  | 82.6867 |  | 24262.64
2017-09-11 | 12:54 |  |  |  |  | 82.6192 |  | 24242.8365
2017-09-11 | 12:56 |  |  |  |  | 82.6493 |  | 24251.6728
2017-09-11 | 12:58 |  |  |  |  | 82.7731 |  | 24287.9951
2017-09-11 | 13:00 | 1.6914 | 0 | 0 | 1.5 | 82.8896 | 0 | 24322.1845
2017-09-11 | 13:02 |  |  |  |  | 83.0875 |  | 24380.2535
2017-09-11 | 13:04 |  |  |  |  | 83.2186 |  | 24418.7096
2017-09-11 | 13:06 |  |  |  |  | 83.2527 |  | 24428.7076
2017-09-11 | 13:08 |  |  |  |  | 83.1366 |  | 24394.6394
2017-09-11 | 13:10 |  |  |  |  | 83.0832 |  | 24378.982
2017-09-11 | 13:12 |  |  |  |  | 83.1405 |  | 24395.799
2017-09-11 | 13:14 |  |  |  |  | 83.2088 |  | 24415.8308
2017-09-11 | 13:15 | 1.7358 | 0 | 0 | 1.5 | 83.2259 | 0 | 24420.852
2017-09-11 | 13:16 |  |  |  |  | 83.2727 |  | 24434.5976
2017-09-11 | 13:18 |  |  |  |  | 83.3739 |  | 24464.2894
2017-09-11 | 13:20 |  |  |  |  | 83.4562 |  | 24488.4221
2017-09-11 | 13:22 |  |  |  |  | 83.54 |  | 24513.0187
2017-09-11 | 13:24 |  |  |  |  | 83.5505 |  | 24516.0992
2017-09-11 | 13:26 |  |  |  |  | 83.5868 |  | 24526.7553
2017-09-11 | 13:28 |  |  |  |  | 83.6187 |  | 24536.1242
2017-09-11 | 13:30 | 1.7117 | 0 | 0 | 1.5 | 83.7198 | 0 | 24565.7933
2017-09-11 | 13:32 |  |  |  |  | 83.829 |  | 24597.8243
2017-09-11 | 13:34 |  |  |  |  | 83.9552 |  | 24634.8567
2017-09-11 | 13:36 |  |  |  |  | 84.0562 |  | 24664.5012
2017-09-11 | 13:38 |  |  |  |  | 84.0486 |  | 24662.2492
2017-09-11 | 13:40 |  |  |  |  | 84.0333 |  | 24657.7718
2017-09-11 | 13:42 |  |  |  |  | 84.0119 |  | 24651.4924
2017-09-11 | 13:44 |  |  |  |  | 84.1309 |  | 24686.4045
2017-09-11 | 13:45 | 1.7132 | 0 | 0 | 1.5 | 84.2075 | 0 | 24708.8765
2017-09-11 | 13:46 |  |  |  |  | 84.2312 |  | 24715.8477
2017-09-11 | 13:48 |  |  |  |  | 84.3077 |  | 24738.2839
2017-09-11 | 13:50 |  |  |  |  | 84.4586 |  | 24782.574
2017-09-11 | 13:52 |  |  |  |  | 84.5603 |  | 24812.4224
2017-09-11 | 13:54 |  |  |  |  | 84.7348 |  | 24863.6052
2017-09-11 | 13:56 |  |  |  |  | 84.7729 |  | 24874.7918
2017-09-11 | 13:58 |  |  |  |  | 84.7479 |  | 24867.4646
2017-09-11 | 14:00 | 1.7522 | 0 | 0 | 1.5 | 84.8353 | 0 | 24893.0909
2017-09-11 | 14:02 |  |  |  |  | 84.9781 |  | 24935.0148
2017-09-11 | 14:04 |  |  |  |  | 85.1388 |  | 24982.1435
2017-09-11 | 14:06 |  |  |  |  | 85.3018 |  | 25029.9929
2017-09-11 | 14:08 |  |  |  |  | 85.4851 |  | 25083.764
2017-09-11 | 14:10 |  |  |  |  | 85.6264 |  | 25125.2223
2017-09-11 | 14:12 |  |  |  |  | 85.8148 |  | 25180.4998
2017-09-11 | 14:14 |  |  |  |  | 85.9039 |  | 25206.6722
2017-09-11 | 14:15 | 1.7686 | 0 | 0 | 1.5 | 85.8657 | 0 | 25195.4429
2017-09-11 | 14:16 |  |  |  |  | 85.7928 |  | 25174.0499
2017-09-11 | 14:18 |  |  |  |  | 85.6032 |  | 25118.4276
2017-09-11 | 14:20 |  |  |  |  | 85.3254 |  | 25036.9017
2017-09-11 | 14:22 |  |  |  |  | 85.0576 |  | 24958.3195
2017-09-11 | 14:24 |  |  |  |  | 84.7775 |  | 24876.153
2017-09-11 | 14:26 |  |  |  |  | 84.5197 |  | 24800.4969
2017-09-11 | 14:28 |  |  |  |  | 84.2957 |  | 24734.7533
2017-09-11 | 14:30 | 1.824 | 0 | 0 | 1.5 | 84.0718 | 0 | 24669.0614
2017-09-11 | 14:32 |  |  |  |  | 83.8882 |  | 24615.1832
2017-09-11 | 14:34 |  |  |  |  | 83.8531 |  | 24604.9033
2017-09-11 | 14:36 |  |  |  |  | 83.9455 |  | 24632.0023
2017-09-11 | 14:38 |  |  |  |  | 84.0881 |  | 24673.8569
2017-09-11 | 14:40 |  |  |  |  | 84.1574 |  | 24694.1727
2017-09-11 | 14:42 |  |  |  |  | 84.1719 |  | 24698.4354
2017-09-11 | 14:44 |  |  |  |  | 84.1888 |  | 24703.3961
2017-09-11 | 14:45 | 1.7413 | 0 | 0 | 1.5 | 84.234 | 0 | 24716.6605
2017-09-11 | 14:46 |  |  |  |  | 84.2909 |  | 24733.3587
2017-09-11 | 14:48 |  |  |  |  | 84.4712 |  | 24786.2767
2017-09-11 | 14:50 |  |  |  |  | 84.643 |  | 24836.6693
2017-09-11 | 14:52 |  |  |  |  | 84.8627 |  | 24901.1458
2017-09-11 | 14:54 |  |  |  |  | 85.0024 |  | 24942.1472
2017-09-11 | 14:56 |  |  |  |  | 85.2017 |  | 25000.626
2017-09-11 | 14:58 |  |  |  |  | 85.3295 |  | 25038.1083
2017-09-11 | 15:00 | 1.6961 | 0 | 0 | 1.5 | 85.5508 | 0 | 25103.0637
2017-09-11 | 15:02 |  |  |  |  | 85.6905 |  | 25144.036
2017-09-11 | 15:04 |  |  |  |  | 85.6684 |  | 25137.5507
2017-09-11 | 15:06 |  |  |  |  | 85.4671 |  | 25078.4829
2017-09-11 | 15:08 |  |  |  |  | 85.2288 |  | 25008.5577
2017-09-11 | 15:10 |  |  |  |  | 84.9456 |  | 24925.4578
2017-09-11 | 15:12 |  |  |  |  | 84.7553 |  | 24869.6339
2017-09-11 | 15:14 |  |  |  |  | 84.5661 |  | 24814.1079
2017-09-11 | 15:15 | 1.8201 | 0 | 0 | 1.5 | 84.4431 | 0 | 24778.0159
2017-09-11 | 15:16 |  |  |  |  | 84.3209 |  | 24742.1747
2017-09-11 | 15:18 |  |  |  |  | 84.0596 |  | 24665.5021
2017-09-11 | 15:20 |  |  |  |  | 83.9446 |  | 24631.7294
2017-09-11 | 15:22 |  |  |  |  | 83.9073 |  | 24620.7977
2017-09-11 | 15:24 |  |  |  |  | 84.0131 |  | 24651.8328
2017-09-11 | 15:26 |  |  |  |  | 84.1181 |  | 24682.6592
2017-09-11 | 15:28 |  |  |  |  | 84.3015 |  | 24736.4772
2017-09-11 | 15:30 | 1.721 | 0 | 0 | 1.5 | 84.4002 | 0 | 24765.4278
2017-09-11 | 15:32 |  |  |  |  | 84.467 |  | 24785.0276
2017-09-11 | 15:34 |  |  |  |  | 84.5023 |  | 24795.3792
2017-09-11 | 15:36 |  |  |  |  | 84.6156 |  | 24828.6414
2017-09-11 | 15:38 |  |  |  |  | 84.7094 |  | 24856.1638
2017-09-11 | 15:40 |  |  |  |  | 84.9102 |  | 24915.0725
2017-09-11 | 15:42 |  |  |  |  | 85.0942 |  | 24969.0695
2017-09-11 | 15:44 |  |  |  |  | 85.2601 |  | 25017.7564
2017-09-11 | 15:45 | 1.6828 | 0 | 0 | 1.5 | 85.3733 | 0 | 25050.9784
2017-09-11 | 15:46 |  |  |  |  | 85.499 |  | 25087.8474
2017-09-11 | 15:48 |  |  |  |  | 85.5929 |  | 25115.4123
2017-09-11 | 15:50 |  |  |  |  | 85.6226 |  | 25124.114
2017-09-11 | 15:52 |  |  |  |  | 85.4431 |  | 25071.4444
2017-09-11 | 15:54 |  |  |  |  | 85.2649 |  | 25019.1557
2017-09-11 | 15:56 |  |  |  |  | 85.1074 |  | 24972.9493
2017-09-11 | 15:58 |  |  |  |  | 84.9696 |  | 24932.4984
2017-09-11 | 16:00 | 1.8232 | 0 | 0 | 1.5 | 84.815 | 0 | 24887.154
2017-09-11 | 16:02 |  |  |  |  | 84.6771 |  | 24846.6899
2017-09-11 | 16:04 |  |  |  |  | 84.5086 |  | 24797.2284
2017-09-11 | 16:06 |  |  |  |  | 84.3227 |  | 24742.6873
2017-09-11 | 16:08 |  |  |  |  | 84.2805 |  | 24730.3185
2017-09-11 | 16:10 |  |  |  |  | 84.3647 |  | 24755.0134
2017-09-11 | 16:12 |  |  |  |  | 84.4835 |  | 24789.8654
2017-09-11 | 16:14 |  |  |  |  | 84.6235 |  | 24830.9609
2017-09-11 | 16:15 | 1.6617 | 0 | 0 | 1.5 | 84.7222 | 0 | 24859.9203
2017-09-11 | 16:16 |  |  |  |  | 84.8399 |  | 24894.4454
2017-09-11 | 16:18 |  |  |  |  | 84.9431 |  | 24924.7234
2017-09-11 | 16:20 |  |  |  |  | 84.9515 |  | 24927.1949
2017-09-11 | 16:22 |  |  |  |  | 85.0421 |  | 24953.7793
2017-09-11 | 16:24 |  |  |  |  | 85.2436 |  | 25012.8984
2017-09-11 | 16:26 |  |  |  |  | 85.382 |  | 25053.5127
2017-09-11 | 16:28 |  |  |  |  | 85.5042 |  | 25089.3852
2017-09-11 | 16:30 | 1.6984 | 0 | 0 | 1.5 | 85.6471 | 0 | 25131.3182
2017-09-11 | 16:32 |  |  |  |  | 85.7742 |  | 25168.5878
2017-09-11 | 16:34 |  |  |  |  | 85.6942 |  | 25145.1129
2017-09-11 | 16:36 |  |  |  |  | 85.5123 |  | 25091.7605
2017-09-11 | 16:38 |  |  |  |  | 85.4279 |  | 25066.994
2017-09-11 | 16:40 |  |  |  |  | 85.3277 |  | 25037.5889
2017-09-11 | 16:42 |  |  |  |  | 85.0618 |  | 24959.5531
2017-09-11 | 16:44 |  |  |  |  | 84.6834 |  | 24848.5411
2017-09-11 | 16:45 | 1.8622 | 0 | 0 | 1.5 | 84.4709 | 0 | 24786.1694
2017-09-11 | 16:46 |  |  |  |  | 84.3484 |  | 24750.2317
2017-09-11 | 16:48 |  |  |  |  | 84.0474 |  | 24661.9
2017-09-11 | 16:50 |  |  |  |  | 83.9834 |  | 24643.1153
2017-09-11 | 16:52 |  |  |  |  | 83.974 |  | 24640.3841
2017-09-11 | 16:54 |  |  |  |  | 84.0086 |  | 24650.534
2017-09-11 | 16:56 |  |  |  |  | 83.9545 |  | 24634.6396
2017-09-11 | 16:58 |  |  |  |  | 83.9926 |  | 24645.8351
2017-09-11 | 17:00 | 1.7444 | 0 | 0 | 1.5 | 84.0702 | 0 | 24668.5981
2017-09-11 | 17:02 |  |  |  |  | 84.1265 |  | 24685.1152
2017-09-11 | 17:04 |  |  |  |  | 84.2395 |  | 24718.2676
2017-09-11 | 17:06 |  |  |  |  | 84.3839 |  | 24760.6437
2017-09-11 | 17:08 |  |  |  |  | 84.5247 |  | 24801.9564
2017-09-11 | 17:10 |  |  |  |  | 84.594 |  | 24822.2992
2017-09-11 | 17:12 |  |  |  |  | 84.5927 |  | 24821.9233
2017-09-11 | 17:14 |  |  |  |  | 84.5772 |  | 24817.3585
2017-09-11 | 17:15 | 1.7405 | 0 | 0 | 1.5 | 84.6325 | 0 | 24833.5801
2017-09-11 | 17:16 |  |  |  |  | 84.6629 |  | 24842.5079
2017-09-11 | 17:18 |  |  |  |  | 84.7903 |  | 24879.8916
2017-09-11 | 17:20 |  |  |  |  | 84.8326 |  | 24892.3142
2017-09-11 | 17:22 |  |  |  |  | 84.8192 |  | 24888.3852
2017-09-11 | 17:24 |  |  |  |  | 84.8429 |  | 24895.3274
2017-09-11 | 17:26 |  |  |  |  | 84.8822 |  | 24906.8545
2017-09-11 | 17:28 |  |  |  |  | 84.8486 |  | 24897.0041
2017-09-11 | 17:30 | 1.8146 | 0 | 0 | 1.5 | 84.681 | 0 | 24847.836
2017-09-11 | 17:32 |  |  |  |  | 84.5845 |  | 24819.4964
2017-09-11 | 17:34 |  |  |  |  | 84.341 |  | 24748.0536
2017-09-11 | 17:36 |  |  |  |  | 84.1069 |  | 24679.3795
2017-09-11 | 17:38 |  |  |  |  | 84.0306 |  | 24656.9927
2017-09-11 | 17:40 |  |  |  |  | 83.9432 |  | 24631.3242
2017-09-11 | 17:42 |  |  |  |  | 83.7599 |  | 24577.5531
2017-09-11 | 17:44 |  |  |  |  | 83.6143 |  | 24534.8167
2017-09-11 | 17:45 | 1.8146 | 0 | 0 | 1.5 | 83.4871 | 0 | 24497.5134
2017-09-11 | 17:46 |  |  |  |  | 83.3735 |  | 24464.1752
2017-09-11 | 17:48 |  |  |  |  | 83.1966 |  | 24412.2668
2017-09-11 | 17:50 |  |  |  |  | 83.0636 |  | 24373.2332
2017-09-11 | 17:52 |  |  |  |  | 82.9329 |  | 24334.8956
2017-09-11 | 17:54 |  |  |  |  | 82.8567 |  | 24312.5222
2017-09-11 | 17:56 |  |  |  |  | 82.8741 |  | 24317.6153
2017-09-11 | 17:58 |  |  |  |  | 82.8713 |  | 24316.8048
2017-09-11 | 18:00 | 1.7405 | 0 | 0 | 1.5 | 82.8858 | 0 | 24321.0695
2017-09-11 | 18:02 |  |  |  |  | 82.8205 |  | 24301.8998
2017-09-11 | 18:04 |  |  |  |  | 82.752 |  | 24281.8076
2017-09-11 | 18:06 |  |  |  |  | 82.6175 |  | 24242.3329
2017-09-11 | 18:08 |  |  |  |  | 82.5237 |  | 24214.797
2017-09-11 | 18:10 |  |  |  |  | 82.3802 |  | 24172.7188
2017-09-11 | 18:12 |  |  |  |  | 82.2411 |  | 24131.8809
2017-09-11 | 18:14 |  |  |  |  | 82.1779 |  | 24113.3423
2017-09-11 | 18:15 | 1.7686 | 0 | 0 | 1.5 | 82.1698 | 0 | 24110.9579
2017-09-11 | 18:16 |  |  |  |  | 82.2221 |  | 24126.313
2017-09-11 | 18:18 |  |  |  |  | 82.1999 |  | 24119.8121
2017-09-11 | 18:20 |  |  |  |  | 82.1911 |  | 24117.2285
2017-09-11 | 18:22 |  |  |  |  | 82.1536 |  | 24106.2232
2017-09-11 | 18:24 |  |  |  |  | 82.0573 |  | 24077.9443
2017-09-11 | 18:26 |  |  |  |  | 81.9495 |  | 24046.3139
2017-09-11 | 18:28 |  |  |  |  | 81.8564 |  | 24019.0177
2017-09-11 | 18:30 | 1.7834 | 0 | 0 | 1.5 | 81.7412 | 0 | 23985.1933
2017-09-11 | 18:32 |  |  |  |  | 81.6862 |  | 23969.0591
2017-09-11 | 18:34 |  |  |  |  | 81.59 |  | 23940.8427
2017-09-11 | 18:36 |  |  |  |  | 81.5928 |  | 23941.6687
2017-09-11 | 18:38 |  |  |  |  | 81.5993 |  | 23943.5605
2017-09-11 | 18:40 |  |  |  |  | 81.5989 |  | 23943.4419
2017-09-11 | 18:42 |  |  |  |  | 81.5768 |  | 23936.9765
2017-09-11 | 18:44 |  |  |  |  | 81.4906 |  | 23911.6683
2017-09-11 | 18:45 | 1.7826 | 0 | 0 | 1.5 | 81.4305 | 0 | 23894.0476
2017-09-11 | 18:46 |  |  |  |  | 81.3898 |  | 23882.0863
2017-09-11 | 18:48 |  |  |  |  | 81.3216 |  | 23862.0859
2017-09-11 | 18:50 |  |  |  |  | 81.2552 |  | 23842.5826
2017-09-11 | 18:52 |  |  |  |  | 81.2125 |  | 23830.0749
2017-09-11 | 18:54 |  |  |  |  | 81.2336 |  | 23836.2604
2017-09-11 | 18:56 |  |  |  |  | 81.2573 |  | 23843.2161
2017-09-11 | 18:58 |  |  |  |  | 81.253 |  | 23841.9491
2017-09-11 | 19:00 | 1.7881 | 0 | 0 | 1.5 | 81.1676 | 0 | 23816.8914
2017-09-11 | 19:02 |  |  |  |  | 81.0734 |  | 23789.2549
2017-09-11 | 19:04 |  |  |  |  | 80.9739 |  | 23760.0535
2017-09-11 | 19:06 |  |  |  |  | 80.8582 |  | 23726.095
2017-09-11 | 19:08 |  |  |  |  | 80.7827 |  | 23703.9388
2017-09-11 | 19:10 |  |  |  |  | 80.6796 |  | 23673.7053
2017-09-11 | 19:12 |  |  |  |  | 80.647 |  | 23664.1214
2017-09-11 | 19:14 |  |  |  |  | 80.6588 |  | 23667.5915
2017-09-11 | 19:15 | 1.7475 | 0 | 0 | 1.5 | 80.6674 | 0 | 23670.1279
2017-09-11 | 19:16 |  |  |  |  | 80.6402 |  | 23662.1516
2017-09-11 | 19:18 |  |  |  |  | 80.5541 |  | 23636.861
2017-09-11 | 19:20 |  |  |  |  | 80.4555 |  | 23607.9462
2017-09-11 | 19:22 |  |  |  |  | 80.3595 |  | 23579.7589
2017-09-11 | 19:24 |  |  |  |  | 80.2876 |  | 23558.684
2017-09-11 | 19:26 |  |  |  |  | 80.1623 |  | 23521.9048
2017-09-11 | 19:28 |  |  |  |  | 80.036 |  | 23484.8612
2017-09-11 | 19:30 | 1.7647 | 0 | 0 | 1.5 | 79.9844 | 0 | 23469.7009
2017-09-11 | 19:32 |  |  |  |  | 79.8656 |  | 23434.858
2017-09-11 | 19:34 |  |  |  |  | 79.8552 |  | 23431.809
2017-09-11 | 19:36 |  |  |  |  | 79.8749 |  | 23437.5781
2017-09-11 | 19:38 |  |  |  |  | 79.8739 |  | 23437.2715
2017-09-11 | 19:40 |  |  |  |  | 79.8302 |  | 23424.4639
2017-09-11 | 19:42 |  |  |  |  | 79.6879 |  | 23382.7146
2017-09-11 | 19:44 |  |  |  |  | 79.6149 |  | 23361.277
2017-09-11 | 19:45 | 1.7764 | 0 | 0 | 1.5 | 79.5644 | 0 | 23346.4682
2017-09-11 | 19:46 |  |  |  |  | 79.532 |  | 23336.9582
2017-09-11 | 19:48 |  |  |  |  | 79.409 |  | 23300.8841
2017-09-11 | 19:50 |  |  |  |  | 79.3376 |  | 23279.9078
2017-09-11 | 19:52 |  |  |  |  | 79.259 |  | 23256.8449
2017-09-11 | 19:54 |  |  |  |  | 79.1665 |  | 23229.723
2017-09-11 | 19:56 |  |  |  |  | 79.1599 |  | 23227.791
2017-09-11 | 19:58 |  |  |  |  | 79.1492 |  | 23224.6414
2017-09-11 | 20:00 | 1.7678 | 0 | 0 | 1.5 | 79.1119 | 0 | 23213.6941
2017-09-11 | 20:02 |  |  |  |  | 78.9752 |  | 23173.5657
2017-09-11 | 20:04 |  |  |  |  | 78.9189 |  | 23157.0533
2017-09-11 | 20:06 |  |  |  |  | 78.8319 |  | 23131.53
2017-09-11 | 20:08 |  |  |  |  | 78.7327 |  | 23102.434
2017-09-11 | 20:10 |  |  |  |  | 78.622 |  | 23069.9485
2017-09-11 | 20:12 |  |  |  |  | 78.4926 |  | 23031.9624
2017-09-11 | 20:14 |  |  |  |  | 78.436 |  | 23015.3581
2017-09-11 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 78.405 | 0 | 23006.2534
2017-09-11 | 20:16 |  |  |  |  | 78.3299 |  | 22984.2315
2017-09-11 | 20:18 |  |  |  |  | 78.2836 |  | 22970.6537
2017-09-11 | 20:20 |  |  |  |  | 78.1855 |  | 22941.869
2017-09-11 | 20:22 |  |  |  |  | 78.1418 |  | 22929.0391
2017-09-11 | 20:24 |  |  |  |  | 78.1367 |  | 22927.5256
2017-09-11 | 20:26 |  |  |  |  | 78.153 |  | 22932.3231
2017-09-11 | 20:28 |  |  |  |  | 78.2464 |  | 22959.7402
2017-09-11 | 20:30 | 1.7483 | 0 | 0 | 1.5 | 78.2312 | 0 | 22955.2607
2017-09-11 | 20:32 |  |  |  |  | 78.1256 |  | 22924.2729
2017-09-11 | 20:34 |  |  |  |  | 78.0502 |  | 22902.1569
2017-09-11 | 20:36 |  |  |  |  | 77.9773 |  | 22880.7707
2017-09-11 | 20:38 |  |  |  |  | 77.9093 |  | 22860.8263
2017-09-11 | 20:40 |  |  |  |  | 77.8471 |  | 22842.5519
2017-09-11 | 20:42 |  |  |  |  | 77.8163 |  | 22833.519
2017-09-11 | 20:44 |  |  |  |  | 77.7303 |  | 22808.28
2017-09-11 | 20:45 | 1.7772 | 0 | 0 | 1.5 | 77.6888 | 0 | 22796.1036
2017-09-11 | 20:46 |  |  |  |  | 77.6608 |  | 22787.9011
2017-09-11 | 20:48 |  |  |  |  | 77.6078 |  | 22772.3468
2017-09-11 | 20:50 |  |  |  |  | 77.5284 |  | 22749.0512
2017-09-11 | 20:52 |  |  |  |  | 77.4604 |  | 22729.0842
2017-09-11 | 20:54 |  |  |  |  | 77.3539 |  | 22697.8458
2017-09-11 | 20:56 |  |  |  |  | 77.2354 |  | 22663.059
2017-09-11 | 20:58 |  |  |  |  | 77.1492 |  | 22637.7795
2017-09-11 | 21:00 | 1.7663 | 0 | 0 | 1.5 | 77.0769 | 0 | 22616.5503
2017-09-11 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:15 | 0.04168 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:30 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:45 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-11 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 5:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 5:02 |  |  |  |  | 69.625 |  | 20429.9643
2017-09-12 | 5:04 |  |  |  |  | 99.7964 |  | 29283.1292
2017-09-12 | 5:06 |  |  |  |  | 98.2516 |  | 28829.8407
2017-09-12 | 5:08 |  |  |  |  | 96.313 |  | 28260.9737
2017-09-12 | 5:10 |  |  |  |  | 94.8235 |  | 27823.9112
2017-09-12 | 5:12 |  |  |  |  | 93.3927 |  | 27404.0865
2017-09-12 | 5:14 |  |  |  |  | 92.1852 |  | 27049.7771
2017-09-12 | 5:15 | 2.1344 | 0 | 0 | 1.5 | 91.6193 | 0 | 26883.7206
2017-09-12 | 5:16 |  |  |  |  | 91.1347 |  | 26741.5283
2017-09-12 | 5:18 |  |  |  |  | 90.2171 |  | 26472.2754
2017-09-12 | 5:20 |  |  |  |  | 89.3598 |  | 26220.717
2017-09-12 | 5:22 |  |  |  |  | 88.5367 |  | 25979.21
2017-09-12 | 5:24 |  |  |  |  | 87.7898 |  | 25760.025
2017-09-12 | 5:26 |  |  |  |  | 87.0482 |  | 25542.4208
2017-09-12 | 5:28 |  |  |  |  | 86.3067 |  | 25324.8567
2017-09-12 | 5:30 | 1.9566 | 0 | 0 | 1.5 | 85.6493 | 0 | 25131.9382
2017-09-12 | 5:32 |  |  |  |  | 85.0579 |  | 24958.4201
2017-09-12 | 5:34 |  |  |  |  | 84.5307 |  | 24803.736
2017-09-12 | 5:36 |  |  |  |  | 84.0113 |  | 24651.3266
2017-09-12 | 5:38 |  |  |  |  | 83.493 |  | 24499.2305
2017-09-12 | 5:40 |  |  |  |  | 83.0727 |  | 24375.8993
2017-09-12 | 5:42 |  |  |  |  | 82.6906 |  | 24263.7905
2017-09-12 | 5:44 |  |  |  |  | 82.2805 |  | 24143.439
2017-09-12 | 5:45 | 1.8575 | 0 | 0 | 1.5 | 82.1522 | 0 | 24105.8024
2017-09-12 | 5:46 |  |  |  |  | 81.9717 |  | 24052.8374
2017-09-12 | 5:48 |  |  |  |  | 81.682 |  | 23967.8434
2017-09-12 | 5:50 |  |  |  |  | 81.4218 |  | 23891.4842
2017-09-12 | 5:52 |  |  |  |  | 81.1289 |  | 23805.5234
2017-09-12 | 5:54 |  |  |  |  | 80.8895 |  | 23735.2913
2017-09-12 | 5:56 |  |  |  |  | 80.7173 |  | 23684.7532
2017-09-12 | 5:58 |  |  |  |  | 80.6262 |  | 23658.0257
2017-09-12 | 6:00 | 1.7741 | 0 | 0 | 1.5 | 80.5701 | 0 | 23641.5825
2017-09-12 | 6:02 |  |  |  |  | 80.392 |  | 23589.3003
2017-09-12 | 6:04 |  |  |  |  | 80.2881 |  | 23558.8295
2017-09-12 | 6:06 |  |  |  |  | 80.093 |  | 23501.5819
2017-09-12 | 6:08 |  |  |  |  | 79.9804 |  | 23468.5257
2017-09-12 | 6:10 |  |  |  |  | 79.8397 |  | 23427.2509
2017-09-12 | 6:12 |  |  |  |  | 79.7513 |  | 23401.3115
2017-09-12 | 6:14 |  |  |  |  | 79.7539 |  | 23402.0592
2017-09-12 | 6:15 | 1.7577 | 0 | 0 | 1.5 | 79.7536 | 0 | 23401.9964
2017-09-12 | 6:16 |  |  |  |  | 79.7656 |  | 23405.5178
2017-09-12 | 6:18 |  |  |  |  | 79.6232 |  | 23363.7283
2017-09-12 | 6:20 |  |  |  |  | 79.5221 |  | 23334.0568
2017-09-12 | 6:22 |  |  |  |  | 79.4031 |  | 23299.1268
2017-09-12 | 6:24 |  |  |  |  | 79.2702 |  | 23260.1424
2017-09-12 | 6:26 |  |  |  |  | 79.1046 |  | 23211.5586
2017-09-12 | 6:28 |  |  |  |  | 79.0915 |  | 23207.6968
2017-09-12 | 6:30 | 1.7374 | 0 | 0 | 1.5 | 79.1139 | 0 | 23214.2696
2017-09-12 | 6:32 |  |  |  |  | 79.0271 |  | 23188.8023
2017-09-12 | 6:34 |  |  |  |  | 78.9153 |  | 23156.0079
2017-09-12 | 6:36 |  |  |  |  | 78.7849 |  | 23117.7374
2017-09-12 | 6:38 |  |  |  |  | 78.6762 |  | 23085.852
2017-09-12 | 6:40 |  |  |  |  | 78.5653 |  | 23053.3081
2017-09-12 | 6:42 |  |  |  |  | 78.4979 |  | 23033.5272
2017-09-12 | 6:44 |  |  |  |  | 78.5045 |  | 23035.4592
2017-09-12 | 6:45 | 1.7631 | 0 | 0 | 1.5 | 78.4771 | 0 | 23027.4178
2017-09-12 | 6:46 |  |  |  |  | 78.5186 |  | 23039.5986
2017-09-12 | 6:48 |  |  |  |  | 78.4043 |  | 23006.0585
2017-09-12 | 6:50 |  |  |  |  | 78.3129 |  | 22979.2347
2017-09-12 | 6:52 |  |  |  |  | 78.1905 |  | 22943.3241
2017-09-12 | 6:54 |  |  |  |  | 78.0788 |  | 22910.5519
2017-09-12 | 6:56 |  |  |  |  | 77.9874 |  | 22883.7325
2017-09-12 | 6:58 |  |  |  |  | 78.0346 |  | 22897.5698
2017-09-12 | 7:00 | 1.7538 | 0 | 0 | 1.5 | 78.0722 | 0 | 22908.5997
2017-09-12 | 7:02 |  |  |  |  | 78.047 |  | 22901.23
2017-09-12 | 7:04 |  |  |  |  | 77.9878 |  | 22883.8355
2017-09-12 | 7:06 |  |  |  |  | 77.8729 |  | 22850.1479
2017-09-12 | 7:08 |  |  |  |  | 77.7965 |  | 22827.7296
2017-09-12 | 7:10 |  |  |  |  | 77.705 |  | 22800.8698
2017-09-12 | 7:12 |  |  |  |  | 77.7279 |  | 22807.5746
2017-09-12 | 7:14 |  |  |  |  | 77.7652 |  | 22818.5175
2017-09-12 | 7:15 | 1.721 | 0 | 0 | 1.5 | 77.8347 | 0 | 22838.9319
2017-09-12 | 7:16 |  |  |  |  | 77.9038 |  | 22859.2078
2017-09-12 | 7:18 |  |  |  |  | 77.8314 |  | 22837.9603
2017-09-12 | 7:20 |  |  |  |  | 77.7695 |  | 22819.8047
2017-09-12 | 7:22 |  |  |  |  | 77.7213 |  | 22805.6383
2017-09-12 | 7:24 |  |  |  |  | 77.665 |  | 22789.1438
2017-09-12 | 7:26 |  |  |  |  | 77.6434 |  | 22782.779
2017-09-12 | 7:28 |  |  |  |  | 77.7079 |  | 22801.7184
2017-09-12 | 7:30 | 1.728 | 0 | 0 | 1.5 | 77.766 | 0 | 22818.7592
2017-09-12 | 7:32 |  |  |  |  | 77.7598 |  | 22816.9438
2017-09-12 | 7:34 |  |  |  |  | 77.7561 |  | 22815.8511
2017-09-12 | 7:36 |  |  |  |  | 77.762 |  | 22817.5794
2017-09-12 | 7:38 |  |  |  |  | 77.7506 |  | 22814.246
2017-09-12 | 7:40 |  |  |  |  | 77.7365 |  | 22810.1245
2017-09-12 | 7:42 |  |  |  |  | 77.6878 |  | 22795.8196
2017-09-12 | 7:44 |  |  |  |  | 77.6158 |  | 22774.6974
2017-09-12 | 7:45 | 1.7741 | 0 | 0 | 1.5 | 77.6068 | 0 | 22772.058
2017-09-12 | 7:46 |  |  |  |  | 77.571 |  | 22761.5407
2017-09-12 | 7:48 |  |  |  |  | 77.6565 |  | 22786.6499
2017-09-12 | 7:50 |  |  |  |  | 77.7218 |  | 22805.7838
2017-09-12 | 7:52 |  |  |  |  | 77.7533 |  | 22815.0318
2017-09-12 | 7:54 |  |  |  |  | 77.7275 |  | 22807.4628
2017-09-12 | 7:56 |  |  |  |  | 77.7288 |  | 22807.8434
2017-09-12 | 7:58 |  |  |  |  | 77.6908 |  | 22796.7148
2017-09-12 | 8:00 | 1.7421 | 0 | 0 | 1.5 | 77.738 | 0 | 22810.5567
2017-09-12 | 8:02 |  |  |  |  | 77.8007 |  | 22828.9541
2017-09-12 | 8:04 |  |  |  |  | 77.8604 |  | 22846.4651
2017-09-12 | 8:06 |  |  |  |  | 77.9221 |  | 22864.5582
2017-09-12 | 8:08 |  |  |  |  | 77.9528 |  | 22873.5802
2017-09-12 | 8:10 |  |  |  |  | 78.0177 |  | 22892.6111
2017-09-12 | 8:12 |  |  |  |  | 78.1226 |  | 22923.4041
2017-09-12 | 8:14 |  |  |  |  | 78.2509 |  | 22961.0498
2017-09-12 | 8:15 | 1.7015 | 0 | 0 | 1.5 | 78.3174 | 0 | 22980.5534
2017-09-12 | 8:16 |  |  |  |  | 78.3605 |  | 22993.2219
2017-09-12 | 8:18 |  |  |  |  | 78.3488 |  | 22989.7879
2017-09-12 | 8:20 |  |  |  |  | 78.3505 |  | 22990.2759
2017-09-12 | 8:22 |  |  |  |  | 78.3736 |  | 22997.0591
2017-09-12 | 8:24 |  |  |  |  | 78.3806 |  | 22999.1119
2017-09-12 | 8:26 |  |  |  |  | 78.3993 |  | 23004.6078
2017-09-12 | 8:28 |  |  |  |  | 78.4466 |  | 23018.4788
2017-09-12 | 8:30 | 1.7358 | 0 | 0 | 1.5 | 78.467 | 0 | 23024.4673
2017-09-12 | 8:32 |  |  |  |  | 78.5238 |  | 23041.1118
2017-09-12 | 8:34 |  |  |  |  | 78.5273 |  | 23042.1438
2017-09-12 | 8:36 |  |  |  |  | 78.5625 |  | 23052.4956
2017-09-12 | 8:38 |  |  |  |  | 78.5832 |  | 23058.5491
2017-09-12 | 8:40 |  |  |  |  | 78.6698 |  | 23083.9603
2017-09-12 | 8:42 |  |  |  |  | 78.7092 |  | 23095.5275
2017-09-12 | 8:44 |  |  |  |  | 78.78 |  | 23116.307
2017-09-12 | 8:45 | 1.7374 | 0 | 0 | 1.5 | 78.8061 | 0 | 23123.9722
2017-09-12 | 8:46 |  |  |  |  | 78.8481 |  | 23136.2918
2017-09-12 | 8:48 |  |  |  |  | 78.8435 |  | 23134.9461
2017-09-12 | 8:50 |  |  |  |  | 78.8948 |  | 23149.9747
2017-09-12 | 8:52 |  |  |  |  | 78.9552 |  | 23167.7227
2017-09-12 | 8:54 |  |  |  |  | 79.0061 |  | 23182.6368
2017-09-12 | 8:56 |  |  |  |  | 79.0225 |  | 23187.4522
2017-09-12 | 8:58 |  |  |  |  | 79.0818 |  | 23204.849
2017-09-12 | 9:00 | 1.7382 | 0 | 0 | 1.5 | 79.1406 | 0 | 23222.1003
2017-09-12 | 9:02 |  |  |  |  | 79.1509 |  | 23225.1449
2017-09-12 | 9:04 |  |  |  |  | 79.1303 |  | 23219.0938
2017-09-12 | 9:06 |  |  |  |  | 79.1514 |  | 23225.2837
2017-09-12 | 9:08 |  |  |  |  | 79.1603 |  | 23227.9052
2017-09-12 | 9:10 |  |  |  |  | 79.1953 |  | 23238.172
2017-09-12 | 9:12 |  |  |  |  | 79.172 |  | 23231.3192
2017-09-12 | 9:14 |  |  |  |  | 79.2356 |  | 23249.983
2017-09-12 | 9:15 | 1.7241 | 0 | 0 | 1.5 | 79.2447 | 0 | 23252.6717
2017-09-12 | 9:16 |  |  |  |  | 79.3002 |  | 23268.9403
2017-09-12 | 9:18 |  |  |  |  | 79.3368 |  | 23279.6771
2017-09-12 | 9:20 |  |  |  |  | 79.472 |  | 23319.3689
2017-09-12 | 9:22 |  |  |  |  | 79.5824 |  | 23351.7447
2017-09-12 | 9:24 |  |  |  |  | 79.769 |  | 23406.5096
2017-09-12 | 9:26 |  |  |  |  | 80.0173 |  | 23479.3585
2017-09-12 | 9:28 |  |  |  |  | 80.1768 |  | 23526.156
2017-09-12 | 9:30 | 1.7234 | 0 | 0 | 1.5 | 80.2558 | 0 | 23549.3509
2017-09-12 | 9:32 |  |  |  |  | 80.3063 |  | 23564.1711
2017-09-12 | 9:34 |  |  |  |  | 80.4043 |  | 23592.9157
2017-09-12 | 9:36 |  |  |  |  | 80.4852 |  | 23616.6681
2017-09-12 | 9:38 |  |  |  |  | 80.5446 |  | 23634.0784
2017-09-12 | 9:40 |  |  |  |  | 80.5892 |  | 23647.1747
2017-09-12 | 9:42 |  |  |  |  | 80.7258 |  | 23687.265
2017-09-12 | 9:44 |  |  |  |  | 80.9008 |  | 23738.5936
2017-09-12 | 9:45 | 1.6914 | 0 | 0 | 1.5 | 80.9937 | 0 | 23765.8583
2017-09-12 | 9:46 |  |  |  |  | 81.0221 |  | 23774.2043
2017-09-12 | 9:48 |  |  |  |  | 81.0699 |  | 23788.2205
2017-09-12 | 9:50 |  |  |  |  | 81.1147 |  | 23801.3573
2017-09-12 | 9:52 |  |  |  |  | 81.0903 |  | 23794.2
2017-09-12 | 9:54 |  |  |  |  | 81.1574 |  | 23813.887
2017-09-12 | 9:56 |  |  |  |  | 81.2184 |  | 23831.8032
2017-09-12 | 9:58 |  |  |  |  | 81.299 |  | 23855.4459
2017-09-12 | 10:00 | 1.7187 | 0 | 0 | 1.5 | 81.4216 | 0 | 23891.415
2017-09-12 | 10:02 |  |  |  |  | 81.5483 |  | 23928.6085
2017-09-12 | 10:04 |  |  |  |  | 81.6445 |  | 23956.8225
2017-09-12 | 10:06 |  |  |  |  | 81.6833 |  | 23968.224
2017-09-12 | 10:08 |  |  |  |  | 81.6834 |  | 23968.2487
2017-09-12 | 10:10 |  |  |  |  | 81.73 |  | 23981.916
2017-09-12 | 10:12 |  |  |  |  | 81.7468 |  | 23986.8409
2017-09-12 | 10:14 |  |  |  |  | 81.8555 |  | 24018.7421
2017-09-12 | 10:15 | 1.6945 | 0 | 0 | 1.5 | 81.944 | 0 | 24044.7132
2017-09-12 | 10:16 |  |  |  |  | 81.9959 |  | 24059.9316
2017-09-12 | 10:18 |  |  |  |  | 82.1383 |  | 24101.7167
2017-09-12 | 10:20 |  |  |  |  | 82.1211 |  | 24096.6641
2017-09-12 | 10:22 |  |  |  |  | 82.1004 |  | 24090.5972
2017-09-12 | 10:24 |  |  |  |  | 82.0467 |  | 24074.8369
2017-09-12 | 10:26 |  |  |  |  | 82.0873 |  | 24086.758
2017-09-12 | 10:28 |  |  |  |  | 82.2137 |  | 24123.835
2017-09-12 | 10:30 | 1.7374 | 0 | 0 | 1.5 | 82.2675 | 0 | 24139.6265
2017-09-12 | 10:32 |  |  |  |  | 82.3204 |  | 24155.1609
2017-09-12 | 10:34 |  |  |  |  | 82.2596 |  | 24137.3298
2017-09-12 | 10:36 |  |  |  |  | 82.1769 |  | 24113.0624
2017-09-12 | 10:38 |  |  |  |  | 82.1724 |  | 24111.7437
2017-09-12 | 10:40 |  |  |  |  | 82.2365 |  | 24130.5352
2017-09-12 | 10:42 |  |  |  |  | 82.3646 |  | 24168.1407
2017-09-12 | 10:44 |  |  |  |  | 82.4261 |  | 24186.1801
2017-09-12 | 10:45 | 1.7639 | 0 | 0 | 1.5 | 82.3881 | 0 | 24175.0178
2017-09-12 | 10:46 |  |  |  |  | 82.3806 |  | 24172.8174
2017-09-12 | 10:48 |  |  |  |  | 82.3202 |  | 24155.1025
2017-09-12 | 10:50 |  |  |  |  | 82.3597 |  | 24166.6765
2017-09-12 | 10:52 |  |  |  |  | 82.408 |  | 24180.8608
2017-09-12 | 10:54 |  |  |  |  | 82.4837 |  | 24203.0619
2017-09-12 | 10:56 |  |  |  |  | 82.4832 |  | 24202.9231
2017-09-12 | 10:58 |  |  |  |  | 82.461 |  | 24196.4175
2017-09-12 | 11:00 | 1.7733 | 0 | 0 | 1.5 | 82.4282 | 0 | 24186.7934
2017-09-12 | 11:02 |  |  |  |  | 82.4673 |  | 24198.262
2017-09-12 | 11:04 |  |  |  |  | 82.6398 |  | 24248.8899
2017-09-12 | 11:06 |  |  |  |  | 82.8085 |  | 24298.3872
2017-09-12 | 11:08 |  |  |  |  | 83.0459 |  | 24368.046
2017-09-12 | 11:10 |  |  |  |  | 83.1575 |  | 24400.78
2017-09-12 | 11:12 |  |  |  |  | 83.1472 |  | 24397.7512
2017-09-12 | 11:14 |  |  |  |  | 83.1082 |  | 24386.3248
2017-09-12 | 11:15 | 1.7639 | 0 | 0 | 1.5 | 83.0713 | 0 | 24375.5052
2017-09-12 | 11:16 |  |  |  |  | 83.1093 |  | 24386.6561
2017-09-12 | 11:18 |  |  |  |  | 83.2801 |  | 24436.7534
2017-09-12 | 11:20 |  |  |  |  | 83.3967 |  | 24470.9851
2017-09-12 | 11:22 |  |  |  |  | 83.5143 |  | 24505.4856
2017-09-12 | 11:24 |  |  |  |  | 83.5761 |  | 24523.6209
2017-09-12 | 11:26 |  |  |  |  | 83.5385 |  | 24512.5754
2017-09-12 | 11:28 |  |  |  |  | 83.5993 |  | 24530.4176
2017-09-12 | 11:30 | 1.7007 | 0 | 0 | 1.5 | 83.7475 | 0 | 24573.8973
2017-09-12 | 11:32 |  |  |  |  | 83.8535 |  | 24605.0107
2017-09-12 | 11:34 |  |  |  |  | 83.8912 |  | 24616.0764
2017-09-12 | 11:36 |  |  |  |  | 83.9028 |  | 24619.4702
2017-09-12 | 11:38 |  |  |  |  | 83.9569 |  | 24635.3626
2017-09-12 | 11:40 |  |  |  |  | 84.0335 |  | 24657.8413
2017-09-12 | 11:42 |  |  |  |  | 84.1876 |  | 24703.0334
2017-09-12 | 11:44 |  |  |  |  | 84.3107 |  | 24739.1703
2017-09-12 | 11:45 | 1.7117 | 0 | 0 | 1.5 | 84.3432 | 0 | 24748.7003
2017-09-12 | 11:46 |  |  |  |  | 84.3875 |  | 24761.7138
2017-09-12 | 11:48 |  |  |  |  | 84.4175 |  | 24770.5073
2017-09-12 | 11:50 |  |  |  |  | 84.3174 |  | 24741.1313
2017-09-12 | 11:52 |  |  |  |  | 84.2441 |  | 24719.6356
2017-09-12 | 11:54 |  |  |  |  | 84.2826 |  | 24730.9141
2017-09-12 | 11:56 |  |  |  |  | 84.408 |  | 24767.7068
2017-09-12 | 11:58 |  |  |  |  | 84.4719 |  | 24786.4581
2017-09-12 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 84.5494 | 0 | 24809.2188
2017-09-12 | 12:02 |  |  |  |  | 84.5155 |  | 24799.2721
2017-09-12 | 12:04 |  |  |  |  | 84.4173 |  | 24770.4516
2017-09-12 | 12:06 |  |  |  |  | 84.4561 |  | 24781.8328
2017-09-12 | 12:08 |  |  |  |  | 84.527 |  | 24802.6304
2017-09-12 | 12:10 |  |  |  |  | 84.6076 |  | 24826.2775
2017-09-12 | 12:12 |  |  |  |  | 84.7046 |  | 24854.7377
2017-09-12 | 12:14 |  |  |  |  | 84.7532 |  | 24869.0095
2017-09-12 | 12:15 | 1.739 | 0 | 0 | 1.5 | 84.7698 | 0 | 24873.8696
2017-09-12 | 12:16 |  |  |  |  | 84.7763 |  | 24875.7904
2017-09-12 | 12:18 |  |  |  |  | 84.7997 |  | 24882.6431
2017-09-12 | 12:20 |  |  |  |  | 84.9212 |  | 24918.3143
2017-09-12 | 12:22 |  |  |  |  | 84.9313 |  | 24921.2715
2017-09-12 | 12:24 |  |  |  |  | 84.8422 |  | 24895.117
2017-09-12 | 12:26 |  |  |  |  | 84.8009 |  | 24882.9967
2017-09-12 | 12:28 |  |  |  |  | 84.853 |  | 24898.3048
2017-09-12 | 12:30 | 1.7117 | 0 | 0 | 1.5 | 84.9048 | 0 | 24913.5009
2017-09-12 | 12:32 |  |  |  |  | 84.9906 |  | 24938.6794
2017-09-12 | 12:34 |  |  |  |  | 85.0295 |  | 24950.0856
2017-09-12 | 12:36 |  |  |  |  | 85.1256 |  | 24978.2794
2017-09-12 | 12:38 |  |  |  |  | 85.0533 |  | 24957.0768
2017-09-12 | 12:40 |  |  |  |  | 84.9797 |  | 24935.4737
2017-09-12 | 12:42 |  |  |  |  | 84.93 |  | 24920.8977
2017-09-12 | 12:44 |  |  |  |  | 84.9898 |  | 24938.4265
2017-09-12 | 12:45 | 1.7124 | 0 | 0 | 1.5 | 85.0544 | 0 | 24957.3882
2017-09-12 | 12:46 |  |  |  |  | 85.1231 |  | 24977.5631
2017-09-12 | 12:48 |  |  |  |  | 85.1905 |  | 24997.3396
2017-09-12 | 12:50 |  |  |  |  | 85.2768 |  | 25022.6613
2017-09-12 | 12:52 |  |  |  |  | 85.3267 |  | 25037.289
2017-09-12 | 12:54 |  |  |  |  | 85.354 |  | 25045.2879
2017-09-12 | 12:56 |  |  |  |  | 85.2767 |  | 25022.6323
2017-09-12 | 12:58 |  |  |  |  | 85.3296 |  | 25038.1329
2017-09-12 | 13:00 | 1.7117 | 0 | 0 | 1.5 | 85.4319 | 0 | 25068.158
2017-09-12 | 13:02 |  |  |  |  | 85.4798 |  | 25082.2036
2017-09-12 | 13:04 |  |  |  |  | 85.5502 |  | 25102.8621
2017-09-12 | 13:06 |  |  |  |  | 85.6651 |  | 25136.5791
2017-09-12 | 13:08 |  |  |  |  | 85.7453 |  | 25160.1232
2017-09-12 | 13:10 |  |  |  |  | 85.8184 |  | 25181.5831
2017-09-12 | 13:12 |  |  |  |  | 85.9435 |  | 25218.2752
2017-09-12 | 13:14 |  |  |  |  | 85.9759 |  | 25227.794
2017-09-12 | 13:15 | 1.7483 | 0 | 0 | 1.5 | 85.9913 | 0 | 25232.3005
2017-09-12 | 13:16 |  |  |  |  | 85.9868 |  | 25230.9933
2017-09-12 | 13:18 |  |  |  |  | 86.0643 |  | 25253.7181
2017-09-12 | 13:20 |  |  |  |  | 86.2308 |  | 25302.5907
2017-09-12 | 13:22 |  |  |  |  | 86.3418 |  | 25335.1545
2017-09-12 | 13:24 |  |  |  |  | 86.504 |  | 25382.749
2017-09-12 | 13:26 |  |  |  |  | 86.6202 |  | 25416.8553
2017-09-12 | 13:28 |  |  |  |  | 86.7029 |  | 25441.1113
2017-09-12 | 13:30 | 1.7117 | 0 | 0 | 1.5 | 86.754 | 0 | 25456.0926
2017-09-12 | 13:32 |  |  |  |  | 86.864 |  | 25488.3744
2017-09-12 | 13:34 |  |  |  |  | 86.8414 |  | 25481.7547
2017-09-12 | 13:36 |  |  |  |  | 86.5971 |  | 25410.0677
2017-09-12 | 13:38 |  |  |  |  | 86.4021 |  | 25352.8536
2017-09-12 | 13:40 |  |  |  |  | 86.3224 |  | 25329.4503
2017-09-12 | 13:42 |  |  |  |  | 86.1856 |  | 25289.3154
2017-09-12 | 13:44 |  |  |  |  | 86.0363 |  | 25245.5089
2017-09-12 | 13:45 | 1.8287 | 0 | 0 | 1.5 | 85.9821 | 0 | 25229.6051
2017-09-12 | 13:46 |  |  |  |  | 85.8327 |  | 25185.7742
2017-09-12 | 13:48 |  |  |  |  | 85.7664 |  | 25166.2996
2017-09-12 | 13:50 |  |  |  |  | 85.7052 |  | 25148.3679
2017-09-12 | 13:52 |  |  |  |  | 85.7306 |  | 25155.8004
2017-09-12 | 13:54 |  |  |  |  | 85.8337 |  | 25186.0582
2017-09-12 | 13:56 |  |  |  |  | 85.8433 |  | 25188.8904
2017-09-12 | 13:58 |  |  |  |  | 85.8399 |  | 25187.8851
2017-09-12 | 14:00 | 1.6922 | 0 | 0 | 1.5 | 86.0064 | 0 | 25236.7445
2017-09-12 | 14:02 |  |  |  |  | 86.2203 |  | 25299.5036
2017-09-12 | 14:04 |  |  |  |  | 86.4902 |  | 25378.6835
2017-09-12 | 14:06 |  |  |  |  | 86.7053 |  | 25441.812
2017-09-12 | 14:08 |  |  |  |  | 86.9099 |  | 25501.8446
2017-09-12 | 14:10 |  |  |  |  | 87.1902 |  | 25584.1005
2017-09-12 | 14:12 |  |  |  |  | 87.5109 |  | 25678.1878
2017-09-12 | 14:14 |  |  |  |  | 87.926 |  | 25800.0079
2017-09-12 | 14:15 | 1.5986 | 0 | 0 | 1.5 | 88.1612 | 0 | 25869.0267
2017-09-12 | 14:16 |  |  |  |  | 88.3329 |  | 25919.3879
2017-09-12 | 14:18 |  |  |  |  | 88.6003 |  | 25997.8694
2017-09-12 | 14:20 |  |  |  |  | 88.6005 |  | 25997.9164
2017-09-12 | 14:22 |  |  |  |  | 88.5269 |  | 25976.3086
2017-09-12 | 14:24 |  |  |  |  | 88.3738 |  | 25931.3985
2017-09-12 | 14:26 |  |  |  |  | 88.3906 |  | 25936.3392
2017-09-12 | 14:28 |  |  |  |  | 88.4088 |  | 25941.6629
2017-09-12 | 14:30 | 1.7725 | 0 | 0 | 1.5 | 88.3059 | 0 | 25911.4764
2017-09-12 | 14:32 |  |  |  |  | 88.0795 |  | 25845.0524
2017-09-12 | 14:34 |  |  |  |  | 87.7335 |  | 25743.515
2017-09-12 | 14:36 |  |  |  |  | 87.5755 |  | 25697.1474
2017-09-12 | 14:38 |  |  |  |  | 87.387 |  | 25641.8405
2017-09-12 | 14:40 |  |  |  |  | 85.7137 |  | 25150.8594
2017-09-12 | 14:42 |  |  |  |  | 86.255 |  | 25309.6694
2017-09-12 | 14:44 |  |  |  |  | 86.1841 |  | 25288.8832
2017-09-12 | 14:45 | 1.7873 | 0 | 0 | 1.5 | 86.133 | 0 | 25273.8752
2017-09-12 | 14:46 |  |  |  |  | 86.1222 |  | 25270.7118
2017-09-12 | 14:48 |  |  |  |  | 86.1599 |  | 25281.7866
2017-09-12 | 14:50 |  |  |  |  | 86.3067 |  | 25324.8655
2017-09-12 | 14:52 |  |  |  |  | 86.5332 |  | 25391.3118
2017-09-12 | 14:54 |  |  |  |  | 86.7504 |  | 25455.0383
2017-09-12 | 14:56 |  |  |  |  | 86.992 |  | 25525.9239
2017-09-12 | 14:58 |  |  |  |  | 87.2488 |  | 25601.2778
2017-09-12 | 15:00 | 1.6633 | 0 | 0 | 1.5 | 87.5048 | 0 | 25676.4149
2017-09-12 | 15:02 |  |  |  |  | 87.6974 |  | 25732.9125
2017-09-12 | 15:04 |  |  |  |  | 88.0096 |  | 25824.5374
2017-09-12 | 15:06 |  |  |  |  | 88.3062 |  | 25911.5571
2017-09-12 | 15:08 |  |  |  |  | 88.6336 |  | 26007.6391
2017-09-12 | 15:10 |  |  |  |  | 88.9053 |  | 26087.3631
2017-09-12 | 15:12 |  |  |  |  | 89.21 |  | 26176.767
2017-09-12 | 15:14 |  |  |  |  | 89.4876 |  | 26258.2304
2017-09-12 | 15:15 | 1.6836 | 0 | 0 | 1.5 | 89.5701 | 0 | 26282.4397
2017-09-12 | 15:16 |  |  |  |  | 89.6367 |  | 26301.9609
2017-09-12 | 15:18 |  |  |  |  | 89.7094 |  | 26323.3134
2017-09-12 | 15:20 |  |  |  |  | 89.6175 |  | 26296.3238
2017-09-12 | 15:22 |  |  |  |  | 89.3775 |  | 26225.9127
2017-09-12 | 15:24 |  |  |  |  | 89.1022 |  | 26145.1389
2017-09-12 | 15:26 |  |  |  |  | 88.8893 |  | 26082.653
2017-09-12 | 15:28 |  |  |  |  | 88.6771 |  | 26020.3974
2017-09-12 | 15:30 | 1.845 | 0 | 0 | 1.5 | 88.4163 | 0 | 25943.8792
2017-09-12 | 15:32 |  |  |  |  | 88.0145 |  | 25825.9699
2017-09-12 | 15:34 |  |  |  |  | 87.7065 |  | 25735.5921
2017-09-12 | 15:36 |  |  |  |  | 87.5178 |  | 25680.2295
2017-09-12 | 15:38 |  |  |  |  | 87.1805 |  | 25581.2372
2017-09-12 | 15:40 |  |  |  |  | 86.8806 |  | 25493.2615
2017-09-12 | 15:42 |  |  |  |  | 86.5541 |  | 25397.4527
2017-09-12 | 15:44 |  |  |  |  | 86.4206 |  | 25358.287
2017-09-12 | 15:45 | 1.7592 | 0 | 0 | 1.5 | 86.397 | 0 | 25351.3627
2017-09-12 | 15:46 |  |  |  |  | 86.4108 |  | 25355.3879
2017-09-12 | 15:48 |  |  |  |  | 86.4752 |  | 25374.2844
2017-09-12 | 15:50 |  |  |  |  | 86.566 |  | 25400.9383
2017-09-12 | 15:52 |  |  |  |  | 86.7218 |  | 25446.6565
2017-09-12 | 15:54 |  |  |  |  | 86.7458 |  | 25453.6815
2017-09-12 | 15:56 |  |  |  |  | 86.8395 |  | 25481.186
2017-09-12 | 15:58 |  |  |  |  | 87.0149 |  | 25532.6534
2017-09-12 | 16:00 | 1.6906 | 0 | 0 | 1.5 | 87.2794 | 0 | 25610.2597
2017-09-12 | 16:02 |  |  |  |  | 87.4934 |  | 25673.0569
2017-09-12 | 16:04 |  |  |  |  | 87.742 |  | 25746.0088
2017-09-12 | 16:06 |  |  |  |  | 88.0958 |  | 25849.8233
2017-09-12 | 16:08 |  |  |  |  | 88.4071 |  | 25941.1793
2017-09-12 | 16:10 |  |  |  |  | 88.57 |  | 25988.973
2017-09-12 | 16:12 |  |  |  |  | 88.6407 |  | 26009.7122
2017-09-12 | 16:14 |  |  |  |  | 88.6449 |  | 26010.9546
2017-09-12 | 16:15 | 1.7967 | 0 | 0 | 1.5 | 88.5414 | 0 | 25980.5689
2017-09-12 | 16:16 |  |  |  |  | 88.4003 |  | 25939.1711
2017-09-12 | 16:18 |  |  |  |  | 88.1332 |  | 25860.8084
2017-09-12 | 16:20 |  |  |  |  | 87.974 |  | 25814.0714
2017-09-12 | 16:22 |  |  |  |  | 87.7465 |  | 25747.3228
2017-09-12 | 16:24 |  |  |  |  | 87.4069 |  | 25647.6836
2017-09-12 | 16:26 |  |  |  |  | 87.1659 |  | 25576.9523
2017-09-12 | 16:28 |  |  |  |  | 87.1525 |  | 25573.0347
2017-09-12 | 16:30 | 1.7249 | 0 | 0 | 1.5 | 87.2018 | 0 | 25587.4923
2017-09-12 | 16:32 |  |  |  |  | 87.2771 |  | 25609.588
2017-09-12 | 16:34 |  |  |  |  | 87.3627 |  | 25634.7037
2017-09-12 | 16:36 |  |  |  |  | 87.4857 |  | 25670.7958
2017-09-12 | 16:38 |  |  |  |  | 87.6152 |  | 25708.8085
2017-09-12 | 16:40 |  |  |  |  | 87.7092 |  | 25736.3982
2017-09-12 | 16:42 |  |  |  |  | 87.8722 |  | 25784.2209
2017-09-12 | 16:44 |  |  |  |  | 88.0245 |  | 25828.9094
2017-09-12 | 16:45 | 1.6968 | 0 | 0 | 1.5 | 88.1144 | 0 | 25855.2722
2017-09-12 | 16:46 |  |  |  |  | 88.1965 |  | 25879.3604
2017-09-12 | 16:48 |  |  |  |  | 88.3395 |  | 25921.3333
2017-09-12 | 16:50 |  |  |  |  | 88.4477 |  | 25953.0958
2017-09-12 | 16:52 |  |  |  |  | 88.6068 |  | 25999.7814
2017-09-12 | 16:54 |  |  |  |  | 88.7492 |  | 26041.5642
2017-09-12 | 16:56 |  |  |  |  | 88.9223 |  | 26092.344
2017-09-12 | 16:58 |  |  |  |  | 89.0384 |  | 26126.4237
2017-09-12 | 17:00 | 1.7234 | 0 | 0 | 1.5 | 89.1827 | 0 | 26168.7549
2017-09-12 | 17:02 |  |  |  |  | 89.13 |  | 26153.2877
2017-09-12 | 17:04 |  |  |  |  | 88.9449 |  | 26098.984
2017-09-12 | 17:06 |  |  |  |  | 88.6123 |  | 26001.3888
2017-09-12 | 17:08 |  |  |  |  | 88.2822 |  | 25904.5342
2017-09-12 | 17:10 |  |  |  |  | 88.0671 |  | 25841.4124
2017-09-12 | 17:12 |  |  |  |  | 87.7994 |  | 25762.866
2017-09-12 | 17:14 |  |  |  |  | 87.3344 |  | 25626.4071
2017-09-12 | 17:15 | 1.934 | 0 | 0 | 1.5 | 87.0456 | 0 | 25541.6596
2017-09-12 | 17:16 |  |  |  |  | 86.8008 |  | 25469.8403
2017-09-12 | 17:18 |  |  |  |  | 86.5281 |  | 25389.8188
2017-09-12 | 17:20 |  |  |  |  | 86.2584 |  | 25310.6747
2017-09-12 | 17:22 |  |  |  |  | 86.0423 |  | 25247.2797
2017-09-12 | 17:24 |  |  |  |  | 85.9227 |  | 25212.186
2017-09-12 | 17:26 |  |  |  |  | 85.8327 |  | 25185.7762
2017-09-12 | 17:28 |  |  |  |  | 85.7474 |  | 25160.7253
2017-09-12 | 17:30 | 1.7608 | 0 | 0 | 1.5 | 85.724 | 0 | 25153.8729
2017-09-12 | 17:32 |  |  |  |  | 85.6383 |  | 25128.719
2017-09-12 | 17:34 |  |  |  |  | 85.6186 |  | 25122.9341
2017-09-12 | 17:36 |  |  |  |  | 85.6544 |  | 25133.4562
2017-09-12 | 17:38 |  |  |  |  | 85.7449 |  | 25160.0047
2017-09-12 | 17:40 |  |  |  |  | 85.7956 |  | 25174.8715
2017-09-12 | 17:42 |  |  |  |  | 85.847 |  | 25189.9602
2017-09-12 | 17:44 |  |  |  |  | 85.9377 |  | 25216.5783
2017-09-12 | 17:45 | 1.7296 | 0 | 0 | 1.5 | 85.9529 | 0 | 25221.0287
2017-09-12 | 17:46 |  |  |  |  | 85.9951 |  | 25233.4243
2017-09-12 | 17:48 |  |  |  |  | 86.0618 |  | 25253.0039
2017-09-12 | 17:50 |  |  |  |  | 86.1523 |  | 25279.5457
2017-09-12 | 17:52 |  |  |  |  | 86.1383 |  | 25275.4354
2017-09-12 | 17:54 |  |  |  |  | 86.0808 |  | 25258.5738
2017-09-12 | 17:56 |  |  |  |  | 86.0869 |  | 25260.3534
2017-09-12 | 17:58 |  |  |  |  | 86.1574 |  | 25281.0346
2017-09-12 | 18:00 | 1.7218 | 0 | 0 | 1.5 | 86.2553 | 0 | 25309.7589
2017-09-12 | 18:02 |  |  |  |  | 86.306 |  | 25324.6439
2017-09-12 | 18:04 |  |  |  |  | 86.3548 |  | 25338.9603
2017-09-12 | 18:06 |  |  |  |  | 86.3653 |  | 25342.0542
2017-09-12 | 18:08 |  |  |  |  | 86.3828 |  | 25347.1696
2017-09-12 | 18:10 |  |  |  |  | 86.3392 |  | 25334.389
2017-09-12 | 18:12 |  |  |  |  | 86.2567 |  | 25310.1732
2017-09-12 | 18:14 |  |  |  |  | 86.1689 |  | 25284.4037
2017-09-12 | 18:15 | 1.7709 | 0 | 0 | 1.5 | 86.1544 | 0 | 25280.1748
2017-09-12 | 18:16 |  |  |  |  | 86.1958 |  | 25292.3219
2017-09-12 | 18:18 |  |  |  |  | 86.1875 |  | 25289.875
2017-09-12 | 18:20 |  |  |  |  | 86.1584 |  | 25281.3254
2017-09-12 | 18:22 |  |  |  |  | 86.1535 |  | 25279.9108
2017-09-12 | 18:24 |  |  |  |  | 86.0918 |  | 25261.7974
2017-09-12 | 18:26 |  |  |  |  | 86.0323 |  | 25244.3469
2017-09-12 | 18:28 |  |  |  |  | 85.8449 |  | 25189.3426
2017-09-12 | 18:30 | 1.8209 | 0 | 0 | 1.5 | 85.6113 | 0 | 25120.8097
2017-09-12 | 18:32 |  |  |  |  | 85.4251 |  | 25066.1768
2017-09-12 | 18:34 |  |  |  |  | 85.3526 |  | 25044.8938
2017-09-12 | 18:36 |  |  |  |  | 85.2405 |  | 25011.9896
2017-09-12 | 18:38 |  |  |  |  | 85.1296 |  | 24979.466
2017-09-12 | 18:40 |  |  |  |  | 85.04 |  | 24953.1549
2017-09-12 | 18:42 |  |  |  |  | 84.8487 |  | 24897.0466
2017-09-12 | 18:44 |  |  |  |  | 84.6424 |  | 24836.5014
2017-09-12 | 18:45 | 1.8357 | 0 | 0 | 1.5 | 84.5172 | 0 | 24799.7671
2017-09-12 | 18:46 |  |  |  |  | 84.4518 |  | 24780.5792
2017-09-12 | 18:48 |  |  |  |  | 84.391 |  | 24762.7438
2017-09-12 | 18:50 |  |  |  |  | 84.2485 |  | 24720.9026
2017-09-12 | 18:52 |  |  |  |  | 84.1277 |  | 24685.4732
2017-09-12 | 18:54 |  |  |  |  | 83.8745 |  | 24611.1782
2017-09-12 | 18:56 |  |  |  |  | 83.649 |  | 24545.0004
2017-09-12 | 18:58 |  |  |  |  | 83.442 |  | 24484.2695
2017-09-12 | 19:00 | 1.8092 | 0 | 0 | 1.5 | 83.3058 | 0 | 24444.291
2017-09-12 | 19:02 |  |  |  |  | 83.259 |  | 24430.5835
2017-09-12 | 19:04 |  |  |  |  | 83.1444 |  | 24396.9563
2017-09-12 | 19:06 |  |  |  |  | 82.9244 |  | 24332.4017
2017-09-12 | 19:08 |  |  |  |  | 82.683 |  | 24261.5654
2017-09-12 | 19:10 |  |  |  |  | 82.5255 |  | 24215.3255
2017-09-12 | 19:12 |  |  |  |  | 82.3949 |  | 24177.0216
2017-09-12 | 19:14 |  |  |  |  | 82.3271 |  | 24157.1242
2017-09-12 | 19:15 | 1.7912 | 0 | 0 | 1.5 | 82.2898 | 0 | 24146.1814
2017-09-12 | 19:16 |  |  |  |  | 82.2192 |  | 24125.4668
2017-09-12 | 19:18 |  |  |  |  | 82.0297 |  | 24069.8536
2017-09-12 | 19:20 |  |  |  |  | 81.8421 |  | 24014.8087
2017-09-12 | 19:22 |  |  |  |  | 81.6766 |  | 23966.2451
2017-09-12 | 19:24 |  |  |  |  | 81.6122 |  | 23947.3395
2017-09-12 | 19:26 |  |  |  |  | 81.6063 |  | 23945.6068
2017-09-12 | 19:28 |  |  |  |  | 81.5081 |  | 23916.8059
2017-09-12 | 19:30 | 1.7881 | 0 | 0 | 1.5 | 81.4191 | 0 | 23890.6829
2017-09-12 | 19:32 |  |  |  |  | 81.2016 |  | 23826.8803
2017-09-12 | 19:34 |  |  |  |  | 81.0859 |  | 23792.9151
2017-09-12 | 19:36 |  |  |  |  | 81.0158 |  | 23772.3552
2017-09-12 | 19:38 |  |  |  |  | 80.9634 |  | 23756.9798
2017-09-12 | 19:40 |  |  |  |  | 80.9099 |  | 23741.2866
2017-09-12 | 19:42 |  |  |  |  | 80.7642 |  | 23698.5121
2017-09-12 | 19:44 |  |  |  |  | 80.6393 |  | 23661.8649
2017-09-12 | 19:45 | 1.785 | 0 | 0 | 1.5 | 80.5902 | 0 | 23647.4746
2017-09-12 | 19:46 |  |  |  |  | 80.5737 |  | 23642.6345
2017-09-12 | 19:48 |  |  |  |  | 80.4194 |  | 23597.3573
2017-09-12 | 19:50 |  |  |  |  | 80.3905 |  | 23588.8614
2017-09-12 | 19:52 |  |  |  |  | 80.4237 |  | 23598.5997
2017-09-12 | 19:54 |  |  |  |  | 80.3501 |  | 23577.0256
2017-09-12 | 19:56 |  |  |  |  | 80.2526 |  | 23548.4108
2017-09-12 | 19:58 |  |  |  |  | 80.1205 |  | 23509.648
2017-09-12 | 20:00 | 1.7787 | 0 | 0 | 1.5 | 80.0295 | 0 | 23482.9495
2017-09-12 | 20:02 |  |  |  |  | 79.9572 |  | 23461.7179
2017-09-12 | 20:04 |  |  |  |  | 79.9048 |  | 23446.3402
2017-09-12 | 20:06 |  |  |  |  | 79.8823 |  | 23439.7474
2017-09-12 | 20:08 |  |  |  |  | 79.9017 |  | 23445.447
2017-09-12 | 20:10 |  |  |  |  | 79.858 |  | 23432.6083
2017-09-12 | 20:12 |  |  |  |  | 79.7336 |  | 23396.1064
2017-09-12 | 20:14 |  |  |  |  | 79.6466 |  | 23370.5878
2017-09-12 | 20:15 | 1.767 | 0 | 0 | 1.5 | 79.5742 | 0 | 23349.3562
2017-09-12 | 20:16 |  |  |  |  | 79.5621 |  | 23345.7922
2017-09-12 | 20:18 |  |  |  |  | 79.5211 |  | 23333.7593
2017-09-12 | 20:20 |  |  |  |  | 79.5559 |  | 23343.9653
2017-09-12 | 20:22 |  |  |  |  | 79.5319 |  | 23336.9248
2017-09-12 | 20:24 |  |  |  |  | 79.4494 |  | 23312.738
2017-09-12 | 20:26 |  |  |  |  | 79.3628 |  | 23287.3086
2017-09-12 | 20:28 |  |  |  |  | 79.2509 |  | 23254.4919
2017-09-12 | 20:30 | 1.778 | 0 | 0 | 1.5 | 79.2084 | 0 | 23242.0179
2017-09-12 | 20:32 |  |  |  |  | 79.1039 |  | 23211.3323
2017-09-12 | 20:34 |  |  |  |  | 79.0522 |  | 23196.163
2017-09-12 | 20:36 |  |  |  |  | 79.0309 |  | 23189.9214
2017-09-12 | 20:38 |  |  |  |  | 79.0431 |  | 23193.4922
2017-09-12 | 20:40 |  |  |  |  | 79.0048 |  | 23182.2518
2017-09-12 | 20:42 |  |  |  |  | 78.8575 |  | 23139.0497
2017-09-12 | 20:44 |  |  |  |  | 78.719 |  | 23098.4131
2017-09-12 | 20:45 | 1.7943 | 0 | 0 | 1.5 | 78.6677 | 0 | 23083.3467
2017-09-12 | 20:46 |  |  |  |  | 78.6333 |  | 23073.2528
2017-09-12 | 20:48 |  |  |  |  | 78.5425 |  | 23046.6259
2017-09-12 | 20:50 |  |  |  |  | 78.4099 |  | 23007.7085
2017-09-12 | 20:52 |  |  |  |  | 78.4216 |  | 23011.1313
2017-09-12 | 20:54 |  |  |  |  | 78.4757 |  | 23027.0037
2017-09-12 | 20:56 |  |  |  |  | 78.5894 |  | 23060.3757
2017-09-12 | 20:58 |  |  |  |  | 78.6198 |  | 23069.2836
2017-09-12 | 21:00 | 1.7257 | 0 | 0 | 1.5 | 78.6561 | 0 | 23079.9576
2017-09-12 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-12 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:45 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 5:00 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 5:02 |  |  |  |  | 69.625 |  | 20429.9643
2017-09-13 | 5:04 |  |  |  |  | 99.3337 |  | 29147.3439
2017-09-13 | 5:06 |  |  |  |  | 96.988 |  | 28459.0567
2017-09-13 | 5:08 |  |  |  |  | 94.466 |  | 27719.0223
2017-09-13 | 5:10 |  |  |  |  | 92.4839 |  | 27137.4236
2017-09-13 | 5:12 |  |  |  |  | 90.855 |  | 26659.4449
2017-09-13 | 5:14 |  |  |  |  | 89.4818 |  | 26256.5156
2017-09-13 | 5:15 | 2.1531 | 0 | 0 | 1.5 | 88.8511 | 0 | 26071.437
2017-09-13 | 5:16 |  |  |  |  | 88.2553 |  | 25896.6339
2017-09-13 | 5:18 |  |  |  |  | 87.2758 |  | 25609.223
2017-09-13 | 5:20 |  |  |  |  | 86.4241 |  | 25359.3078
2017-09-13 | 5:22 |  |  |  |  | 85.7087 |  | 25149.3708
2017-09-13 | 5:24 |  |  |  |  | 85.1228 |  | 24977.476
2017-09-13 | 5:26 |  |  |  |  | 84.6058 |  | 24825.7447
2017-09-13 | 5:28 |  |  |  |  | 84.2044 |  | 24707.9833
2017-09-13 | 5:30 | 1.8887 | 0 | 0 | 1.5 | 83.8273 | 0 | 24597.3208
2017-09-13 | 5:32 |  |  |  |  | 83.5164 |  | 24506.1012
2017-09-13 | 5:34 |  |  |  |  | 83.2324 |  | 24422.7639
2017-09-13 | 5:36 |  |  |  |  | 83.0119 |  | 24358.075
2017-09-13 | 5:38 |  |  |  |  | 82.844 |  | 24308.8083
2017-09-13 | 5:40 |  |  |  |  | 82.6654 |  | 24256.3805
2017-09-13 | 5:42 |  |  |  |  | 82.5406 |  | 24219.7624
2017-09-13 | 5:44 |  |  |  |  | 82.4023 |  | 24179.1862
2017-09-13 | 5:45 | 1.8021 | 0 | 0 | 1.5 | 82.4013 | 0 | 24178.8908
2017-09-13 | 5:46 |  |  |  |  | 82.3715 |  | 24170.1621
2017-09-13 | 5:48 |  |  |  |  | 82.2614 |  | 24137.8377
2017-09-13 | 5:50 |  |  |  |  | 82.2015 |  | 24120.2775
2017-09-13 | 5:52 |  |  |  |  | 82.1174 |  | 24095.6008
2017-09-13 | 5:54 |  |  |  |  | 82.0938 |  | 24088.6673
2017-09-13 | 5:56 |  |  |  |  | 82.0563 |  | 24077.662
2017-09-13 | 5:58 |  |  |  |  | 82.013 |  | 24064.9642
2017-09-13 | 6:00 | 1.7748 | 0 | 0 | 1.5 | 82.0158 | 0 | 24065.7837
2017-09-13 | 6:02 |  |  |  |  | 81.9947 |  | 24059.5959
2017-09-13 | 6:04 |  |  |  |  | 81.9808 |  | 24055.5081
2017-09-13 | 6:06 |  |  |  |  | 81.9836 |  | 24056.3274
2017-09-13 | 6:08 |  |  |  |  | 81.9616 |  | 24049.8778
2017-09-13 | 6:10 |  |  |  |  | 81.9546 |  | 24047.8294
2017-09-13 | 6:12 |  |  |  |  | 82.0024 |  | 24061.8547
2017-09-13 | 6:14 |  |  |  |  | 81.9737 |  | 24053.4395
2017-09-13 | 6:15 | 1.7514 | 0 | 0 | 1.5 | 81.9764 | 0 | 24054.2276
2017-09-13 | 6:16 |  |  |  |  | 82.0105 |  | 24064.2121
2017-09-13 | 6:18 |  |  |  |  | 81.9613 |  | 24049.7971
2017-09-13 | 6:20 |  |  |  |  | 81.9909 |  | 24058.4721
2017-09-13 | 6:22 |  |  |  |  | 81.9919 |  | 24058.7632
2017-09-13 | 6:24 |  |  |  |  | 81.9743 |  | 24053.5985
2017-09-13 | 6:26 |  |  |  |  | 81.9941 |  | 24059.4011
2017-09-13 | 6:28 |  |  |  |  | 81.9685 |  | 24051.9128
2017-09-13 | 6:30 | 1.7655 | 0 | 0 | 1.5 | 81.976 | 0 | 24054.1
2017-09-13 | 6:32 |  |  |  |  | 81.9755 |  | 24053.95
2017-09-13 | 6:34 |  |  |  |  | 81.9842 |  | 24056.4976
2017-09-13 | 6:36 |  |  |  |  | 82.0038 |  | 24062.2444
2017-09-13 | 6:38 |  |  |  |  | 81.9911 |  | 24058.5281
2017-09-13 | 6:40 |  |  |  |  | 81.9857 |  | 24056.9477
2017-09-13 | 6:42 |  |  |  |  | 82.0215 |  | 24067.4381
2017-09-13 | 6:44 |  |  |  |  | 82.0311 |  | 24070.2811
2017-09-13 | 6:45 | 1.7319 | 0 | 0 | 1.5 | 82.0032 | 0 | 24062.0942
2017-09-13 | 6:46 |  |  |  |  | 82.0019 |  | 24061.6892
2017-09-13 | 6:48 |  |  |  |  | 82.0526 |  | 24076.5875
2017-09-13 | 6:50 |  |  |  |  | 82.0346 |  | 24071.2864
2017-09-13 | 6:52 |  |  |  |  | 82.0584 |  | 24078.2756
2017-09-13 | 6:54 |  |  |  |  | 82.0512 |  | 24076.1599
2017-09-13 | 6:56 |  |  |  |  | 82.0838 |  | 24085.7213
2017-09-13 | 6:58 |  |  |  |  | 82.1022 |  | 24091.1368
2017-09-13 | 7:00 | 1.7468 | 0 | 0 | 1.5 | 82.1294 | 0 | 24099.1222
2017-09-13 | 7:02 |  |  |  |  | 82.1361 |  | 24101.0855
2017-09-13 | 7:04 |  |  |  |  | 82.1497 |  | 24105.0703
2017-09-13 | 7:06 |  |  |  |  | 82.1905 |  | 24117.0337
2017-09-13 | 7:08 |  |  |  |  | 82.2278 |  | 24127.9788
2017-09-13 | 7:10 |  |  |  |  | 82.2295 |  | 24128.478
2017-09-13 | 7:12 |  |  |  |  | 82.2823 |  | 24143.983
2017-09-13 | 7:14 |  |  |  |  | 82.3022 |  | 24149.8102
2017-09-13 | 7:15 | 1.7483 | 0 | 0 | 1.5 | 82.3065 | 0 | 24151.0907
2017-09-13 | 7:16 |  |  |  |  | 82.3563 |  | 24165.6871
2017-09-13 | 7:18 |  |  |  |  | 82.3782 |  | 24172.1187
2017-09-13 | 7:20 |  |  |  |  | 82.4011 |  | 24178.8283
2017-09-13 | 7:22 |  |  |  |  | 82.4047 |  | 24179.8825
2017-09-13 | 7:24 |  |  |  |  | 82.4937 |  | 24206.008
2017-09-13 | 7:26 |  |  |  |  | 82.5298 |  | 24216.5902
2017-09-13 | 7:28 |  |  |  |  | 82.5664 |  | 24227.3426
2017-09-13 | 7:30 | 1.7257 | 0 | 0 | 1.5 | 82.6712 | 0 | 24258.1021
2017-09-13 | 7:32 |  |  |  |  | 82.7106 |  | 24269.6494
2017-09-13 | 7:34 |  |  |  |  | 82.8413 |  | 24308.0181
2017-09-13 | 7:36 |  |  |  |  | 82.9524 |  | 24340.6066
2017-09-13 | 7:38 |  |  |  |  | 83.0592 |  | 24371.948
2017-09-13 | 7:40 |  |  |  |  | 83.1953 |  | 24411.8751
2017-09-13 | 7:42 |  |  |  |  | 83.3069 |  | 24444.6223
2017-09-13 | 7:44 |  |  |  |  | 83.4557 |  | 24488.2901
2017-09-13 | 7:45 | 1.7046 | 0 | 0 | 1.5 | 83.5108 | 0 | 24504.4624
2017-09-13 | 7:46 |  |  |  |  | 83.5421 |  | 24513.6253
2017-09-13 | 7:48 |  |  |  |  | 83.7121 |  | 24563.5122
2017-09-13 | 7:50 |  |  |  |  | 83.9471 |  | 24632.4905
2017-09-13 | 7:52 |  |  |  |  | 84.1271 |  | 24685.283
2017-09-13 | 7:54 |  |  |  |  | 84.3589 |  | 24753.3256
2017-09-13 | 7:56 |  |  |  |  | 84.5665 |  | 24814.2334
2017-09-13 | 7:58 |  |  |  |  | 84.8012 |  | 24883.0818
2017-09-13 | 8:00 | 1.6867 | 0 | 0 | 1.5 | 85.0005 | 0 | 24941.5606
2017-09-13 | 8:02 |  |  |  |  | 85.2134 |  | 25004.0603
2017-09-13 | 8:04 |  |  |  |  | 85.4309 |  | 25067.8625
2017-09-13 | 8:06 |  |  |  |  | 85.711 |  | 25150.0425
2017-09-13 | 8:08 |  |  |  |  | 85.938 |  | 25216.6543
2017-09-13 | 8:10 |  |  |  |  | 86.1846 |  | 25289.0311
2017-09-13 | 8:12 |  |  |  |  | 86.4171 |  | 25357.255
2017-09-13 | 8:14 |  |  |  |  | 86.681 |  | 25434.6887
2017-09-13 | 8:15 | 1.6586 | 0 | 0 | 1.5 | 86.8131 | 0 | 25473.4424
2017-09-13 | 8:16 |  |  |  |  | 86.9309 |  | 25508.0165
2017-09-13 | 8:18 |  |  |  |  | 87.2012 |  | 25587.313
2017-09-13 | 8:20 |  |  |  |  | 87.4532 |  | 25661.279
2017-09-13 | 8:22 |  |  |  |  | 87.758 |  | 25750.7189
2017-09-13 | 8:24 |  |  |  |  | 88.0534 |  | 25837.3716
2017-09-13 | 8:26 |  |  |  |  | 88.3613 |  | 25927.7247
2017-09-13 | 8:28 |  |  |  |  | 88.4086 |  | 25941.6227
2017-09-13 | 8:30 | 1.7343 | 0 | 0 | 1.5 | 88.4399 | 0 | 25950.8055
2017-09-13 | 8:32 |  |  |  |  | 88.4026 |  | 25939.834
2017-09-13 | 8:34 |  |  |  |  | 88.2537 |  | 25896.1683
2017-09-13 | 8:36 |  |  |  |  | 88.0164 |  | 25826.5341
2017-09-13 | 8:38 |  |  |  |  | 87.7171 |  | 25738.7083
2017-09-13 | 8:40 |  |  |  |  | 87.4173 |  | 25650.7326
2017-09-13 | 8:42 |  |  |  |  | 86.9751 |  | 25520.9808
2017-09-13 | 8:44 |  |  |  |  | 86.4423 |  | 25364.6538
2017-09-13 | 8:45 | 1.9004 | 0 | 0 | 1.5 | 86.2344 | 0 | 25303.6318
2017-09-13 | 8:46 |  |  |  |  | 85.9763 |  | 25227.8994
2017-09-13 | 8:48 |  |  |  |  | 85.5539 |  | 25103.9636
2017-09-13 | 8:50 |  |  |  |  | 85.1892 |  | 24996.9388
2017-09-13 | 8:52 |  |  |  |  | 84.7814 |  | 24877.2836
2017-09-13 | 8:54 |  |  |  |  | 84.4865 |  | 24790.7474
2017-09-13 | 8:56 |  |  |  |  | 84.2379 |  | 24717.8087
2017-09-13 | 8:58 |  |  |  |  | 84.0329 |  | 24657.6465
2017-09-13 | 9:00 | 1.8146 | 0 | 0 | 1.5 | 83.9438 | 0 | 24631.5099
2017-09-13 | 9:02 |  |  |  |  | 83.8082 |  | 24591.706
2017-09-13 | 9:04 |  |  |  |  | 83.5425 |  | 24513.7485
2017-09-13 | 9:06 |  |  |  |  | 83.35 |  | 24457.2755
2017-09-13 | 9:08 |  |  |  |  | 83.1158 |  | 24388.5569
2017-09-13 | 9:10 |  |  |  |  | 82.9887 |  | 24351.2695
2017-09-13 | 9:12 |  |  |  |  | 82.8666 |  | 24315.4416
2017-09-13 | 9:14 |  |  |  |  | 82.7775 |  | 24289.2803
2017-09-13 | 9:15 | 1.7725 | 0 | 0 | 1.5 | 82.7432 | 0 | 24279.2152
2017-09-13 | 9:16 |  |  |  |  | 82.7162 |  | 24271.3081
2017-09-13 | 9:18 |  |  |  |  | 82.6134 |  | 24241.1308
2017-09-13 | 9:20 |  |  |  |  | 82.528 |  | 24216.0819
2017-09-13 | 9:22 |  |  |  |  | 82.5145 |  | 24212.1107
2017-09-13 | 9:24 |  |  |  |  | 82.5392 |  | 24219.3707
2017-09-13 | 9:26 |  |  |  |  | 82.5258 |  | 24215.4285
2017-09-13 | 9:28 |  |  |  |  | 82.4531 |  | 24194.0983
2017-09-13 | 9:30 | 1.7967 | 0 | 0 | 1.5 | 82.3686 | 0 | 24169.3115
2017-09-13 | 9:32 |  |  |  |  | 82.317 |  | 24154.1735
2017-09-13 | 9:34 |  |  |  |  | 82.1797 |  | 24113.8817
2017-09-13 | 9:36 |  |  |  |  | 82.1509 |  | 24105.4151
2017-09-13 | 9:38 |  |  |  |  | 82.1022 |  | 24091.1254
2017-09-13 | 9:40 |  |  |  |  | 82.0403 |  | 24072.961
2017-09-13 | 9:42 |  |  |  |  | 82.0523 |  | 24076.4912
2017-09-13 | 9:44 |  |  |  |  | 82.0967 |  | 24089.5068
2017-09-13 | 9:45 | 1.7436 | 0 | 0 | 1.5 | 82.092 | 0 | 24088.1412
2017-09-13 | 9:46 |  |  |  |  | 82.0852 |  | 24086.1377
2017-09-13 | 9:48 |  |  |  |  | 81.975 |  | 24053.7954
2017-09-13 | 9:50 |  |  |  |  | 81.9667 |  | 24051.3711
2017-09-13 | 9:52 |  |  |  |  | 81.9151 |  | 24036.2419
2017-09-13 | 9:54 |  |  |  |  | 81.8825 |  | 24026.6627
2017-09-13 | 9:56 |  |  |  |  | 81.8514 |  | 24017.5268
2017-09-13 | 9:58 |  |  |  |  | 81.7737 |  | 23994.7256
2017-09-13 | 10:00 | 1.7397 | 0 | 0 | 1.5 | 81.8395 | 0 | 24014.059
2017-09-13 | 10:02 |  |  |  |  | 81.8902 |  | 24028.935
2017-09-13 | 10:04 |  |  |  |  | 81.9424 |  | 24044.2543
2017-09-13 | 10:06 |  |  |  |  | 81.9107 |  | 24034.9414
2017-09-13 | 10:08 |  |  |  |  | 81.8275 |  | 24010.5129
2017-09-13 | 10:10 |  |  |  |  | 81.8266 |  | 24010.2665
2017-09-13 | 10:12 |  |  |  |  | 81.8424 |  | 24014.8871
2017-09-13 | 10:14 |  |  |  |  | 81.8928 |  | 24029.6759
2017-09-13 | 10:15 | 1.739 | 0 | 0 | 1.5 | 81.8545 | 0 | 24018.4534
2017-09-13 | 10:16 |  |  |  |  | 81.8583 |  | 24019.5772
2017-09-13 | 10:18 |  |  |  |  | 81.9073 |  | 24033.9429
2017-09-13 | 10:20 |  |  |  |  | 82.0428 |  | 24073.6884
2017-09-13 | 10:22 |  |  |  |  | 82.0775 |  | 24083.8721
2017-09-13 | 10:24 |  |  |  |  | 82.0979 |  | 24089.883
2017-09-13 | 10:26 |  |  |  |  | 82.1022 |  | 24091.1301
2017-09-13 | 10:28 |  |  |  |  | 82.0804 |  | 24084.7407
2017-09-13 | 10:30 | 1.7366 | 0 | 0 | 1.5 | 82.0901 | 0 | 24087.5661
2017-09-13 | 10:32 |  |  |  |  | 82.1942 |  | 24118.1149
2017-09-13 | 10:34 |  |  |  |  | 82.2833 |  | 24144.2765
2017-09-13 | 10:36 |  |  |  |  | 82.4472 |  | 24192.3609
2017-09-13 | 10:38 |  |  |  |  | 82.431 |  | 24187.5971
2017-09-13 | 10:40 |  |  |  |  | 82.4175 |  | 24183.6502
2017-09-13 | 10:42 |  |  |  |  | 82.3515 |  | 24164.2812
2017-09-13 | 10:44 |  |  |  |  | 82.2932 |  | 24147.1823
2017-09-13 | 10:45 | 1.7483 | 0 | 0 | 1.5 | 82.2747 | 0 | 24141.76
2017-09-13 | 10:46 |  |  |  |  | 82.2693 |  | 24140.1729
2017-09-13 | 10:48 |  |  |  |  | 82.2358 |  | 24130.3383
2017-09-13 | 10:50 |  |  |  |  | 82.2857 |  | 24144.9637
2017-09-13 | 10:52 |  |  |  |  | 82.3251 |  | 24156.5512
2017-09-13 | 10:54 |  |  |  |  | 82.2539 |  | 24135.635
2017-09-13 | 10:56 |  |  |  |  | 82.2315 |  | 24129.0601
2017-09-13 | 10:58 |  |  |  |  | 82.166 |  | 24109.8587
2017-09-13 | 11:00 | 1.778 | 0 | 0 | 1.5 | 82.0966 | 0 | 24089.4757
2017-09-13 | 11:02 |  |  |  |  | 82.0295 |  | 24069.7999
2017-09-13 | 11:04 |  |  |  |  | 82.1364 |  | 24101.1571
2017-09-13 | 11:06 |  |  |  |  | 82.1112 |  | 24093.7762
2017-09-13 | 11:08 |  |  |  |  | 82.0025 |  | 24061.8885
2017-09-13 | 11:10 |  |  |  |  | 81.9178 |  | 24037.0257
2017-09-13 | 11:12 |  |  |  |  | 81.8882 |  | 24028.3282
2017-09-13 | 11:14 |  |  |  |  | 82.014 |  | 24065.262
2017-09-13 | 11:15 | 1.7374 | 0 | 0 | 1.5 | 82.0317 | 0 | 24070.4557
2017-09-13 | 11:16 |  |  |  |  | 82.0577 |  | 24078.0875
2017-09-13 | 11:18 |  |  |  |  | 82.0687 |  | 24081.2932
2017-09-13 | 11:20 |  |  |  |  | 81.9834 |  | 24056.2805
2017-09-13 | 11:22 |  |  |  |  | 81.9432 |  | 24044.4738
2017-09-13 | 11:24 |  |  |  |  | 81.9225 |  | 24038.4001
2017-09-13 | 11:26 |  |  |  |  | 82.0291 |  | 24069.6925
2017-09-13 | 11:28 |  |  |  |  | 82.0246 |  | 24068.3583
2017-09-13 | 11:30 | 1.7585 | 0 | 0 | 1.5 | 81.9817 | 0 | 24055.7813
2017-09-13 | 11:32 |  |  |  |  | 81.942 |  | 24044.1131
2017-09-13 | 11:34 |  |  |  |  | 81.9793 |  | 24055.058
2017-09-13 | 11:36 |  |  |  |  | 81.8829 |  | 24026.7791
2017-09-13 | 11:38 |  |  |  |  | 81.8536 |  | 24018.1914
2017-09-13 | 11:40 |  |  |  |  | 81.8278 |  | 24010.6092
2017-09-13 | 11:42 |  |  |  |  | 81.8219 |  | 24008.8897
2017-09-13 | 11:44 |  |  |  |  | 81.7189 |  | 23978.6742
2017-09-13 | 11:45 | 1.7608 | 0 | 0 | 1.5 | 81.7136 | 0 | 23977.114
2017-09-13 | 11:46 |  |  |  |  | 81.6629 |  | 23962.2401
2017-09-13 | 11:48 |  |  |  |  | 81.6881 |  | 23969.6366
2017-09-13 | 11:50 |  |  |  |  | 81.8054 |  | 24004.0384
2017-09-13 | 11:52 |  |  |  |  | 81.9449 |  | 24044.9638
2017-09-13 | 11:54 |  |  |  |  | 82.0477 |  | 24075.1526
2017-09-13 | 11:56 |  |  |  |  | 82.0361 |  | 24071.743
2017-09-13 | 11:58 |  |  |  |  | 81.9982 |  | 24060.6279
2017-09-13 | 12:00 | 1.7608 | 0 | 0 | 1.5 | 81.9742 | 0 | 24053.5739
2017-09-13 | 12:02 |  |  |  |  | 82.0597 |  | 24078.6673
2017-09-13 | 12:04 |  |  |  |  | 82.2272 |  | 24127.8198
2017-09-13 | 12:06 |  |  |  |  | 82.3573 |  | 24165.9869
2017-09-13 | 12:08 |  |  |  |  | 82.4757 |  | 24200.7224
2017-09-13 | 12:10 |  |  |  |  | 82.4993 |  | 24207.6623
2017-09-13 | 12:12 |  |  |  |  | 82.4919 |  | 24205.4707
2017-09-13 | 12:14 |  |  |  |  | 82.4932 |  | 24205.8624
2017-09-13 | 12:15 | 1.7639 | 0 | 0 | 1.5 | 82.4513 | 0 | 24193.5698
2017-09-13 | 12:16 |  |  |  |  | 82.5206 |  | 24213.915
2017-09-13 | 12:18 |  |  |  |  | 82.6085 |  | 24239.6845
2017-09-13 | 12:20 |  |  |  |  | 82.723 |  | 24273.2894
2017-09-13 | 12:22 |  |  |  |  | 82.7504 |  | 24281.3443
2017-09-13 | 12:24 |  |  |  |  | 82.7946 |  | 24294.315
2017-09-13 | 12:26 |  |  |  |  | 82.7072 |  | 24268.6597
2017-09-13 | 12:28 |  |  |  |  | 82.6484 |  | 24251.4131
2017-09-13 | 12:30 | 1.7499 | 0 | 0 | 1.5 | 82.6435 | 0 | 24249.9735
2017-09-13 | 12:32 |  |  |  |  | 82.7131 |  | 24270.3791
2017-09-13 | 12:34 |  |  |  |  | 82.8114 |  | 24299.2334
2017-09-13 | 12:36 |  |  |  |  | 82.8199 |  | 24301.7364
2017-09-13 | 12:38 |  |  |  |  | 82.7555 |  | 24282.8328
2017-09-13 | 12:40 |  |  |  |  | 82.7073 |  | 24268.6934
2017-09-13 | 12:42 |  |  |  |  | 82.6764 |  | 24259.6088
2017-09-13 | 12:44 |  |  |  |  | 82.7107 |  | 24269.6805
2017-09-13 | 12:45 | 1.7468 | 0 | 0 | 1.5 | 82.7249 | 0 | 24273.8624
2017-09-13 | 12:46 |  |  |  |  | 82.7237 |  | 24273.4954
2017-09-13 | 12:48 |  |  |  |  | 82.7586 |  | 24283.7328
2017-09-13 | 12:50 |  |  |  |  | 82.6727 |  | 24258.5408
2017-09-13 | 12:52 |  |  |  |  | 82.6375 |  | 24248.1983
2017-09-13 | 12:54 |  |  |  |  | 82.6085 |  | 24239.6801
2017-09-13 | 12:56 |  |  |  |  | 82.6589 |  | 24254.4956
2017-09-13 | 12:58 |  |  |  |  | 82.7761 |  | 24288.8819
2017-09-13 | 13:00 | 1.7179 | 0 | 0 | 1.5 | 82.8321 | 0 | 24305.2957
2017-09-13 | 13:02 |  |  |  |  | 82.8388 |  | 24307.259
2017-09-13 | 13:04 |  |  |  |  | 82.7754 |  | 24288.658
2017-09-13 | 13:06 |  |  |  |  | 82.7459 |  | 24280.0098
2017-09-13 | 13:08 |  |  |  |  | 82.8408 |  | 24307.8591
2017-09-13 | 13:10 |  |  |  |  | 82.9761 |  | 24347.5509
2017-09-13 | 13:12 |  |  |  |  | 83.0332 |  | 24364.3253
2017-09-13 | 13:14 |  |  |  |  | 83.075 |  | 24376.5844
2017-09-13 | 13:15 | 1.7655 | 0 | 0 | 1.5 | 83.0106 | 0 | 24357.6853
2017-09-13 | 13:16 |  |  |  |  | 82.9945 |  | 24352.9596
2017-09-13 | 13:18 |  |  |  |  | 82.9527 |  | 24340.6805
2017-09-13 | 13:20 |  |  |  |  | 83.0362 |  | 24365.2029
2017-09-13 | 13:22 |  |  |  |  | 83.1055 |  | 24385.5144
2017-09-13 | 13:24 |  |  |  |  | 83.1674 |  | 24403.6905
2017-09-13 | 13:26 |  |  |  |  | 83.1884 |  | 24409.8513
2017-09-13 | 13:28 |  |  |  |  | 83.2835 |  | 24437.754
2017-09-13 | 13:30 | 1.739 | 0 | 0 | 1.5 | 83.2591 | 0 | 24430.5859
2017-09-13 | 13:32 |  |  |  |  | 83.2605 |  | 24431.0225
2017-09-13 | 13:34 |  |  |  |  | 83.3621 |  | 24460.826
2017-09-13 | 13:36 |  |  |  |  | 83.5254 |  | 24508.745
2017-09-13 | 13:38 |  |  |  |  | 83.6568 |  | 24547.2997
2017-09-13 | 13:40 |  |  |  |  | 83.7702 |  | 24580.5619
2017-09-13 | 13:42 |  |  |  |  | 83.8306 |  | 24598.3011
2017-09-13 | 13:44 |  |  |  |  | 83.8429 |  | 24601.8944
2017-09-13 | 13:45 | 1.7553 | 0 | 0 | 1.5 | 83.8101 | 0 | 24592.2747
2017-09-13 | 13:46 |  |  |  |  | 83.8854 |  | 24614.3748
2017-09-13 | 13:48 |  |  |  |  | 83.9919 |  | 24645.6112
2017-09-13 | 13:50 |  |  |  |  | 84.0378 |  | 24659.0972
2017-09-13 | 13:52 |  |  |  |  | 84.1183 |  | 24682.7085
2017-09-13 | 13:54 |  |  |  |  | 84.1305 |  | 24686.3015
2017-09-13 | 13:56 |  |  |  |  | 84.2071 |  | 24708.7714
2017-09-13 | 13:58 |  |  |  |  | 84.2845 |  | 24731.4737
2017-09-13 | 14:00 | 1.6859 | 0 | 0 | 1.5 | 84.4629 | 0 | 24783.841
2017-09-13 | 14:02 |  |  |  |  | 84.6904 |  | 24850.574
2017-09-13 | 14:04 |  |  |  |  | 84.8572 |  | 24899.5249
2017-09-13 | 14:06 |  |  |  |  | 84.9165 |  | 24916.9285
2017-09-13 | 14:08 |  |  |  |  | 85.0691 |  | 24961.691
2017-09-13 | 14:10 |  |  |  |  | 85.1152 |  | 24975.2439
2017-09-13 | 14:12 |  |  |  |  | 85.1848 |  | 24995.6674
2017-09-13 | 14:14 |  |  |  |  | 85.1858 |  | 24995.9517
2017-09-13 | 14:15 | 1.7452 | 0 | 0 | 1.5 | 85.221 | 0 | 25006.2877
2017-09-13 | 14:16 |  |  |  |  | 85.1912 |  | 24997.5345
2017-09-13 | 14:18 |  |  |  |  | 85.2208 |  | 25006.2249
2017-09-13 | 14:20 |  |  |  |  | 85.3112 |  | 25032.7444
2017-09-13 | 14:22 |  |  |  |  | 85.3548 |  | 25045.5385
2017-09-13 | 14:24 |  |  |  |  | 85.4743 |  | 25080.6141
2017-09-13 | 14:26 |  |  |  |  | 85.5132 |  | 25092.0135
2017-09-13 | 14:28 |  |  |  |  | 85.6132 |  | 25121.356
2017-09-13 | 14:30 | 1.7514 | 0 | 0 | 1.5 | 85.6592 | 0 | 25134.8576
2017-09-13 | 14:32 |  |  |  |  | 85.5857 |  | 25113.3011
2017-09-13 | 14:34 |  |  |  |  | 85.5593 |  | 25105.5552
2017-09-13 | 14:36 |  |  |  |  | 85.6595 |  | 25134.9336
2017-09-13 | 14:38 |  |  |  |  | 85.7253 |  | 25154.2579
2017-09-13 | 14:40 |  |  |  |  | 85.834 |  | 25186.1457
2017-09-13 | 14:42 |  |  |  |  | 85.9501 |  | 25220.2183
2017-09-13 | 14:44 |  |  |  |  | 85.9842 |  | 25230.2142
2017-09-13 | 14:45 | 1.746 | 0 | 0 | 1.5 | 85.9633 | 0 | 25224.098
2017-09-13 | 14:46 |  |  |  |  | 85.9783 |  | 25228.5015
2017-09-13 | 14:48 |  |  |  |  | 86.0018 |  | 25235.3856
2017-09-13 | 14:50 |  |  |  |  | 86.0557 |  | 25251.1996
2017-09-13 | 14:52 |  |  |  |  | 86.0596 |  | 25252.3434
2017-09-13 | 14:54 |  |  |  |  | 85.9776 |  | 25228.2799
2017-09-13 | 14:56 |  |  |  |  | 86.0231 |  | 25241.6336
2017-09-13 | 14:58 |  |  |  |  | 86.1727 |  | 25285.532
2017-09-13 | 15:00 | 1.7249 | 0 | 0 | 1.5 | 86.2137 | 0 | 25297.5649
2017-09-13 | 15:02 |  |  |  |  | 86.1867 |  | 25289.6265
2017-09-13 | 15:04 |  |  |  |  | 86.1707 |  | 25284.9589
2017-09-13 | 15:06 |  |  |  |  | 86.1206 |  | 25270.2417
2017-09-13 | 15:08 |  |  |  |  | 86.167 |  | 25283.8574
2017-09-13 | 15:10 |  |  |  |  | 86.2656 |  | 25312.7991
2017-09-13 | 15:12 |  |  |  |  | 86.2639 |  | 25312.2953
2017-09-13 | 15:14 |  |  |  |  | 86.1036 |  | 25265.2695
2017-09-13 | 15:15 | 1.8014 | 0 | 0 | 1.5 | 85.9869 | 0 | 25231.0044
2017-09-13 | 15:16 |  |  |  |  | 85.983 |  | 25229.8782
2017-09-13 | 15:18 |  |  |  |  | 86.0018 |  | 25235.39
2017-09-13 | 15:20 |  |  |  |  | 86.0489 |  | 25249.2026
2017-09-13 | 15:22 |  |  |  |  | 86.1179 |  | 25269.4515
2017-09-13 | 15:24 |  |  |  |  | 86.0382 |  | 25246.0708
2017-09-13 | 15:26 |  |  |  |  | 86.0154 |  | 25239.3839
2017-09-13 | 15:28 |  |  |  |  | 86.0331 |  | 25244.5573
2017-09-13 | 15:30 | 1.7561 | 0 | 0 | 1.5 | 86.0173 | 0 | 25239.9458
2017-09-13 | 15:32 |  |  |  |  | 86.0245 |  | 25242.0479
2017-09-13 | 15:34 |  |  |  |  | 86.0246 |  | 25242.0881
2017-09-13 | 15:36 |  |  |  |  | 86.0215 |  | 25241.1726
2017-09-13 | 15:38 |  |  |  |  | 86.0246 |  | 25242.0814
2017-09-13 | 15:40 |  |  |  |  | 86.0344 |  | 25244.9537
2017-09-13 | 15:42 |  |  |  |  | 85.9941 |  | 25233.1379
2017-09-13 | 15:44 |  |  |  |  | 85.8068 |  | 25178.1738
2017-09-13 | 15:45 | 1.7897 | 0 | 0 | 1.5 | 85.7108 | 0 | 25150.0111
2017-09-13 | 15:46 |  |  |  |  | 85.671 |  | 25138.3095
2017-09-13 | 15:48 |  |  |  |  | 85.7196 |  | 25152.5721
2017-09-13 | 15:50 |  |  |  |  | 85.7085 |  | 25149.3283
2017-09-13 | 15:52 |  |  |  |  | 85.7182 |  | 25152.1669
2017-09-13 | 15:54 |  |  |  |  | 85.7701 |  | 25167.3944
2017-09-13 | 15:56 |  |  |  |  | 85.8281 |  | 25184.4106
2017-09-13 | 15:58 |  |  |  |  | 85.83 |  | 25184.9793
2017-09-13 | 16:00 | 1.7826 | 0 | 0 | 1.5 | 85.719 | 0 | 25152.4087
2017-09-13 | 16:02 |  |  |  |  | 85.6164 |  | 25122.3053
2017-09-13 | 16:04 |  |  |  |  | 85.5869 |  | 25113.6392
2017-09-13 | 16:06 |  |  |  |  | 85.5978 |  | 25116.8428
2017-09-13 | 16:08 |  |  |  |  | 85.6143 |  | 25121.6694
2017-09-13 | 16:10 |  |  |  |  | 85.6325 |  | 25127.0333
2017-09-13 | 16:12 |  |  |  |  | 85.6941 |  | 25145.1017
2017-09-13 | 16:14 |  |  |  |  | 85.7415 |  | 25158.9994
2017-09-13 | 16:15 | 1.7436 | 0 | 0 | 1.5 | 85.7284 | 0 | 25155.1646
2017-09-13 | 16:16 |  |  |  |  | 85.7663 |  | 25166.2908
2017-09-13 | 16:18 |  |  |  |  | 85.7888 |  | 25172.895
2017-09-13 | 16:20 |  |  |  |  | 85.737 |  | 25157.6875
2017-09-13 | 16:22 |  |  |  |  | 85.5973 |  | 25116.6817
2017-09-13 | 16:24 |  |  |  |  | 85.5295 |  | 25096.7975
2017-09-13 | 16:26 |  |  |  |  | 85.5297 |  | 25096.8671
2017-09-13 | 16:28 |  |  |  |  | 85.5972 |  | 25116.6615
2017-09-13 | 16:30 | 1.7413 | 0 | 0 | 1.5 | 85.5986 | 0 | 25117.0822
2017-09-13 | 16:32 |  |  |  |  | 85.5727 |  | 25109.4866
2017-09-13 | 16:34 |  |  |  |  | 85.5336 |  | 25097.9977
2017-09-13 | 16:36 |  |  |  |  | 85.5107 |  | 25091.2702
2017-09-13 | 16:38 |  |  |  |  | 85.4935 |  | 25086.2356
2017-09-13 | 16:40 |  |  |  |  | 85.3071 |  | 25031.5355
2017-09-13 | 16:42 |  |  |  |  | 85.1801 |  | 24994.2727
2017-09-13 | 16:44 |  |  |  |  | 85.2004 |  | 25000.241
2017-09-13 | 16:45 | 1.7483 | 0 | 0 | 1.5 | 85.1887 | 0 | 24996.7956
2017-09-13 | 16:46 |  |  |  |  | 85.1769 |  | 24993.339
2017-09-13 | 16:48 |  |  |  |  | 85.1904 |  | 24997.2883
2017-09-13 | 16:50 |  |  |  |  | 85.1883 |  | 24996.6859
2017-09-13 | 16:52 |  |  |  |  | 85.1873 |  | 24996.3904
2017-09-13 | 16:54 |  |  |  |  | 85.0736 |  | 24963.0387
2017-09-13 | 16:56 |  |  |  |  | 85.0077 |  | 24943.6739
2017-09-13 | 16:58 |  |  |  |  | 85.0101 |  | 24944.3813
2017-09-13 | 17:00 | 1.739 | 0 | 0 | 1.5 | 84.9885 | 0 | 24938.0615
2017-09-13 | 17:02 |  |  |  |  | 85.0059 |  | 24943.1545
2017-09-13 | 17:04 |  |  |  |  | 84.9242 |  | 24919.1849
2017-09-13 | 17:06 |  |  |  |  | 84.9069 |  | 24914.1098
2017-09-13 | 17:08 |  |  |  |  | 84.8967 |  | 24911.128
2017-09-13 | 17:10 |  |  |  |  | 84.833 |  | 24892.4283
2017-09-13 | 17:12 |  |  |  |  | 84.7894 |  | 24879.6319
2017-09-13 | 17:14 |  |  |  |  | 84.6161 |  | 24828.7758
2017-09-13 | 17:15 | 1.7943 | 0 | 0 | 1.5 | 84.5349 | 0 | 24804.9585
2017-09-13 | 17:16 |  |  |  |  | 84.4935 |  | 24792.8047
2017-09-13 | 17:18 |  |  |  |  | 84.3663 |  | 24755.4791
2017-09-13 | 17:20 |  |  |  |  | 84.1627 |  | 24695.7443
2017-09-13 | 17:22 |  |  |  |  | 84.0149 |  | 24652.3609
2017-09-13 | 17:24 |  |  |  |  | 83.8256 |  | 24596.8193
2017-09-13 | 17:26 |  |  |  |  | 83.5944 |  | 24528.9915
2017-09-13 | 17:28 |  |  |  |  | 83.3416 |  | 24454.7996
2017-09-13 | 17:30 | 1.7982 | 0 | 0 | 1.5 | 83.2074 | 0 | 24415.43
2017-09-13 | 17:32 |  |  |  |  | 83.1013 |  | 24384.3034
2017-09-13 | 17:34 |  |  |  |  | 82.9723 |  | 24346.4294
2017-09-13 | 17:36 |  |  |  |  | 82.8316 |  | 24305.1636
2017-09-13 | 17:38 |  |  |  |  | 82.6526 |  | 24252.6332
2017-09-13 | 17:40 |  |  |  |  | 82.414 |  | 24182.6361
2017-09-13 | 17:42 |  |  |  |  | 82.279 |  | 24143.0115
2017-09-13 | 17:44 |  |  |  |  | 82.2211 |  | 24126.0243
2017-09-13 | 17:45 | 1.7819 | 0 | 0 | 1.5 | 82.1751 | 0 | 24112.5295
2017-09-13 | 17:46 |  |  |  |  | 82.1172 |  | 24095.5424
2017-09-13 | 17:48 |  |  |  |  | 82.0598 |  | 24078.6896
2017-09-13 | 17:50 |  |  |  |  | 81.8997 |  | 24031.7266
2017-09-13 | 17:52 |  |  |  |  | 81.7396 |  | 23984.7323
2017-09-13 | 17:54 |  |  |  |  | 81.5809 |  | 23938.1743
2017-09-13 | 17:56 |  |  |  |  | 81.565 |  | 23933.5067
2017-09-13 | 17:58 |  |  |  |  | 81.5008 |  | 23914.6613
2017-09-13 | 18:00 | 1.7756 | 0 | 0 | 1.5 | 81.4067 | 0 | 23887.0628
2017-09-13 | 18:02 |  |  |  |  | 81.2331 |  | 23836.1216
2017-09-13 | 18:04 |  |  |  |  | 81.0825 |  | 23791.9189
2017-09-13 | 18:06 |  |  |  |  | 81.0005 |  | 23767.8733
2017-09-13 | 18:08 |  |  |  |  | 80.9738 |  | 23760.0244
2017-09-13 | 18:10 |  |  |  |  | 80.8674 |  | 23728.8171
2017-09-13 | 18:12 |  |  |  |  | 80.7509 |  | 23694.628
2017-09-13 | 18:14 |  |  |  |  | 80.5794 |  | 23644.2844
2017-09-13 | 18:15 | 1.8099 | 0 | 0 | 1.5 | 80.4758 | 0 | 23613.9034
2017-09-13 | 18:16 |  |  |  |  | 80.418 |  | 23596.9365
2017-09-13 | 18:18 |  |  |  |  | 80.4017 |  | 23592.1457
2017-09-13 | 18:20 |  |  |  |  | 80.3222 |  | 23568.8208
2017-09-13 | 18:22 |  |  |  |  | 80.2634 |  | 23551.5628
2017-09-13 | 18:24 |  |  |  |  | 80.1182 |  | 23508.9719
2017-09-13 | 18:26 |  |  |  |  | 79.9592 |  | 23462.3109
2017-09-13 | 18:28 |  |  |  |  | 79.8612 |  | 23433.5687
2017-09-13 | 18:30 | 1.7592 | 0 | 0 | 1.5 | 79.8034 | 0 | 23416.595
2017-09-13 | 18:32 |  |  |  |  | 79.7706 |  | 23406.9618
2017-09-13 | 18:34 |  |  |  |  | 79.6976 |  | 23385.5579
2017-09-13 | 18:36 |  |  |  |  | 79.5082 |  | 23329.9714
2017-09-13 | 18:38 |  |  |  |  | 79.3751 |  | 23290.9263
2017-09-13 | 18:40 |  |  |  |  | 79.2747 |  | 23261.4496
2017-09-13 | 18:42 |  |  |  |  | 79.2499 |  | 23254.1808
2017-09-13 | 18:44 |  |  |  |  | 79.2028 |  | 23240.3791
2017-09-13 | 18:45 | 1.7897 | 0 | 0 | 1.5 | 79.1559 | 0 | 23226.5936
2017-09-13 | 18:46 |  |  |  |  | 79.13 |  | 23219.0131
2017-09-13 | 18:48 |  |  |  |  | 79.0049 |  | 23182.2876
2017-09-13 | 18:50 |  |  |  |  | 78.887 |  | 23147.7068
2017-09-13 | 18:52 |  |  |  |  | 78.8108 |  | 23125.3287
2017-09-13 | 18:54 |  |  |  |  | 78.77 |  | 23113.3609
2017-09-13 | 18:56 |  |  |  |  | 78.7234 |  | 23099.6804
2017-09-13 | 18:58 |  |  |  |  | 78.6264 |  | 23071.2355
2017-09-13 | 19:00 | 1.7975 | 0 | 0 | 1.5 | 78.4715 | 0 | 23025.7857
2017-09-13 | 19:02 |  |  |  |  | 78.4592 |  | 23022.1636
2017-09-13 | 19:04 |  |  |  |  | 78.5015 |  | 23034.5974
2017-09-13 | 19:06 |  |  |  |  | 78.7065 |  | 23094.7329
2017-09-13 | 19:08 |  |  |  |  | 78.7429 |  | 23105.4158
2017-09-13 | 19:10 |  |  |  |  | 78.7819 |  | 23116.8665
2017-09-13 | 19:12 |  |  |  |  | 78.7923 |  | 23119.9044
2017-09-13 | 19:14 |  |  |  |  | 78.7375 |  | 23103.8263
2017-09-13 | 19:15 | 1.778 | 0 | 0 | 1.5 | 78.6804 | 0 | 23087.0832
2017-09-13 | 19:16 |  |  |  |  | 78.6439 |  | 23076.3555
2017-09-13 | 19:18 |  |  |  |  | 78.5208 |  | 23040.2432
2017-09-13 | 19:20 |  |  |  |  | 78.4748 |  | 23026.762
2017-09-13 | 19:22 |  |  |  |  | 78.4598 |  | 23022.3338
2017-09-13 | 19:24 |  |  |  |  | 78.3515 |  | 22990.5781
2017-09-13 | 19:26 |  |  |  |  | 78.2131 |  | 22949.9438
2017-09-13 | 19:28 |  |  |  |  | 78.2246 |  | 22953.3265
2017-09-13 | 19:30 | 1.7156 | 0 | 0 | 1.5 | 78.3011 | 0 | 22975.7758
2017-09-13 | 19:32 |  |  |  |  | 78.2973 |  | 22974.6567
2017-09-13 | 19:34 |  |  |  |  | 78.2466 |  | 22959.7895
2017-09-13 | 19:36 |  |  |  |  | 78.2955 |  | 22974.1417
2017-09-13 | 19:38 |  |  |  |  | 78.3203 |  | 22981.4196
2017-09-13 | 19:40 |  |  |  |  | 78.2101 |  | 22949.0885
2017-09-13 | 19:42 |  |  |  |  | 78.1183 |  | 22922.155
2017-09-13 | 19:44 |  |  |  |  | 77.9768 |  | 22880.6275
2017-09-13 | 19:45 | 1.7741 | 0 | 0 | 1.5 | 77.9677 | 0 | 22877.9388
2017-09-13 | 19:46 |  |  |  |  | 77.8667 |  | 22848.321
2017-09-13 | 19:48 |  |  |  |  | 77.915 |  | 22862.4739
2017-09-13 | 19:50 |  |  |  |  | 78.0929 |  | 22914.6981
2017-09-13 | 19:52 |  |  |  |  | 78.241 |  | 22958.1551
2017-09-13 | 19:54 |  |  |  |  | 78.2205 |  | 22952.1219
2017-09-13 | 19:56 |  |  |  |  | 78.2683 |  | 22966.1698
2017-09-13 | 19:58 |  |  |  |  | 78.1996 |  | 22945.9858
2017-09-13 | 20:00 | 1.7842 | 0 | 0 | 1.5 | 78.0757 | 0 | 22909.6543
2017-09-13 | 20:02 |  |  |  |  | 78.0698 |  | 22907.9237
2017-09-13 | 20:04 |  |  |  |  | 78.1303 |  | 22925.6676
2017-09-13 | 20:06 |  |  |  |  | 78.2547 |  | 22962.1601
2017-09-13 | 20:08 |  |  |  |  | 78.2655 |  | 22965.3459
2017-09-13 | 20:10 |  |  |  |  | 78.2727 |  | 22967.448
2017-09-13 | 20:12 |  |  |  |  | 78.2292 |  | 22954.6965
2017-09-13 | 20:14 |  |  |  |  | 78.1343 |  | 22926.8316
2017-09-13 | 20:15 | 1.7819 | 0 | 0 | 1.5 | 78.0747 | 0 | 22909.3342
2017-09-13 | 20:16 |  |  |  |  | 77.995 |  | 22885.9512
2017-09-13 | 20:18 |  |  |  |  | 78.0973 |  | 22915.9874
2017-09-13 | 20:20 |  |  |  |  | 78.1889 |  | 22942.8493
2017-09-13 | 20:22 |  |  |  |  | 78.1802 |  | 22940.3062
2017-09-13 | 20:24 |  |  |  |  | 78.1419 |  | 22929.0523
2017-09-13 | 20:26 |  |  |  |  | 78.1437 |  | 22929.5963
2017-09-13 | 20:28 |  |  |  |  | 78.0852 |  | 22912.4369
2017-09-13 | 20:30 | 1.7663 | 0 | 0 | 1.5 | 78.0793 | 0 | 22910.711
2017-09-13 | 20:32 |  |  |  |  | 78.0198 |  | 22893.2514
2017-09-13 | 20:34 |  |  |  |  | 78.1013 |  | 22917.1514
2017-09-13 | 20:36 |  |  |  |  | 78.2023 |  | 22946.776
2017-09-13 | 20:38 |  |  |  |  | 78.1472 |  | 22930.6218
2017-09-13 | 20:40 |  |  |  |  | 78.1201 |  | 22922.6834
2017-09-13 | 20:42 |  |  |  |  | 78.0114 |  | 22890.771
2017-09-13 | 20:44 |  |  |  |  | 78.0649 |  | 22906.4574
2017-09-13 | 20:45 | 1.7507 | 0 | 0 | 1.5 | 78.0582 | 0 | 22904.4964
2017-09-13 | 20:46 |  |  |  |  | 78.0531 |  | 22903.0099
2017-09-13 | 20:48 |  |  |  |  | 78.152 |  | 22932.0321
2017-09-13 | 20:50 |  |  |  |  | 78.2258 |  | 22953.6891
2017-09-13 | 20:52 |  |  |  |  | 78.254 |  | 22961.9544
2017-09-13 | 20:54 |  |  |  |  | 78.1381 |  | 22927.9443
2017-09-13 | 20:56 |  |  |  |  | 78.0877 |  | 22913.1711
2017-09-13 | 20:58 |  |  |  |  | 78.0045 |  | 22888.7361
2017-09-13 | 21:00 | 1.806 | 0 | 0 | 1.5 | 77.85 | 0 | 22843.416
2017-09-13 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:15 | 0.04168 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:30 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:45 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:30 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-13 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:45 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:00 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 5:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-14 | 5:04 |  |  |  |  | 99.6178 |  | 29230.7149
2017-09-14 | 5:06 |  |  |  |  | 97.497 |  | 28608.4128
2017-09-14 | 5:08 |  |  |  |  | 94.9214 |  | 27852.6423
2017-09-14 | 5:10 |  |  |  |  | 92.8909 |  | 27256.8306
2017-09-14 | 5:12 |  |  |  |  | 91.0986 |  | 26730.9417
2017-09-14 | 5:14 |  |  |  |  | 89.4917 |  | 26259.4325
2017-09-14 | 5:15 | 2.2343 | 0 | 0 | 1.5 | 88.7485 | 0 | 26041.3423
2017-09-14 | 5:16 |  |  |  |  | 88.1294 |  | 25859.6757
2017-09-14 | 5:18 |  |  |  |  | 86.9782 |  | 25521.8966
2017-09-14 | 5:20 |  |  |  |  | 85.9592 |  | 25222.8847
2017-09-14 | 5:22 |  |  |  |  | 85.0762 |  | 24963.7884
2017-09-14 | 5:24 |  |  |  |  | 84.2736 |  | 24728.2835
2017-09-14 | 5:26 |  |  |  |  | 83.5441 |  | 24514.2321
2017-09-14 | 5:28 |  |  |  |  | 83.057 |  | 24371.2945
2017-09-14 | 5:30 | 1.8583 | 0 | 0 | 1.5 | 82.6954 | 0 | 24265.1875
2017-09-14 | 5:32 |  |  |  |  | 82.2313 |  | 24128.9997
2017-09-14 | 5:34 |  |  |  |  | 81.7742 |  | 23994.8867
2017-09-14 | 5:36 |  |  |  |  | 81.3581 |  | 23872.7937
2017-09-14 | 5:38 |  |  |  |  | 81.1825 |  | 23821.2612
2017-09-14 | 5:40 |  |  |  |  | 81.0512 |  | 23782.7402
2017-09-14 | 5:42 |  |  |  |  | 80.8662 |  | 23728.4612
2017-09-14 | 5:44 |  |  |  |  | 80.5698 |  | 23641.4884
2017-09-14 | 5:45 | 1.8224 | 0 | 0 | 1.5 | 80.4731 | 0 | 23613.1041
2017-09-14 | 5:46 |  |  |  |  | 80.3435 |  | 23575.089
2017-09-14 | 5:48 |  |  |  |  | 80.2457 |  | 23546.3735
2017-09-14 | 5:50 |  |  |  |  | 80.2189 |  | 23538.5046
2017-09-14 | 5:52 |  |  |  |  | 80.1242 |  | 23510.7225
2017-09-14 | 5:54 |  |  |  |  | 79.9034 |  | 23445.9417
2017-09-14 | 5:56 |  |  |  |  | 79.6751 |  | 23378.9605
2017-09-14 | 5:58 |  |  |  |  | 79.7053 |  | 23387.8188
2017-09-14 | 6:00 | 1.7577 | 0 | 0 | 1.5 | 79.7405 | 0 | 23398.1413
2017-09-14 | 6:02 |  |  |  |  | 79.6386 |  | 23368.2459
2017-09-14 | 6:04 |  |  |  |  | 79.487 |  | 23323.7501
2017-09-14 | 6:06 |  |  |  |  | 79.337 |  | 23279.7443
2017-09-14 | 6:08 |  |  |  |  | 79.3356 |  | 23279.33
2017-09-14 | 6:10 |  |  |  |  | 79.3883 |  | 23294.7861
2017-09-14 | 6:12 |  |  |  |  | 79.3505 |  | 23283.7179
2017-09-14 | 6:14 |  |  |  |  | 79.2259 |  | 23247.1512
2017-09-14 | 6:15 | 1.7717 | 0 | 0 | 1.5 | 79.131 | 0 | 23219.2998
2017-09-14 | 6:16 |  |  |  |  | 79.0518 |  | 23196.0488
2017-09-14 | 6:18 |  |  |  |  | 79.1032 |  | 23211.1264
2017-09-14 | 6:20 |  |  |  |  | 79.1433 |  | 23222.9063
2017-09-14 | 6:22 |  |  |  |  | 79.1004 |  | 23210.3115
2017-09-14 | 6:24 |  |  |  |  | 78.9907 |  | 23178.1215
2017-09-14 | 6:26 |  |  |  |  | 78.8645 |  | 23141.107
2017-09-14 | 6:28 |  |  |  |  | 78.883 |  | 23146.5292
2017-09-14 | 6:30 | 1.7335 | 0 | 0 | 1.5 | 78.9726 | 0 | 23172.8181
2017-09-14 | 6:32 |  |  |  |  | 78.9496 |  | 23166.0663
2017-09-14 | 6:34 |  |  |  |  | 78.8089 |  | 23124.7915
2017-09-14 | 6:36 |  |  |  |  | 78.6726 |  | 23084.7751
2017-09-14 | 6:38 |  |  |  |  | 78.7136 |  | 23096.8192
2017-09-14 | 6:40 |  |  |  |  | 78.7682 |  | 23112.8369
2017-09-14 | 6:42 |  |  |  |  | 78.7001 |  | 23092.8547
2017-09-14 | 6:44 |  |  |  |  | 78.6182 |  | 23068.8358
2017-09-14 | 6:45 | 1.7819 | 0 | 0 | 1.5 | 78.5565 | 0 | 23050.7336
2017-09-14 | 6:46 |  |  |  |  | 78.5093 |  | 23036.865
2017-09-14 | 6:48 |  |  |  |  | 78.5432 |  | 23046.8116
2017-09-14 | 6:50 |  |  |  |  | 78.5838 |  | 23058.7436
2017-09-14 | 6:52 |  |  |  |  | 78.684 |  | 23088.1422
2017-09-14 | 6:54 |  |  |  |  | 78.772 |  | 23113.9587
2017-09-14 | 6:56 |  |  |  |  | 78.9384 |  | 23162.7752
2017-09-14 | 6:58 |  |  |  |  | 79.084 |  | 23205.496
2017-09-14 | 7:00 | 1.7054 | 0 | 0 | 1.5 | 79.2619 | 0 | 23257.6999
2017-09-14 | 7:02 |  |  |  |  | 79.4037 |  | 23299.3125
2017-09-14 | 7:04 |  |  |  |  | 79.5586 |  | 23344.7555
2017-09-14 | 7:06 |  |  |  |  | 79.7155 |  | 23390.7918
2017-09-14 | 7:08 |  |  |  |  | 79.8861 |  | 23440.8577
2017-09-14 | 7:10 |  |  |  |  | 79.9899 |  | 23471.3329
2017-09-14 | 7:12 |  |  |  |  | 80.1192 |  | 23509.2606
2017-09-14 | 7:14 |  |  |  |  | 80.2521 |  | 23548.2541
2017-09-14 | 7:15 | 1.7015 | 0 | 0 | 1.5 | 80.281 | 0 | 23556.7342
2017-09-14 | 7:16 |  |  |  |  | 80.3591 |  | 23579.6539
2017-09-14 | 7:18 |  |  |  |  | 80.4711 |  | 23612.5334
2017-09-14 | 7:20 |  |  |  |  | 80.5761 |  | 23643.3331
2017-09-14 | 7:22 |  |  |  |  | 80.6345 |  | 23660.4635
2017-09-14 | 7:24 |  |  |  |  | 80.7429 |  | 23692.2685
2017-09-14 | 7:26 |  |  |  |  | 80.7841 |  | 23704.3707
2017-09-14 | 7:28 |  |  |  |  | 80.8731 |  | 23730.4805
2017-09-14 | 7:30 | 1.7444 | 0 | 0 | 1.5 | 80.9228 | 0 | 23745.0475
2017-09-14 | 7:32 |  |  |  |  | 80.9745 |  | 23760.2236
2017-09-14 | 7:34 |  |  |  |  | 81.0522 |  | 23783.0245
2017-09-14 | 7:36 |  |  |  |  | 81.1312 |  | 23806.2174
2017-09-14 | 7:38 |  |  |  |  | 81.2005 |  | 23826.5423
2017-09-14 | 7:40 |  |  |  |  | 81.2929 |  | 23853.673
2017-09-14 | 7:42 |  |  |  |  | 81.373 |  | 23877.1678
2017-09-14 | 7:44 |  |  |  |  | 81.4702 |  | 23905.6932
2017-09-14 | 7:45 | 1.7312 | 0 | 0 | 1.5 | 81.4989 | 0 | 23914.1128
2017-09-14 | 7:46 |  |  |  |  | 81.5457 |  | 23927.8406
2017-09-14 | 7:48 |  |  |  |  | 81.674 |  | 23965.4796
2017-09-14 | 7:50 |  |  |  |  | 81.7153 |  | 23977.5929
2017-09-14 | 7:52 |  |  |  |  | 81.8514 |  | 24017.5467
2017-09-14 | 7:54 |  |  |  |  | 81.987 |  | 24057.3327
2017-09-14 | 7:56 |  |  |  |  | 82.0272 |  | 24069.1215
2017-09-14 | 7:58 |  |  |  |  | 82.1184 |  | 24095.8983
2017-09-14 | 8:00 | 1.7171 | 0 | 0 | 1.5 | 82.2382 | 0 | 24131.0235
2017-09-14 | 8:02 |  |  |  |  | 82.311 |  | 24152.4027
2017-09-14 | 8:04 |  |  |  |  | 82.2084 |  | 24122.306
2017-09-14 | 8:06 |  |  |  |  | 82.1946 |  | 24118.2338
2017-09-14 | 8:08 |  |  |  |  | 82.1393 |  | 24102.0054
2017-09-14 | 8:10 |  |  |  |  | 82.0552 |  | 24077.3442
2017-09-14 | 8:12 |  |  |  |  | 81.9743 |  | 24053.6029
2017-09-14 | 8:14 |  |  |  |  | 81.8623 |  | 24020.7301
2017-09-14 | 8:15 | 1.7772 | 0 | 0 | 1.5 | 81.8337 | 0 | 24012.3395
2017-09-14 | 8:16 |  |  |  |  | 81.7476 |  | 23987.0695
2017-09-14 | 8:18 |  |  |  |  | 81.6465 |  | 23957.4044
2017-09-14 | 8:20 |  |  |  |  | 81.5867 |  | 23939.86
2017-09-14 | 8:22 |  |  |  |  | 81.4959 |  | 23913.2331
2017-09-14 | 8:24 |  |  |  |  | 81.3564 |  | 23872.2831
2017-09-14 | 8:26 |  |  |  |  | 81.1582 |  | 23814.14
2017-09-14 | 8:28 |  |  |  |  | 81.1272 |  | 23805.0375
2017-09-14 | 8:30 | 1.7327 | 0 | 0 | 1.5 | 81.1853 | 0 | 23822.0784
2017-09-14 | 8:32 |  |  |  |  | 81.1649 |  | 23816.108
2017-09-14 | 8:34 |  |  |  |  | 81.0637 |  | 23786.4072
2017-09-14 | 8:36 |  |  |  |  | 80.9825 |  | 23762.5898
2017-09-14 | 8:38 |  |  |  |  | 80.9041 |  | 23739.5607
2017-09-14 | 8:40 |  |  |  |  | 80.8209 |  | 23715.1521
2017-09-14 | 8:42 |  |  |  |  | 80.8114 |  | 23712.3719
2017-09-14 | 8:44 |  |  |  |  | 80.7823 |  | 23703.829
2017-09-14 | 8:45 | 1.7592 | 0 | 0 | 1.5 | 80.7271 | 0 | 23687.6277
2017-09-14 | 8:46 |  |  |  |  | 80.711 |  | 23682.9243
2017-09-14 | 8:48 |  |  |  |  | 80.8552 |  | 23725.2197
2017-09-14 | 8:50 |  |  |  |  | 81.0063 |  | 23769.5567
2017-09-14 | 8:52 |  |  |  |  | 81.1412 |  | 23809.159
2017-09-14 | 8:54 |  |  |  |  | 81.175 |  | 23819.0517
2017-09-14 | 8:56 |  |  |  |  | 81.2118 |  | 23829.8625
2017-09-14 | 8:58 |  |  |  |  | 81.2031 |  | 23827.3214
2017-09-14 | 9:00 | 1.7826 | 0 | 0 | 1.5 | 81.1246 | 0 | 23804.2855
2017-09-14 | 9:02 |  |  |  |  | 81.1606 |  | 23814.8251
2017-09-14 | 9:04 |  |  |  |  | 81.2198 |  | 23832.2175
2017-09-14 | 9:06 |  |  |  |  | 81.272 |  | 23847.5122
2017-09-14 | 9:08 |  |  |  |  | 81.2241 |  | 23833.4643
2017-09-14 | 9:10 |  |  |  |  | 81.261 |  | 23844.2862
2017-09-14 | 9:12 |  |  |  |  | 81.3015 |  | 23856.1959
2017-09-14 | 9:14 |  |  |  |  | 81.342 |  | 23868.0586
2017-09-14 | 9:15 | 1.7585 | 0 | 0 | 1.5 | 81.3485 | 0 | 23869.9862
2017-09-14 | 9:16 |  |  |  |  | 81.3459 |  | 23869.2115
2017-09-14 | 9:18 |  |  |  |  | 81.3899 |  | 23882.12
2017-09-14 | 9:20 |  |  |  |  | 81.3958 |  | 23883.8392
2017-09-14 | 9:22 |  |  |  |  | 81.4137 |  | 23889.1204
2017-09-14 | 9:24 |  |  |  |  | 81.4386 |  | 23896.4118
2017-09-14 | 9:26 |  |  |  |  | 81.3894 |  | 23881.9856
2017-09-14 | 9:28 |  |  |  |  | 81.3619 |  | 23873.9108
2017-09-14 | 9:30 | 1.7663 | 0 | 0 | 1.5 | 81.2918 | 0 | 23853.3461
2017-09-14 | 9:32 |  |  |  |  | 81.2722 |  | 23847.5905
2017-09-14 | 9:34 |  |  |  |  | 81.2902 |  | 23852.8538
2017-09-14 | 9:36 |  |  |  |  | 81.2408 |  | 23838.376
2017-09-14 | 9:38 |  |  |  |  | 81.327 |  | 23863.6643
2017-09-14 | 9:40 |  |  |  |  | 81.4897 |  | 23911.4042
2017-09-14 | 9:42 |  |  |  |  | 81.6923 |  | 23970.8455
2017-09-14 | 9:44 |  |  |  |  | 81.7725 |  | 23994.3832
2017-09-14 | 9:45 | 1.7226 | 0 | 0 | 1.5 | 81.8385 | 0 | 24013.7453
2017-09-14 | 9:46 |  |  |  |  | 81.8705 |  | 24023.1345
2017-09-14 | 9:48 |  |  |  |  | 81.8739 |  | 24024.1398
2017-09-14 | 9:50 |  |  |  |  | 81.9693 |  | 24052.1478
2017-09-14 | 9:52 |  |  |  |  | 82.0931 |  | 24088.4549
2017-09-14 | 9:54 |  |  |  |  | 82.1466 |  | 24104.1457
2017-09-14 | 9:56 |  |  |  |  | 82.1067 |  | 24092.4485
2017-09-14 | 9:58 |  |  |  |  | 82.0836 |  | 24085.6767
2017-09-14 | 10:00 | 1.7538 | 0 | 0 | 1.5 | 82.1064 | 0 | 24092.3569
2017-09-14 | 10:02 |  |  |  |  | 82.069 |  | 24081.385
2017-09-14 | 10:04 |  |  |  |  | 81.9867 |  | 24057.2297
2017-09-14 | 10:06 |  |  |  |  | 81.9461 |  | 24045.3244
2017-09-14 | 10:08 |  |  |  |  | 81.8791 |  | 24025.6574
2017-09-14 | 10:10 |  |  |  |  | 81.8407 |  | 24014.4102
2017-09-14 | 10:12 |  |  |  |  | 81.8107 |  | 24005.608
2017-09-14 | 10:14 |  |  |  |  | 81.7546 |  | 23989.1422
2017-09-14 | 10:15 | 1.8045 | 0 | 0 | 1.5 | 81.6666 | 0 | 23963.3012
2017-09-14 | 10:16 |  |  |  |  | 81.6124 |  | 23947.4223
2017-09-14 | 10:18 |  |  |  |  | 81.5523 |  | 23929.7793
2017-09-14 | 10:20 |  |  |  |  | 81.4831 |  | 23909.4834
2017-09-14 | 10:22 |  |  |  |  | 81.4028 |  | 23885.8988
2017-09-14 | 10:24 |  |  |  |  | 81.3593 |  | 23873.1429
2017-09-14 | 10:26 |  |  |  |  | 81.3371 |  | 23866.6393
2017-09-14 | 10:28 |  |  |  |  | 81.311 |  | 23858.9788
2017-09-14 | 10:30 | 1.7975 | 0 | 0 | 1.5 | 81.2193 | 0 | 23832.074
2017-09-14 | 10:32 |  |  |  |  | 81.192 |  | 23824.0664
2017-09-14 | 10:34 |  |  |  |  | 81.1232 |  | 23803.8711
2017-09-14 | 10:36 |  |  |  |  | 81.1143 |  | 23801.252
2017-09-14 | 10:38 |  |  |  |  | 81.1431 |  | 23809.7098
2017-09-14 | 10:40 |  |  |  |  | 81.228 |  | 23834.604
2017-09-14 | 10:42 |  |  |  |  | 81.2307 |  | 23835.403
2017-09-14 | 10:44 |  |  |  |  | 81.2065 |  | 23828.3108
2017-09-14 | 10:45 | 1.7772 | 0 | 0 | 1.5 | 81.1677 | 0 | 23816.9296
2017-09-14 | 10:46 |  |  |  |  | 81.1458 |  | 23810.5
2017-09-14 | 10:48 |  |  |  |  | 81.084 |  | 23792.3508
2017-09-14 | 10:50 |  |  |  |  | 81.1928 |  | 23824.2879
2017-09-14 | 10:52 |  |  |  |  | 81.2478 |  | 23840.4221
2017-09-14 | 10:54 |  |  |  |  | 81.3803 |  | 23879.2946
2017-09-14 | 10:56 |  |  |  |  | 81.463 |  | 23903.5776
2017-09-14 | 10:58 |  |  |  |  | 81.3977 |  | 23884.3967
2017-09-14 | 11:00 | 1.7733 | 0 | 0 | 1.5 | 81.3558 | 0 | 23872.1264
2017-09-14 | 11:02 |  |  |  |  | 81.3649 |  | 23874.7793
2017-09-14 | 11:04 |  |  |  |  | 81.4619 |  | 23903.2375
2017-09-14 | 11:06 |  |  |  |  | 81.5731 |  | 23935.8797
2017-09-14 | 11:08 |  |  |  |  | 81.5966 |  | 23942.7837
2017-09-14 | 11:10 |  |  |  |  | 81.4997 |  | 23914.3347
2017-09-14 | 11:12 |  |  |  |  | 81.4557 |  | 23901.4285
2017-09-14 | 11:14 |  |  |  |  | 81.4159 |  | 23889.7583
2017-09-14 | 11:15 | 1.7616 | 0 | 0 | 1.5 | 81.4182 | 0 | 23890.4141
2017-09-14 | 11:16 |  |  |  |  | 81.422 |  | 23891.5447
2017-09-14 | 11:18 |  |  |  |  | 81.4633 |  | 23903.6492
2017-09-14 | 11:20 |  |  |  |  | 81.5667 |  | 23933.9923
2017-09-14 | 11:22 |  |  |  |  | 81.5619 |  | 23932.5842
2017-09-14 | 11:24 |  |  |  |  | 81.53 |  | 23923.2379
2017-09-14 | 11:26 |  |  |  |  | 81.4534 |  | 23900.7569
2017-09-14 | 11:28 |  |  |  |  | 81.447 |  | 23898.8719
2017-09-14 | 11:30 | 1.7132 | 0 | 0 | 1.5 | 81.5342 | 0 | 23924.4512
2017-09-14 | 11:32 |  |  |  |  | 81.5382 |  | 23925.649
2017-09-14 | 11:34 |  |  |  |  | 81.5728 |  | 23935.7902
2017-09-14 | 11:36 |  |  |  |  | 81.5321 |  | 23923.8511
2017-09-14 | 11:38 |  |  |  |  | 81.5265 |  | 23922.1945
2017-09-14 | 11:40 |  |  |  |  | 81.472 |  | 23906.2038
2017-09-14 | 11:42 |  |  |  |  | 81.5081 |  | 23916.815
2017-09-14 | 11:44 |  |  |  |  | 81.5501 |  | 23929.1211
2017-09-14 | 11:45 | 1.7226 | 0 | 0 | 1.5 | 81.6019 | 0 | 23944.3395
2017-09-14 | 11:46 |  |  |  |  | 81.6237 |  | 23950.731
2017-09-14 | 11:48 |  |  |  |  | 81.569 |  | 23934.664
2017-09-14 | 11:50 |  |  |  |  | 81.4875 |  | 23910.7707
2017-09-14 | 11:52 |  |  |  |  | 81.4432 |  | 23897.7639
2017-09-14 | 11:54 |  |  |  |  | 81.456 |  | 23901.5069
2017-09-14 | 11:56 |  |  |  |  | 81.5553 |  | 23930.6657
2017-09-14 | 11:58 |  |  |  |  | 81.6117 |  | 23947.2139
2017-09-14 | 12:00 | 1.7444 | 0 | 0 | 1.5 | 81.5833 | 0 | 23938.875
2017-09-14 | 12:02 |  |  |  |  | 81.5808 |  | 23938.1408
2017-09-14 | 12:04 |  |  |  |  | 81.5886 |  | 23940.4152
2017-09-14 | 12:06 |  |  |  |  | 81.6493 |  | 23958.226
2017-09-14 | 12:08 |  |  |  |  | 81.688 |  | 23969.6055
2017-09-14 | 12:10 |  |  |  |  | 81.7925 |  | 24000.2573
2017-09-14 | 12:12 |  |  |  |  | 81.8334 |  | 24012.2544
2017-09-14 | 12:14 |  |  |  |  | 81.797 |  | 24001.5915
2017-09-14 | 12:15 | 1.7842 | 0 | 0 | 1.5 | 81.7854 | 0 | 23998.1599
2017-09-14 | 12:16 |  |  |  |  | 81.7772 |  | 23995.7555
2017-09-14 | 12:18 |  |  |  |  | 81.7057 |  | 23974.7857
2017-09-14 | 12:20 |  |  |  |  | 81.7258 |  | 23980.6912
2017-09-14 | 12:22 |  |  |  |  | 81.7985 |  | 24002.0193
2017-09-14 | 12:24 |  |  |  |  | 81.8903 |  | 24028.9438
2017-09-14 | 12:26 |  |  |  |  | 81.9011 |  | 24032.114
2017-09-14 | 12:28 |  |  |  |  | 81.8894 |  | 24028.6776
2017-09-14 | 12:30 | 1.7592 | 0 | 0 | 1.5 | 81.8745 | 0 | 24024.3255
2017-09-14 | 12:32 |  |  |  |  | 81.9979 |  | 24060.5205
2017-09-14 | 12:34 |  |  |  |  | 82.0222 |  | 24067.6529
2017-09-14 | 12:36 |  |  |  |  | 82.0932 |  | 24088.4816
2017-09-14 | 12:38 |  |  |  |  | 82.0602 |  | 24078.8105
2017-09-14 | 12:40 |  |  |  |  | 82.0319 |  | 24070.5073
2017-09-14 | 12:42 |  |  |  |  | 81.9042 |  | 24033.0339
2017-09-14 | 12:44 |  |  |  |  | 81.9151 |  | 24036.2173
2017-09-14 | 12:45 | 1.7304 | 0 | 0 | 1.5 | 81.9579 | 0 | 24048.7989
2017-09-14 | 12:46 |  |  |  |  | 82.0181 |  | 24066.4574
2017-09-14 | 12:48 |  |  |  |  | 82.1066 |  | 24092.4127
2017-09-14 | 12:50 |  |  |  |  | 82.1694 |  | 24110.8482
2017-09-14 | 12:52 |  |  |  |  | 82.1142 |  | 24094.665
2017-09-14 | 12:54 |  |  |  |  | 82.0236 |  | 24068.0672
2017-09-14 | 12:56 |  |  |  |  | 81.9958 |  | 24059.9204
2017-09-14 | 12:58 |  |  |  |  | 82.1014 |  | 24090.9106
2017-09-14 | 13:00 | 1.707 | 0 | 0 | 1.5 | 82.215 | 0 | 24124.2423
2017-09-14 | 13:02 |  |  |  |  | 82.2742 |  | 24141.6101
2017-09-14 | 13:04 |  |  |  |  | 82.3248 |  | 24156.4414
2017-09-14 | 13:06 |  |  |  |  | 82.3504 |  | 24163.9611
2017-09-14 | 13:08 |  |  |  |  | 82.3635 |  | 24167.8003
2017-09-14 | 13:10 |  |  |  |  | 82.3858 |  | 24174.3485
2017-09-14 | 13:12 |  |  |  |  | 82.5552 |  | 24224.0518
2017-09-14 | 13:14 |  |  |  |  | 82.6365 |  | 24247.9005
2017-09-14 | 13:15 | 1.7179 | 0 | 0 | 1.5 | 82.6617 | 0 | 24255.3128
2017-09-14 | 13:16 |  |  |  |  | 82.7156 |  | 24271.1066
2017-09-14 | 13:18 |  |  |  |  | 82.7077 |  | 24268.8099
2017-09-14 | 13:20 |  |  |  |  | 82.7114 |  | 24269.8912
2017-09-14 | 13:22 |  |  |  |  | 82.7501 |  | 24281.2433
2017-09-14 | 13:24 |  |  |  |  | 82.8985 |  | 24324.7746
2017-09-14 | 13:26 |  |  |  |  | 83.0216 |  | 24360.9112
2017-09-14 | 13:28 |  |  |  |  | 83.102 |  | 24384.4935
2017-09-14 | 13:30 | 1.7296 | 0 | 0 | 1.5 | 83.0983 | 0 | 24383.4169
2017-09-14 | 13:32 |  |  |  |  | 83.0657 |  | 24373.8465
2017-09-14 | 13:34 |  |  |  |  | 83.1001 |  | 24383.9363
2017-09-14 | 13:36 |  |  |  |  | 83.156 |  | 24400.348
2017-09-14 | 13:38 |  |  |  |  | 83.2818 |  | 24437.264
2017-09-14 | 13:40 |  |  |  |  | 83.3542 |  | 24458.5044
2017-09-14 | 13:42 |  |  |  |  | 83.4461 |  | 24485.4605
2017-09-14 | 13:44 |  |  |  |  | 83.4365 |  | 24482.6577
2017-09-14 | 13:45 | 1.76 | 0 | 0 | 1.5 | 83.4098 | 0 | 24474.8155
2017-09-14 | 13:46 |  |  |  |  | 83.4072 |  | 24474.0409
2017-09-14 | 13:48 |  |  |  |  | 83.42 |  | 24477.822
2017-09-14 | 13:50 |  |  |  |  | 83.5272 |  | 24509.2778
2017-09-14 | 13:52 |  |  |  |  | 83.6416 |  | 24542.8422
2017-09-14 | 13:54 |  |  |  |  | 83.6987 |  | 24559.5944
2017-09-14 | 13:56 |  |  |  |  | 83.7915 |  | 24586.8169
2017-09-14 | 13:58 |  |  |  |  | 83.7653 |  | 24579.1223
2017-09-14 | 14:00 | 1.7826 | 0 | 0 | 1.5 | 83.7025 | 0 | 24560.7047
2017-09-14 | 14:02 |  |  |  |  | 83.7453 |  | 24573.2526
2017-09-14 | 14:04 |  |  |  |  | 83.852 |  | 24604.5605
2017-09-14 | 14:06 |  |  |  |  | 83.9232 |  | 24625.4656
2017-09-14 | 14:08 |  |  |  |  | 83.9756 |  | 24640.845
2017-09-14 | 14:10 |  |  |  |  | 84.0491 |  | 24662.417
2017-09-14 | 14:12 |  |  |  |  | 84.0509 |  | 24662.932
2017-09-14 | 14:14 |  |  |  |  | 84.0701 |  | 24668.5579
2017-09-14 | 14:15 | 1.7436 | 0 | 0 | 1.5 | 84.0841 | 0 | 24672.6636
2017-09-14 | 14:16 |  |  |  |  | 84.1569 |  | 24694.0272
2017-09-14 | 14:18 |  |  |  |  | 84.2551 |  | 24722.8437
2017-09-14 | 14:20 |  |  |  |  | 84.3095 |  | 24738.8144
2017-09-14 | 14:22 |  |  |  |  | 84.3615 |  | 24754.0689
2017-09-14 | 14:24 |  |  |  |  | 84.4371 |  | 24776.2518
2017-09-14 | 14:26 |  |  |  |  | 84.4929 |  | 24792.6189
2017-09-14 | 14:28 |  |  |  |  | 84.4717 |  | 24786.4176
2017-09-14 | 14:30 | 1.7475 | 0 | 0 | 1.5 | 84.5145 | 0 | 24798.9722
2017-09-14 | 14:32 |  |  |  |  | 84.523 |  | 24801.4505
2017-09-14 | 14:34 |  |  |  |  | 84.4411 |  | 24777.4451
2017-09-14 | 14:36 |  |  |  |  | 84.4445 |  | 24778.4167
2017-09-14 | 14:38 |  |  |  |  | 84.5161 |  | 24799.4379
2017-09-14 | 14:40 |  |  |  |  | 84.5551 |  | 24810.8866
2017-09-14 | 14:42 |  |  |  |  | 84.5581 |  | 24811.773
2017-09-14 | 14:44 |  |  |  |  | 84.5571 |  | 24811.4732
2017-09-14 | 14:45 | 1.7725 | 0 | 0 | 1.5 | 84.5173 | 0 | 24799.7803
2017-09-14 | 14:46 |  |  |  |  | 84.4904 |  | 24791.8959
2017-09-14 | 14:48 |  |  |  |  | 84.4793 |  | 24788.6497
2017-09-14 | 14:50 |  |  |  |  | 84.5404 |  | 24806.577
2017-09-14 | 14:52 |  |  |  |  | 84.6111 |  | 24827.3095
2017-09-14 | 14:54 |  |  |  |  | 84.6285 |  | 24832.4228
2017-09-14 | 14:56 |  |  |  |  | 84.664 |  | 24842.8348
2017-09-14 | 14:58 |  |  |  |  | 84.6942 |  | 24851.7066
2017-09-14 | 15:00 | 1.7382 | 0 | 0 | 1.5 | 84.7068 | 0 | 24855.405
2017-09-14 | 15:02 |  |  |  |  | 84.7279 |  | 24861.5793
2017-09-14 | 15:04 |  |  |  |  | 84.7816 |  | 24877.3508
2017-09-14 | 15:06 |  |  |  |  | 84.8767 |  | 24905.2582
2017-09-14 | 15:08 |  |  |  |  | 84.9613 |  | 24930.0808
2017-09-14 | 15:10 |  |  |  |  | 85.0556 |  | 24957.7464
2017-09-14 | 15:12 |  |  |  |  | 85.0534 |  | 24957.0859
2017-09-14 | 15:14 |  |  |  |  | 85.0337 |  | 24951.3145
2017-09-14 | 15:15 | 1.7663 | 0 | 0 | 1.5 | 85.0012 | 0 | 24941.7689
2017-09-14 | 15:16 |  |  |  |  | 84.9987 |  | 24941.048
2017-09-14 | 15:18 |  |  |  |  | 85.039 |  | 24952.8661
2017-09-14 | 15:20 |  |  |  |  | 85.1294 |  | 24979.4079
2017-09-14 | 15:22 |  |  |  |  | 85.1246 |  | 24977.9772
2017-09-14 | 15:24 |  |  |  |  | 85.1346 |  | 24980.937
2017-09-14 | 15:26 |  |  |  |  | 85.1427 |  | 24983.292
2017-09-14 | 15:28 |  |  |  |  | 85.0931 |  | 24968.7406
2017-09-14 | 15:30 | 1.739 | 0 | 0 | 1.5 | 85.0983 | 0 | 24970.2852
2017-09-14 | 15:32 |  |  |  |  | 85.0795 |  | 24964.7647
2017-09-14 | 15:34 |  |  |  |  | 84.9446 |  | 24925.1847
2017-09-14 | 15:36 |  |  |  |  | 84.8608 |  | 24900.5728
2017-09-14 | 15:38 |  |  |  |  | 84.8703 |  | 24903.3597
2017-09-14 | 15:40 |  |  |  |  | 84.8114 |  | 24886.0997
2017-09-14 | 15:42 |  |  |  |  | 84.8522 |  | 24898.0722
2017-09-14 | 15:44 |  |  |  |  | 84.8315 |  | 24891.9917
2017-09-14 | 15:45 | 1.721 | 0 | 0 | 1.5 | 84.8685 | 0 | 24902.8448
2017-09-14 | 15:46 |  |  |  |  | 84.8958 |  | 24910.8571
2017-09-14 | 15:48 |  |  |  |  | 84.8584 |  | 24899.8832
2017-09-14 | 15:50 |  |  |  |  | 84.7797 |  | 24876.7889
2017-09-14 | 15:52 |  |  |  |  | 84.6656 |  | 24843.3093
2017-09-14 | 15:54 |  |  |  |  | 84.6994 |  | 24853.2245
2017-09-14 | 15:56 |  |  |  |  | 84.7153 |  | 24857.8809
2017-09-14 | 15:58 |  |  |  |  | 84.6858 |  | 24849.2239
2017-09-14 | 16:00 | 1.7413 | 0 | 0 | 1.5 | 84.6772 | 0 | 24846.7166
2017-09-14 | 16:02 |  |  |  |  | 84.6937 |  | 24851.5611
2017-09-14 | 16:04 |  |  |  |  | 84.7809 |  | 24877.1293
2017-09-14 | 16:06 |  |  |  |  | 84.8331 |  | 24892.4483
2017-09-14 | 16:08 |  |  |  |  | 84.771 |  | 24874.2211
2017-09-14 | 16:10 |  |  |  |  | 84.6702 |  | 24844.6549
2017-09-14 | 16:12 |  |  |  |  | 84.704 |  | 24854.5878
2017-09-14 | 16:14 |  |  |  |  | 84.5835 |  | 24819.2279
2017-09-14 | 16:15 | 1.7546 | 0 | 0 | 1.5 | 84.5897 | 0 | 24821.0254
2017-09-14 | 16:16 |  |  |  |  | 84.5619 |  | 24812.8699
2017-09-14 | 16:18 |  |  |  |  | 84.4617 |  | 24783.476
2017-09-14 | 16:20 |  |  |  |  | 84.4198 |  | 24771.1813
2017-09-14 | 16:22 |  |  |  |  | 84.3873 |  | 24761.651
2017-09-14 | 16:24 |  |  |  |  | 84.3226 |  | 24742.665
2017-09-14 | 16:26 |  |  |  |  | 84.2601 |  | 24724.3211
2017-09-14 | 16:28 |  |  |  |  | 84.1942 |  | 24704.9967
2017-09-14 | 16:30 | 1.7897 | 0 | 0 | 1.5 | 84.1218 | 0 | 24683.7384
2017-09-14 | 16:32 |  |  |  |  | 83.9103 |  | 24621.6888
2017-09-14 | 16:34 |  |  |  |  | 83.7358 |  | 24570.4788
2017-09-14 | 16:36 |  |  |  |  | 83.6149 |  | 24535.0071
2017-09-14 | 16:38 |  |  |  |  | 83.5425 |  | 24513.7441
2017-09-14 | 16:40 |  |  |  |  | 83.4782 |  | 24494.8966
2017-09-14 | 16:42 |  |  |  |  | 83.3932 |  | 24469.942
2017-09-14 | 16:44 |  |  |  |  | 83.3334 |  | 24452.402
2017-09-14 | 16:45 | 1.8099 | 0 | 0 | 1.5 | 83.1846 | 0 | 24408.7251
2017-09-14 | 16:46 |  |  |  |  | 83.112 |  | 24387.4486
2017-09-14 | 16:48 |  |  |  |  | 82.9032 |  | 24326.1781
2017-09-14 | 16:50 |  |  |  |  | 82.8185 |  | 24301.3042
2017-09-14 | 16:52 |  |  |  |  | 82.7647 |  | 24285.5259
2017-09-14 | 16:54 |  |  |  |  | 82.6848 |  | 24262.0959
2017-09-14 | 16:56 |  |  |  |  | 82.7162 |  | 24271.297
2017-09-14 | 16:58 |  |  |  |  | 82.6904 |  | 24263.7324
2017-09-14 | 17:00 | 1.7725 | 0 | 0 | 1.5 | 82.6512 | 0 | 24252.2144
2017-09-14 | 17:02 |  |  |  |  | 82.5 |  | 24207.8436
2017-09-14 | 17:04 |  |  |  |  | 82.3996 |  | 24178.3825
2017-09-14 | 17:06 |  |  |  |  | 82.4186 |  | 24183.977
2017-09-14 | 17:08 |  |  |  |  | 82.4264 |  | 24186.2538
2017-09-14 | 17:10 |  |  |  |  | 82.4248 |  | 24185.7816
2017-09-14 | 17:12 |  |  |  |  | 82.3857 |  | 24174.3306
2017-09-14 | 17:14 |  |  |  |  | 82.3113 |  | 24152.4901
2017-09-14 | 17:15 | 1.8045 | 0 | 0 | 1.5 | 82.2099 | 0 | 24122.7312
2017-09-14 | 17:16 |  |  |  |  | 82.0965 |  | 24089.4443
2017-09-14 | 17:18 |  |  |  |  | 81.9563 |  | 24048.3062
2017-09-14 | 17:20 |  |  |  |  | 81.7833 |  | 23997.571
2017-09-14 | 17:22 |  |  |  |  | 81.7681 |  | 23993.0868
2017-09-14 | 17:24 |  |  |  |  | 81.6685 |  | 23963.8857
2017-09-14 | 17:26 |  |  |  |  | 81.5399 |  | 23926.1437
2017-09-14 | 17:28 |  |  |  |  | 81.3596 |  | 23873.2435
2017-09-14 | 17:30 | 1.7756 | 0 | 0 | 1.5 | 81.2621 | 0 | 23844.6331
2017-09-14 | 17:32 |  |  |  |  | 81.2432 |  | 23839.0746
2017-09-14 | 17:34 |  |  |  |  | 81.2262 |  | 23834.1025
2017-09-14 | 17:36 |  |  |  |  | 81.2014 |  | 23826.8087
2017-09-14 | 17:38 |  |  |  |  | 81.1033 |  | 23798.0328
2017-09-14 | 17:40 |  |  |  |  | 80.9663 |  | 23757.8216
2017-09-14 | 17:42 |  |  |  |  | 80.9207 |  | 23744.4545
2017-09-14 | 17:44 |  |  |  |  | 80.9165 |  | 23743.2098
2017-09-14 | 17:45 | 1.7538 | 0 | 0 | 1.5 | 80.852 | 0 | 23724.2907
2017-09-14 | 17:46 |  |  |  |  | 80.8103 |  | 23712.0518
2017-09-14 | 17:48 |  |  |  |  | 80.7088 |  | 23682.2729
2017-09-14 | 17:50 |  |  |  |  | 80.5578 |  | 23637.9737
2017-09-14 | 17:52 |  |  |  |  | 80.4504 |  | 23606.453
2017-09-14 | 17:54 |  |  |  |  | 80.4268 |  | 23599.5354
2017-09-14 | 17:56 |  |  |  |  | 80.3422 |  | 23574.6973
2017-09-14 | 17:58 |  |  |  |  | 80.2902 |  | 23559.4384
2017-09-14 | 18:00 | 1.7951 | 0 | 0 | 1.5 | 80.1566 | 0 | 23520.2258
2017-09-14 | 18:02 |  |  |  |  | 80.1189 |  | 23509.1667
2017-09-14 | 18:04 |  |  |  |  | 79.9974 |  | 23473.5111
2017-09-14 | 18:06 |  |  |  |  | 79.9238 |  | 23451.9235
2017-09-14 | 18:08 |  |  |  |  | 79.9205 |  | 23450.9587
2017-09-14 | 18:10 |  |  |  |  | 79.869 |  | 23435.8342
2017-09-14 | 18:12 |  |  |  |  | 79.7416 |  | 23398.4661
2017-09-14 | 18:14 |  |  |  |  | 79.6467 |  | 23370.6259
2017-09-14 | 18:15 | 1.7686 | 0 | 0 | 1.5 | 79.5916 | 0 | 23354.4424
2017-09-14 | 18:16 |  |  |  |  | 79.5582 |  | 23344.6413
2017-09-14 | 18:18 |  |  |  |  | 79.5329 |  | 23337.2179
2017-09-14 | 18:20 |  |  |  |  | 79.4406 |  | 23310.15
2017-09-14 | 18:22 |  |  |  |  | 79.35 |  | 23283.5434
2017-09-14 | 18:24 |  |  |  |  | 79.2121 |  | 23243.0813
2017-09-14 | 18:26 |  |  |  |  | 79.079 |  | 23204.0298
2017-09-14 | 18:28 |  |  |  |  | 78.9991 |  | 23180.6042
2017-09-14 | 18:30 | 1.7592 | 0 | 0 | 1.5 | 78.9617 | 0 | 23169.6279
2017-09-14 | 18:32 |  |  |  |  | 78.9368 |  | 23162.3119
2017-09-14 | 18:34 |  |  |  |  | 78.8282 |  | 23130.442
2017-09-14 | 18:36 |  |  |  |  | 78.6914 |  | 23090.2913
2017-09-14 | 18:38 |  |  |  |  | 78.572 |  | 23055.2647
2017-09-14 | 18:40 |  |  |  |  | 78.4425 |  | 23017.2833
2017-09-14 | 18:42 |  |  |  |  | 78.4611 |  | 23022.7256
2017-09-14 | 18:44 |  |  |  |  | 78.6701 |  | 23084.0542
2017-09-14 | 18:45 | 1.6922 | 0 | 0 | 1.5 | 78.7596 | 0 | 23110.3298
2017-09-14 | 18:46 |  |  |  |  | 78.91 |  | 23154.4518
2017-09-14 | 18:48 |  |  |  |  | 78.9445 |  | 23164.5686
2017-09-14 | 18:50 |  |  |  |  | 78.9975 |  | 23180.1115
2017-09-14 | 18:52 |  |  |  |  | 79.0023 |  | 23181.5423
2017-09-14 | 18:54 |  |  |  |  | 78.9437 |  | 23164.3512
2017-09-14 | 18:56 |  |  |  |  | 78.8455 |  | 23135.5148
2017-09-14 | 18:58 |  |  |  |  | 78.7217 |  | 23099.1989
2017-09-14 | 19:00 | 1.806 | 0 | 0 | 1.5 | 78.5774 | 0 | 23056.8498
2017-09-14 | 19:02 |  |  |  |  | 78.5331 |  | 23043.8589
2017-09-14 | 19:04 |  |  |  |  | 78.4869 |  | 23030.3101
2017-09-14 | 19:06 |  |  |  |  | 78.4146 |  | 23009.0832
2017-09-14 | 19:08 |  |  |  |  | 78.4096 |  | 23007.619
2017-09-14 | 19:10 |  |  |  |  | 78.5117 |  | 23037.5636
2017-09-14 | 19:12 |  |  |  |  | 78.5504 |  | 23048.9182
2017-09-14 | 19:14 |  |  |  |  | 78.4895 |  | 23031.0601
2017-09-14 | 19:15 | 1.7702 | 0 | 0 | 1.5 | 78.4596 | 0 | 23022.298
2017-09-14 | 19:16 |  |  |  |  | 78.4299 |  | 23013.5715
2017-09-14 | 19:18 |  |  |  |  | 78.4205 |  | 23010.8091
2017-09-14 | 19:20 |  |  |  |  | 78.4258 |  | 23012.3807
2017-09-14 | 19:22 |  |  |  |  | 78.4263 |  | 23012.5172
2017-09-14 | 19:24 |  |  |  |  | 78.3412 |  | 22987.5446
2017-09-14 | 19:26 |  |  |  |  | 78.1486 |  | 22931.018
2017-09-14 | 19:28 |  |  |  |  | 78.2056 |  | 22947.7522
2017-09-14 | 19:30 | 1.6984 | 0 | 0 | 1.5 | 78.3294 | 0 | 22984.0792
2017-09-14 | 19:32 |  |  |  |  | 78.4099 |  | 23007.6973
2017-09-14 | 19:34 |  |  |  |  | 78.3046 |  | 22976.8057
2017-09-14 | 19:36 |  |  |  |  | 78.282 |  | 22970.1637
2017-09-14 | 19:38 |  |  |  |  | 78.326 |  | 22983.101
2017-09-14 | 19:40 |  |  |  |  | 78.258 |  | 22963.1364
2017-09-14 | 19:42 |  |  |  |  | 78.2357 |  | 22956.5771
2017-09-14 | 19:44 |  |  |  |  | 78.3336 |  | 22985.3037
2017-09-14 | 19:45 | 1.7163 | 0 | 0 | 1.5 | 78.3806 | 0 | 22999.121
2017-09-14 | 19:46 |  |  |  |  | 78.4296 |  | 23013.4752
2017-09-14 | 19:48 |  |  |  |  | 78.3894 |  | 23001.682
2017-09-14 | 19:50 |  |  |  |  | 78.3072 |  | 22977.5824
2017-09-14 | 19:52 |  |  |  |  | 78.3247 |  | 22982.7025
2017-09-14 | 19:54 |  |  |  |  | 78.3102 |  | 22978.4601
2017-09-14 | 19:56 |  |  |  |  | 78.2657 |  | 22965.3796
2017-09-14 | 19:58 |  |  |  |  | 78.2926 |  | 22973.2931
2017-09-14 | 20:00 | 1.7156 | 0 | 0 | 1.5 | 78.3838 | 0 | 23000.0611
2017-09-14 | 20:02 |  |  |  |  | 78.4443 |  | 23017.805
2017-09-14 | 20:04 |  |  |  |  | 78.3485 |  | 22989.687
2017-09-14 | 20:06 |  |  |  |  | 78.2896 |  | 22972.4178
2017-09-14 | 20:08 |  |  |  |  | 78.2643 |  | 22964.9744
2017-09-14 | 20:10 |  |  |  |  | 78.2067 |  | 22948.0791
2017-09-14 | 20:12 |  |  |  |  | 78.2192 |  | 22951.7549
2017-09-14 | 20:14 |  |  |  |  | 78.2604 |  | 22963.828
2017-09-14 | 20:15 | 1.7124 | 0 | 0 | 1.5 | 78.352 | 0 | 22990.726
2017-09-14 | 20:16 |  |  |  |  | 78.3888 |  | 23001.5142
2017-09-14 | 20:18 |  |  |  |  | 78.3096 |  | 22978.2653
2017-09-14 | 20:20 |  |  |  |  | 78.2239 |  | 22953.1384
2017-09-14 | 20:22 |  |  |  |  | 78.1453 |  | 22930.0664
2017-09-14 | 20:24 |  |  |  |  | 78.0042 |  | 22888.6689
2017-09-14 | 20:26 |  |  |  |  | 77.9746 |  | 22879.967
2017-09-14 | 20:28 |  |  |  |  | 78.0683 |  | 22907.4739
2017-09-14 | 20:30 | 1.7031 | 0 | 0 | 1.5 | 78.2192 | 0 | 22951.7414
2017-09-14 | 20:32 |  |  |  |  | 78.3515 |  | 22990.5737
2017-09-14 | 20:34 |  |  |  |  | 78.2772 |  | 22968.7711
2017-09-14 | 20:36 |  |  |  |  | 78.1963 |  | 22945.0166
2017-09-14 | 20:38 |  |  |  |  | 78.0618 |  | 22905.5619
2017-09-14 | 20:40 |  |  |  |  | 77.8751 |  | 22850.7679
2017-09-14 | 20:42 |  |  |  |  | 77.7557 |  | 22815.746
2017-09-14 | 20:44 |  |  |  |  | 77.8153 |  | 22833.2188
2017-09-14 | 20:45 | 1.7218 | 0 | 0 | 1.5 | 77.8474 | 0 | 22842.666
2017-09-14 | 20:46 |  |  |  |  | 77.8812 |  | 22852.5789
2017-09-14 | 20:48 |  |  |  |  | 77.789 |  | 22825.5201
2017-09-14 | 20:50 |  |  |  |  | 77.6784 |  | 22793.0593
2017-09-14 | 20:52 |  |  |  |  | 77.618 |  | 22775.3356
2017-09-14 | 20:54 |  |  |  |  | 77.8175 |  | 22833.8905
2017-09-14 | 20:56 |  |  |  |  | 78.0222 |  | 22893.9318
2017-09-14 | 20:58 |  |  |  |  | 78.0361 |  | 22898.0199
2017-09-14 | 21:00 | 1.7405 | 0 | 0 | 1.5 | 78.0631 | 0 | 22905.9424
2017-09-14 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:15 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:30 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:45 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-14 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:00 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:15 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:45 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:00 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:45 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:00 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:30 | 0.0409 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:45 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:00 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:15 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:30 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:45 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 5:00 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 5:02 |  |  |  |  | 70 |  | 20540
2017-09-15 | 5:04 |  |  |  |  | 99.236 |  | 29118.6801
2017-09-15 | 5:06 |  |  |  |  | 96.6833 |  | 28369.6526
2017-09-15 | 5:08 |  |  |  |  | 93.9316 |  | 27562.2225
2017-09-15 | 5:10 |  |  |  |  | 91.8385 |  | 26948.0267
2017-09-15 | 5:12 |  |  |  |  | 90.006 |  | 26410.3244
2017-09-15 | 5:14 |  |  |  |  | 88.5204 |  | 25974.4216
2017-09-15 | 5:15 | 2.2046 | 0 | 0 | 1.5 | 87.8488 | 0 | 25777.3549
2017-09-15 | 5:16 |  |  |  |  | 87.2555 |  | 25603.2459
2017-09-15 | 5:18 |  |  |  |  | 86.2429 |  | 25306.1392
2017-09-15 | 5:20 |  |  |  |  | 85.3513 |  | 25044.5177
2017-09-15 | 5:22 |  |  |  |  | 84.5997 |  | 24823.9603
2017-09-15 | 5:24 |  |  |  |  | 84.0107 |  | 24651.1365
2017-09-15 | 5:26 |  |  |  |  | 83.4911 |  | 24498.6598
2017-09-15 | 5:28 |  |  |  |  | 83.0171 |  | 24359.5838
2017-09-15 | 5:30 | 1.8614 | 0 | 0 | 1.5 | 82.6941 | 0 | 24264.8204
2017-09-15 | 5:32 |  |  |  |  | 82.3783 |  | 24172.1501
2017-09-15 | 5:34 |  |  |  |  | 82.1425 |  | 24102.9591
2017-09-15 | 5:36 |  |  |  |  | 81.8749 |  | 24024.4308
2017-09-15 | 5:38 |  |  |  |  | 81.7485 |  | 23987.3335
2017-09-15 | 5:40 |  |  |  |  | 81.5639 |  | 23933.1886
2017-09-15 | 5:42 |  |  |  |  | 81.4547 |  | 23901.1421
2017-09-15 | 5:44 |  |  |  |  | 81.3149 |  | 23860.1023
2017-09-15 | 5:45 | 1.7951 | 0 | 0 | 1.5 | 81.262 | 0 | 23844.5952
2017-09-15 | 5:46 |  |  |  |  | 81.2041 |  | 23827.6168
2017-09-15 | 5:48 |  |  |  |  | 81.1566 |  | 23813.6631
2017-09-15 | 5:50 |  |  |  |  | 81.0956 |  | 23795.774
2017-09-15 | 5:52 |  |  |  |  | 80.9902 |  | 23764.8264
2017-09-15 | 5:54 |  |  |  |  | 80.9804 |  | 23761.9631
2017-09-15 | 5:56 |  |  |  |  | 80.9444 |  | 23751.3964
2017-09-15 | 5:58 |  |  |  |  | 80.8911 |  | 23735.7526
2017-09-15 | 6:00 | 1.7631 | 0 | 0 | 1.5 | 80.8712 | 0 | 23729.9321
2017-09-15 | 6:02 |  |  |  |  | 80.8838 |  | 23733.6238
2017-09-15 | 6:04 |  |  |  |  | 80.8768 |  | 23731.5706
2017-09-15 | 6:06 |  |  |  |  | 80.8296 |  | 23717.7155
2017-09-15 | 6:08 |  |  |  |  | 80.8413 |  | 23721.1451
2017-09-15 | 6:10 |  |  |  |  | 80.8421 |  | 23721.3737
2017-09-15 | 6:12 |  |  |  |  | 80.8373 |  | 23719.9834
2017-09-15 | 6:14 |  |  |  |  | 80.8512 |  | 23724.0489
2017-09-15 | 6:15 | 1.7741 | 0 | 0 | 1.5 | 80.882 | 0 | 23733.0976
2017-09-15 | 6:16 |  |  |  |  | 80.8562 |  | 23725.5286
2017-09-15 | 6:18 |  |  |  |  | 80.9151 |  | 23742.7978
2017-09-15 | 6:20 |  |  |  |  | 80.9323 |  | 23747.8571
2017-09-15 | 6:22 |  |  |  |  | 80.9686 |  | 23758.4997
2017-09-15 | 6:24 |  |  |  |  | 80.9884 |  | 23764.3181
2017-09-15 | 6:26 |  |  |  |  | 81.0415 |  | 23779.8971
2017-09-15 | 6:28 |  |  |  |  | 81.0364 |  | 23778.3927
2017-09-15 | 6:30 | 1.7577 | 0 | 0 | 1.5 | 81.0766 | 0 | 23790.1906
2017-09-15 | 6:32 |  |  |  |  | 81.0904 |  | 23794.2493
2017-09-15 | 6:34 |  |  |  |  | 81.096 |  | 23795.8905
2017-09-15 | 6:36 |  |  |  |  | 81.1321 |  | 23806.4882
2017-09-15 | 6:38 |  |  |  |  | 81.1483 |  | 23811.2297
2017-09-15 | 6:40 |  |  |  |  | 81.1618 |  | 23815.1855
2017-09-15 | 6:42 |  |  |  |  | 81.2365 |  | 23837.109
2017-09-15 | 6:44 |  |  |  |  | 81.2469 |  | 23840.1492
2017-09-15 | 6:45 | 1.7405 | 0 | 0 | 1.5 | 81.2377 | 0 | 23837.4693
2017-09-15 | 6:46 |  |  |  |  | 81.2718 |  | 23847.4652
2017-09-15 | 6:48 |  |  |  |  | 81.2944 |  | 23854.0894
2017-09-15 | 6:50 |  |  |  |  | 81.3076 |  | 23857.9691
2017-09-15 | 6:52 |  |  |  |  | 81.3411 |  | 23867.799
2017-09-15 | 6:54 |  |  |  |  | 81.3617 |  | 23873.8368
2017-09-15 | 6:56 |  |  |  |  | 81.3933 |  | 23883.1183
2017-09-15 | 6:58 |  |  |  |  | 81.3883 |  | 23881.6476
2017-09-15 | 7:00 | 1.728 | 0 | 0 | 1.5 | 81.4122 | 0 | 23888.6658
2017-09-15 | 7:02 |  |  |  |  | 81.4526 |  | 23900.5151
2017-09-15 | 7:04 |  |  |  |  | 81.476 |  | 23907.3745
2017-09-15 | 7:06 |  |  |  |  | 81.5188 |  | 23919.9403
2017-09-15 | 7:08 |  |  |  |  | 81.536 |  | 23924.9952
2017-09-15 | 7:10 |  |  |  |  | 81.5503 |  | 23929.1904
2017-09-15 | 7:12 |  |  |  |  | 81.5664 |  | 23933.9072
2017-09-15 | 7:14 |  |  |  |  | 81.5603 |  | 23932.1097
2017-09-15 | 7:15 | 1.7569 | 0 | 0 | 1.5 | 81.5592 | 0 | 23931.8098
2017-09-15 | 7:16 |  |  |  |  | 81.5659 |  | 23933.7596
2017-09-15 | 7:18 |  |  |  |  | 81.6022 |  | 23944.4179
2017-09-15 | 7:20 |  |  |  |  | 81.5785 |  | 23937.4533
2017-09-15 | 7:22 |  |  |  |  | 81.6015 |  | 23944.2054
2017-09-15 | 7:24 |  |  |  |  | 81.6186 |  | 23949.2357
2017-09-15 | 7:26 |  |  |  |  | 81.6561 |  | 23960.2319
2017-09-15 | 7:28 |  |  |  |  | 81.6602 |  | 23961.4388
2017-09-15 | 7:30 | 1.7553 | 0 | 0 | 1.5 | 81.6533 | 0 | 23959.4059
2017-09-15 | 7:32 |  |  |  |  | 81.6616 |  | 23961.8372
2017-09-15 | 7:34 |  |  |  |  | 81.7158 |  | 23977.7408
2017-09-15 | 7:36 |  |  |  |  | 81.7332 |  | 23982.8494
2017-09-15 | 7:38 |  |  |  |  | 81.8077 |  | 24004.7168
2017-09-15 | 7:40 |  |  |  |  | 81.9105 |  | 24034.8898
2017-09-15 | 7:42 |  |  |  |  | 81.9545 |  | 24047.7781
2017-09-15 | 7:44 |  |  |  |  | 82.011 |  | 24064.3665
2017-09-15 | 7:45 | 1.7358 | 0 | 0 | 1.5 | 82.029 | 0 | 24069.6388
2017-09-15 | 7:46 |  |  |  |  | 82.0451 |  | 24074.3645
2017-09-15 | 7:48 |  |  |  |  | 82.1103 |  | 24093.4986
2017-09-15 | 7:50 |  |  |  |  | 82.1565 |  | 24107.0694
2017-09-15 | 7:52 |  |  |  |  | 82.2076 |  | 24122.0463
2017-09-15 | 7:54 |  |  |  |  | 82.264 |  | 24138.6124
2017-09-15 | 7:56 |  |  |  |  | 82.2906 |  | 24146.4255
2017-09-15 | 7:58 |  |  |  |  | 82.3836 |  | 24173.7082
2017-09-15 | 8:00 | 1.7405 | 0 | 0 | 1.5 | 82.446 | 0 | 24192.0073
2017-09-15 | 8:02 |  |  |  |  | 82.4828 |  | 24202.8134
2017-09-15 | 8:04 |  |  |  |  | 82.5933 |  | 24235.2361
2017-09-15 | 8:06 |  |  |  |  | 82.6489 |  | 24251.5472
2017-09-15 | 8:08 |  |  |  |  | 82.7006 |  | 24266.7078
2017-09-15 | 8:10 |  |  |  |  | 82.7419 |  | 24278.8413
2017-09-15 | 8:12 |  |  |  |  | 82.7969 |  | 24294.9732
2017-09-15 | 8:14 |  |  |  |  | 82.8283 |  | 24304.1965
2017-09-15 | 8:15 | 1.7483 | 0 | 0 | 1.5 | 82.8522 | 0 | 24311.2103
2017-09-15 | 8:16 |  |  |  |  | 82.8844 |  | 24320.6396
2017-09-15 | 8:18 |  |  |  |  | 82.9231 |  | 24331.9921
2017-09-15 | 8:20 |  |  |  |  | 82.9621 |  | 24343.4496
2017-09-15 | 8:22 |  |  |  |  | 82.9849 |  | 24350.1477
2017-09-15 | 8:24 |  |  |  |  | 83.0094 |  | 24357.3229
2017-09-15 | 8:26 |  |  |  |  | 83.0424 |  | 24367.0207
2017-09-15 | 8:28 |  |  |  |  | 83.1409 |  | 24395.9199
2017-09-15 | 8:30 | 1.7218 | 0 | 0 | 1.5 | 83.1513 | 0 | 24398.9645
2017-09-15 | 8:32 |  |  |  |  | 83.232 |  | 24422.6454
2017-09-15 | 8:34 |  |  |  |  | 83.284 |  | 24437.8996
2017-09-15 | 8:36 |  |  |  |  | 83.3724 |  | 24463.8504
2017-09-15 | 8:38 |  |  |  |  | 83.4094 |  | 24474.6946
2017-09-15 | 8:40 |  |  |  |  | 83.4936 |  | 24499.4075
2017-09-15 | 8:42 |  |  |  |  | 83.584 |  | 24525.9246
2017-09-15 | 8:44 |  |  |  |  | 83.6831 |  | 24555.0096
2017-09-15 | 8:45 | 1.6844 | 0 | 0 | 1.5 | 83.8025 | 0 | 24590.0405
2017-09-15 | 8:46 |  |  |  |  | 83.9709 |  | 24639.4615
2017-09-15 | 8:48 |  |  |  |  | 84.2229 |  | 24713.3964
2017-09-15 | 8:50 |  |  |  |  | 84.5711 |  | 24815.5653
2017-09-15 | 8:52 |  |  |  |  | 84.9833 |  | 24936.5327
2017-09-15 | 8:54 |  |  |  |  | 85.402 |  | 25059.3936
2017-09-15 | 8:56 |  |  |  |  | 85.9303 |  | 25214.4046
2017-09-15 | 8:58 |  |  |  |  | 86.5528 |  | 25397.0765
2017-09-15 | 9:00 | 1.5432 | 0 | 0 | 1.5 | 87.178 | 0 | 25580.5119
2017-09-15 | 9:02 |  |  |  |  | 87.7121 |  | 25737.2265
2017-09-15 | 9:04 |  |  |  |  | 88.0371 |  | 25832.592
2017-09-15 | 9:06 |  |  |  |  | 88.2862 |  | 25905.6938
2017-09-15 | 9:08 |  |  |  |  | 88.35 |  | 25924.4228
2017-09-15 | 9:10 |  |  |  |  | 88.3872 |  | 25935.3342
2017-09-15 | 9:12 |  |  |  |  | 88.3344 |  | 25919.8424
2017-09-15 | 9:14 |  |  |  |  | 88.0681 |  | 25841.7035
2017-09-15 | 9:15 | 1.8505 | 0 | 0 | 1.5 | 87.8882 | 0 | 25788.9107
2017-09-15 | 9:16 |  |  |  |  | 87.7046 |  | 25735.0258
2017-09-15 | 9:18 |  |  |  |  | 87.3969 |  | 25644.7396
2017-09-15 | 9:20 |  |  |  |  | 87.0646 |  | 25547.2362
2017-09-15 | 9:22 |  |  |  |  | 86.6627 |  | 25429.3114
2017-09-15 | 9:24 |  |  |  |  | 86.3198 |  | 25328.6915
2017-09-15 | 9:26 |  |  |  |  | 85.9657 |  | 25224.7943
2017-09-15 | 9:28 |  |  |  |  | 85.6331 |  | 25127.1923
2017-09-15 | 9:30 | 1.8552 | 0 | 0 | 1.5 | 85.2514 | 0 | 25015.1886
2017-09-15 | 9:32 |  |  |  |  | 84.9045 |  | 24913.4003
2017-09-15 | 9:34 |  |  |  |  | 84.6091 |  | 24826.7141
2017-09-15 | 9:36 |  |  |  |  | 84.4134 |  | 24769.2984
2017-09-15 | 9:38 |  |  |  |  | 84.2254 |  | 24714.1306
2017-09-15 | 9:40 |  |  |  |  | 84.0849 |  | 24672.9053
2017-09-15 | 9:42 |  |  |  |  | 83.8683 |  | 24609.3581
2017-09-15 | 9:44 |  |  |  |  | 83.6644 |  | 24549.516
2017-09-15 | 9:45 | 1.8053 | 0 | 0 | 1.5 | 83.5637 | 0 | 24519.9654
2017-09-15 | 9:46 |  |  |  |  | 83.5108 |  | 24504.4556
2017-09-15 | 9:48 |  |  |  |  | 83.3296 |  | 24451.2826
2017-09-15 | 9:50 |  |  |  |  | 83.1029 |  | 24384.7734
2017-09-15 | 9:52 |  |  |  |  | 82.9796 |  | 24348.5852
2017-09-15 | 9:54 |  |  |  |  | 82.8181 |  | 24301.2056
2017-09-15 | 9:56 |  |  |  |  | 82.6374 |  | 24248.1736
2017-09-15 | 9:58 |  |  |  |  | 82.4416 |  | 24190.7356
2017-09-15 | 10:00 | 1.7967 | 0 | 0 | 1.5 | 82.3345 | 0 | 24159.2844
2017-09-15 | 10:02 |  |  |  |  | 82.1957 |  | 24118.5539
2017-09-15 | 10:04 |  |  |  |  | 82.1679 |  | 24110.4095
2017-09-15 | 10:06 |  |  |  |  | 82.1777 |  | 24113.2839
2017-09-15 | 10:08 |  |  |  |  | 82.1951 |  | 24118.3972
2017-09-15 | 10:10 |  |  |  |  | 82.2079 |  | 24122.1514
2017-09-15 | 10:12 |  |  |  |  | 82.0841 |  | 24085.8267
2017-09-15 | 10:14 |  |  |  |  | 82.0089 |  | 24063.7643
2017-09-15 | 10:15 | 1.7624 | 0 | 0 | 1.5 | 81.9737 | 0 | 24053.4327
2017-09-15 | 10:16 |  |  |  |  | 81.8931 |  | 24029.7677
2017-09-15 | 10:18 |  |  |  |  | 81.8225 |  | 24009.0464
2017-09-15 | 10:20 |  |  |  |  | 81.7897 |  | 23999.4269
2017-09-15 | 10:22 |  |  |  |  | 81.8249 |  | 24009.7673
2017-09-15 | 10:24 |  |  |  |  | 81.8324 |  | 24011.9501
2017-09-15 | 10:26 |  |  |  |  | 81.8049 |  | 24003.8817
2017-09-15 | 10:28 |  |  |  |  | 81.7446 |  | 23986.2121
2017-09-15 | 10:30 | 1.7795 | 0 | 0 | 1.5 | 81.6542 | 0 | 23959.6723
2017-09-15 | 10:32 |  |  |  |  | 81.5848 |  | 23939.3248
2017-09-15 | 10:34 |  |  |  |  | 81.5209 |  | 23920.558
2017-09-15 | 10:36 |  |  |  |  | 81.568 |  | 23934.3864
2017-09-15 | 10:38 |  |  |  |  | 81.5517 |  | 23929.6114
2017-09-15 | 10:40 |  |  |  |  | 81.6119 |  | 23947.2565
2017-09-15 | 10:42 |  |  |  |  | 81.6765 |  | 23966.2249
2017-09-15 | 10:44 |  |  |  |  | 81.7569 |  | 23989.8206
2017-09-15 | 10:45 | 1.7397 | 0 | 0 | 1.5 | 81.7378 | 0 | 23984.1994
2017-09-15 | 10:46 |  |  |  |  | 81.6614 |  | 23961.7768
2017-09-15 | 10:48 |  |  |  |  | 81.6436 |  | 23956.574
2017-09-15 | 10:50 |  |  |  |  | 81.6102 |  | 23946.7618
2017-09-15 | 10:52 |  |  |  |  | 81.5312 |  | 23923.5847
2017-09-15 | 10:54 |  |  |  |  | 81.4951 |  | 23912.9779
2017-09-15 | 10:56 |  |  |  |  | 81.4912 |  | 23911.8584
2017-09-15 | 10:58 |  |  |  |  | 81.5662 |  | 23933.8515
2017-09-15 | 11:00 | 1.7616 | 0 | 0 | 1.5 | 81.5483 | 0 | 23928.5906
2017-09-15 | 11:02 |  |  |  |  | 81.5162 |  | 23919.1701
2017-09-15 | 11:04 |  |  |  |  | 81.4411 |  | 23897.1459
2017-09-15 | 11:06 |  |  |  |  | 81.481 |  | 23908.8499
2017-09-15 | 11:08 |  |  |  |  | 81.3995 |  | 23884.9408
2017-09-15 | 11:10 |  |  |  |  | 81.4197 |  | 23890.8798
2017-09-15 | 11:12 |  |  |  |  | 81.487 |  | 23910.6073
2017-09-15 | 11:14 |  |  |  |  | 81.4163 |  | 23889.8768
2017-09-15 | 11:15 | 1.7639 | 0 | 0 | 1.5 | 81.4249 | 0 | 23892.3953
2017-09-15 | 11:16 |  |  |  |  | 81.3826 |  | 23879.9909
2017-09-15 | 11:18 |  |  |  |  | 81.2074 |  | 23828.5819
2017-09-15 | 11:20 |  |  |  |  | 81.1429 |  | 23809.6335
2017-09-15 | 11:22 |  |  |  |  | 81.1015 |  | 23797.5067
2017-09-15 | 11:24 |  |  |  |  | 81.1052 |  | 23798.588
2017-09-15 | 11:26 |  |  |  |  | 81.0406 |  | 23779.6219
2017-09-15 | 11:28 |  |  |  |  | 81.0902 |  | 23794.1754
2017-09-15 | 11:30 | 1.7304 | 0 | 0 | 1.5 | 81.1561 | 0 | 23813.5044
2017-09-15 | 11:32 |  |  |  |  | 81.1354 |  | 23807.4419
2017-09-15 | 11:34 |  |  |  |  | 81.0558 |  | 23784.0747
2017-09-15 | 11:36 |  |  |  |  | 80.9861 |  | 23763.6286
2017-09-15 | 11:38 |  |  |  |  | 80.9166 |  | 23743.2544
2017-09-15 | 11:40 |  |  |  |  | 80.9122 |  | 23741.9604
2017-09-15 | 11:42 |  |  |  |  | 80.9026 |  | 23739.1264
2017-09-15 | 11:44 |  |  |  |  | 80.9824 |  | 23762.5587
2017-09-15 | 11:45 | 1.7475 | 0 | 0 | 1.5 | 81.0253 | 0 | 23775.1377
2017-09-15 | 11:46 |  |  |  |  | 81.0536 |  | 23783.45
2017-09-15 | 11:48 |  |  |  |  | 81.0861 |  | 23792.9823
2017-09-15 | 11:50 |  |  |  |  | 81.0074 |  | 23769.8745
2017-09-15 | 11:52 |  |  |  |  | 80.9822 |  | 23762.4983
2017-09-15 | 11:54 |  |  |  |  | 81.0299 |  | 23776.4787
2017-09-15 | 11:56 |  |  |  |  | 81.0737 |  | 23789.3535
2017-09-15 | 11:58 |  |  |  |  | 81.2124 |  | 23830.037
2017-09-15 | 12:00 | 1.7226 | 0 | 0 | 1.5 | 81.2842 | 0 | 23851.1164
2017-09-15 | 12:02 |  |  |  |  | 81.3402 |  | 23867.546
2017-09-15 | 12:04 |  |  |  |  | 81.2992 |  | 23855.5043
2017-09-15 | 12:06 |  |  |  |  | 81.231 |  | 23835.4972
2017-09-15 | 12:08 |  |  |  |  | 81.1926 |  | 23824.2389
2017-09-15 | 12:10 |  |  |  |  | 81.1278 |  | 23805.2121
2017-09-15 | 12:12 |  |  |  |  | 81.1869 |  | 23822.5532
2017-09-15 | 12:14 |  |  |  |  | 81.3181 |  | 23861.0607
2017-09-15 | 12:15 | 1.7109 | 0 | 0 | 1.5 | 81.3557 | 0 | 23872.0815
2017-09-15 | 12:16 |  |  |  |  | 81.3436 |  | 23868.5223
2017-09-15 | 12:18 |  |  |  |  | 81.3333 |  | 23865.5246
2017-09-15 | 12:20 |  |  |  |  | 81.2676 |  | 23846.2293
2017-09-15 | 12:22 |  |  |  |  | 81.1509 |  | 23811.9932
2017-09-15 | 12:24 |  |  |  |  | 81.1017 |  | 23797.5492
2017-09-15 | 12:26 |  |  |  |  | 81.0786 |  | 23790.7772
2017-09-15 | 12:28 |  |  |  |  | 81.155 |  | 23813.1954
2017-09-15 | 12:30 | 1.7421 | 0 | 0 | 1.5 | 81.1716 | 0 | 23818.0599
2017-09-15 | 12:32 |  |  |  |  | 81.2395 |  | 23838.0022
2017-09-15 | 12:34 |  |  |  |  | 81.1536 |  | 23812.7767
2017-09-15 | 12:36 |  |  |  |  | 81.0545 |  | 23783.7053
2017-09-15 | 12:38 |  |  |  |  | 81.0169 |  | 23772.6594
2017-09-15 | 12:40 |  |  |  |  | 81.0195 |  | 23773.4253
2017-09-15 | 12:42 |  |  |  |  | 81.1093 |  | 23799.7857
2017-09-15 | 12:44 |  |  |  |  | 81.1307 |  | 23806.0631
2017-09-15 | 12:45 | 1.7421 | 0 | 0 | 1.5 | 81.1517 | 0 | 23812.2306
2017-09-15 | 12:46 |  |  |  |  | 81.153 |  | 23812.6224
2017-09-15 | 12:48 |  |  |  |  | 81.0722 |  | 23788.8899
2017-09-15 | 12:50 |  |  |  |  | 81.0217 |  | 23774.0811
2017-09-15 | 12:52 |  |  |  |  | 81.0292 |  | 23776.2862
2017-09-15 | 12:54 |  |  |  |  | 81.1161 |  | 23801.7916
2017-09-15 | 12:56 |  |  |  |  | 81.1896 |  | 23823.3589
2017-09-15 | 12:58 |  |  |  |  | 81.1995 |  | 23826.2603
2017-09-15 | 13:00 | 1.7678 | 0 | 0 | 1.5 | 81.1341 | 0 | 23807.0545
2017-09-15 | 13:02 |  |  |  |  | 81.1072 |  | 23799.1678
2017-09-15 | 13:04 |  |  |  |  | 81.1196 |  | 23802.8101
2017-09-15 | 13:06 |  |  |  |  | 81.1614 |  | 23815.0737
2017-09-15 | 13:08 |  |  |  |  | 81.0726 |  | 23789.0175
2017-09-15 | 13:10 |  |  |  |  | 80.9279 |  | 23746.5475
2017-09-15 | 13:12 |  |  |  |  | 80.8655 |  | 23728.2508
2017-09-15 | 13:14 |  |  |  |  | 80.7454 |  | 23692.9959
2017-09-15 | 13:15 | 1.7647 | 0 | 0 | 1.5 | 80.7601 | 0 | 23697.3143
2017-09-15 | 13:16 |  |  |  |  | 80.7248 |  | 23686.9651
2017-09-15 | 13:18 |  |  |  |  | 80.7642 |  | 23698.5188
2017-09-15 | 13:20 |  |  |  |  | 80.8455 |  | 23722.3878
2017-09-15 | 13:22 |  |  |  |  | 80.9318 |  | 23747.6916
2017-09-15 | 13:24 |  |  |  |  | 80.9716 |  | 23759.3753
2017-09-15 | 13:26 |  |  |  |  | 80.9405 |  | 23750.2658
2017-09-15 | 13:28 |  |  |  |  | 80.9434 |  | 23751.1188
2017-09-15 | 13:30 | 1.7507 | 0 | 0 | 1.5 | 80.921 | 0 | 23744.5328
2017-09-15 | 13:32 |  |  |  |  | 80.978 |  | 23761.2624
2017-09-15 | 13:34 |  |  |  |  | 81.104 |  | 23798.2432
2017-09-15 | 13:36 |  |  |  |  | 81.2377 |  | 23837.4649
2017-09-15 | 13:38 |  |  |  |  | 81.2724 |  | 23847.6486
2017-09-15 | 13:40 |  |  |  |  | 81.2431 |  | 23839.0453
2017-09-15 | 13:42 |  |  |  |  | 81.1879 |  | 23822.853
2017-09-15 | 13:44 |  |  |  |  | 81.1832 |  | 23821.4786
2017-09-15 | 13:45 | 1.7312 | 0 | 0 | 1.5 | 81.2478 | 0 | 23840.4133
2017-09-15 | 13:46 |  |  |  |  | 81.3158 |  | 23860.3755
2017-09-15 | 13:48 |  |  |  |  | 81.4075 |  | 23887.2732
2017-09-15 | 13:50 |  |  |  |  | 81.4563 |  | 23901.601
2017-09-15 | 13:52 |  |  |  |  | 81.4642 |  | 23903.9335
2017-09-15 | 13:54 |  |  |  |  | 81.4569 |  | 23901.7733
2017-09-15 | 13:56 |  |  |  |  | 81.4639 |  | 23903.8373
2017-09-15 | 13:58 |  |  |  |  | 81.5644 |  | 23933.3321
2017-09-15 | 14:00 | 1.6859 | 0 | 0 | 1.5 | 81.7448 | 0 | 23986.2479
2017-09-15 | 14:02 |  |  |  |  | 81.875 |  | 24024.4687
2017-09-15 | 14:04 |  |  |  |  | 82.0133 |  | 24065.0472
2017-09-15 | 14:06 |  |  |  |  | 82.0861 |  | 24086.3953
2017-09-15 | 14:08 |  |  |  |  | 82.1007 |  | 24090.6935
2017-09-15 | 14:10 |  |  |  |  | 82.1562 |  | 24106.9799
2017-09-15 | 14:12 |  |  |  |  | 82.2806 |  | 24143.4748
2017-09-15 | 14:14 |  |  |  |  | 82.4428 |  | 24191.0692
2017-09-15 | 14:15 | 1.7366 | 0 | 0 | 1.5 | 82.4646 | 0 | 24197.4583
2017-09-15 | 14:16 |  |  |  |  | 82.5304 |  | 24216.7806
2017-09-15 | 14:18 |  |  |  |  | 82.4676 |  | 24198.3606
2017-09-15 | 14:20 |  |  |  |  | 82.4145 |  | 24182.7705
2017-09-15 | 14:22 |  |  |  |  | 82.4257 |  | 24186.0457
2017-09-15 | 14:24 |  |  |  |  | 82.4972 |  | 24207.0311
2017-09-15 | 14:26 |  |  |  |  | 82.647 |  | 24251.0055
2017-09-15 | 14:28 |  |  |  |  | 82.7385 |  | 24277.8316
2017-09-15 | 14:30 | 1.7429 | 0 | 0 | 1.5 | 82.7595 | 0 | 24284.0036
2017-09-15 | 14:32 |  |  |  |  | 82.7143 |  | 24270.7462
2017-09-15 | 14:34 |  |  |  |  | 82.6147 |  | 24241.5067
2017-09-15 | 14:36 |  |  |  |  | 82.5905 |  | 24234.4057
2017-09-15 | 14:38 |  |  |  |  | 82.652 |  | 24252.4539
2017-09-15 | 14:40 |  |  |  |  | 82.753 |  | 24282.1007
2017-09-15 | 14:42 |  |  |  |  | 82.7648 |  | 24285.5597
2017-09-15 | 14:44 |  |  |  |  | 82.7059 |  | 24268.2814
2017-09-15 | 14:45 | 1.7787 | 0 | 0 | 1.5 | 82.7107 | 0 | 24269.694
2017-09-15 | 14:46 |  |  |  |  | 82.7016 |  | 24267.0255
2017-09-15 | 14:48 |  |  |  |  | 82.7486 |  | 24280.8114
2017-09-15 | 14:50 |  |  |  |  | 82.859 |  | 24313.2027
2017-09-15 | 14:52 |  |  |  |  | 82.9397 |  | 24336.8815
2017-09-15 | 14:54 |  |  |  |  | 82.9867 |  | 24350.6694
2017-09-15 | 14:56 |  |  |  |  | 82.9498 |  | 24339.8275
2017-09-15 | 14:58 |  |  |  |  | 82.8805 |  | 24319.5114
2017-09-15 | 15:00 | 1.7741 | 0 | 0 | 1.5 | 82.8076 | 0 | 24298.1073
2017-09-15 | 15:02 |  |  |  |  | 82.8552 |  | 24312.0947
2017-09-15 | 15:04 |  |  |  |  | 82.9288 |  | 24333.6822
2017-09-15 | 15:06 |  |  |  |  | 82.9716 |  | 24346.2278
2017-09-15 | 15:08 |  |  |  |  | 83.0304 |  | 24363.4837
2017-09-15 | 15:10 |  |  |  |  | 83.0213 |  | 24360.8218
2017-09-15 | 15:12 |  |  |  |  | 82.9627 |  | 24343.6198
2017-09-15 | 15:14 |  |  |  |  | 82.8942 |  | 24323.5255
2017-09-15 | 15:15 | 1.7522 | 0 | 0 | 1.5 | 82.8929 | 0 | 24323.1402
2017-09-15 | 15:16 |  |  |  |  | 82.935 |  | 24335.498
2017-09-15 | 15:18 |  |  |  |  | 83.0582 |  | 24371.6437
2017-09-15 | 15:20 |  |  |  |  | 83.0808 |  | 24378.2813
2017-09-15 | 15:22 |  |  |  |  | 83.2302 |  | 24422.1102
2017-09-15 | 15:24 |  |  |  |  | 83.2696 |  | 24433.6798
2017-09-15 | 15:26 |  |  |  |  | 83.2282 |  | 24421.5236
2017-09-15 | 15:28 |  |  |  |  | 83.2959 |  | 24441.3964
2017-09-15 | 15:30 | 1.7163 | 0 | 0 | 1.5 | 83.4361 | 0 | 24482.5301
2017-09-15 | 15:32 |  |  |  |  | 83.4882 |  | 24497.818
2017-09-15 | 15:34 |  |  |  |  | 83.531 |  | 24510.3679
2017-09-15 | 15:36 |  |  |  |  | 83.4751 |  | 24493.9741
2017-09-15 | 15:38 |  |  |  |  | 83.3917 |  | 24469.5165
2017-09-15 | 15:40 |  |  |  |  | 83.2794 |  | 24436.5677
2017-09-15 | 15:42 |  |  |  |  | 83.3129 |  | 24446.3709
2017-09-15 | 15:44 |  |  |  |  | 83.3486 |  | 24456.8659
2017-09-15 | 15:45 | 1.7249 | 0 | 0 | 1.5 | 83.3912 | 0 | 24469.3463
2017-09-15 | 15:46 |  |  |  |  | 83.4228 |  | 24478.6257
2017-09-15 | 15:48 |  |  |  |  | 83.4283 |  | 24480.251
2017-09-15 | 15:50 |  |  |  |  | 83.3667 |  | 24462.1758
2017-09-15 | 15:52 |  |  |  |  | 83.2269 |  | 24421.1386
2017-09-15 | 15:54 |  |  |  |  | 83.1508 |  | 24398.8099
2017-09-15 | 15:56 |  |  |  |  | 83.1321 |  | 24393.3386
2017-09-15 | 15:58 |  |  |  |  | 83.1294 |  | 24392.5373
2017-09-15 | 16:00 | 1.7631 | 0 | 0 | 1.5 | 83.0571 | 0 | 24371.3124
2017-09-15 | 16:02 |  |  |  |  | 82.9803 |  | 24348.8047
2017-09-15 | 16:04 |  |  |  |  | 82.8782 |  | 24318.8175
2017-09-15 | 16:06 |  |  |  |  | 82.841 |  | 24307.9016
2017-09-15 | 16:08 |  |  |  |  | 82.8526 |  | 24311.3089
2017-09-15 | 16:10 |  |  |  |  | 82.8241 |  | 24302.9676
2017-09-15 | 16:12 |  |  |  |  | 82.7667 |  | 24286.1125
2017-09-15 | 16:14 |  |  |  |  | 82.5944 |  | 24235.563
2017-09-15 | 16:15 | 1.8099 | 0 | 0 | 1.5 | 82.5403 | 0 | 24219.6729
2017-09-15 | 16:16 |  |  |  |  | 82.4737 |  | 24200.1517
2017-09-15 | 16:18 |  |  |  |  | 82.4317 |  | 24187.8254
2017-09-15 | 16:20 |  |  |  |  | 82.498 |  | 24207.2773
2017-09-15 | 16:22 |  |  |  |  | 82.4725 |  | 24199.7799
2017-09-15 | 16:24 |  |  |  |  | 82.3559 |  | 24165.5864
2017-09-15 | 16:26 |  |  |  |  | 82.1866 |  | 24115.9101
2017-09-15 | 16:28 |  |  |  |  | 81.9997 |  | 24061.0466
2017-09-15 | 16:30 | 1.8037 | 0 | 0 | 1.5 | 81.8179 | 0 | 24007.7145
2017-09-15 | 16:32 |  |  |  |  | 81.741 |  | 23985.1487
2017-09-15 | 16:34 |  |  |  |  | 81.6324 |  | 23953.292
2017-09-15 | 16:36 |  |  |  |  | 81.5636 |  | 23933.0903
2017-09-15 | 16:38 |  |  |  |  | 81.4814 |  | 23908.9641
2017-09-15 | 16:40 |  |  |  |  | 81.3036 |  | 23856.7916
2017-09-15 | 16:42 |  |  |  |  | 81.1369 |  | 23807.8896
2017-09-15 | 16:44 |  |  |  |  | 81.0076 |  | 23769.9464
2017-09-15 | 16:45 | 1.8053 | 0 | 0 | 1.5 | 80.9426 | 0 | 23750.8615
2017-09-15 | 16:46 |  |  |  |  | 80.9354 |  | 23748.755
2017-09-15 | 16:48 |  |  |  |  | 80.9566 |  | 23754.9672
2017-09-15 | 16:50 |  |  |  |  | 80.9335 |  | 23748.1931
2017-09-15 | 16:52 |  |  |  |  | 80.9111 |  | 23741.6291
2017-09-15 | 16:54 |  |  |  |  | 80.8536 |  | 23724.7675
2017-09-15 | 16:56 |  |  |  |  | 80.6697 |  | 23670.8039
2017-09-15 | 16:58 |  |  |  |  | 80.627 |  | 23658.2516
2017-09-15 | 17:00 | 1.7366 | 0 | 0 | 1.5 | 80.6594 | 0 | 23667.7617
2017-09-15 | 17:02 |  |  |  |  | 80.6835 |  | 23674.8559
2017-09-15 | 17:04 |  |  |  |  | 80.7168 |  | 23684.6009
2017-09-15 | 17:06 |  |  |  |  | 80.6056 |  | 23651.9811
2017-09-15 | 17:08 |  |  |  |  | 80.5019 |  | 23621.5643
2017-09-15 | 17:10 |  |  |  |  | 80.3586 |  | 23579.4992
2017-09-15 | 17:12 |  |  |  |  | 80.3704 |  | 23582.9828
2017-09-15 | 17:14 |  |  |  |  | 80.3326 |  | 23571.8877
2017-09-15 | 17:15 | 1.7717 | 0 | 0 | 1.5 | 80.3099 | 0 | 23565.2054
2017-09-15 | 17:16 |  |  |  |  | 80.2568 |  | 23549.6241
2017-09-15 | 17:18 |  |  |  |  | 80.125 |  | 23510.9599
2017-09-15 | 17:20 |  |  |  |  | 79.8739 |  | 23437.2982
2017-09-15 | 17:22 |  |  |  |  | 79.6695 |  | 23377.2994
2017-09-15 | 17:24 |  |  |  |  | 79.5675 |  | 23347.3726
2017-09-15 | 17:26 |  |  |  |  | 79.5605 |  | 23345.3376
2017-09-15 | 17:28 |  |  |  |  | 79.4357 |  | 23308.7172
2017-09-15 | 17:30 | 1.799 | 0 | 0 | 1.5 | 79.2931 | 0 | 23266.8652
2017-09-15 | 17:32 |  |  |  |  | 79.1424 |  | 23222.6511
2017-09-15 | 17:34 |  |  |  |  | 78.9854 |  | 23176.5611
2017-09-15 | 17:36 |  |  |  |  | 78.8577 |  | 23139.1058
2017-09-15 | 17:38 |  |  |  |  | 78.8008 |  | 23122.4073
2017-09-15 | 17:40 |  |  |  |  | 78.7794 |  | 23116.1189
2017-09-15 | 17:42 |  |  |  |  | 78.7473 |  | 23106.703
2017-09-15 | 17:44 |  |  |  |  | 78.6257 |  | 23071.0251
2017-09-15 | 17:45 | 1.7842 | 0 | 0 | 1.5 | 78.5799 | 0 | 23057.5775
2017-09-15 | 17:46 |  |  |  |  | 78.5081 |  | 23036.527
2017-09-15 | 17:48 |  |  |  |  | 78.4381 |  | 23015.9937
2017-09-15 | 17:50 |  |  |  |  | 78.3263 |  | 22983.1635
2017-09-15 | 17:52 |  |  |  |  | 78.2936 |  | 22973.5686
2017-09-15 | 17:54 |  |  |  |  | 78.3319 |  | 22984.8246
2017-09-15 | 17:56 |  |  |  |  | 78.2925 |  | 22973.2485
2017-09-15 | 17:58 |  |  |  |  | 78.1684 |  | 22936.8317
2017-09-15 | 18:00 | 1.7951 | 0 | 0 | 1.5 | 78.0556 | 0 | 22903.7464
2017-09-15 | 18:02 |  |  |  |  | 77.9995 |  | 22887.2898
2017-09-15 | 18:04 |  |  |  |  | 77.9183 |  | 22863.4478
2017-09-15 | 18:06 |  |  |  |  | 77.9154 |  | 22862.6127
2017-09-15 | 18:08 |  |  |  |  | 77.9166 |  | 22862.9464
2017-09-15 | 18:10 |  |  |  |  | 77.9074 |  | 22860.2621
2017-09-15 | 18:12 |  |  |  |  | 77.7801 |  | 22822.8939
2017-09-15 | 18:14 |  |  |  |  | 77.6854 |  | 22795.13
2017-09-15 | 18:15 | 1.7616 | 0 | 0 | 1.5 | 77.6933 | 0 | 22797.429
2017-09-15 | 18:16 |  |  |  |  | 77.6519 |  | 22785.2999
2017-09-15 | 18:18 |  |  |  |  | 77.5729 |  | 22762.0982
2017-09-15 | 18:20 |  |  |  |  | 77.5557 |  | 22757.0453
2017-09-15 | 18:22 |  |  |  |  | 77.5981 |  | 22769.497
2017-09-15 | 18:24 |  |  |  |  | 77.6142 |  | 22774.2364
2017-09-15 | 18:26 |  |  |  |  | 77.5408 |  | 22752.6733
2017-09-15 | 18:28 |  |  |  |  | 77.4631 |  | 22729.8859
2017-09-15 | 18:30 | 1.7694 | 0 | 0 | 1.5 | 77.3898 | 0 | 22708.3676
2017-09-15 | 18:32 |  |  |  |  | 77.2718 |  | 22673.7395
2017-09-15 | 18:34 |  |  |  |  | 77.2303 |  | 22661.5657
2017-09-15 | 18:36 |  |  |  |  | 77.1507 |  | 22638.232
2017-09-15 | 18:38 |  |  |  |  | 77.2952 |  | 22680.6169
2017-09-15 | 18:40 |  |  |  |  | 77.5574 |  | 22757.5603
2017-09-15 | 18:42 |  |  |  |  | 77.791 |  | 22826.1111
2017-09-15 | 18:44 |  |  |  |  | 77.7873 |  | 22825.0254
2017-09-15 | 18:45 | 1.7312 | 0 | 0 | 1.5 | 77.8 | 0 | 22828.7302
2017-09-15 | 18:46 |  |  |  |  | 77.8052 |  | 22830.2572
2017-09-15 | 18:48 |  |  |  |  | 77.8099 |  | 22831.6472
2017-09-15 | 18:50 |  |  |  |  | 77.7331 |  | 22809.0993
2017-09-15 | 18:52 |  |  |  |  | 77.6821 |  | 22794.1517
2017-09-15 | 18:54 |  |  |  |  | 77.5603 |  | 22758.4201
2017-09-15 | 18:56 |  |  |  |  | 77.4809 |  | 22735.0951
2017-09-15 | 18:58 |  |  |  |  | 77.4172 |  | 22716.409
2017-09-15 | 19:00 | 1.7351 | 0 | 0 | 1.5 | 77.3841 | 0 | 22706.693
2017-09-15 | 19:02 |  |  |  |  | 77.3898 |  | 22708.3922
2017-09-15 | 19:04 |  |  |  |  | 77.495 |  | 22739.2615
2017-09-15 | 19:06 |  |  |  |  | 77.6874 |  | 22795.6963
2017-09-15 | 19:08 |  |  |  |  | 77.6389 |  | 22781.4695
2017-09-15 | 19:10 |  |  |  |  | 77.5864 |  | 22766.0562
2017-09-15 | 19:12 |  |  |  |  | 77.5264 |  | 22748.467
2017-09-15 | 19:14 |  |  |  |  | 77.5001 |  | 22740.7413
2017-09-15 | 19:15 | 1.7296 | 0 | 0 | 1.5 | 77.49 | 0 | 22737.7862
2017-09-15 | 19:16 |  |  |  |  | 77.5273 |  | 22748.722
2017-09-15 | 19:18 |  |  |  |  | 77.5238 |  | 22747.6923
2017-09-15 | 19:20 |  |  |  |  | 77.3693 |  | 22702.3702
2017-09-15 | 19:22 |  |  |  |  | 77.286 |  | 22677.9103
2017-09-15 | 19:24 |  |  |  |  | 77.3976 |  | 22710.6578
2017-09-15 | 19:26 |  |  |  |  | 77.573 |  | 22762.1451
2017-09-15 | 19:28 |  |  |  |  | 77.549 |  | 22755.1067
2017-09-15 | 19:30 | 1.7803 | 0 | 0 | 1.5 | 77.4503 | 0 | 22726.1247
2017-09-15 | 19:32 |  |  |  |  | 77.453 |  | 22726.9105
2017-09-15 | 19:34 |  |  |  |  | 77.4889 |  | 22737.4569
2017-09-15 | 19:36 |  |  |  |  | 77.4727 |  | 22732.6999
2017-09-15 | 19:38 |  |  |  |  | 77.5064 |  | 22742.5969
2017-09-15 | 19:40 |  |  |  |  | 77.653 |  | 22785.5954
2017-09-15 | 19:42 |  |  |  |  | 77.7726 |  | 22820.7114
2017-09-15 | 19:44 |  |  |  |  | 77.6834 |  | 22794.5232
2017-09-15 | 19:45 | 1.7834 | 0 | 0 | 1.5 | 77.6276 | 0 | 22778.1631
2017-09-15 | 19:46 |  |  |  |  | 77.5989 |  | 22769.7388
2017-09-15 | 19:48 |  |  |  |  | 77.517 |  | 22745.7043
2017-09-15 | 19:50 |  |  |  |  | 77.4143 |  | 22715.5581
2017-09-15 | 19:52 |  |  |  |  | 77.4299 |  | 22720.1543
2017-09-15 | 19:54 |  |  |  |  | 77.6246 |  | 22777.2787
2017-09-15 | 19:56 |  |  |  |  | 77.8583 |  | 22845.8541
2017-09-15 | 19:58 |  |  |  |  | 77.8642 |  | 22847.5757
2017-09-15 | 20:00 | 1.7592 | 0 | 0 | 1.5 | 77.8408 | 0 | 22840.7027
2017-09-15 | 20:02 |  |  |  |  | 77.7505 |  | 22814.2214
2017-09-15 | 20:04 |  |  |  |  | 77.6204 |  | 22776.0316
2017-09-15 | 20:06 |  |  |  |  | 77.4437 |  | 22724.2083
2017-09-15 | 20:08 |  |  |  |  | 77.4521 |  | 22726.6508
2017-09-15 | 20:10 |  |  |  |  | 77.5527 |  | 22756.1656
2017-09-15 | 20:12 |  |  |  |  | 77.6684 |  | 22790.113
2017-09-15 | 20:14 |  |  |  |  | 77.5143 |  | 22744.9118
2017-09-15 | 20:15 | 1.7858 | 0 | 0 | 1.5 | 77.4712 | 0 | 22732.2656
2017-09-15 | 20:16 |  |  |  |  | 77.3801 |  | 22705.5222
2017-09-15 | 20:18 |  |  |  |  | 77.2773 |  | 22675.376
2017-09-15 | 20:20 |  |  |  |  | 77.2409 |  | 22664.6999
2017-09-15 | 20:22 |  |  |  |  | 77.2368 |  | 22663.4977
2017-09-15 | 20:24 |  |  |  |  | 77.3642 |  | 22700.8746
2017-09-15 | 20:26 |  |  |  |  | 77.4698 |  | 22731.8536
2017-09-15 | 20:28 |  |  |  |  | 77.3648 |  | 22701.036
2017-09-15 | 20:30 | 1.7834 | 0 | 0 | 1.5 | 77.2779 | 0 | 22675.5441
2017-09-15 | 20:32 |  |  |  |  | 77.2101 |  | 22655.6535
2017-09-15 | 20:34 |  |  |  |  | 77.3181 |  | 22687.3373
2017-09-15 | 20:36 |  |  |  |  | 77.4517 |  | 22726.5279
2017-09-15 | 20:38 |  |  |  |  | 77.4053 |  | 22712.9166
2017-09-15 | 20:40 |  |  |  |  | 77.3423 |  | 22694.4341
2017-09-15 | 20:42 |  |  |  |  | 77.3588 |  | 22699.2763
2017-09-15 | 20:44 |  |  |  |  | 77.3068 |  | 22684.0242
2017-09-15 | 20:45 | 1.7811 | 0 | 0 | 1.5 | 77.2466 | 0 | 22666.3542
2017-09-15 | 20:46 |  |  |  |  | 77.1775 |  | 22646.0695
2017-09-15 | 20:48 |  |  |  |  | 77.1573 |  | 22640.1707
2017-09-15 | 20:50 |  |  |  |  | 77.2303 |  | 22661.5678
2017-09-15 | 20:52 |  |  |  |  | 77.2945 |  | 22680.4244
2017-09-15 | 20:54 |  |  |  |  | 77.1532 |  | 22638.9439
2017-09-15 | 20:56 |  |  |  |  | 77.0362 |  | 22604.6136
2017-09-15 | 20:58 |  |  |  |  | 77.0595 |  | 22611.4484
2017-09-15 | 21:00 | 1.714 | 0 | 0 | 1.5 | 77.1868 | 0 | 22648.8254
2017-09-15 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:15 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:15 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-15 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-15 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:45 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:00 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:30 | 0.03778 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:15 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:30 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:45 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:00 | 0.03856 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:15 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:30 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:45 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:00 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:15 | 0.03934 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:30 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:45 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 5:00 | 0.04012 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 5:02 |  |  |  |  | 69.625 |  | 20429.9643
2017-09-16 | 5:04 |  |  |  |  | 98.7086 |  | 28963.9288
2017-09-16 | 5:06 |  |  |  |  | 96.0109 |  | 28172.3533
2017-09-16 | 5:08 |  |  |  |  | 93.4014 |  | 27406.6476
2017-09-16 | 5:10 |  |  |  |  | 91.3214 |  | 26796.2956
2017-09-16 | 5:12 |  |  |  |  | 89.5205 |  | 26267.8704
2017-09-16 | 5:14 |  |  |  |  | 88.0801 |  | 25845.2226
2017-09-16 | 5:15 | 2.1937 | 0 | 0 | 1.5 | 87.4126 | 0 | 25649.3491
2017-09-16 | 5:16 |  |  |  |  | 86.808 |  | 25471.9424
2017-09-16 | 5:18 |  |  |  |  | 85.789 |  | 25172.9352
2017-09-16 | 5:20 |  |  |  |  | 84.8772 |  | 24905.3994
2017-09-16 | 5:22 |  |  |  |  | 84.171 |  | 24698.1666
2017-09-16 | 5:24 |  |  |  |  | 83.5697 |  | 24521.7383
2017-09-16 | 5:26 |  |  |  |  | 83.049 |  | 24368.9415
2017-09-16 | 5:28 |  |  |  |  | 82.6322 |  | 24246.6513
2017-09-16 | 5:30 | 1.8716 | 0 | 0 | 1.5 | 82.2589 | 0 | 24137.1147
2017-09-16 | 5:32 |  |  |  |  | 81.9483 |  | 24045.9714
2017-09-16 | 5:34 |  |  |  |  | 81.6826 |  | 23967.9981
2017-09-16 | 5:36 |  |  |  |  | 81.4773 |  | 23907.7818
2017-09-16 | 5:38 |  |  |  |  | 81.3289 |  | 23864.2373
2017-09-16 | 5:40 |  |  |  |  | 81.1484 |  | 23811.2723
2017-09-16 | 5:42 |  |  |  |  | 81.0533 |  | 23783.3426
2017-09-16 | 5:44 |  |  |  |  | 80.9186 |  | 23743.8321
2017-09-16 | 5:45 | 1.7631 | 0 | 0 | 1.5 | 80.89 | 0 | 23735.4348
2017-09-16 | 5:46 |  |  |  |  | 80.8324 |  | 23718.5439
2017-09-16 | 5:48 |  |  |  |  | 80.8048 |  | 23710.4376
2017-09-16 | 5:50 |  |  |  |  | 80.7409 |  | 23691.6796
2017-09-16 | 5:52 |  |  |  |  | 80.6852 |  | 23675.3573
2017-09-16 | 5:54 |  |  |  |  | 80.6643 |  | 23669.21
2017-09-16 | 5:56 |  |  |  |  | 80.6352 |  | 23660.6806
2017-09-16 | 5:58 |  |  |  |  | 80.6287 |  | 23658.7575
2017-09-16 | 6:00 | 1.7553 | 0 | 0 | 1.5 | 80.6189 | 0 | 23655.8854
2017-09-16 | 6:02 |  |  |  |  | 80.581 |  | 23644.7613
2017-09-16 | 6:04 |  |  |  |  | 80.6042 |  | 23651.587
2017-09-16 | 6:06 |  |  |  |  | 80.5729 |  | 23642.3772
2017-09-16 | 6:08 |  |  |  |  | 80.562 |  | 23639.2049
2017-09-16 | 6:10 |  |  |  |  | 80.5663 |  | 23640.4476
2017-09-16 | 6:12 |  |  |  |  | 80.5827 |  | 23645.256
2017-09-16 | 6:14 |  |  |  |  | 80.5892 |  | 23647.1859
2017-09-16 | 6:15 | 1.7413 | 0 | 0 | 1.5 | 80.6394 | 0 | 23661.9186
2017-09-16 | 6:16 |  |  |  |  | 80.6058 |  | 23652.0348
2017-09-16 | 6:18 |  |  |  |  | 80.6263 |  | 23658.0726
2017-09-16 | 6:20 |  |  |  |  | 80.6468 |  | 23664.0812
2017-09-16 | 6:22 |  |  |  |  | 80.6616 |  | 23668.404
2017-09-16 | 6:24 |  |  |  |  | 80.6587 |  | 23667.5645
2017-09-16 | 6:26 |  |  |  |  | 80.7009 |  | 23679.9354
2017-09-16 | 6:28 |  |  |  |  | 80.6903 |  | 23676.8395
2017-09-16 | 6:30 | 1.7483 | 0 | 0 | 1.5 | 80.7175 | 0 | 23684.8225
2017-09-16 | 6:32 |  |  |  |  | 80.7426 |  | 23692.1834
2017-09-16 | 6:34 |  |  |  |  | 80.7516 |  | 23694.8296
2017-09-16 | 6:36 |  |  |  |  | 80.7398 |  | 23691.3662
2017-09-16 | 6:38 |  |  |  |  | 80.7727 |  | 23701.0039
2017-09-16 | 6:40 |  |  |  |  | 80.7725 |  | 23700.9681
2017-09-16 | 6:42 |  |  |  |  | 80.7852 |  | 23704.6999
2017-09-16 | 6:44 |  |  |  |  | 80.8198 |  | 23714.8299
2017-09-16 | 6:45 | 1.7624 | 0 | 0 | 1.5 | 80.8317 | 0 | 23718.32
2017-09-16 | 6:46 |  |  |  |  | 80.8551 |  | 23725.195
2017-09-16 | 6:48 |  |  |  |  | 80.8564 |  | 23725.5779
2017-09-16 | 6:50 |  |  |  |  | 80.8685 |  | 23729.1372
2017-09-16 | 6:52 |  |  |  |  | 80.8782 |  | 23731.9759
2017-09-16 | 6:54 |  |  |  |  | 80.8893 |  | 23735.2221
2017-09-16 | 6:56 |  |  |  |  | 80.9141 |  | 23742.5067
2017-09-16 | 6:58 |  |  |  |  | 80.9578 |  | 23755.3342
2017-09-16 | 7:00 | 1.753 | 0 | 0 | 1.5 | 80.9254 | 0 | 23745.8266
2017-09-16 | 7:02 |  |  |  |  | 80.9473 |  | 23752.2406
2017-09-16 | 7:04 |  |  |  |  | 80.9666 |  | 23757.9223
2017-09-16 | 7:06 |  |  |  |  | 80.9789 |  | 23761.5221
2017-09-16 | 7:08 |  |  |  |  | 81.0187 |  | 23773.2058
2017-09-16 | 7:10 |  |  |  |  | 81.0196 |  | 23773.4722
2017-09-16 | 7:12 |  |  |  |  | 81.0422 |  | 23780.1055
2017-09-16 | 7:14 |  |  |  |  | 81.0309 |  | 23776.7877
2017-09-16 | 7:15 | 1.7468 | 0 | 0 | 1.5 | 81.0638 | 0 | 23786.4251
2017-09-16 | 7:16 |  |  |  |  | 81.0771 |  | 23790.3318
2017-09-16 | 7:18 |  |  |  |  | 81.0995 |  | 23796.9178
2017-09-16 | 7:20 |  |  |  |  | 81.1297 |  | 23805.7696
2017-09-16 | 7:22 |  |  |  |  | 81.1497 |  | 23811.6505
2017-09-16 | 7:24 |  |  |  |  | 81.1248 |  | 23804.3257
2017-09-16 | 7:26 |  |  |  |  | 81.1999 |  | 23826.3701
2017-09-16 | 7:28 |  |  |  |  | 81.215 |  | 23830.8094
2017-09-16 | 7:30 | 1.7421 | 0 | 0 | 1.5 | 81.2392 | 0 | 23837.9083
2017-09-16 | 7:32 |  |  |  |  | 81.2345 |  | 23836.5248
2017-09-16 | 7:34 |  |  |  |  | 81.2797 |  | 23849.7845
2017-09-16 | 7:36 |  |  |  |  | 81.2815 |  | 23850.3194
2017-09-16 | 7:38 |  |  |  |  | 81.3479 |  | 23869.8072
2017-09-16 | 7:40 |  |  |  |  | 81.3861 |  | 23881.005
2017-09-16 | 7:42 |  |  |  |  | 81.3897 |  | 23882.0528
2017-09-16 | 7:44 |  |  |  |  | 81.4049 |  | 23886.5347
2017-09-16 | 7:45 | 1.7179 | 0 | 0 | 1.5 | 81.4321 | 0 | 23894.5065
2017-09-16 | 7:46 |  |  |  |  | 81.4322 |  | 23894.5244
2017-09-16 | 7:48 |  |  |  |  | 81.4721 |  | 23906.2284
2017-09-16 | 7:50 |  |  |  |  | 81.5042 |  | 23915.6642
2017-09-16 | 7:52 |  |  |  |  | 81.5505 |  | 23929.2599
2017-09-16 | 7:54 |  |  |  |  | 81.5807 |  | 23938.1206
2017-09-16 | 7:56 |  |  |  |  | 81.593 |  | 23941.718
2017-09-16 | 7:58 |  |  |  |  | 81.6311 |  | 23952.907
2017-09-16 | 8:00 | 1.7288 | 0 | 0 | 1.5 | 81.6558 | 0 | 23960.1515
2017-09-16 | 8:02 |  |  |  |  | 81.7565 |  | 23989.6997
2017-09-16 | 8:04 |  |  |  |  | 81.8199 |  | 24008.2852
2017-09-16 | 8:06 |  |  |  |  | 81.8998 |  | 24031.7401
2017-09-16 | 8:08 |  |  |  |  | 81.8175 |  | 24007.5892
2017-09-16 | 8:10 |  |  |  |  | 81.7643 |  | 23991.9697
2017-09-16 | 8:12 |  |  |  |  | 81.6257 |  | 23951.2996
2017-09-16 | 8:14 |  |  |  |  | 81.512 |  | 23917.95
2017-09-16 | 8:15 | 1.8092 | 0 | 0 | 1.5 | 81.3639 | 0 | 23874.495
2017-09-16 | 8:16 |  |  |  |  | 81.2669 |  | 23846.0324
2017-09-16 | 8:18 |  |  |  |  | 81.1361 |  | 23807.657
2017-09-16 | 8:20 |  |  |  |  | 81.0774 |  | 23790.4189
2017-09-16 | 8:22 |  |  |  |  | 81.0012 |  | 23768.0591
2017-09-16 | 8:24 |  |  |  |  | 80.6751 |  | 23672.3688
2017-09-16 | 8:26 |  |  |  |  | 80.4367 |  | 23602.4122
2017-09-16 | 8:28 |  |  |  |  | 80.3487 |  | 23576.6001
2017-09-16 | 8:30 | 1.7444 | 0 | 0 | 1.5 | 80.3688 | 0 | 23582.506
2017-09-16 | 8:32 |  |  |  |  | 80.3205 |  | 23568.3349
2017-09-16 | 8:34 |  |  |  |  | 80.0635 |  | 23492.907
2017-09-16 | 8:36 |  |  |  |  | 79.8761 |  | 23437.934
2017-09-16 | 8:38 |  |  |  |  | 79.8272 |  | 23423.5862
2017-09-16 | 8:40 |  |  |  |  | 79.871 |  | 23436.4408
2017-09-16 | 8:42 |  |  |  |  | 79.8775 |  | 23438.3436
2017-09-16 | 8:44 |  |  |  |  | 79.6637 |  | 23375.6045
2017-09-16 | 8:45 | 1.8014 | 0 | 0 | 1.5 | 79.565 | 0 | 23346.654
2017-09-16 | 8:46 |  |  |  |  | 79.4923 |  | 23325.317
2017-09-16 | 8:48 |  |  |  |  | 79.4919 |  | 23325.2073
2017-09-16 | 8:50 |  |  |  |  | 79.5692 |  | 23347.8875
2017-09-16 | 8:52 |  |  |  |  | 79.5661 |  | 23346.9697
2017-09-16 | 8:54 |  |  |  |  | 79.3605 |  | 23286.6282
2017-09-16 | 8:56 |  |  |  |  | 79.2294 |  | 23248.1632
2017-09-16 | 8:58 |  |  |  |  | 79.1749 |  | 23232.1699
2017-09-16 | 9:00 | 1.7514 | 0 | 0 | 1.5 | 79.2689 | 0 | 23259.7483
2017-09-16 | 9:02 |  |  |  |  | 79.2692 |  | 23259.8378
2017-09-16 | 9:04 |  |  |  |  | 79.0933 |  | 23208.2249
2017-09-16 | 9:06 |  |  |  |  | 78.9116 |  | 23154.931
2017-09-16 | 9:08 |  |  |  |  | 78.8908 |  | 23148.8194
2017-09-16 | 9:10 |  |  |  |  | 78.9682 |  | 23171.5352
2017-09-16 | 9:12 |  |  |  |  | 79.0069 |  | 23182.8944
2017-09-16 | 9:14 |  |  |  |  | 78.86 |  | 23139.7795
2017-09-16 | 9:15 | 1.7733 | 0 | 0 | 1.5 | 78.751 | 0 | 23107.782
2017-09-16 | 9:16 |  |  |  |  | 78.6545 |  | 23079.4919
2017-09-16 | 9:18 |  |  |  |  | 78.6265 |  | 23071.249
2017-09-16 | 9:20 |  |  |  |  | 78.7146 |  | 23097.117
2017-09-16 | 9:22 |  |  |  |  | 78.7451 |  | 23106.0651
2017-09-16 | 9:24 |  |  |  |  | 78.5798 |  | 23057.5573
2017-09-16 | 9:26 |  |  |  |  | 78.4548 |  | 23020.8743
2017-09-16 | 9:28 |  |  |  |  | 78.4104 |  | 23007.8584
2017-09-16 | 9:30 | 1.7382 | 0 | 0 | 1.5 | 78.4722 | 0 | 23025.9785
2017-09-16 | 9:32 |  |  |  |  | 78.5333 |  | 23043.917
2017-09-16 | 9:34 |  |  |  |  | 78.3411 |  | 22987.5179
2017-09-16 | 9:36 |  |  |  |  | 78.2144 |  | 22950.3446
2017-09-16 | 9:38 |  |  |  |  | 78.1775 |  | 22939.5227
2017-09-16 | 9:40 |  |  |  |  | 78.2895 |  | 22972.3641
2017-09-16 | 9:42 |  |  |  |  | 78.3714 |  | 22996.4053
2017-09-16 | 9:44 |  |  |  |  | 78.1935 |  | 22944.2105
2017-09-16 | 9:45 | 1.785 | 0 | 0 | 1.5 | 78.1247 | 0 | 22924.0086
2017-09-16 | 9:46 |  |  |  |  | 78.0627 |  | 22905.8351
2017-09-16 | 9:48 |  |  |  |  | 78.0483 |  | 22901.6129
2017-09-16 | 9:50 |  |  |  |  | 78.1384 |  | 22928.0426
2017-09-16 | 9:52 |  |  |  |  | 78.2286 |  | 22954.5128
2017-09-16 | 9:54 |  |  |  |  | 78.0407 |  | 22899.3696
2017-09-16 | 9:56 |  |  |  |  | 77.9046 |  | 22859.4249
2017-09-16 | 9:58 |  |  |  |  | 77.8891 |  | 22854.8736
2017-09-16 | 10:00 | 1.7312 | 0 | 0 | 1.5 | 77.9541 | 0 | 22873.9608
2017-09-16 | 10:02 |  |  |  |  | 78.0211 |  | 22893.6073
2017-09-16 | 10:04 |  |  |  |  | 77.8757 |  | 22850.9448
2017-09-16 | 10:06 |  |  |  |  | 77.7824 |  | 22823.5703
2017-09-16 | 10:08 |  |  |  |  | 77.7329 |  | 22809.0547
2017-09-16 | 10:10 |  |  |  |  | 77.8582 |  | 22845.8181
2017-09-16 | 10:12 |  |  |  |  | 77.9516 |  | 22873.2175
2017-09-16 | 10:14 |  |  |  |  | 77.7873 |  | 22825.0163
2017-09-16 | 10:15 | 1.7975 | 0 | 0 | 1.5 | 77.7269 | 0 | 22807.2994
2017-09-16 | 10:16 |  |  |  |  | 77.6864 |  | 22795.4144
2017-09-16 | 10:18 |  |  |  |  | 77.6682 |  | 22790.0751
2017-09-16 | 10:20 |  |  |  |  | 77.7997 |  | 22828.6586
2017-09-16 | 10:22 |  |  |  |  | 77.9119 |  | 22861.5807
2017-09-16 | 10:24 |  |  |  |  | 77.745 |  | 22812.6096
2017-09-16 | 10:26 |  |  |  |  | 77.6131 |  | 22773.9072
2017-09-16 | 10:28 |  |  |  |  | 77.6336 |  | 22779.909
2017-09-16 | 10:30 | 1.7156 | 0 | 0 | 1.5 | 77.7325 | 0 | 22808.9493
2017-09-16 | 10:32 |  |  |  |  | 77.8536 |  | 22844.4615
2017-09-16 | 10:34 |  |  |  |  | 77.7293 |  | 22807.9957
2017-09-16 | 10:36 |  |  |  |  | 77.6036 |  | 22771.1223
2017-09-16 | 10:38 |  |  |  |  | 77.6409 |  | 22782.0604
2017-09-16 | 10:40 |  |  |  |  | 77.7621 |  | 22817.6219
2017-09-16 | 10:42 |  |  |  |  | 77.8495 |  | 22843.2685
2017-09-16 | 10:44 |  |  |  |  | 77.7019 |  | 22799.9722
2017-09-16 | 10:45 | 1.7748 | 0 | 0 | 1.5 | 77.6258 | 0 | 22777.6255
2017-09-16 | 10:46 |  |  |  |  | 77.5808 |  | 22764.4107
2017-09-16 | 10:48 |  |  |  |  | 77.6177 |  | 22775.2549
2017-09-16 | 10:50 |  |  |  |  | 77.7396 |  | 22811.0268
2017-09-16 | 10:52 |  |  |  |  | 77.8332 |  | 22838.4729
2017-09-16 | 10:54 |  |  |  |  | 77.6849 |  | 22794.9554
2017-09-16 | 10:56 |  |  |  |  | 77.5754 |  | 22762.8482
2017-09-16 | 10:58 |  |  |  |  | 77.6276 |  | 22778.1496
2017-09-16 | 11:00 | 1.7023 | 0 | 0 | 1.5 | 77.7308 | 0 | 22808.4411
2017-09-16 | 11:02 |  |  |  |  | 77.857 |  | 22845.4554
2017-09-16 | 11:04 |  |  |  |  | 77.723 |  | 22806.1621
2017-09-16 | 11:06 |  |  |  |  | 77.6239 |  | 22777.0795
2017-09-16 | 11:08 |  |  |  |  | 77.675 |  | 22792.0719
2017-09-16 | 11:10 |  |  |  |  | 77.8171 |  | 22833.7561
2017-09-16 | 11:12 |  |  |  |  | 77.9244 |  | 22865.2454
2017-09-16 | 11:14 |  |  |  |  | 77.7795 |  | 22822.7261
2017-09-16 | 11:15 | 1.7756 | 0 | 0 | 1.5 | 77.739 | 0 | 22810.8411
2017-09-16 | 11:16 |  |  |  |  | 77.6858 |  | 22795.2398
2017-09-16 | 11:18 |  |  |  |  | 77.7262 |  | 22807.0779
2017-09-16 | 11:20 |  |  |  |  | 77.8358 |  | 22839.2432
2017-09-16 | 11:22 |  |  |  |  | 77.9618 |  | 22876.2263
2017-09-16 | 11:24 |  |  |  |  | 77.8338 |  | 22838.6745
2017-09-16 | 11:26 |  |  |  |  | 77.7332 |  | 22809.1442
2017-09-16 | 11:28 |  |  |  |  | 77.7964 |  | 22827.6827
2017-09-16 | 11:30 | 1.6867 | 0 | 0 | 1.5 | 77.9595 | 0 | 22875.5591
2017-09-16 | 11:32 |  |  |  |  | 78.0504 |  | 22902.213
2017-09-16 | 11:34 |  |  |  |  | 77.925 |  | 22865.4247
2017-09-16 | 11:36 |  |  |  |  | 77.8046 |  | 22830.0803
2017-09-16 | 11:38 |  |  |  |  | 77.7126 |  | 22803.1042
2017-09-16 | 11:40 |  |  |  |  | 77.6124 |  | 22773.6857
2017-09-16 | 11:42 |  |  |  |  | 77.4984 |  | 22740.2554
2017-09-16 | 11:44 |  |  |  |  | 77.5907 |  | 22767.3233
2017-09-16 | 11:45 | 1.7249 | 0 | 0 | 1.5 | 77.6206 | 0 | 22776.0988
2017-09-16 | 11:46 |  |  |  |  | 77.6858 |  | 22795.2263
2017-09-16 | 11:48 |  |  |  |  | 77.619 |  | 22775.6288
2017-09-16 | 11:50 |  |  |  |  | 77.4746 |  | 22733.2571
2017-09-16 | 11:52 |  |  |  |  | 77.408 |  | 22713.7045
2017-09-16 | 11:54 |  |  |  |  | 77.5465 |  | 22754.3479
2017-09-16 | 11:56 |  |  |  |  | 77.6896 |  | 22796.3454
2017-09-16 | 11:58 |  |  |  |  | 77.6599 |  | 22787.6303
2017-09-16 | 12:00 | 1.76 | 0 | 0 | 1.5 | 77.5915 | 0 | 22767.5627
2017-09-16 | 12:02 |  |  |  |  | 77.5573 |  | 22757.5269
2017-09-16 | 12:04 |  |  |  |  | 77.6812 |  | 22793.883
2017-09-16 | 12:06 |  |  |  |  | 77.8731 |  | 22850.1881
2017-09-16 | 12:08 |  |  |  |  | 77.8815 |  | 22852.6438
2017-09-16 | 12:10 |  |  |  |  | 77.8127 |  | 22832.46
2017-09-16 | 12:12 |  |  |  |  | 77.7228 |  | 22806.0905
2017-09-16 | 12:14 |  |  |  |  | 77.7047 |  | 22800.7671
2017-09-16 | 12:15 | 1.7725 | 0 | 0 | 1.5 | 77.6619 | 0 | 22788.2145
2017-09-16 | 12:16 |  |  |  |  | 77.6311 |  | 22779.1772
2017-09-16 | 12:18 |  |  |  |  | 77.7154 |  | 22803.9123
2017-09-16 | 12:20 |  |  |  |  | 77.8056 |  | 22830.4004
2017-09-16 | 12:22 |  |  |  |  | 77.9283 |  | 22866.385
2017-09-16 | 12:24 |  |  |  |  | 77.8159 |  | 22833.4204
2017-09-16 | 12:26 |  |  |  |  | 77.7495 |  | 22813.9282
2017-09-16 | 12:28 |  |  |  |  | 77.6961 |  | 22798.2506
2017-09-16 | 12:30 | 1.7787 | 0 | 0 | 1.5 | 77.6276 | 0 | 22778.1429
2017-09-16 | 12:32 |  |  |  |  | 77.5754 |  | 22762.837
2017-09-16 | 12:34 |  |  |  |  | 77.7069 |  | 22801.4138
2017-09-16 | 12:36 |  |  |  |  | 77.8948 |  | 22856.5684
2017-09-16 | 12:38 |  |  |  |  | 77.8573 |  | 22845.5472
2017-09-16 | 12:40 |  |  |  |  | 77.8089 |  | 22831.3429
2017-09-16 | 12:42 |  |  |  |  | 77.7713 |  | 22820.315
2017-09-16 | 12:44 |  |  |  |  | 77.7134 |  | 22803.3258
2017-09-16 | 12:45 | 1.7764 | 0 | 0 | 1.5 | 77.6675 | 0 | 22789.8712
2017-09-16 | 12:46 |  |  |  |  | 77.6419 |  | 22782.3627
2017-09-16 | 12:48 |  |  |  |  | 77.6941 |  | 22797.682
2017-09-16 | 12:50 |  |  |  |  | 77.8337 |  | 22838.6185
2017-09-16 | 12:52 |  |  |  |  | 77.9811 |  | 22881.8925
2017-09-16 | 12:54 |  |  |  |  | 77.8852 |  | 22853.7565
2017-09-16 | 12:56 |  |  |  |  | 77.8726 |  | 22850.0314
2017-09-16 | 12:58 |  |  |  |  | 77.8109 |  | 22831.9518
2017-09-16 | 13:00 | 1.7546 | 0 | 0 | 1.5 | 77.7879 | 0 | 22825.1798
2017-09-16 | 13:02 |  |  |  |  | 77.7478 |  | 22813.4312
2017-09-16 | 13:04 |  |  |  |  | 77.8637 |  | 22847.4301
2017-09-16 | 13:06 |  |  |  |  | 78.0561 |  | 22903.8852
2017-09-16 | 13:08 |  |  |  |  | 78.0381 |  | 22898.6108
2017-09-16 | 13:10 |  |  |  |  | 78.0002 |  | 22887.4958
2017-09-16 | 13:12 |  |  |  |  | 77.9851 |  | 22883.07
2017-09-16 | 13:14 |  |  |  |  | 77.9199 |  | 22863.9246
2017-09-16 | 13:15 | 1.7546 | 0 | 0 | 1.5 | 77.9252 | 0 | 22865.4919
2017-09-16 | 13:16 |  |  |  |  | 77.8875 |  | 22854.4079
2017-09-16 | 13:18 |  |  |  |  | 77.806 |  | 22830.4987
2017-09-16 | 13:20 |  |  |  |  | 77.7094 |  | 22802.1594
2017-09-16 | 13:22 |  |  |  |  | 77.6671 |  | 22789.7594
2017-09-16 | 13:24 |  |  |  |  | 77.7504 |  | 22814.1744
2017-09-16 | 13:26 |  |  |  |  | 77.8853 |  | 22853.7744
2017-09-16 | 13:28 |  |  |  |  | 77.9133 |  | 22861.9748
2017-09-16 | 13:30 | 1.7639 | 0 | 0 | 1.5 | 77.8641 | 0 | 22847.5419
2017-09-16 | 13:32 |  |  |  |  | 77.8278 |  | 22836.8858
2017-09-16 | 13:34 |  |  |  |  | 77.8519 |  | 22843.9736
2017-09-16 | 13:36 |  |  |  |  | 77.7791 |  | 22822.6164
2017-09-16 | 13:38 |  |  |  |  | 77.6996 |  | 22799.2894
2017-09-16 | 13:40 |  |  |  |  | 77.6421 |  | 22782.3985
2017-09-16 | 13:42 |  |  |  |  | 77.5891 |  | 22766.8711
2017-09-16 | 13:44 |  |  |  |  | 77.6829 |  | 22794.3844
2017-09-16 | 13:45 | 1.7023 | 0 | 0 | 1.5 | 77.7684 | 0 | 22819.4667
2017-09-16 | 13:46 |  |  |  |  | 77.8364 |  | 22839.4178
2017-09-16 | 13:48 |  |  |  |  | 77.8482 |  | 22842.8832
2017-09-16 | 13:50 |  |  |  |  | 77.813 |  | 22832.5539
2017-09-16 | 13:52 |  |  |  |  | 77.8124 |  | 22832.3861
2017-09-16 | 13:54 |  |  |  |  | 77.7782 |  | 22822.3567
2017-09-16 | 13:56 |  |  |  |  | 77.7749 |  | 22821.3784
2017-09-16 | 13:58 |  |  |  |  | 77.7142 |  | 22803.5564
2017-09-16 | 14:00 | 1.7631 | 0 | 0 | 1.5 | 77.6484 | 0 | 22784.2702
2017-09-16 | 14:02 |  |  |  |  | 77.5452 |  | 22753.9696
2017-09-16 | 14:04 |  |  |  |  | 77.4512 |  | 22726.4091
2017-09-16 | 14:06 |  |  |  |  | 77.3518 |  | 22697.2211
2017-09-16 | 14:08 |  |  |  |  | 77.4072 |  | 22713.492
2017-09-16 | 14:10 |  |  |  |  | 77.5131 |  | 22744.5626
2017-09-16 | 14:12 |  |  |  |  | 77.6919 |  | 22797.035
2017-09-16 | 14:14 |  |  |  |  | 77.6012 |  | 22770.4104
2017-09-16 | 14:15 | 1.7655 | 0 | 0 | 1.5 | 77.5887 | 0 | 22766.7391
2017-09-16 | 14:16 |  |  |  |  | 77.6303 |  | 22778.9422
2017-09-16 | 14:18 |  |  |  |  | 77.5966 |  | 22769.0492
2017-09-16 | 14:20 |  |  |  |  | 77.5637 |  | 22759.4118
2017-09-16 | 14:22 |  |  |  |  | 77.5085 |  | 22743.2061
2017-09-16 | 14:24 |  |  |  |  | 77.4755 |  | 22733.5282
2017-09-16 | 14:26 |  |  |  |  | 77.3954 |  | 22710.0129
2017-09-16 | 14:28 |  |  |  |  | 77.3243 |  | 22689.153
2017-09-16 | 14:30 | 1.7694 | 0 | 0 | 1.5 | 77.2935 | 0 | 22680.1087
2017-09-16 | 14:32 |  |  |  |  | 77.2405 |  | 22664.5587
2017-09-16 | 14:34 |  |  |  |  | 77.431 |  | 22720.4677
2017-09-16 | 14:36 |  |  |  |  | 77.6208 |  | 22776.1572
2017-09-16 | 14:38 |  |  |  |  | 77.6339 |  | 22779.992
2017-09-16 | 14:40 |  |  |  |  | 77.6195 |  | 22775.7699
2017-09-16 | 14:42 |  |  |  |  | 77.616 |  | 22774.7646
2017-09-16 | 14:44 |  |  |  |  | 77.625 |  | 22777.3838
2017-09-16 | 14:45 | 1.7546 | 0 | 0 | 1.5 | 77.6298 | 0 | 22778.7943
2017-09-16 | 14:46 |  |  |  |  | 77.5832 |  | 22765.1384
2017-09-16 | 14:48 |  |  |  |  | 77.5641 |  | 22759.5169
2017-09-16 | 14:50 |  |  |  |  | 77.4834 |  | 22735.8475
2017-09-16 | 14:52 |  |  |  |  | 77.4146 |  | 22715.6432
2017-09-16 | 14:54 |  |  |  |  | 77.3786 |  | 22705.0991
2017-09-16 | 14:56 |  |  |  |  | 77.3002 |  | 22682.0943
2017-09-16 | 14:58 |  |  |  |  | 77.3844 |  | 22706.8004
2017-09-16 | 15:00 | 1.7046 | 0 | 0 | 1.5 | 77.5332 | 0 | 22750.4435
2017-09-16 | 15:02 |  |  |  |  | 77.7367 |  | 22810.1559
2017-09-16 | 15:04 |  |  |  |  | 77.7041 |  | 22800.5922
2017-09-16 | 15:06 |  |  |  |  | 77.7096 |  | 22802.2131
2017-09-16 | 15:08 |  |  |  |  | 77.7178 |  | 22804.6219
2017-09-16 | 15:10 |  |  |  |  | 77.6808 |  | 22793.78
2017-09-16 | 15:12 |  |  |  |  | 77.6272 |  | 22778.024
2017-09-16 | 15:14 |  |  |  |  | 77.5664 |  | 22760.1953
2017-09-16 | 15:15 | 1.7912 | 0 | 0 | 1.5 | 77.5081 | 0 | 22743.0984
2017-09-16 | 15:16 |  |  |  |  | 77.5092 |  | 22743.4209
2017-09-16 | 15:18 |  |  |  |  | 77.4312 |  | 22720.537
2017-09-16 | 15:20 |  |  |  |  | 77.351 |  | 22696.9928
2017-09-16 | 15:22 |  |  |  |  | 77.3297 |  | 22690.7378
2017-09-16 | 15:24 |  |  |  |  | 77.2346 |  | 22662.8463
2017-09-16 | 15:26 |  |  |  |  | 77.155 |  | 22639.4788
2017-09-16 | 15:28 |  |  |  |  | 77.2483 |  | 22666.8557
2017-09-16 | 15:30 | 1.6976 | 0 | 0 | 1.5 | 77.4005 | 0 | 22711.5061
2017-09-16 | 15:32 |  |  |  |  | 77.5511 |  | 22755.7158
2017-09-16 | 15:34 |  |  |  |  | 77.5263 |  | 22748.4221
2017-09-16 | 15:36 |  |  |  |  | 77.5155 |  | 22745.2542
2017-09-16 | 15:38 |  |  |  |  | 77.5085 |  | 22743.2193
2017-09-16 | 15:40 |  |  |  |  | 77.516 |  | 22745.4133
2017-09-16 | 15:42 |  |  |  |  | 77.4755 |  | 22733.5215
2017-09-16 | 15:44 |  |  |  |  | 77.4278 |  | 22719.534
2017-09-16 | 15:45 | 1.7928 | 0 | 0 | 1.5 | 77.3574 | 0 | 22698.8778
2017-09-16 | 15:46 |  |  |  |  | 77.354 |  | 22697.8772
2017-09-16 | 15:48 |  |  |  |  | 77.3076 |  | 22684.2616
2017-09-16 | 15:50 |  |  |  |  | 77.2228 |  | 22659.3853
2017-09-16 | 15:52 |  |  |  |  | 77.1529 |  | 22638.8655
2017-09-16 | 15:54 |  |  |  |  | 77.0992 |  | 22623.1028
2017-09-16 | 15:56 |  |  |  |  | 77.0493 |  | 22608.4596
2017-09-16 | 15:58 |  |  |  |  | 77.0935 |  | 22621.4215
2017-09-16 | 16:00 | 1.7031 | 0 | 0 | 1.5 | 77.2813 | 0 | 22676.5538
2017-09-16 | 16:02 |  |  |  |  | 77.4278 |  | 22719.5431
2017-09-16 | 16:04 |  |  |  |  | 77.3807 |  | 22705.7036
2017-09-16 | 16:06 |  |  |  |  | 77.3646 |  | 22700.9776
2017-09-16 | 16:08 |  |  |  |  | 77.3926 |  | 22709.1892
2017-09-16 | 16:10 |  |  |  |  | 77.3749 |  | 22704.0111
2017-09-16 | 16:12 |  |  |  |  | 77.3105 |  | 22685.1055
2017-09-16 | 16:14 |  |  |  |  | 77.2376 |  | 22663.726
2017-09-16 | 16:15 | 1.7624 | 0 | 0 | 1.5 | 77.2404 | 0 | 22664.5388
2017-09-16 | 16:16 |  |  |  |  | 77.1892 |  | 22649.5193
2017-09-16 | 16:18 |  |  |  |  | 77.289 |  | 22678.8079
2017-09-16 | 16:20 |  |  |  |  | 77.4734 |  | 22732.8947
2017-09-16 | 16:22 |  |  |  |  | 77.6511 |  | 22785.0537
2017-09-16 | 16:24 |  |  |  |  | 77.6004 |  | 22770.1842
2017-09-16 | 16:26 |  |  |  |  | 77.5458 |  | 22754.1642
2017-09-16 | 16:28 |  |  |  |  | 77.549 |  | 22755.1046
2017-09-16 | 16:30 | 1.7561 | 0 | 0 | 1.5 | 77.5067 | 0 | 22742.6911
2017-09-16 | 16:32 |  |  |  |  | 77.4768 |  | 22733.8953
2017-09-16 | 16:34 |  |  |  |  | 77.3736 |  | 22703.6237
2017-09-16 | 16:36 |  |  |  |  | 77.3147 |  | 22686.3458
2017-09-16 | 16:38 |  |  |  |  | 77.4105 |  | 22714.4545
2017-09-16 | 16:40 |  |  |  |  | 77.5673 |  | 22760.4752
2017-09-16 | 16:42 |  |  |  |  | 77.7208 |  | 22805.5018
2017-09-16 | 16:44 |  |  |  |  | 77.6522 |  | 22785.3694
2017-09-16 | 16:45 | 1.7764 | 0 | 0 | 1.5 | 77.6468 | 0 | 22783.7931
2017-09-16 | 16:46 |  |  |  |  | 77.6194 |  | 22775.7632
2017-09-16 | 16:48 |  |  |  |  | 77.5965 |  | 22769.0404
2017-09-16 | 16:50 |  |  |  |  | 77.5537 |  | 22756.4858
2017-09-16 | 16:52 |  |  |  |  | 77.4822 |  | 22735.4825
2017-09-16 | 16:54 |  |  |  |  | 77.3878 |  | 22707.7945
2017-09-16 | 16:56 |  |  |  |  | 77.297 |  | 22681.1474
2017-09-16 | 16:58 |  |  |  |  | 77.3593 |  | 22699.4397
2017-09-16 | 17:00 | 1.7039 | 0 | 0 | 1.5 | 77.528 | 0 | 22748.9438
2017-09-16 | 17:02 |  |  |  |  | 77.6581 |  | 22787.1089
2017-09-16 | 17:04 |  |  |  |  | 77.5466 |  | 22754.3793
2017-09-16 | 17:06 |  |  |  |  | 77.5334 |  | 22750.5198
2017-09-16 | 17:08 |  |  |  |  | 77.5076 |  | 22742.9417
2017-09-16 | 17:10 |  |  |  |  | 77.4504 |  | 22726.1673
2017-09-16 | 17:12 |  |  |  |  | 77.3516 |  | 22697.1651
2017-09-16 | 17:14 |  |  |  |  | 77.2745 |  | 22674.5344
2017-09-16 | 17:15 | 1.778 | 0 | 0 | 1.5 | 77.2315 | 0 | 22661.9193
2017-09-16 | 17:16 |  |  |  |  | 77.1789 |  | 22646.4994
2017-09-16 | 17:18 |  |  |  |  | 77.2409 |  | 22664.6975
2017-09-16 | 17:20 |  |  |  |  | 77.3699 |  | 22702.5381
2017-09-16 | 17:22 |  |  |  |  | 77.4978 |  | 22740.0717
2017-09-16 | 17:24 |  |  |  |  | 77.3971 |  | 22710.5123
2017-09-16 | 17:26 |  |  |  |  | 77.335 |  | 22692.2939
2017-09-16 | 17:28 |  |  |  |  | 77.2714 |  | 22673.6433
2017-09-16 | 17:30 | 1.7826 | 0 | 0 | 1.5 | 77.1982 | 0 | 22652.1699
2017-09-16 | 17:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:45 | 0.04012 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 17:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 17:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:00 | 0.03934 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 18:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:15 | 0.03778 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 18:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:30 | 0.037 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 18:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:45 | 0.03778 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 18:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 18:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:00 | 0.037 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 19:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:15 | 0.037 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 19:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:30 | 0.037 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 19:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:45 | 0.03622 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 19:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 19:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:00 | 0.03622 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 20:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:15 | 0.03544 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 20:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:30 | 0.03544 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 20:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:45 | 0.03544 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 20:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 20:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-16 | 21:00 | 0.03544 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-16 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-16 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-16 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:15 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:45 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 5:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 5:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 5:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 5:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 5:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 6:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 6:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 6:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 6:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 6:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 7:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 7:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:30 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 7:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 7:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 7:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 8:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 8:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 8:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 8:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 8:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 9:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 9:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:30 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 9:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 9:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 9:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:00 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 10:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:15 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 10:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 10:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:45 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 10:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 10:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:00 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 11:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:15 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 11:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:30 | 0.03388 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 11:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:45 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 11:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 11:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:00 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 12:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:15 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 12:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:30 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 12:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 12:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 12:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:00 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 13:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 13:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 13:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:45 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 13:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 13:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:00 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 14:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 14:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:30 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 14:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:45 | 0.03388 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 14:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 14:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:00 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 15:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:15 | 0.0331 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 15:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 15:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 15:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 15:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 16:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:15 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 16:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:30 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 16:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:45 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 16:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 16:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:00 | 0.03076 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 17:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:15 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 17:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:30 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 17:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:45 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 17:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 17:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:00 | 0.03232 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 18:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:15 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 18:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:30 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 18:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:45 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 18:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 18:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:00 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 19:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:15 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 19:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:30 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 19:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:45 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 19:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 19:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:00 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 20:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:15 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 20:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:30 | 0.03076 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 20:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:45 | 0.03076 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 20:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 20:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-17 | 21:00 | 0.03154 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-17 | 21:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 21:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 21:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 21:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 21:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 22:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:15 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 22:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 22:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 22:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 22:58 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 23:02 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:04 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:06 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:08 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:10 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:12 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:14 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:15 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 23:16 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:18 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:20 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:22 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:24 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:26 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:28 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 23:32 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:34 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:36 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:38 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:40 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:42 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:44 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:45 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-17 | 23:46 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:48 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:50 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:52 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:54 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:56 |  |  |  |  | 0 |  | 0
2017-09-17 | 23:58 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 0:02 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:04 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:06 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:08 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:10 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:12 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:14 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 0:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 0:16 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:18 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:20 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:22 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:24 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:26 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:28 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 0:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 0:32 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:34 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:36 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:38 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:40 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:42 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:44 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 0:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 0:46 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:48 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:50 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:52 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:54 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:56 |  |  |  |  | 0 |  | 0
2017-09-18 | 0:58 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 1:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 1:02 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:04 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:06 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:08 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:10 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:12 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:14 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 1:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 1:16 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:18 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:20 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:22 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:24 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:26 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:28 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 1:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 1:32 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:34 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:36 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:38 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:40 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:42 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:44 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 1:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 1:46 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:48 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:50 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:52 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:54 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:56 |  |  |  |  | 0 |  | 0
2017-09-18 | 1:58 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 2:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 2:02 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:04 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:06 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:08 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:10 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:12 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:14 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 2:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 2:16 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:18 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:20 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:22 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:24 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:26 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:28 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 2:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 2:32 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:34 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:36 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:38 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:40 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:42 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:44 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 2:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 2:46 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:48 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:50 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:52 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:54 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:56 |  |  |  |  | 0 |  | 0
2017-09-18 | 2:58 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 3:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 3:02 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:04 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:06 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:08 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:10 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:12 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:14 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 3:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 3:16 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:18 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:20 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:22 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:24 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:26 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:28 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 3:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 3:32 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:34 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:36 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:38 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:40 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:42 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:44 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:45 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 3:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 3:46 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:48 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:50 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:52 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:54 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:56 |  |  |  |  | 0 |  | 0
2017-09-18 | 3:58 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:00 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 4:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 4:02 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:04 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:06 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:08 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:10 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:12 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:14 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:15 | 0.03076 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 4:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 4:16 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:18 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:20 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:22 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:24 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:26 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:28 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:30 | 0.03076 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 4:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 4:32 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:34 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:36 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:38 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:40 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:42 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:44 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:45 | 0.02998 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 4:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 4:46 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:48 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:50 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:52 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:54 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:56 |  |  |  |  | 0 |  | 0
2017-09-18 | 4:58 |  |  |  |  | 0 |  | 0
2017-09-18 | 5:00 | 0.02998 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-18 | 5:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 5:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:14 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:15 | 0.02998 | 0 | 0 |  | 25 | 0 | 7335.7143
2017-09-18 | 5:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 5:16 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:18 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:20 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:22 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:24 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:26 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:28 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:30 | 0.02998 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-18 | 5:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 5:32 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:34 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:36 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:38 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:40 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:42 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:44 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:45 | 0.0292 | 0 | 0 |  | 25 | 0 | 7335.7143
2017-09-18 | 5:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 5:46 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:48 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:50 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:52 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:54 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:56 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 5:58 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:00 | 0.0292 | 0 | 0 | 1.5 | 25 | 0 | 7335.7143
2017-09-18 | 6:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 6:02 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:04 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:06 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:08 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:10 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:12 |  |  |  |  | 25 |  | 7335.7143
2017-09-18 | 6:14 |  |  |  |  | 45.625 |  | 13387.6786
2017-09-18 | 6:15 | 0.54244 | 0 | 0 |  | 68.125 | 0 | 19989.8214
2017-09-18 | 6:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 6:16 |  |  |  |  | 90.625 |  | 26591.9643
2017-09-18 | 6:18 |  |  |  |  | 98.6247 |  | 28939.2966
2017-09-18 | 6:20 |  |  |  |  | 96.3869 |  | 28282.671
2017-09-18 | 6:22 |  |  |  |  | 94.6297 |  | 27767.0553
2017-09-18 | 6:24 |  |  |  |  | 93.165 |  | 27337.2755
2017-09-18 | 6:26 |  |  |  |  | 91.9299 |  | 26974.8619
2017-09-18 | 6:28 |  |  |  |  | 90.7909 |  | 26640.6579
2017-09-18 | 6:30 | 2.0884 | 0 | 0 | 1.5 | 89.7113 | 0 | 26323.8486
2017-09-18 | 6:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 6:32 |  |  |  |  | 88.7654 |  | 26046.3033
2017-09-18 | 6:34 |  |  |  |  | 87.926 |  | 25800.0035
2017-09-18 | 6:36 |  |  |  |  | 87.1166 |  | 25562.5106
2017-09-18 | 6:38 |  |  |  |  | 86.39 |  | 25349.2963
2017-09-18 | 6:40 |  |  |  |  | 85.7097 |  | 25149.6754
2017-09-18 | 6:42 |  |  |  |  | 85.0637 |  | 24960.1305
2017-09-18 | 6:44 |  |  |  |  | 84.4071 |  | 24767.4606
2017-09-18 | 6:45 | 1.9527 | 0 | 0 |  | 84.1038 | 0 | 24678.464
2017-09-18 | 6:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 6:46 |  |  |  |  | 83.8443 |  | 24602.3085
2017-09-18 | 6:48 |  |  |  |  | 83.374 |  | 24464.3228
2017-09-18 | 6:50 |  |  |  |  | 82.9776 |  | 24348.003
2017-09-18 | 6:52 |  |  |  |  | 82.6206 |  | 24243.2396
2017-09-18 | 6:54 |  |  |  |  | 82.1414 |  | 24102.6325
2017-09-18 | 6:56 |  |  |  |  | 81.7967 |  | 24001.4909
2017-09-18 | 6:58 |  |  |  |  | 81.4598 |  | 23902.6374
2017-09-18 | 7:00 | 1.8669 | 0 | 0 | 1.5 | 81.1472 | 0 | 23810.914
2017-09-18 | 7:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 7:02 |  |  |  |  | 80.7948 |  | 23707.5115
2017-09-18 | 7:04 |  |  |  |  | 80.66 |  | 23667.9541
2017-09-18 | 7:06 |  |  |  |  | 80.5233 |  | 23627.848
2017-09-18 | 7:08 |  |  |  |  | 80.2954 |  | 23560.9563
2017-09-18 | 7:10 |  |  |  |  | 80.0118 |  | 23477.7602
2017-09-18 | 7:12 |  |  |  |  | 79.8132 |  | 23419.4738
2017-09-18 | 7:14 |  |  |  |  | 79.772 |  | 23407.3872
2017-09-18 | 7:15 | 1.7803 | 0 | 0 |  | 79.7201 | 0 | 23392.1642
2017-09-18 | 7:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 7:16 |  |  |  |  | 79.6769 |  | 23379.4754
2017-09-18 | 7:18 |  |  |  |  | 79.5508 |  | 23342.47
2017-09-18 | 7:20 |  |  |  |  | 79.4059 |  | 23299.9619
2017-09-18 | 7:22 |  |  |  |  | 79.2361 |  | 23250.1377
2017-09-18 | 7:24 |  |  |  |  | 79.2273 |  | 23247.5496
2017-09-18 | 7:26 |  |  |  |  | 79.1897 |  | 23236.5062
2017-09-18 | 7:28 |  |  |  |  | 79.1082 |  | 23212.6196
2017-09-18 | 7:30 | 1.7764 | 0 | 0 | 1.5 | 79.0042 | 0 | 23182.0951
2017-09-18 | 7:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 7:32 |  |  |  |  | 78.8855 |  | 23147.2566
2017-09-18 | 7:34 |  |  |  |  | 78.9514 |  | 23166.6036
2017-09-18 | 7:36 |  |  |  |  | 78.9912 |  | 23178.2603
2017-09-18 | 7:38 |  |  |  |  | 79.0926 |  | 23208.0213
2017-09-18 | 7:40 |  |  |  |  | 79.1912 |  | 23236.9539
2017-09-18 | 7:42 |  |  |  |  | 79.3124 |  | 23272.5178
2017-09-18 | 7:44 |  |  |  |  | 79.4636 |  | 23316.8974
2017-09-18 | 7:45 | 1.6883 | 0 | 0 |  | 79.5557 | 0 | 23343.9295
2017-09-18 | 7:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 7:46 |  |  |  |  | 79.6428 |  | 23369.4595
2017-09-18 | 7:48 |  |  |  |  | 79.8132 |  | 23419.4715
2017-09-18 | 7:50 |  |  |  |  | 80.0197 |  | 23480.0683
2017-09-18 | 7:52 |  |  |  |  | 80.2463 |  | 23546.5504
2017-09-18 | 7:54 |  |  |  |  | 80.4703 |  | 23612.2916
2017-09-18 | 7:56 |  |  |  |  | 80.7221 |  | 23686.1634
2017-09-18 | 7:58 |  |  |  |  | 80.9519 |  | 23753.6039
2017-09-18 | 8:00 | 1.6485 | 0 | 0 | 1.5 | 81.2285 | 0 | 23834.7742
2017-09-18 | 8:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 8:02 |  |  |  |  | 81.5294 |  | 23923.0586
2017-09-18 | 8:04 |  |  |  |  | 81.7884 |  | 23999.0575
2017-09-18 | 8:06 |  |  |  |  | 82.0773 |  | 24083.814
2017-09-18 | 8:08 |  |  |  |  | 82.2609 |  | 24137.6969
2017-09-18 | 8:10 |  |  |  |  | 82.3094 |  | 24151.9437
2017-09-18 | 8:12 |  |  |  |  | 82.4251 |  | 24185.8911
2017-09-18 | 8:14 |  |  |  |  | 82.3357 |  | 24159.6539
2017-09-18 | 8:15 | 1.7702 | 0 | 0 |  | 82.3124 | 0 | 24152.8079
2017-09-18 | 8:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 8:16 |  |  |  |  | 82.255 |  | 24135.9686
2017-09-18 | 8:18 |  |  |  |  | 82.0881 |  | 24087.0042
2017-09-18 | 8:20 |  |  |  |  | 81.9043 |  | 24033.0653
2017-09-18 | 8:22 |  |  |  |  | 81.749 |  | 23987.4902
2017-09-18 | 8:24 |  |  |  |  | 81.5322 |  | 23923.8849
2017-09-18 | 8:26 |  |  |  |  | 81.3669 |  | 23875.3858
2017-09-18 | 8:28 |  |  |  |  | 81.2679 |  | 23846.31
2017-09-18 | 8:30 | 1.7858 | 0 | 0 | 1.5 | 81.1354 | 0 | 23807.4398
2017-09-18 | 8:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 8:32 |  |  |  |  | 81.0644 |  | 23786.6064
2017-09-18 | 8:34 |  |  |  |  | 81.0151 |  | 23772.158
2017-09-18 | 8:36 |  |  |  |  | 81.0172 |  | 23772.758
2017-09-18 | 8:38 |  |  |  |  | 81.0588 |  | 23784.9723
2017-09-18 | 8:40 |  |  |  |  | 81.108 |  | 23799.4184
2017-09-18 | 8:42 |  |  |  |  | 81.2239 |  | 23833.3994
2017-09-18 | 8:44 |  |  |  |  | 81.3778 |  | 23878.5807
2017-09-18 | 8:45 | 1.6773 | 0 | 0 |  | 81.4713 | 0 | 23906.0201
2017-09-18 | 8:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 8:46 |  |  |  |  | 81.5079 |  | 23916.759
2017-09-18 | 8:48 |  |  |  |  | 81.7532 |  | 23988.737
2017-09-18 | 8:50 |  |  |  |  | 81.9675 |  | 24051.6038
2017-09-18 | 8:52 |  |  |  |  | 82.203 |  | 24120.7141
2017-09-18 | 8:54 |  |  |  |  | 82.4541 |  | 24194.3894
2017-09-18 | 8:56 |  |  |  |  | 82.6945 |  | 24264.9302
2017-09-18 | 8:58 |  |  |  |  | 83.0237 |  | 24361.5336
2017-09-18 | 9:00 | 1.6438 | 0 | 0 | 1.5 | 83.3794 | 0 | 24465.89
2017-09-18 | 9:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 9:02 |  |  |  |  | 83.7003 |  | 24560.0465
2017-09-18 | 9:04 |  |  |  |  | 84.1104 |  | 24680.4048
2017-09-18 | 9:06 |  |  |  |  | 84.558 |  | 24811.7238
2017-09-18 | 9:08 |  |  |  |  | 84.9977 |  | 24940.7414
2017-09-18 | 9:10 |  |  |  |  | 85.4397 |  | 25070.4506
2017-09-18 | 9:12 |  |  |  |  | 85.862 |  | 25194.3752
2017-09-18 | 9:14 |  |  |  |  | 86.3095 |  | 25325.6627
2017-09-18 | 9:15 | 1.6227 | 0 | 0 |  | 86.5134 | 0 | 25385.5136
2017-09-18 | 9:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 9:16 |  |  |  |  | 86.7423 |  | 25452.6563
2017-09-18 | 9:18 |  |  |  |  | 87.1748 |  | 25579.5852
2017-09-18 | 9:20 |  |  |  |  | 87.5924 |  | 25702.1014
2017-09-18 | 9:22 |  |  |  |  | 88.0085 |  | 25824.2037
2017-09-18 | 9:24 |  |  |  |  | 88.333 |  | 25919.4239
2017-09-18 | 9:26 |  |  |  |  | 88.5892 |  | 25994.6033
2017-09-18 | 9:28 |  |  |  |  | 88.8652 |  | 26075.5787
2017-09-18 | 9:30 | 1.6742 | 0 | 0 | 1.5 | 89.1311 | 0 | 26153.6146
2017-09-18 | 9:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 9:32 |  |  |  |  | 89.3879 |  | 26228.9553
2017-09-18 | 9:34 |  |  |  |  | 89.4328 |  | 26242.1299
2017-09-18 | 9:36 |  |  |  |  | 89.4595 |  | 26249.9586
2017-09-18 | 9:38 |  |  |  |  | 89.4652 |  | 26251.6488
2017-09-18 | 9:40 |  |  |  |  | 89.4643 |  | 26251.3823
2017-09-18 | 9:42 |  |  |  |  | 89.3686 |  | 26223.3071
2017-09-18 | 9:44 |  |  |  |  | 89.3074 |  | 26205.3349
2017-09-18 | 9:45 | 1.8099 | 0 | 0 |  | 89.2196 | 0 | 26179.59
2017-09-18 | 9:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 9:46 |  |  |  |  | 89.1157 |  | 26149.0881
2017-09-18 | 9:48 |  |  |  |  | 88.9381 |  | 26096.9758
2017-09-18 | 9:50 |  |  |  |  | 88.6353 |  | 26008.1406
2017-09-18 | 9:52 |  |  |  |  | 88.1565 |  | 25867.6499
2017-09-18 | 9:54 |  |  |  |  | 87.7182 |  | 25739.0308
2017-09-18 | 9:56 |  |  |  |  | 87.3104 |  | 25619.3665
2017-09-18 | 9:58 |  |  |  |  | 86.9053 |  | 25500.508
2017-09-18 | 10:00 | 1.9043 | 0 | 0 | 1.5 | 86.4867 | 0 | 25377.6829
2017-09-18 | 10:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 10:02 |  |  |  |  | 86.1128 |  | 25267.9582
2017-09-18 | 10:04 |  |  |  |  | 85.7113 |  | 25150.1475
2017-09-18 | 10:06 |  |  |  |  | 85.2963 |  | 25028.3744
2017-09-18 | 10:08 |  |  |  |  | 84.8732 |  | 24904.233
2017-09-18 | 10:10 |  |  |  |  | 84.4638 |  | 24784.0963
2017-09-18 | 10:12 |  |  |  |  | 84.0547 |  | 24664.0582
2017-09-18 | 10:14 |  |  |  |  | 83.8858 |  | 24614.5004
2017-09-18 | 10:15 | 1.8092 | 0 | 0 |  | 83.8063 | 0 | 24591.16
2017-09-18 | 10:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 10:16 |  |  |  |  | 83.7346 |  | 24570.1117
2017-09-18 | 10:18 |  |  |  |  | 83.5451 |  | 24514.5141
2017-09-18 | 10:20 |  |  |  |  | 83.2279 |  | 24421.4341
2017-09-18 | 10:22 |  |  |  |  | 82.9556 |  | 24341.5332
2017-09-18 | 10:24 |  |  |  |  | 82.6919 |  | 24264.1802
2017-09-18 | 10:26 |  |  |  |  | 82.4153 |  | 24183.0146
2017-09-18 | 10:28 |  |  |  |  | 82.1395 |  | 24102.075
2017-09-18 | 10:30 | 1.8435 | 0 | 0 | 1.5 | 81.8511 | 0 | 24017.4528
2017-09-18 | 10:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 10:32 |  |  |  |  | 81.593 |  | 23941.7069
2017-09-18 | 10:34 |  |  |  |  | 81.544 |  | 23927.328
2017-09-18 | 10:36 |  |  |  |  | 81.4744 |  | 23906.9291
2017-09-18 | 10:38 |  |  |  |  | 81.4736 |  | 23906.6782
2017-09-18 | 10:40 |  |  |  |  | 81.4944 |  | 23912.7719
2017-09-18 | 10:42 |  |  |  |  | 81.4839 |  | 23909.7138
2017-09-18 | 10:44 |  |  |  |  | 81.4476 |  | 23899.0488
2017-09-18 | 10:45 | 1.8014 | 0 | 0 |  | 81.3464 | 0 | 23869.3571
2017-09-18 | 10:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 10:46 |  |  |  |  | 81.291 |  | 23853.0908
2017-09-18 | 10:48 |  |  |  |  | 81.1742 |  | 23818.8345
2017-09-18 | 10:50 |  |  |  |  | 81.0562 |  | 23784.2179
2017-09-18 | 10:52 |  |  |  |  | 80.8992 |  | 23738.1279
2017-09-18 | 10:54 |  |  |  |  | 80.8 |  | 23709.0206
2017-09-18 | 10:56 |  |  |  |  | 80.8314 |  | 23718.2416
2017-09-18 | 10:58 |  |  |  |  | 80.8856 |  | 23734.1519
2017-09-18 | 11:00 | 1.778 | 0 | 0 | 1.5 | 80.8552 | 0 | 23725.2241
2017-09-18 | 11:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 11:02 |  |  |  |  | 80.6897 |  | 23676.649
2017-09-18 | 11:04 |  |  |  |  | 80.6838 |  | 23674.9457
2017-09-18 | 11:06 |  |  |  |  | 80.7607 |  | 23697.4957
2017-09-18 | 11:08 |  |  |  |  | 80.8025 |  | 23709.7704
2017-09-18 | 11:10 |  |  |  |  | 80.7433 |  | 23692.4006
2017-09-18 | 11:12 |  |  |  |  | 80.6916 |  | 23677.2156
2017-09-18 | 11:14 |  |  |  |  | 80.823 |  | 23715.7792
2017-09-18 | 11:15 | 1.7171 | 0 | 0 |  | 80.8986 | 0 | 23737.9509
2017-09-18 | 11:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 11:16 |  |  |  |  | 80.9667 |  | 23757.9493
2017-09-18 | 11:18 |  |  |  |  | 81.0493 |  | 23782.1918
2017-09-18 | 11:20 |  |  |  |  | 81.0494 |  | 23782.2208
2017-09-18 | 11:22 |  |  |  |  | 80.9267 |  | 23746.2071
2017-09-18 | 11:24 |  |  |  |  | 80.7507 |  | 23694.5631
2017-09-18 | 11:26 |  |  |  |  | 80.6598 |  | 23667.9004
2017-09-18 | 11:28 |  |  |  |  | 80.5438 |  | 23633.8454
2017-09-18 | 11:30 | 1.7585 | 0 | 0 | 1.5 | 80.4684 | 0 | 23611.7365
2017-09-18 | 11:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 11:32 |  |  |  |  | 80.4671 |  | 23611.3356
2017-09-18 | 11:34 |  |  |  |  | 80.4598 |  | 23609.1954
2017-09-18 | 11:36 |  |  |  |  | 80.3776 |  | 23585.0961
2017-09-18 | 11:38 |  |  |  |  | 80.3618 |  | 23580.4576
2017-09-18 | 11:40 |  |  |  |  | 80.4207 |  | 23597.7311
2017-09-18 | 11:42 |  |  |  |  | 80.5415 |  | 23633.1673
2017-09-18 | 11:44 |  |  |  |  | 80.4847 |  | 23616.5226
2017-09-18 | 11:45 | 1.7522 | 0 | 0 |  | 80.5395 | 0 | 23632.5851
2017-09-18 | 11:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 11:46 |  |  |  |  | 80.5283 |  | 23629.3099
2017-09-18 | 11:48 |  |  |  |  | 80.605 |  | 23651.8176
2017-09-18 | 11:50 |  |  |  |  | 80.6781 |  | 23673.2485
2017-09-18 | 11:52 |  |  |  |  | 80.6402 |  | 23662.1313
2017-09-18 | 11:54 |  |  |  |  | 80.5966 |  | 23649.3461
2017-09-18 | 11:56 |  |  |  |  | 80.4862 |  | 23616.9436
2017-09-18 | 11:58 |  |  |  |  | 80.3748 |  | 23584.2633
2017-09-18 | 12:00 | 1.7826 | 0 | 0 | 1.5 | 80.236 | 0 | 23543.546
2017-09-18 | 12:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 12:02 |  |  |  |  | 80.1161 |  | 23508.3428
2017-09-18 | 12:04 |  |  |  |  | 80.2177 |  | 23538.1754
2017-09-18 | 12:06 |  |  |  |  | 80.3691 |  | 23582.5776
2017-09-18 | 12:08 |  |  |  |  | 80.414 |  | 23595.761
2017-09-18 | 12:10 |  |  |  |  | 80.4759 |  | 23613.9281
2017-09-18 | 12:12 |  |  |  |  | 80.5278 |  | 23629.1488
2017-09-18 | 12:14 |  |  |  |  | 80.4347 |  | 23601.8347
2017-09-18 | 12:15 | 1.7881 | 0 | 0 |  | 80.378 | 0 | 23585.1944
2017-09-18 | 12:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 12:16 |  |  |  |  | 80.2863 |  | 23558.3058
2017-09-18 | 12:18 |  |  |  |  | 80.3098 |  | 23565.2031
2017-09-18 | 12:20 |  |  |  |  | 80.33 |  | 23571.1133
2017-09-18 | 12:22 |  |  |  |  | 80.4255 |  | 23599.1504
2017-09-18 | 12:24 |  |  |  |  | 80.4583 |  | 23608.7499
2017-09-18 | 12:26 |  |  |  |  | 80.4752 |  | 23613.7221
2017-09-18 | 12:28 |  |  |  |  | 80.433 |  | 23601.3265
2017-09-18 | 12:30 | 1.8146 | 0 | 0 | 1.5 | 80.2786 | 0 | 23556.0267
2017-09-18 | 12:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 12:32 |  |  |  |  | 80.123 |  | 23510.3801
2017-09-18 | 12:34 |  |  |  |  | 79.948 |  | 23459.0403
2017-09-18 | 12:36 |  |  |  |  | 79.7819 |  | 23410.2907
2017-09-18 | 12:38 |  |  |  |  | 79.7625 |  | 23404.5821
2017-09-18 | 12:40 |  |  |  |  | 79.84 |  | 23427.3451
2017-09-18 | 12:42 |  |  |  |  | 79.8825 |  | 23439.8079
2017-09-18 | 12:44 |  |  |  |  | 79.8432 |  | 23428.2741
2017-09-18 | 12:45 | 1.7678 | 0 | 0 |  | 79.7897 | 0 | 23412.5698
2017-09-18 | 12:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 12:46 |  |  |  |  | 79.8045 |  | 23416.9216
2017-09-18 | 12:48 |  |  |  |  | 79.7034 |  | 23387.268
2017-09-18 | 12:50 |  |  |  |  | 79.6215 |  | 23363.2201
2017-09-18 | 12:52 |  |  |  |  | 79.4745 |  | 23320.101
2017-09-18 | 12:54 |  |  |  |  | 79.4597 |  | 23315.7333
2017-09-18 | 12:56 |  |  |  |  | 79.5808 |  | 23351.2678
2017-09-18 | 12:58 |  |  |  |  | 79.7505 |  | 23401.0741
2017-09-18 | 13:00 | 1.6797 | 0 | 0 | 1.5 | 79.9621 | 0 | 23463.1595
2017-09-18 | 13:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 13:02 |  |  |  |  | 80.1975 |  | 23532.2249
2017-09-18 | 13:04 |  |  |  |  | 80.3182 |  | 23567.6679
2017-09-18 | 13:06 |  |  |  |  | 80.4481 |  | 23605.7702
2017-09-18 | 13:08 |  |  |  |  | 80.7641 |  | 23698.5009
2017-09-18 | 13:10 |  |  |  |  | 81.0584 |  | 23784.849
2017-09-18 | 13:12 |  |  |  |  | 81.3568 |  | 23872.4084
2017-09-18 | 13:14 |  |  |  |  | 81.6659 |  | 23963.1019
2017-09-18 | 13:15 | 1.6438 | 0 | 0 |  | 81.8051 | 0 | 24003.9445
2017-09-18 | 13:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 13:16 |  |  |  |  | 81.9374 |  | 24042.7678
2017-09-18 | 13:18 |  |  |  |  | 82.2641 |  | 24138.6505
2017-09-18 | 13:20 |  |  |  |  | 82.5962 |  | 24236.0914
2017-09-18 | 13:22 |  |  |  |  | 82.9773 |  | 24347.898
2017-09-18 | 13:24 |  |  |  |  | 83.3179 |  | 24447.8415
2017-09-18 | 13:26 |  |  |  |  | 83.6523 |  | 24545.9676
2017-09-18 | 13:28 |  |  |  |  | 83.9592 |  | 24636.0208
2017-09-18 | 13:30 | 1.6571 | 0 | 0 | 1.5 | 84.2165 | 0 | 24711.5361
2017-09-18 | 13:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 13:32 |  |  |  |  | 84.4561 |  | 24781.8307
2017-09-18 | 13:34 |  |  |  |  | 84.5993 |  | 24823.8485
2017-09-18 | 13:36 |  |  |  |  | 84.6735 |  | 24845.6265
2017-09-18 | 13:38 |  |  |  |  | 84.6139 |  | 24828.1311
2017-09-18 | 13:40 |  |  |  |  | 84.4537 |  | 24781.1368
2017-09-18 | 13:42 |  |  |  |  | 84.1474 |  | 24691.2402
2017-09-18 | 13:44 |  |  |  |  | 83.9141 |  | 24622.808
2017-09-18 | 13:45 | 1.8138 | 0 | 0 |  | 83.813 | 0 | 24593.1388
2017-09-18 | 13:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 13:46 |  |  |  |  | 83.7661 |  | 24579.3641
2017-09-18 | 13:48 |  |  |  |  | 83.6376 |  | 24541.6468
2017-09-18 | 13:50 |  |  |  |  | 83.5216 |  | 24507.6255
2017-09-18 | 13:52 |  |  |  |  | 83.3971 |  | 24471.0992
2017-09-18 | 13:54 |  |  |  |  | 83.4227 |  | 24478.6122
2017-09-18 | 13:56 |  |  |  |  | 83.5541 |  | 24517.1714
2017-09-18 | 13:58 |  |  |  |  | 83.6065 |  | 24532.5221
2017-09-18 | 14:00 | 1.728 | 0 | 0 | 1.5 | 83.7016 | 0 | 24560.4497
2017-09-18 | 14:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 14:02 |  |  |  |  | 83.8765 |  | 24611.7581
2017-09-18 | 14:04 |  |  |  |  | 83.9915 |  | 24645.5062
2017-09-18 | 14:06 |  |  |  |  | 84.0504 |  | 24662.8
2017-09-18 | 14:08 |  |  |  |  | 83.9128 |  | 24622.4274
2017-09-18 | 14:10 |  |  |  |  | 83.6675 |  | 24550.4203
2017-09-18 | 14:12 |  |  |  |  | 83.3973 |  | 24471.1418
2017-09-18 | 14:14 |  |  |  |  | 83.3596 |  | 24460.076
2017-09-18 | 14:15 | 1.7546 | 0 | 0 |  | 83.3462 | 0 | 24456.1426
2017-09-18 | 14:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 14:16 |  |  |  |  | 83.4037 |  | 24473.0335
2017-09-18 | 14:18 |  |  |  |  | 83.4434 |  | 24484.6835
2017-09-18 | 14:20 |  |  |  |  | 83.5044 |  | 24502.5841
2017-09-18 | 14:22 |  |  |  |  | 83.5395 |  | 24512.8776
2017-09-18 | 14:24 |  |  |  |  | 83.4363 |  | 24482.5838
2017-09-18 | 14:26 |  |  |  |  | 83.2477 |  | 24427.2549
2017-09-18 | 14:28 |  |  |  |  | 83.1263 |  | 24391.6282
2017-09-18 | 14:30 | 1.7561 | 0 | 0 | 1.5 | 83.0976 | 0 | 24383.2042
2017-09-18 | 14:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 14:32 |  |  |  |  | 83.1608 |  | 24401.7471
2017-09-18 | 14:34 |  |  |  |  | 83.1862 |  | 24409.202
2017-09-18 | 14:36 |  |  |  |  | 83.2471 |  | 24427.0668
2017-09-18 | 14:38 |  |  |  |  | 83.3006 |  | 24442.789
2017-09-18 | 14:40 |  |  |  |  | 83.2212 |  | 24419.4887
2017-09-18 | 14:42 |  |  |  |  | 83.1092 |  | 24386.6203
2017-09-18 | 14:44 |  |  |  |  | 83.133 |  | 24393.5895
2017-09-18 | 14:45 | 1.7475 | 0 | 0 |  | 83.1103 | 0 | 24386.9293
2017-09-18 | 14:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 14:46 |  |  |  |  | 83.2061 |  | 24415.045
2017-09-18 | 14:48 |  |  |  |  | 83.409 |  | 24474.5805
2017-09-18 | 14:50 |  |  |  |  | 83.5825 |  | 24525.4947
2017-09-18 | 14:52 |  |  |  |  | 83.7386 |  | 24571.3072
2017-09-18 | 14:54 |  |  |  |  | 83.8675 |  | 24609.1163
2017-09-18 | 14:56 |  |  |  |  | 83.9317 |  | 24627.9615
2017-09-18 | 14:58 |  |  |  |  | 84.0478 |  | 24662.032
2017-09-18 | 15:00 | 1.7748 | 0 | 0 | 1.5 | 83.9068 | 0 | 24620.641
2017-09-18 | 15:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 15:02 |  |  |  |  | 83.684 |  | 24555.2783
2017-09-18 | 15:04 | 1.7702 |  |  |  | 83.6738 |  | 24552.2895
2017-09-18 | 15:06 | 1.7171 |  |  |  | 83.7272 |  | 24567.9536
2017-09-18 | 15:08 | 1.7304 |  |  |  | 83.8185 |  | 24594.753
2017-09-18 | 15:10 | 1.7187 |  |  |  | 83.855 |  | 24605.4584
2017-09-18 | 15:12 | 1.746 |  |  |  | 83.8728 |  | 24610.6656
2017-09-18 | 15:14 | 1.7678 |  |  |  | 83.8155 |  | 24593.8551
2017-09-18 | 15:15 | 1.7811 | 0 | 0 |  | 83.7593 | 0 | 24577.3717
2017-09-18 | 15:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 15:16 | 1.7889 |  |  |  | 83.7166 |  | 24564.8353
2017-09-18 | 15:18 | 1.7569 |  |  |  | 83.6907 |  | 24557.2326
2017-09-18 | 15:20 | 1.7538 |  |  |  | 83.6699 |  | 24551.1366
2017-09-18 | 15:22 | 1.7382 |  |  |  | 83.7204 |  | 24565.9591
2017-09-18 | 15:24 | 1.7756 |  |  |  | 83.6057 |  | 24532.2891
2017-09-18 | 15:26 | 1.7725 |  |  |  | 83.5299 |  | 24510.0613
2017-09-18 | 15:28 | 1.7834 |  |  |  | 83.418 |  | 24477.231
2017-09-18 | 15:30 | 1.8232 | 0 | 0 | 1.5 | 83.2178 | 0 | 24418.4881
2017-09-18 | 15:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 15:32 | 1.8357 |  |  |  | 82.9717 |  | 24346.2615
2017-09-18 | 15:34 | 1.7686 |  |  |  | 82.8913 |  | 24322.6614
2017-09-18 | 15:36 | 1.7475 |  |  |  | 82.914 |  | 24329.3348
2017-09-18 | 15:38 | 1.7686 |  |  |  | 82.9516 |  | 24340.3692
2017-09-18 | 15:40 | 1.7397 |  |  |  | 82.9724 |  | 24346.4652
2017-09-18 | 15:42 | 1.739 |  |  |  | 83.0101 |  | 24357.5444
2017-09-18 | 15:44 | 1.7202 |  |  |  | 83.1227 |  | 24390.5739
2017-09-18 | 15:45 | 1.7179 | 0 | 0 |  | 83.2148 | 0 | 24417.5949
2017-09-18 | 15:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 15:46 | 1.7062 |  |  |  | 83.2721 |  | 24434.4207
2017-09-18 | 15:48 | 1.707 |  |  |  | 83.435 |  | 24482.2211
2017-09-18 | 15:50 | 1.7413 |  |  |  | 83.4852 |  | 24496.9494
2017-09-18 | 15:52 | 1.7475 |  |  |  | 83.5203 |  | 24507.2541
2017-09-18 | 15:54 | 1.7624 |  |  |  | 83.5402 |  | 24513.0768
2017-09-18 | 15:56 | 1.8107 |  |  |  | 83.3584 |  | 24459.7356
2017-09-18 | 15:58 | 1.7998 |  |  |  | 83.1468 |  | 24397.6324
2017-09-18 | 16:00 | 1.7826 | 0 | 0 | 1.5 | 83.0332 | 0 | 24364.3118
2017-09-18 | 16:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 16:02 | 1.7234 |  |  |  | 83.0742 |  | 24376.3471
2017-09-18 | 16:04 | 1.7405 |  |  |  | 83.0654 |  | 24373.7546
2017-09-18 | 16:06 | 1.7608 |  |  |  | 83.0211 |  | 24360.766
2017-09-18 | 16:08 | 1.7553 |  |  |  | 83.0003 |  | 24354.6542
2017-09-18 | 16:10 | 1.7967 |  |  |  | 82.8616 |  | 24313.9483
2017-09-18 | 16:12 | 1.7959 |  |  |  | 82.7471 |  | 24280.3657
2017-09-18 | 16:14 | 1.7741 |  |  |  | 82.7142 |  | 24270.6993
2017-09-18 | 16:15 | 1.7717 | 0 | 0 |  | 82.6625 | 0 | 24255.5255
2017-09-18 | 16:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 16:16 | 1.7397 |  |  |  | 82.6986 |  | 24266.1256
2017-09-18 | 16:18 | 1.7608 |  |  |  | 82.7014 |  | 24266.9607
2017-09-18 | 16:20 | 1.7382 |  |  |  | 82.6979 |  | 24265.924
2017-09-18 | 16:22 | 1.7273 |  |  |  | 82.7259 |  | 24274.1312
2017-09-18 | 16:24 | 1.7655 |  |  |  | 82.7027 |  | 24267.3254
2017-09-18 | 16:26 | 1.7538 |  |  |  | 82.7021 |  | 24267.1552
2017-09-18 | 16:28 | 1.7624 |  |  |  | 82.6337 |  | 24247.0765
2017-09-18 | 16:30 | 1.7561 | 0 | 0 | 1.5 | 82.6106 | 0 | 24240.3001
2017-09-18 | 16:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 16:32 | 1.7397 |  |  |  | 82.6099 |  | 24240.1076
2017-09-18 | 16:34 | 1.7491 |  |  |  | 82.5766 |  | 24230.3291
2017-09-18 | 16:36 | 1.7249 |  |  |  | 82.6275 |  | 24245.2834
2017-09-18 | 16:38 | 1.7257 |  |  |  | 82.7154 |  | 24271.0596
2017-09-18 | 16:40 | 1.7296 |  |  |  | 82.7483 |  | 24280.7284
2017-09-18 | 16:42 | 1.7787 |  |  |  | 82.6297 |  | 24245.9169
2017-09-18 | 16:44 | 1.7647 |  |  |  | 82.6222 |  | 24243.7253
2017-09-18 | 16:45 | 1.7405 | 0 | 0 |  | 82.6438 | 0 | 24250.0495
2017-09-18 | 16:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 16:46 | 1.7483 |  |  |  | 82.6194 |  | 24242.879
2017-09-18 | 16:48 | 1.7343 |  |  |  | 82.6937 |  | 24264.7083
2017-09-18 | 16:50 | 1.7078 |  |  |  | 82.8166 |  | 24300.7648
2017-09-18 | 16:52 | 1.728 |  |  |  | 82.8919 |  | 24322.8515
2017-09-18 | 16:54 | 1.7366 |  |  |  | 82.9175 |  | 24330.3645
2017-09-18 | 16:56 | 1.7694 |  |  |  | 82.8901 |  | 24322.3254
2017-09-18 | 16:58 | 1.7382 |  |  |  | 82.8805 |  | 24319.507
2017-09-18 | 17:00 | 1.7436 | 0 | 0 | 1.5 | 82.8922 | 0 | 24322.9433
2017-09-18 | 17:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 17:02 | 1.7249 |  |  |  | 82.9427 |  | 24337.7679
2017-09-18 | 17:04 | 1.7421 |  |  |  | 82.9374 |  | 24336.2007
2017-09-18 | 17:06 | 1.739 |  |  |  | 82.9654 |  | 24344.4323
2017-09-18 | 17:08 | 1.739 |  |  |  | 83.0228 |  | 24361.2472
2017-09-18 | 17:10 | 1.7764 |  |  |  | 82.9547 |  | 24341.2782
2017-09-18 | 17:12 | 1.7998 |  |  |  | 82.803 |  | 24296.7642
2017-09-18 | 17:14 | 1.8045 |  |  |  | 82.72 |  | 24272.4252
2017-09-18 | 17:15 | 1.7858 | 0 | 0 |  | 82.6779 | 0 | 24260.0499
2017-09-18 | 17:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 17:16 | 1.7904 |  |  |  | 82.6143 |  | 24241.3949
2017-09-18 | 17:18 | 1.8185 |  |  |  | 82.4335 |  | 24188.3312
2017-09-18 | 17:20 | 1.8154 |  |  |  | 82.2264 |  | 24127.5645
2017-09-18 | 17:22 | 1.8099 |  |  |  | 82.0917 |  | 24088.0517
2017-09-18 | 17:24 | 1.7546 |  |  |  | 82.1036 |  | 24091.5353
2017-09-18 | 17:26 | 1.7475 |  |  |  | 82.1182 |  | 24095.829
2017-09-18 | 17:28 | 1.7889 |  |  |  | 82.0797 |  | 24084.5303
2017-09-18 | 17:30 | 1.7951 | 0 | 0 | 1.5 | 81.9616 | 0 | 24049.8667
2017-09-18 | 17:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 17:32 | 1.7826 |  |  |  | 81.81 |  | 24005.3973
2017-09-18 | 17:34 | 1.7585 |  |  |  | 81.8491 |  | 24016.8639
2017-09-18 | 17:36 | 1.7483 |  |  |  | 81.8898 |  | 24028.8029
2017-09-18 | 17:38 | 1.7741 |  |  |  | 81.8928 |  | 24029.6782
2017-09-18 | 17:40 | 1.8037 |  |  |  | 81.7284 |  | 23981.4524
2017-09-18 | 17:42 | 1.7959 |  |  |  | 81.6159 |  | 23948.4408
2017-09-18 | 17:44 | 1.7585 |  |  |  | 81.6385 |  | 23955.0608
2017-09-18 | 17:45 | 1.7304 | 0 | 0 |  | 81.6853 | 0 | 23968.8129
2017-09-18 | 17:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 17:46 | 1.7288 |  |  |  | 81.7088 |  | 23975.6991
2017-09-18 | 17:48 | 1.7608 |  |  |  | 81.7002 |  | 23973.1627
2017-09-18 | 17:50 | 1.799 |  |  |  | 81.5262 |  | 23922.1161
2017-09-18 | 17:52 | 1.8014 |  |  |  | 81.3799 |  | 23879.1872
2017-09-18 | 17:54 | 1.7748 |  |  |  | 81.3501 |  | 23870.4474
2017-09-18 | 17:56 | 1.7631 |  |  |  | 81.2777 |  | 23849.2111
2017-09-18 | 17:58 | 1.8154 |  |  |  | 81.1375 |  | 23808.0575
2017-09-18 | 18:00 | 1.8131 | 0 | 0 | 1.5 | 80.9205 | 0 | 23744.3782
2017-09-18 | 18:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 18:02 | 1.7951 |  |  |  | 80.7249 |  | 23687.0009
2017-09-18 | 18:04 | 1.7507 |  |  |  | 80.7662 |  | 23699.0987
2017-09-18 | 18:06 | 1.7085 |  |  |  | 80.8634 |  | 23727.6328
2017-09-18 | 18:08 | 1.778 |  |  |  | 80.8481 |  | 23723.1466
2017-09-18 | 18:10 | 1.792 |  |  |  | 80.7248 |  | 23686.9762
2017-09-18 | 18:12 | 1.7928 |  |  |  | 80.6122 |  | 23653.9309
2017-09-18 | 18:14 | 1.7655 |  |  |  | 80.5955 |  | 23649.0306
2017-09-18 | 18:15 | 1.7858 | 0 | 0 |  | 80.5725 | 0 | 23642.2786
2017-09-18 | 18:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 18:16 | 1.7561 |  |  |  | 80.5378 |  | 23632.0769
2017-09-18 | 18:18 | 1.8084 |  |  |  | 80.4232 |  | 23598.4788
2017-09-18 | 18:20 | 1.7967 |  |  |  | 80.2377 |  | 23544.0475
2017-09-18 | 18:22 | 1.7889 |  |  |  | 80.0916 |  | 23501.1746
2017-09-18 | 18:24 | 1.7273 |  |  |  | 80.1465 |  | 23517.2862
2017-09-18 | 18:26 | 1.7187 |  |  |  | 80.2551 |  | 23549.1361
2017-09-18 | 18:28 | 1.7795 |  |  |  | 80.2378 |  | 23544.0698
2017-09-18 | 18:30 | 1.7764 | 0 | 0 | 1.5 | 80.1403 | 0 | 23515.4505
2017-09-18 | 18:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 18:32 | 1.7787 |  |  |  | 80.046 |  | 23487.7781
2017-09-18 | 18:34 | 1.7795 |  |  |  | 79.9902 |  | 23471.3978
2017-09-18 | 18:36 | 1.7553 |  |  |  | 79.9802 |  | 23468.4876
2017-09-18 | 18:38 | 1.8076 |  |  |  | 79.8618 |  | 23433.723
2017-09-18 | 18:40 | 1.8068 |  |  |  | 79.7068 |  | 23388.253
2017-09-18 | 18:42 | 1.8092 |  |  |  | 79.5072 |  | 23329.6803
2017-09-18 | 18:44 | 1.7366 |  |  |  | 79.5906 |  | 23354.149
2017-09-18 | 18:45 | 1.7148 | 0 | 0 |  | 79.6251 | 0 | 23364.2679
2017-09-18 | 18:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 18:46 | 1.7327 |  |  |  | 79.6517 |  | 23372.0787
2017-09-18 | 18:48 | 1.7709 |  |  |  | 79.6666 |  | 23376.442
2017-09-18 | 18:50 | 1.7663 |  |  |  | 79.6126 |  | 23360.6053
2017-09-18 | 18:52 | 1.7787 |  |  |  | 79.5014 |  | 23327.9946
2017-09-18 | 18:54 | 1.7553 |  |  |  | 79.4961 |  | 23326.4341
2017-09-18 | 18:56 | 1.7382 |  |  |  | 79.5081 |  | 23329.9356
2017-09-18 | 18:58 | 1.746 |  |  |  | 79.5398 |  | 23339.2572
2017-09-18 | 19:00 | 1.7218 | 0 | 0 | 1.5 | 79.6238 | 0 | 23363.9076
2017-09-18 | 19:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 19:02 | 1.7249 |  |  |  | 79.699 |  | 23385.9719
2017-09-18 | 19:04 | 1.7015 |  |  |  | 79.8444 |  | 23428.63
2017-09-18 | 19:06 | 1.6836 |  |  |  | 80.0445 |  | 23487.3486
2017-09-18 | 19:08 | 1.6867 |  |  |  | 80.2215 |  | 23539.2702
2017-09-18 | 19:10 | 1.7015 |  |  |  | 80.3593 |  | 23579.7143
2017-09-18 | 19:12 | 1.7046 |  |  |  | 80.5195 |  | 23626.711
2017-09-18 | 19:14 | 1.7148 |  |  |  | 80.6798 |  | 23673.7455
2017-09-18 | 19:15 | 1.7015 | 0 | 0 |  | 80.7783 | 0 | 23702.6471
2017-09-18 | 19:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 19:16 | 1.6844 |  |  |  | 80.8704 |  | 23729.6836
2017-09-18 | 19:18 | 1.6992 |  |  |  | 81.0023 |  | 23768.3994
2017-09-18 | 19:20 | 1.7171 |  |  |  | 81.1374 |  | 23808.0352
2017-09-18 | 19:22 | 1.675 |  |  |  | 81.3618 |  | 23873.8882
2017-09-18 | 19:24 | 1.7093 |  |  |  | 81.5237 |  | 23921.3819
2017-09-18 | 19:26 | 1.6789 |  |  |  | 81.6937 |  | 23971.2642
2017-09-18 | 19:28 | 1.6851 |  |  |  | 81.8687 |  | 24022.6083
2017-09-18 | 19:30 | 1.6773 | 0 | 0 | 1.5 | 82.0586 | 0 | 24078.3313
2017-09-18 | 19:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 19:32 | 1.6727 |  |  |  | 82.2632 |  | 24138.375
2017-09-18 | 19:34 | 1.6711 |  |  |  | 82.4706 |  | 24199.2292
2017-09-18 | 19:36 | 1.6875 |  |  |  | 82.6688 |  | 24257.3835
2017-09-18 | 19:38 | 1.661 |  |  |  | 82.8954 |  | 24323.8791
2017-09-18 | 19:40 | 1.6867 |  |  |  | 83.0753 |  | 24376.6716
2017-09-18 | 19:42 | 1.6898 |  |  |  | 83.2683 |  | 24433.308
2017-09-18 | 19:44 | 1.6906 |  |  |  | 83.4645 |  | 24490.8713
2017-09-18 | 19:45 | 1.6828 | 0 | 0 |  | 83.5777 | 0 | 24524.071
2017-09-18 | 19:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 19:46 | 1.6844 |  |  |  | 83.6795 |  | 24553.9529
2017-09-18 | 19:48 | 1.6688 |  |  |  | 83.9011 |  | 24618.989
2017-09-18 | 19:50 | 1.6914 |  |  |  | 84.089 |  | 24674.1166
2017-09-18 | 19:52 | 1.6859 |  |  |  | 84.2782 |  | 24729.6424
2017-09-18 | 19:54 | 1.6789 |  |  |  | 84.4803 |  | 24788.934
2017-09-18 | 19:56 | 1.6898 |  |  |  | 84.6973 |  | 24852.6022
2017-09-18 | 19:58 | 1.6844 |  |  |  | 84.8734 |  | 24904.2664
2017-09-18 | 20:00 | 1.6867 | 0 | 0 | 1.5 | 85.0543 | 0 | 24957.3591
2017-09-18 | 20:00 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 20:02 | 1.675 |  |  |  | 85.2765 |  | 25022.5742
2017-09-18 | 20:04 | 1.6695 |  |  |  | 85.4475 |  | 25072.7496
2017-09-18 | 20:06 | 1.6695 |  |  |  | 85.6496 |  | 25132.0524
2017-09-18 | 20:08 | 1.6929 |  |  |  | 85.8193 |  | 25181.8317
2017-09-18 | 20:10 | 1.6906 |  |  |  | 85.9572 |  | 25222.2958
2017-09-18 | 20:12 | 1.7046 |  |  |  | 86.1084 |  | 25266.6578
2017-09-18 | 20:14 | 1.7023 |  |  |  | 86.2175 |  | 25298.6864
2017-09-18 | 20:15 | 1.7078 | 0 | 0 |  | 86.2546 | 0 | 25309.5664
2017-09-18 | 20:15 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 20:16 | 1.714 |  |  |  | 86.3176 |  | 25328.0512
2017-09-18 | 20:18 | 1.7187 |  |  |  | 86.4229 |  | 25358.9361
2017-09-18 | 20:20 | 1.7234 |  |  |  | 86.4795 |  | 25375.5561
2017-09-18 | 20:22 | 1.7319 |  |  |  | 86.5538 |  | 25397.352
2017-09-18 | 20:24 | 1.7405 |  |  |  | 86.6047 |  | 25412.284
2017-09-18 | 20:26 | 1.7468 |  |  |  | 86.6544 |  | 25426.8824
2017-09-18 | 20:28 | 1.7421 |  |  |  | 86.6929 |  | 25438.1676
2017-09-18 | 20:30 | 1.7374 | 0 | 0 | 1.5 | 86.7306 | 0 | 25449.2378
2017-09-18 | 20:30 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 20:32 | 1.7546 |  |  |  | 86.7468 |  | 25453.9793
2017-09-18 | 20:34 | 1.7312 |  |  |  | 86.8286 |  | 25477.9938
2017-09-18 | 20:36 | 1.7413 |  |  |  | 86.8241 |  | 25476.6751
2017-09-18 | 20:38 | 1.7374 |  |  |  | 86.8524 |  | 25484.9783
2017-09-18 | 20:40 | 1.7397 |  |  |  | 86.8862 |  | 25494.8824
2017-09-18 | 20:42 | 1.7483 |  |  |  | 86.8892 |  | 25495.7844
2017-09-18 | 20:44 | 1.7397 |  |  |  | 86.9133 |  | 25502.832
2017-09-18 | 20:45 | 1.7468 | 0 | 0 |  | 86.9015 | 0 | 25499.3821
2017-09-18 | 20:45 |  |  |  | 1.5 |  |  | 0
2017-09-18 | 20:46 | 1.7444 |  |  |  | 86.9167 |  | 25503.8549
2017-09-18 | 20:48 | 1.7436 |  |  |  | 86.9469 |  | 25512.7111
2017-09-18 | 20:50 | 1.7249 |  |  |  | 86.9927 |  | 25526.1343
2017-09-18 | 20:52 | 1.7444 |  |  |  | 87.0035 |  | 25529.3177
2017-09-18 | 20:54 | 1.7569 |  |  |  | 87.0341 |  | 25538.306
2017-09-18 | 20:56 | 1.7639 |  |  |  | 86.9942 |  | 25526.5753
2017-09-18 | 20:58 | 1.7429 |  |  |  | 87.0322 |  | 25537.7353
2017-09-18 | 21:00 | 1.7491 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 21:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 21:02 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 21:04 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:06 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:08 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:10 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:12 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:14 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 21:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 21:16 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:18 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:20 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:22 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:24 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:26 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:28 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 21:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 21:32 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:34 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:36 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:38 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:40 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:42 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:44 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 21:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 21:46 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:48 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:50 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:52 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:54 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:56 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 21:58 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 22:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 22:02 | 0.03076 |  |  |  | 0 |  | 0
2017-09-18 | 22:04 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:06 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 22:08 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:10 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:12 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:14 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 22:15 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 22:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 22:16 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:18 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 22:20 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 22:22 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:24 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:26 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:28 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 22:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 22:32 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:34 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:36 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:38 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:40 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:42 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:44 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:45 | 0.03154 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 22:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 22:46 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 22:48 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:50 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:52 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:54 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:56 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 22:58 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:00 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 23:00 |  |  |  | 0 |  |  | 0
2017-09-18 | 23:02 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:04 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:06 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:08 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:10 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:12 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:14 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:15 | 0.03232 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 23:15 |  |  |  | 0 |  |  | 0
2017-09-18 | 23:16 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:18 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:20 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:22 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:24 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:26 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:28 | 0.03154 |  |  |  | 0 |  | 0
2017-09-18 | 23:30 | 0.03154 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 23:30 |  |  |  | 0 |  |  | 0
2017-09-18 | 23:32 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:34 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:36 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:38 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:40 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:42 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:44 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:45 | 0.03232 | 0 | 0 |  | 0 | 0 | 0
2017-09-18 | 23:45 |  |  |  | 0 |  |  | 0
2017-09-18 | 23:46 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:48 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:50 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:52 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:54 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:56 | 0.03232 |  |  |  | 0 |  | 0
2017-09-18 | 23:58 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:00 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 0:00 |  |  |  | 0 |  |  | 0
2017-09-19 | 0:02 | 0.03154 |  |  |  | 0 |  | 0
2017-09-19 | 0:04 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:06 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:08 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:10 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:12 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 0:14 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:15 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 0:16 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:18 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:20 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:22 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:24 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:26 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 0:28 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:30 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 0:32 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:34 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 0:36 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 0:38 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 0:40 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 0:42 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 0:44 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 0:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 0:46 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 0:48 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 0:50 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 0:52 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 0:54 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 0:56 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 0:58 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 1:00 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 1:02 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 1:04 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 1:06 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 1:08 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:10 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:12 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:14 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:15 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 1:16 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:18 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:20 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:22 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:24 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:26 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:28 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:30 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 1:32 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:34 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:36 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:38 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:40 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:42 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:44 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:45 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 1:46 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:48 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:50 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:52 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:54 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:56 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 1:58 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 2:02 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:04 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:06 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:08 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:10 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:12 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:14 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:15 | 0.03622 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 2:16 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:18 | 0.03622 |  |  |  | 0 |  | 0
2017-09-19 | 2:20 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 2:22 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:24 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:26 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:28 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:30 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 2:32 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:34 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:36 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:38 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:40 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:42 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:44 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:45 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 2:46 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 2:48 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 2:50 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 2:52 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 2:54 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 2:56 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 2:58 | 0.03544 |  |  |  | 0 |  | 0
2017-09-19 | 3:00 | 0.03544 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 3:02 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:04 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:06 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:08 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:10 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:12 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:14 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:15 | 0.03466 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 3:16 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:18 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:20 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:22 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:24 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:26 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:28 | 0.03466 |  |  |  | 0 |  | 0
2017-09-19 | 3:30 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 3:32 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:34 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:36 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:38 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:40 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:42 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:44 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:45 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 3:46 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:48 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:50 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:52 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:54 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:56 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 3:58 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 4:00 | 0.03388 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 4:02 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 4:04 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 4:06 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:08 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 4:10 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 4:12 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:14 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:15 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 4:16 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:18 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:20 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:22 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:24 | 0.03388 |  |  |  | 0 |  | 0
2017-09-19 | 4:26 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:28 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 4:30 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 4:32 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:34 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:36 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:38 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:40 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:42 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:44 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 4:45 | 0.03232 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 4:46 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 4:48 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:50 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:52 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:54 | 0.0331 |  |  |  | 0 |  | 0
2017-09-19 | 4:56 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 4:58 | 0.03232 |  |  |  | 0 |  | 0
2017-09-19 | 5:00 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 5:02 | 0.6883 |  |  |  | 70 |  | 20540
2017-09-19 | 5:04 | 2.0291 |  |  |  | 98.9106 |  | 29023.2002
2017-09-19 | 5:06 | 2.5634 |  |  |  | 96.3441 |  | 28270.1096
2017-09-19 | 5:08 | 2.5743 |  |  |  | 93.6934 |  | 27492.3264
2017-09-19 | 5:10 | 2.4261 |  |  |  | 91.6057 |  | 26879.7335
2017-09-19 | 5:12 | 2.3138 |  |  |  | 89.951 |  | 26394.199
2017-09-19 | 5:14 | 2.2296 |  |  |  | 88.5456 |  | 25981.8092
2017-09-19 | 5:15 | 2.189 | 0 | 0 | 1.5 | 87.8756 | 0 | 25785.2103
2017-09-19 | 5:16 | 2.1563 |  |  |  | 87.3385 |  | 25627.6025
2017-09-19 | 5:18 | 2.0939 |  |  |  | 86.3728 |  | 25344.2526
2017-09-19 | 5:20 | 2.0104 |  |  |  | 85.5845 |  | 25112.9229
2017-09-19 | 5:22 | 1.962 |  |  |  | 84.9201 |  | 24917.976
2017-09-19 | 5:24 | 1.9449 |  |  |  | 84.3755 |  | 24758.188
2017-09-19 | 5:26 | 1.9184 |  |  |  | 83.8652 |  | 24608.4538
2017-09-19 | 5:28 | 1.863 |  |  |  | 83.478 |  | 24494.8159
2017-09-19 | 5:30 | 1.8708 | 0 | 0 | 1.5 | 83.2082 | 0 | 24415.6718
2017-09-19 | 5:32 | 1.8224 |  |  |  | 82.9217 |  | 24331.6004
2017-09-19 | 5:34 | 1.8224 |  |  |  | 82.6885 |  | 24263.1549
2017-09-19 | 5:36 | 1.8076 |  |  |  | 82.4959 |  | 24206.6415
2017-09-19 | 5:38 | 1.8021 |  |  |  | 82.3913 |  | 24175.9738
2017-09-19 | 5:40 | 1.7889 |  |  |  | 82.255 |  | 24135.9798
2017-09-19 | 5:42 | 1.7819 |  |  |  | 82.1687 |  | 24110.6425
2017-09-19 | 5:44 | 1.7803 |  |  |  | 82.0763 |  | 24083.5408
2017-09-19 | 5:45 | 1.7717 | 0 | 0 | 1.5 | 82.0544 | 0 | 24077.1068
2017-09-19 | 5:46 | 1.7733 |  |  |  | 82.031 |  | 24070.2497
2017-09-19 | 5:48 | 1.7694 |  |  |  | 81.9937 |  | 24059.2981
2017-09-19 | 5:50 | 1.7639 |  |  |  | 81.9437 |  | 24044.6258
2017-09-19 | 5:52 | 1.7421 |  |  |  | 81.9107 |  | 24034.9435
2017-09-19 | 5:54 | 1.7585 |  |  |  | 81.8914 |  | 24029.2841
2017-09-19 | 5:56 | 1.753 |  |  |  | 81.8632 |  | 24021.0121
2017-09-19 | 5:58 | 1.76 |  |  |  | 81.8951 |  | 24030.3631
2017-09-19 | 6:00 | 1.7624 | 0 | 0 | 1.5 | 81.8606 | 0 | 24020.2398
2017-09-19 | 6:02 | 1.746 |  |  |  | 81.8667 |  | 24022.0353
2017-09-19 | 6:04 | 1.7514 |  |  |  | 81.884 |  | 24027.0993
2017-09-19 | 6:06 | 1.7546 |  |  |  | 81.8848 |  | 24027.3455
2017-09-19 | 6:08 | 1.7397 |  |  |  | 81.9092 |  | 24034.5116
2017-09-19 | 6:10 | 1.7241 |  |  |  | 81.9349 |  | 24042.0536
2017-09-19 | 6:12 | 1.7171 |  |  |  | 81.9511 |  | 24046.7907
2017-09-19 | 6:14 | 1.7382 |  |  |  | 81.9663 |  | 24051.259
2017-09-19 | 6:15 | 1.7452 | 0 | 0 | 1.5 | 81.9601 | 0 | 24049.4412
2017-09-19 | 6:16 | 1.7436 |  |  |  | 81.9721 |  | 24052.9583
2017-09-19 | 6:18 | 1.7436 |  |  |  | 81.96 |  | 24049.4145
2017-09-19 | 6:20 | 1.746 |  |  |  | 81.9701 |  | 24052.3649
2017-09-19 | 6:22 | 1.7366 |  |  |  | 81.9748 |  | 24053.762
2017-09-19 | 6:24 | 1.7491 |  |  |  | 81.9873 |  | 24057.4266
2017-09-19 | 6:26 | 1.7304 |  |  |  | 82 |  | 24061.1294
2017-09-19 | 6:28 | 1.7288 |  |  |  | 82.0283 |  | 24069.4395
2017-09-19 | 6:30 | 1.7397 | 0 | 0 | 1.5 | 82.0747 | 0 | 24083.0664
2017-09-19 | 6:32 | 1.7553 |  |  |  | 82.0761 |  | 24083.4848
2017-09-19 | 6:34 | 1.739 |  |  |  | 82.1166 |  | 24095.3499
2017-09-19 | 6:36 | 1.7366 |  |  |  | 82.1519 |  | 24105.7015
2017-09-19 | 6:38 | 1.7374 |  |  |  | 82.1808 |  | 24114.195
2017-09-19 | 6:40 | 1.7327 |  |  |  | 82.267 |  | 24139.4856
2017-09-19 | 6:42 | 1.7405 |  |  |  | 82.2822 |  | 24143.9361
2017-09-19 | 6:44 | 1.7304 |  |  |  | 82.3239 |  | 24156.1838
2017-09-19 | 6:45 | 1.7374 | 0 | 0 | 1.5 | 82.3353 | 0 | 24159.5286
2017-09-19 | 6:46 | 1.7413 |  |  |  | 82.3632 |  | 24167.7152
2017-09-19 | 6:48 | 1.7483 |  |  |  | 82.3825 |  | 24173.3793
2017-09-19 | 6:50 | 1.7358 |  |  |  | 82.4051 |  | 24180.0034
2017-09-19 | 6:52 | 1.7585 |  |  |  | 82.4518 |  | 24193.7265
2017-09-19 | 6:54 | 1.7241 |  |  |  | 82.4884 |  | 24204.4566
2017-09-19 | 6:56 | 1.7507 |  |  |  | 82.4759 |  | 24200.7717
2017-09-19 | 6:58 | 1.7452 |  |  |  | 82.5249 |  | 24215.1597
2017-09-19 | 7:00 | 1.7397 | 0 | 0 | 1.5 | 82.5651 | 0 | 24226.9643
2017-09-19 | 7:02 | 1.7374 |  |  |  | 82.6286 |  | 24245.5991
2017-09-19 | 7:04 | 1.76 |  |  |  | 82.6416 |  | 24249.4072
2017-09-19 | 7:06 | 1.7452 |  |  |  | 82.6872 |  | 24262.799
2017-09-19 | 7:08 | 1.7468 |  |  |  | 82.6802 |  | 24260.7347
2017-09-19 | 7:10 | 1.7351 |  |  |  | 82.7314 |  | 24275.7474
2017-09-19 | 7:12 | 1.7374 |  |  |  | 82.7501 |  | 24281.2345
2017-09-19 | 7:14 | 1.7491 |  |  |  | 82.7597 |  | 24284.0597
2017-09-19 | 7:15 | 1.7475 | 0 | 0 | 1.5 | 82.7594 | 0 | 24283.9769
2017-09-19 | 7:16 | 1.7475 |  |  |  | 82.78 |  | 24290.028
2017-09-19 | 7:18 | 1.7397 |  |  |  | 82.82 |  | 24301.7675
2017-09-19 | 7:20 | 1.7507 |  |  |  | 82.842 |  | 24308.1971
2017-09-19 | 7:22 | 1.7312 |  |  |  | 82.889 |  | 24322.0032
2017-09-19 | 7:24 | 1.7421 |  |  |  | 82.9172 |  | 24330.2729
2017-09-19 | 7:26 | 1.7475 |  |  |  | 82.9405 |  | 24337.1209
2017-09-19 | 7:28 | 1.7241 |  |  |  | 83.001 |  | 24354.8713
2017-09-19 | 7:30 | 1.7226 | 0 | 0 | 1.5 | 83.0611 | 0 | 24372.4943
2017-09-19 | 7:32 | 1.7429 |  |  |  | 83.0986 |  | 24383.5108
2017-09-19 | 7:34 | 1.7249 |  |  |  | 83.1269 |  | 24391.8187
2017-09-19 | 7:36 | 1.7436 |  |  |  | 83.2389 |  | 24424.6803
2017-09-19 | 7:38 | 1.7148 |  |  |  | 83.331 |  | 24451.7101
2017-09-19 | 7:40 | 1.7046 |  |  |  | 83.4381 |  | 24483.1234
2017-09-19 | 7:42 | 1.7054 |  |  |  | 83.5748 |  | 24523.2403
2017-09-19 | 7:44 | 1.7124 |  |  |  | 83.6811 |  | 24554.4118
2017-09-19 | 7:45 | 1.7085 | 0 | 0 | 1.5 | 83.7074 | 0 | 24562.1355
2017-09-19 | 7:46 | 1.7 |  |  |  | 83.8034 |  | 24590.2979
2017-09-19 | 7:48 | 1.7023 |  |  |  | 83.9736 |  | 24640.2564
2017-09-19 | 7:50 | 1.6945 |  |  |  | 84.0913 |  | 24674.7947
2017-09-19 | 7:52 | 1.7023 |  |  |  | 84.2499 |  | 24721.3237
2017-09-19 | 7:54 | 1.6961 |  |  |  | 84.4262 |  | 24773.0596
2017-09-19 | 7:56 | 1.6914 |  |  |  | 84.5969 |  | 24823.159
2017-09-19 | 7:58 | 1.7015 |  |  |  | 84.7198 |  | 24859.2108
2017-09-19 | 8:00 | 1.6953 | 0 | 0 | 1.5 | 84.9088 | 0 | 24914.6808
2017-09-19 | 8:02 | 1.7031 |  |  |  | 85.0164 |  | 24946.2373
2017-09-19 | 8:04 | 1.6859 |  |  |  | 85.2232 |  | 25006.9236
2017-09-19 | 8:06 | 1.7039 |  |  |  | 85.3351 |  | 25039.765
2017-09-19 | 8:08 | 1.6867 |  |  |  | 85.5084 |  | 25090.6165
2017-09-19 | 8:10 | 1.6953 |  |  |  | 85.718 |  | 25152.12
2017-09-19 | 8:12 | 1.6695 |  |  |  | 85.8264 |  | 25183.9047
2017-09-19 | 8:14 | 1.6992 |  |  |  | 86.0329 |  | 25244.5239
2017-09-19 | 8:15 | 1.7007 | 0 | 0 | 1.5 | 86.0884 | 0 | 25260.7968
2017-09-19 | 8:16 | 1.6719 |  |  |  | 86.1976 |  | 25292.8413
2017-09-19 | 8:18 | 1.689 |  |  |  | 86.3269 |  | 25330.769
2017-09-19 | 8:20 | 1.6773 |  |  |  | 86.4972 |  | 25380.7498
2017-09-19 | 8:22 | 1.6937 |  |  |  | 86.6622 |  | 25429.1746
2017-09-19 | 8:24 | 1.6929 |  |  |  | 86.7866 |  | 25465.6563
2017-09-19 | 8:26 | 1.7366 |  |  |  | 86.8264 |  | 25477.3468
2017-09-19 | 8:28 | 1.7366 |  |  |  | 86.9096 |  | 25501.7507
2017-09-19 | 8:30 | 1.7351 | 0 | 0 | 1.5 | 86.9849 | 0 | 25523.842
2017-09-19 | 8:32 | 1.7296 |  |  |  | 87.0551 |  | 25544.4445
2017-09-19 | 8:34 | 1.7101 |  |  |  | 87.1798 |  | 25581.0357
2017-09-19 | 8:36 | 1.7195 |  |  |  | 87.2964 |  | 25615.2518
2017-09-19 | 8:38 | 1.6922 |  |  |  | 87.4701 |  | 25666.2312
2017-09-19 | 8:40 | 1.6953 |  |  |  | 87.6716 |  | 25725.3456
2017-09-19 | 8:42 | 1.6812 |  |  |  | 87.8529 |  | 25778.5615
2017-09-19 | 8:44 | 1.6945 |  |  |  | 88.0512 |  | 25836.7516
2017-09-19 | 8:45 | 1.6945 | 0 | 0 | 1.5 | 88.1283 | 0 | 25859.3735
2017-09-19 | 8:46 | 1.6922 |  |  |  | 88.2234 |  | 25887.2786
2017-09-19 | 8:48 | 1.6758 |  |  |  | 88.4385 |  | 25950.3915
2017-09-19 | 8:50 | 1.6539 |  |  |  | 88.6739 |  | 26019.4684
2017-09-19 | 8:52 | 1.6789 |  |  |  | 88.8718 |  | 26077.5329
2017-09-19 | 8:54 | 1.6797 |  |  |  | 89.0794 |  | 26138.432
2017-09-19 | 8:56 | 1.6773 |  |  |  | 89.3243 |  | 26210.3158
2017-09-19 | 8:58 | 1.6649 |  |  |  | 89.538 |  | 26273.0036
2017-09-19 | 9:00 | 1.6454 | 0 | 0 | 1.5 | 89.8781 | 0 | 26372.7996
2017-09-19 | 9:02 | 1.6461 |  |  |  | 90.2231 |  | 26474.0418
2017-09-19 | 9:04 | 1.6298 |  |  |  | 90.5456 |  | 26568.6552
2017-09-19 | 9:06 | 1.668 |  |  |  | 90.8581 |  | 26660.3516
2017-09-19 | 9:08 | 1.6727 |  |  |  | 91.1189 |  | 26736.8898
2017-09-19 | 9:10 | 1.6758 |  |  |  | 91.3388 |  | 26801.4019
2017-09-19 | 9:12 | 1.6578 |  |  |  | 91.5964 |  | 26876.9867
2017-09-19 | 9:14 | 1.6727 |  |  |  | 91.8285 |  | 26945.1029
2017-09-19 | 9:15 | 1.6844 | 0 | 0 | 1.5 | 91.9336 | 0 | 26975.9385
2017-09-19 | 9:16 | 1.6828 |  |  |  | 92.0295 |  | 27004.0856
2017-09-19 | 9:18 | 1.6641 |  |  |  | 92.2887 |  | 27080.1382
2017-09-19 | 9:20 | 1.6695 |  |  |  | 92.5341 |  | 27152.1497
2017-09-19 | 9:22 | 1.6703 |  |  |  | 92.749 |  | 27215.2113
2017-09-19 | 9:24 | 1.6844 |  |  |  | 92.9332 |  | 27269.2552
2017-09-19 | 9:26 | 1.6844 |  |  |  | 93.0954 |  | 27316.852
2017-09-19 | 9:28 | 1.7046 |  |  |  | 93.2869 |  | 27373.0295
2017-09-19 | 9:30 | 1.6929 | 0 | 0 | 1.5 | 93.4928 | 0 | 27433.4602
2017-09-19 | 9:32 | 1.6929 |  |  |  | 93.6642 |  | 27483.7591
2017-09-19 | 9:34 | 1.7101 |  |  |  | 93.8369 |  | 27534.4316
2017-09-19 | 9:36 | 1.7054 |  |  |  | 93.9729 |  | 27574.3452
2017-09-19 | 9:38 | 1.6867 |  |  |  | 94.137 |  | 27622.479
2017-09-19 | 9:40 | 1.7109 |  |  |  | 94.2812 |  | 27664.8125
2017-09-19 | 9:42 | 1.6914 |  |  |  | 94.4451 |  | 27712.8905
2017-09-19 | 9:44 | 1.7148 |  |  |  | 94.5248 |  | 27736.2759
2017-09-19 | 9:45 | 1.7187 | 0 | 0 | 1.5 | 94.6055 | 0 | 27759.9632
2017-09-19 | 9:46 | 1.7296 |  |  |  | 94.6387 |  | 27769.7106
2017-09-19 | 9:48 | 1.7273 |  |  |  | 94.7324 |  | 27797.2037
2017-09-19 | 9:50 | 1.707 |  |  |  | 94.8429 |  | 27829.6219
2017-09-19 | 9:52 | 1.7273 |  |  |  | 94.9503 |  | 27861.118
2017-09-19 | 9:54 | 1.7444 |  |  |  | 95.032 |  | 27885.0923
2017-09-19 | 9:56 | 1.7163 |  |  |  | 95.1218 |  | 27911.446
2017-09-19 | 9:58 | 1.7678 |  |  |  | 95.1159 |  | 27909.7086
2017-09-19 | 10:00 | 1.7889 | 0 | 0 | 1.5 | 95.0212 | 0 | 27881.9379
2017-09-19 | 10:02 | 1.7982 |  |  |  | 94.9398 |  | 27858.0376
2017-09-19 | 10:04 | 1.8053 |  |  |  | 94.8021 |  | 27817.6474
2017-09-19 | 10:06 | 1.8606 |  |  |  | 94.4484 |  | 27713.8711
2017-09-19 | 10:08 | 1.8333 |  |  |  | 94.2558 |  | 27657.3553
2017-09-19 | 10:10 | 1.8443 |  |  |  | 93.9539 |  | 27568.746
2017-09-19 | 10:12 | 1.8372 |  |  |  | 93.7035 |  | 27495.2973
2017-09-19 | 10:14 | 1.8404 |  |  |  | 93.4066 |  | 27408.179
2017-09-19 | 10:15 | 1.8372 | 0 | 0 | 1.5 | 93.2727 | 0 | 27368.8631
2017-09-19 | 10:16 | 1.8458 |  |  |  | 93.1014 |  | 27318.6002
2017-09-19 | 10:18 | 1.8209 |  |  |  | 92.8757 |  | 27252.3869
2017-09-19 | 10:20 | 1.831 |  |  |  | 92.656 |  | 27187.9195
2017-09-19 | 10:22 | 1.8372 |  |  |  | 92.4086 |  | 27115.3235
2017-09-19 | 10:24 | 1.8419 |  |  |  | 92.1395 |  | 27036.3762
2017-09-19 | 10:26 | 1.8411 |  |  |  | 91.8691 |  | 26957.0285
2017-09-19 | 10:28 | 1.8482 |  |  |  | 91.6251 |  | 26885.4199
2017-09-19 | 10:30 | 1.8786 | 0 | 0 | 1.5 | 91.2216 | 0 | 26767.0337
2017-09-19 | 10:32 | 1.934 |  |  |  | 90.7203 |  | 26619.9298
2017-09-19 | 10:34 | 1.8926 |  |  |  | 90.2338 |  | 26477.1648
2017-09-19 | 10:36 | 1.8864 |  |  |  | 89.816 |  | 26354.5677
2017-09-19 | 10:38 | 1.8544 |  |  |  | 89.4833 |  | 26256.9613
2017-09-19 | 10:40 | 1.8271 |  |  |  | 89.2734 |  | 26195.375
2017-09-19 | 10:42 | 1.8014 |  |  |  | 89.1181 |  | 26149.7888
2017-09-19 | 10:44 | 1.8084 |  |  |  | 88.908 |  | 26088.1489
2017-09-19 | 10:45 | 1.8443 | 0 | 0 | 1.5 | 88.7947 | 0 | 26054.8908
2017-09-19 | 10:46 | 1.8521 |  |  |  | 88.6501 |  | 26012.4701
2017-09-19 | 10:48 | 1.8583 |  |  |  | 88.3124 |  | 25913.3928
2017-09-19 | 10:50 | 1.8466 |  |  |  | 88.0075 |  | 25823.915
2017-09-19 | 10:52 | 1.8053 |  |  |  | 87.7885 |  | 25759.6536
2017-09-19 | 10:54 | 1.8006 |  |  |  | 87.6774 |  | 25727.0651
2017-09-19 | 10:56 | 1.7694 |  |  |  | 87.6383 |  | 25715.5762
2017-09-19 | 10:58 | 1.7592 |  |  |  | 87.5953 |  | 25702.9723
2017-09-19 | 11:00 | 1.806 | 0 | 0 | 1.5 | 87.4796 | 0 | 25669.0003
2017-09-19 | 11:02 | 1.831 |  |  |  | 87.2168 |  | 25591.8911
2017-09-19 | 11:04 | 1.8123 |  |  |  | 87.0279 |  | 25536.4747
2017-09-19 | 11:06 | 1.8115 |  |  |  | 86.8399 |  | 25481.3002
2017-09-19 | 11:08 | 1.7912 |  |  |  | 86.719 |  | 25445.8464
2017-09-19 | 11:10 | 1.785 |  |  |  | 86.6937 |  | 25438.3959
2017-09-19 | 11:12 | 1.7889 |  |  |  | 86.6057 |  | 25412.5994
2017-09-19 | 11:14 | 1.8115 |  |  |  | 86.4684 |  | 25372.3079
2017-09-19 | 11:15 | 1.8357 | 0 | 0 | 1.5 | 86.2886 | 0 | 25319.5532
2017-09-19 | 11:16 | 1.8365 |  |  |  | 86.1403 |  | 25276.0152
2017-09-19 | 11:18 | 1.7975 |  |  |  | 85.9684 |  | 25225.5889
2017-09-19 | 11:20 | 1.7561 |  |  |  | 85.8671 |  | 25195.8458
2017-09-19 | 11:22 | 1.7039 |  |  |  | 85.986 |  | 25230.7559
2017-09-19 | 11:24 | 1.7202 |  |  |  | 86.0597 |  | 25252.3883
2017-09-19 | 11:26 | 1.7163 |  |  |  | 86.1254 |  | 25271.6475
2017-09-19 | 11:28 | 1.7343 |  |  |  | 86.1967 |  | 25292.5704
2017-09-19 | 11:30 | 1.7538 | 0 | 0 | 1.5 | 86.1879 | 0 | 25290.0003
2017-09-19 | 11:32 | 1.7717 |  |  |  | 86.1121 |  | 25267.7455
2017-09-19 | 11:34 | 1.8115 |  |  |  | 85.9457 |  | 25218.9222
2017-09-19 | 11:36 | 1.8162 |  |  |  | 85.7166 |  | 25151.7056
2017-09-19 | 11:38 | 1.8193 |  |  |  | 85.5336 |  | 25098.0132
2017-09-19 | 11:40 | 1.7873 |  |  |  | 85.3721 |  | 25050.6001
2017-09-19 | 11:42 | 1.7982 |  |  |  | 85.262 |  | 25018.296
2017-09-19 | 11:44 | 1.7444 |  |  |  | 85.2262 |  | 25007.7942
2017-09-19 | 11:45 | 1.7647 | 0 | 0 | 1.5 | 85.1934 | 0 | 24998.1815
2017-09-19 | 11:46 | 1.7569 |  |  |  | 85.2181 |  | 25005.4124
2017-09-19 | 11:48 | 1.7663 |  |  |  | 85.2281 |  | 25008.3608
2017-09-19 | 11:50 | 1.7616 |  |  |  | 85.1667 |  | 24990.3505
2017-09-19 | 11:52 | 1.7187 |  |  |  | 85.2078 |  | 25002.4104
2017-09-19 | 11:54 | 1.7631 |  |  |  | 85.1541 |  | 24986.65
2017-09-19 | 11:56 | 1.7748 |  |  |  | 85.066 |  | 24960.791
2017-09-19 | 11:58 | 1.8162 |  |  |  | 84.8357 |  | 24893.223
2017-09-19 | 12:00 | 1.7943 | 0 | 0 | 1.5 | 84.6345 | 0 | 24834.171
2017-09-19 | 12:02 | 1.7624 |  |  |  | 84.5626 |  | 24813.0961
2017-09-19 | 12:04 | 1.7226 |  |  |  | 84.6437 |  | 24836.8867
2017-09-19 | 12:06 | 1.6851 |  |  |  | 84.7934 |  | 24880.8206
2017-09-19 | 12:08 | 1.689 |  |  |  | 85.0238 |  | 24948.4221
2017-09-19 | 12:10 | 1.7078 |  |  |  | 85.1486 |  | 24985.0382
2017-09-19 | 12:12 | 1.7265 |  |  |  | 85.2332 |  | 25009.8652
2017-09-19 | 12:14 | 1.7156 |  |  |  | 85.3275 |  | 25037.5261
2017-09-19 | 12:15 | 1.7405 | 0 | 0 | 1.5 | 85.2874 | 0 | 25025.7529
2017-09-19 | 12:16 | 1.7569 |  |  |  | 85.2997 |  | 25029.3662
2017-09-19 | 12:18 | 1.7928 |  |  |  | 85.2219 |  | 25006.5495
2017-09-19 | 12:20 | 1.7943 |  |  |  | 85.079 |  | 24964.6012
2017-09-19 | 12:22 | 1.7811 |  |  |  | 84.9093 |  | 24914.8287
2017-09-19 | 12:24 | 1.7842 |  |  |  | 84.8191 |  | 24888.3538
2017-09-19 | 12:26 | 1.7647 |  |  |  | 84.8058 |  | 24884.4565
2017-09-19 | 12:28 | 1.7631 |  |  |  | 84.6888 |  | 24850.0992
2017-09-19 | 12:30 | 1.7982 | 0 | 0 | 1.5 | 84.6059 | 0 | 24825.7804
2017-09-19 | 12:32 | 1.8185 |  |  |  | 84.3643 |  | 24754.8993
2017-09-19 | 12:34 | 1.7951 |  |  |  | 84.2223 |  | 24713.233
2017-09-19 | 12:36 | 1.7912 |  |  |  | 84.1133 |  | 24681.2534
2017-09-19 | 12:38 | 1.778 |  |  |  | 84.1235 |  | 24684.2352
2017-09-19 | 12:40 | 1.728 |  |  |  | 84.2066 |  | 24708.6347
2017-09-19 | 12:42 | 1.7156 |  |  |  | 84.2152 |  | 24711.1332
2017-09-19 | 12:44 | 1.767 |  |  |  | 84.1542 |  | 24693.2482
2017-09-19 | 12:45 | 1.7709 | 0 | 0 | 1.5 | 84.1601 | 0 | 24694.9653
2017-09-19 | 12:46 | 1.7663 |  |  |  | 84.1791 |  | 24700.5531
2017-09-19 | 12:48 | 1.799 |  |  |  | 84.011 |  | 24651.2148
2017-09-19 | 12:50 | 1.7553 |  |  |  | 83.9141 |  | 24622.808
2017-09-19 | 12:52 | 1.7483 |  |  |  | 83.85 |  | 24603.9986
2017-09-19 | 12:54 | 1.7054 |  |  |  | 83.9809 |  | 24642.3987
2017-09-19 | 12:56 | 1.714 |  |  |  | 84.1369 |  | 24688.1619
2017-09-19 | 12:58 | 1.7093 |  |  |  | 84.2941 |  | 24734.2991
2017-09-19 | 13:00 | 1.707 | 0 | 0 | 1.5 | 84.4057 | 0 | 24767.0575
2017-09-19 | 13:02 | 1.7023 |  |  |  | 84.5061 |  | 24796.4939
2017-09-19 | 13:04 | 1.7195 |  |  |  | 84.59 |  | 24821.1264
2017-09-19 | 13:06 | 1.7538 |  |  |  | 84.6217 |  | 24830.4169
2017-09-19 | 13:08 | 1.7819 |  |  |  | 84.5323 |  | 24804.1838
2017-09-19 | 13:10 | 1.8209 |  |  |  | 84.3135 |  | 24739.9852
2017-09-19 | 13:12 | 1.8076 |  |  |  | 84.1349 |  | 24687.5911
2017-09-19 | 13:14 | 1.7351 |  |  |  | 84.1735 |  | 24698.9055
2017-09-19 | 13:15 | 1.7078 | 0 | 0 | 1.5 | 84.2625 | 0 | 24725.0218
2017-09-19 | 13:16 | 1.7912 |  |  |  | 84.12 |  | 24683.2167
2017-09-19 | 13:18 | 1.6602 |  |  |  | 84.4016 |  | 24765.8553
2017-09-19 | 13:20 | 1.6586 |  |  |  | 84.7186 |  | 24858.866
2017-09-19 | 13:22 | 1.6617 |  |  |  | 84.9764 |  | 24934.5133
2017-09-19 | 13:24 | 1.6937 |  |  |  | 85.1492 |  | 24985.2017
2017-09-19 | 13:26 | 1.6844 |  |  |  | 85.334 |  | 25039.4246
2017-09-19 | 13:28 | 1.8443 |  |  |  | 84.9495 |  | 24926.604
2017-09-19 | 13:30 | 1.7382 | 0 | 0 | 1.5 | 85.048 | 0 | 24955.5099
2017-09-19 | 13:32 | 1.767 |  |  |  | 84.798 |  | 24882.1639
2017-09-19 | 13:34 | 1.7483 |  |  |  | 84.8088 |  | 24885.325
2017-09-19 | 13:36 | 1.7296 |  |  |  | 84.8861 |  | 24908.0029
2017-09-19 | 13:38 | 1.7187 |  |  |  | 85.0178 |  | 24946.656
2017-09-19 | 13:40 | 1.6937 |  |  |  | 85.2 |  | 25000.1202
2017-09-19 | 13:42 | 1.8115 |  |  |  | 85.1739 |  | 24992.4637
2017-09-19 | 13:44 | 1.7522 |  |  |  | 85.1652 |  | 24989.9162
2017-09-19 | 13:45 | 1.7421 | 0 | 0 | 1.5 | 85.1562 | 0 | 24987.2612
2017-09-19 | 13:46 | 1.7616 |  |  |  | 85.1489 |  | 24985.1321
2017-09-19 | 13:48 | 1.7904 |  |  |  | 85.0106 |  | 24944.5492
2017-09-19 | 13:50 | 1.8177 |  |  |  | 84.8191 |  | 24888.3561
2017-09-19 | 13:52 | 1.8263 |  |  |  | 84.6497 |  | 24838.6306
2017-09-19 | 13:54 | 1.7842 |  |  |  | 84.5598 |  | 24812.2678
2017-09-19 | 13:56 | 1.7663 |  |  |  | 84.5228 |  | 24801.4147
2017-09-19 | 13:58 | 1.7639 |  |  |  | 84.46 |  | 24782.9724
2017-09-19 | 14:00 | 1.7351 | 0 | 0 | 1.5 | 84.5476 | 0 | 24808.6882
2017-09-19 | 14:02 | 1.6976 |  |  |  | 84.7131 |  | 24857.2542
2017-09-19 | 14:04 | 1.7312 |  |  |  | 84.7804 |  | 24876.979
2017-09-19 | 14:06 | 1.7187 |  |  |  | 84.8545 |  | 24898.7368
2017-09-19 | 14:08 | 1.7429 |  |  |  | 84.899 |  | 24911.7861
2017-09-19 | 14:10 | 1.7374 |  |  |  | 84.9147 |  | 24916.4135
2017-09-19 | 14:12 | 1.7663 |  |  |  | 84.865 |  | 24901.806
2017-09-19 | 14:14 | 1.8115 |  |  |  | 84.7367 |  | 24864.1559
2017-09-19 | 14:15 | 1.8193 | 0 | 0 | 1.5 | 84.6672 | 0 | 24843.775
2017-09-19 | 14:16 | 1.7772 |  |  |  | 84.6493 |  | 24838.5343
2017-09-19 | 14:18 | 1.7538 |  |  |  | 84.618 |  | 24829.3289
2017-09-19 | 14:20 | 1.7717 |  |  |  | 84.5742 |  | 24816.5011
2017-09-19 | 14:22 | 1.7405 |  |  |  | 84.5882 |  | 24820.5956
2017-09-19 | 14:24 | 1.7561 |  |  |  | 84.6037 |  | 24825.129
2017-09-19 | 14:26 | 1.7616 |  |  |  | 84.4987 |  | 24794.3472
2017-09-19 | 14:28 | 1.8138 |  |  |  | 84.3112 |  | 24739.3024
2017-09-19 | 14:30 | 1.7421 | 0 | 0 | 1.5 | 84.3701 | 0 | 24756.5985
2017-09-19 | 14:32 | 1.7226 |  |  |  | 84.4667 |  | 24784.9446
2017-09-19 | 14:34 | 1.7241 |  |  |  | 84.5057 |  | 24796.3977
2017-09-19 | 14:36 | 1.7421 |  |  |  | 84.4956 |  | 24793.427
2017-09-19 | 14:38 | 1.7522 |  |  |  | 84.5288 |  | 24803.1609
2017-09-19 | 14:40 | 1.7616 |  |  |  | 84.4938 |  | 24792.8988
2017-09-19 | 14:42 | 1.7764 |  |  |  | 84.3906 |  | 24762.6003
2017-09-19 | 14:44 | 1.7928 |  |  |  | 84.2287 |  | 24715.1112
2017-09-19 | 14:45 | 1.7998 | 0 | 0 | 1.5 | 84.1347 | 0 | 24687.5128
2017-09-19 | 14:46 | 1.8115 |  |  |  | 84.0308 |  | 24657.0443
2017-09-19 | 14:48 | 1.7624 |  |  |  | 83.9705 |  | 24639.3474
2017-09-19 | 14:50 | 1.7171 |  |  |  | 84.0716 |  | 24669.0077
2017-09-19 | 14:52 | 1.7015 |  |  |  | 84.2628 |  | 24725.1069
2017-09-19 | 14:54 | 1.6929 |  |  |  | 84.4296 |  | 24774.0713
2017-09-19 | 14:56 | 1.7148 |  |  |  | 84.5007 |  | 24794.9338
2017-09-19 | 14:58 | 1.7202 |  |  |  | 84.5573 |  | 24811.5201
2017-09-19 | 15:00 | 1.7 | 0 | 0 | 1.5 | 84.6556 | 0 | 24840.3788
2017-09-19 | 15:02 | 1.728 |  |  |  | 84.7504 |  | 24868.1879

## ASU-15 (M2) trends
|  | Duct Static Pressure | Exhaust Damper Position | Economizer Mode | Mixed Air Damper Position | Exhaust Fan Speed | Supply Fan Speed
Date | Time | A15DSP IN H2O | A15EAD VOLTS | A15ECM | A15MAD VOLTS | A15EVS % | A15SVS %
2017-06-21 | 15:05 | 1.7148 | 0
2017-06-21 | 15:10 | 1.7288 | 0 |  | 1.5
2017-06-21 | 15:15 | 1.7631 | 0.054218 | 0 | 1.5 | 25.2026 | 82.4829
2017-06-21 | 15:20 | 1.7491 | 0 |  | 1.5
2017-06-21 | 15:25 | 1.7366 | 0 |  | 1.5
2017-06-21 | 15:30 | 1.753 | 0 | 0 | 1.5 | 25 | 82.363
2017-06-21 | 15:35 | 1.7405 | 0 |  | 1.5
2017-06-21 | 15:40 | 1.7624 | 0 |  | 1.5
2017-06-21 | 15:45 | 1.746 | 0 | 0 | 1.5 | 25 | 82.331
2017-06-21 | 15:50 | 1.7358 | 0 |  | 1.5
2017-06-21 | 15:55 | 1.7819 | 0 |  | 1.5
2017-06-21 | 16:00 | 1.7382 | 0 | 0 | 1.5 | 25 | 82.2699
2017-06-21 | 16:05 | 1.7608 | 0 |  | 1.5
2017-06-21 | 16:10 | 1.7694 | 0 |  | 1.5
2017-06-21 | 16:15 | 1.7257 | 0 | 0 | 1.5 | 25 | 82.0949
2017-06-21 | 16:20 | 1.778 | 0 |  | 1.5
2017-06-21 | 16:25 | 1.7187 | 0 |  | 1.5
2017-06-21 | 16:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 81.903
2017-06-21 | 16:35 | 1.7577 | 0 |  | 1.5
2017-06-21 | 16:40 | 1.7444 | 0 |  | 1.5
2017-06-21 | 16:45 | 1.7358 | 0 | 0 | 1.5 | 25 | 81.6486
2017-06-21 | 16:50 | 1.7904 | 0 |  | 1.5
2017-06-21 | 16:55 | 1.7546 | 0 |  | 1.5
2017-06-21 | 17:00 | 1.7725 | 0 | 0 | 1.5 | 25 | 81.4438
2017-06-21 | 17:05 | 1.7709 | 0 |  | 1.5
2017-06-21 | 17:10 | 1.7694 | 0 |  | 1.5
2017-06-21 | 17:15 | 1.7756 | 0 | 0 | 1.5 | 25 | 80.9893
2017-06-21 | 17:20 | 1.7639 | 0 |  | 1.5
2017-06-21 | 17:25 | 1.7772 | 0 |  | 1.5
2017-06-21 | 17:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 80.5437
2017-06-21 | 17:35 | 1.7468 | 0 |  | 1.5
2017-06-21 | 17:40 | 1.739 | 0 |  | 1.5
2017-06-21 | 17:45 | 1.7795 | 0 | 0 | 1.5 | 25 | 80.1225
2017-06-21 | 17:50 | 1.7413 | 0 |  | 1.5
2017-06-21 | 17:55 | 1.7553 | 0 |  | 1.5
2017-06-21 | 18:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 80.0157
2017-06-21 | 18:05 | 1.7709 | 0 |  | 1.5
2017-06-21 | 18:10 | 1.6968 | 0 |  | 1.5
2017-06-21 | 18:15 | 1.7655 | 0 | 0 | 1.5 | 25 | 79.9987
2017-06-21 | 18:20 | 1.7608 | 0 |  | 1.5
2017-06-21 | 18:25 | 1.7546 | 0 |  | 1.5
2017-06-21 | 18:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 79.763
2017-06-21 | 18:35 | 1.7429 | 0 |  | 1.5
2017-06-21 | 18:40 | 1.7624 | 0 |  | 1.5
2017-06-21 | 18:45 | 1.753 | 0 | 0 | 1.5 | 25 | 79.5823
2017-06-21 | 18:50 | 1.7787 | 0 |  | 1.5
2017-06-21 | 18:55 | 1.7678 | 0 |  | 1.5
2017-06-21 | 19:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.4282
2017-06-21 | 19:05 | 1.7538 | 0 |  | 1.5
2017-06-21 | 19:10 | 1.7491 | 0 |  | 1.5
2017-06-21 | 19:15 | 1.7553 | 0.36005 | 0 | 1.5 | 27.0575 | 79.2697
2017-06-21 | 19:20 | 1.7444 | 0 |  | 1.5
2017-06-21 | 19:25 | 1.7475 | 0 |  | 1.5
2017-06-21 | 19:30 | 1.7249 | 0 | 0 | 1.5 | 25 | 79.2947
2017-06-21 | 19:35 | 1.7561 | 0 |  | 1.5
2017-06-21 | 19:40 | 1.7436 | 0 |  | 1.5
2017-06-21 | 19:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 79.3286
2017-06-21 | 19:50 | 1.7795 | 0 |  | 1.5
2017-06-21 | 19:55 | 1.7787 | 0 |  | 1.5
2017-06-21 | 20:00 | 1.7577 | 0 | 0 | 1.5 | 25 | 79.1529
2017-06-21 | 20:05 | 1.7897 | 0 |  | 1.5
2017-06-21 | 20:10 | 1.7546 | 0 |  | 1.5
2017-06-21 | 20:15 | 1.7592 | 0 | 0 | 1.5 | 25 | 78.8488
2017-06-21 | 20:20 | 1.7397 | 0 |  | 1.5
2017-06-21 | 20:25 | 1.7522 | 0 |  | 1.5
2017-06-21 | 20:30 | 1.721 | 0 | 0 | 1.5 | 25 | 78.5996
2017-06-21 | 20:35 | 1.7553 | 0 |  | 1.5
2017-06-21 | 20:40 | 1.7733 | 0 |  | 1.5
2017-06-21 | 20:45 | 1.7733 | 0 | 0 | 1.5 | 25 | 78.3487
2017-06-21 | 20:50 | 1.7702 | 0 |  | 1.5
2017-06-21 | 20:55 | 1.7413 | 0 |  | 1.5
2017-06-21 | 21:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 78.1359
2017-06-21 | 21:05 | -0.10418 | 0 |  | 1.5
2017-06-21 | 21:10 | -0.10574 | 0 |  | 1.5
2017-06-21 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 21:20 | -0.10574 | 0 |  | 1.5
2017-06-21 | 21:25 | -0.1073 | 0 |  | 1.5
2017-06-21 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 21:35 | -0.1073 | 0 |  | 1.5
2017-06-21 | 21:40 | -0.10808 | 0 |  | 1.5
2017-06-21 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 21:50 | -0.1073 | 0 |  | 1.5
2017-06-21 | 21:55 | -0.10808 | 0 |  | 1.5
2017-06-21 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 22:05 | -0.1073 | 0 |  | 1.5
2017-06-21 | 22:10 | -0.1073 | 0 |  | 1.5
2017-06-21 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 22:20 | -0.1112 | 0 |  | 1.5
2017-06-21 | 22:25 | -0.1073 | 0 |  | 1.5
2017-06-21 | 22:30 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 22:35 | -0.1073 | 0 |  | 1.5
2017-06-21 | 22:40 | -0.1073 | 0 |  | 1.5
2017-06-21 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 22:50 | -0.10808 | 0 |  | 1.5
2017-06-21 | 22:55 | -0.10808 | 0 |  | 1.5
2017-06-21 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 23:05 | -0.10808 | 0 |  | 1.5
2017-06-21 | 23:10 | -0.10808 | 0 |  | 1.5
2017-06-21 | 23:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 23:20 | -0.10808 | 0 |  | 1.5
2017-06-21 | 23:25 | -0.1073 | 0 |  | 1.5
2017-06-21 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 23:35 | -0.10808 | 0 |  | 1.5
2017-06-21 | 23:40 | -0.1073 | 0 |  | 1.5
2017-06-21 | 23:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-21 | 23:50 | -0.1073 | 0 |  | 1.5
2017-06-21 | 23:55 | -0.10808 | 0 |  | 1.5
2017-06-22 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 0:05 | -0.10808 | 0 |  | 1.5
2017-06-22 | 0:10 | -0.10652 | 0 |  | 1.5
2017-06-22 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 0:20 | -0.1073 | 0 |  | 1.5
2017-06-22 | 0:25 | -0.1073 | 0 |  | 1.5
2017-06-22 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 0:35 | -0.1073 | 0 |  | 1.5
2017-06-22 | 0:40 | -0.1073 | 0 |  | 1.5
2017-06-22 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 0:50 | -0.10808 | 0 |  | 1.5
2017-06-22 | 0:55 | -0.1073 | 0 |  | 1.5
2017-06-22 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 1:05 | -0.1073 | 0 |  | 1.5
2017-06-22 | 1:10 | -0.1073 | 0 |  | 1.5
2017-06-22 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 1:20 | -0.1073 | 0 |  | 1.5
2017-06-22 | 1:25 | -0.11042 | 0 |  | 1.5
2017-06-22 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 1:35 | -0.11042 | 0 |  | 1.5
2017-06-22 | 1:40 | -0.11042 | 0 |  | 1.5
2017-06-22 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 1:50 | -0.11042 | 0 |  | 1.5
2017-06-22 | 1:55 | -0.11042 | 0 |  | 1.5
2017-06-22 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 2:05 | -0.11042 | 0 |  | 1.5
2017-06-22 | 2:10 | -0.1112 | 0 |  | 1.5
2017-06-22 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 2:20 | -0.11042 | 0 |  | 1.5
2017-06-22 | 2:25 | -0.11042 | 0 |  | 1.5
2017-06-22 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 2:35 | -0.11042 | 0 |  | 1.5
2017-06-22 | 2:40 | -0.1112 | 0 |  | 1.5
2017-06-22 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 2:50 | -0.1112 | 0 |  | 1.5
2017-06-22 | 2:55 | -0.1112 | 0 |  | 1.5
2017-06-22 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 3:05 | -0.1112 | 0 |  | 1.5
2017-06-22 | 3:10 | -0.1112 | 0 |  | 1.5
2017-06-22 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 3:20 | -0.11042 | 0 |  | 1.5
2017-06-22 | 3:25 | -0.1112 | 0 |  | 1.5
2017-06-22 | 3:30 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 3:35 | -0.11198 | 0 |  | 1.5
2017-06-22 | 3:40 | -0.1112 | 0 |  | 1.5
2017-06-22 | 3:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 3:50 | -0.11198 | 0 |  | 1.5
2017-06-22 | 3:55 | -0.11198 | 0 |  | 1.5
2017-06-22 | 4:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 4:05 | -0.1112 | 0 |  | 1.5
2017-06-22 | 4:10 | -0.1112 | 0 |  | 1.5
2017-06-22 | 4:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 4:20 | -0.11198 | 0 |  | 1.5
2017-06-22 | 4:25 | -0.11198 | 0 |  | 1.5
2017-06-22 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 4:35 | -0.11198 | 0 |  | 1.5
2017-06-22 | 4:40 | -0.11198 | 0 |  | 1.5
2017-06-22 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 4:50 | -0.11198 | 0 |  | 1.5
2017-06-22 | 4:55 | -0.11198 | 0 |  | 1.5
2017-06-22 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 5:05 | 2.7405 | 5.7816 |  | 10
2017-06-22 | 5:10 | 2.2935 | 9.5207 |  | 7.9014
2017-06-22 | 5:15 | 2.0042 | 7.7389 | 1 | 6.9608 | 81.504 | 85.6331
2017-06-22 | 5:20 | 2.0291 | 7.059 |  | 8.0959
2017-06-22 | 5:25 | 1.9394 | 6.3092 |  | 7.6047
2017-06-22 | 5:30 | 1.8341 | 5.8536 | 1 | 6.9913 | 62.3443 | 80.4852
2017-06-22 | 5:35 | 1.8474 | 5.5337 |  | 7.3543
2017-06-22 | 5:40 | 1.8404 | 5.1835 |  | 7.909
2017-06-22 | 5:45 | 1.7951 | 5.2002 | 1 | 7.7103 | 55.9502 | 78.5771
2017-06-22 | 5:50 | 1.7702 | 4.8901 |  | 7.43
2017-06-22 | 5:55 | 1.7756 | 4.8619 |  | 6.9916
2017-06-22 | 6:00 | 1.817 | 4.728 | 1 | 7.5144 | 51.2587 | 77.5291
2017-06-22 | 6:05 | 1.792 | 5.1292 |  | 7.7323
2017-06-22 | 6:10 | 1.7717 | 5.506 |  | 7.5453
2017-06-22 | 6:15 | 1.806 | 5.723 | 1 | 9.7914 | 60.6159 | 76.7185
2017-06-22 | 6:20 | 1.7865 | 5.956 |  | 10
2017-06-22 | 6:25 | 1.7865 | 6.029 |  | 10
2017-06-22 | 6:30 | 1.7748 | 6.2434 | 1 | 10 | 65.6808 | 75.6974
2017-06-22 | 6:35 | 1.7296 | 6.2334 |  | 10
2017-06-22 | 6:40 | 1.7483 | 6.1156 |  | 10
2017-06-22 | 6:45 | 1.7452 | 5.5552 | 1 | 10 | 59.352 | 75.6094
2017-06-22 | 6:50 | 1.7881 | 5.2687 |  | 10
2017-06-22 | 6:55 | 1.753 | 5.2962 |  | 10
2017-06-22 | 7:00 | 1.7842 | 5.0124 | 1 | 10 | 54.219 | 75.1838
2017-06-22 | 7:05 | 1.7569 | 5.1025 |  | 10
2017-06-22 | 7:10 | 1.7304 | 5.5386 |  | 10
2017-06-22 | 7:15 | 1.7054 | 5.5766 | 1 | 10 | 59.5351 | 75.295
2017-06-22 | 7:20 | 1.7569 | 6.1306 |  | 10
2017-06-22 | 7:25 | 1.7499 | 6.4488 |  | 10
2017-06-22 | 7:30 | 1.7132 | 6.2173 | 1 | 10 | 66.4172 | 75.3713
2017-06-22 | 7:35 | 1.6828 | 6.1606 |  | 10
2017-06-22 | 7:40 | 1.7218 | 6.5344 |  | 10
2017-06-22 | 7:45 | 1.7522 | 6.8679 | 1 | 10 | 72.0646 | 76.132
2017-06-22 | 7:50 | 1.7702 | 6.491 |  | 10
2017-06-22 | 7:55 | 1.7343 | 6.0657 |  | 10
2017-06-22 | 8:00 | 1.7982 | 5.5528 | 1 | 10 | 60.0615 | 76.0293
2017-06-22 | 8:05 | 1.7951 | 5.2259 |  | 10
2017-06-22 | 8:10 | 1.7678 | 5.6848 |  | 10
2017-06-22 | 8:15 | 1.7343 | 5.9225 | 1 | 10 | 61.9841 | 75.6027
2017-06-22 | 8:20 | 1.7561 | 5.7806 |  | 10
2017-06-22 | 8:25 | 1.6805 | 5.9895 |  | 10
2017-06-22 | 8:30 | 1.6867 | 5.995 | 1 | 10 | 63.8998 | 76.5905
2017-06-22 | 8:35 | 1.7093 | 5.919 |  | 10
2017-06-22 | 8:40 | 1.6875 | 6.8149 |  | 10
2017-06-22 | 8:45 | 1.6851 | 7.1363 | 1 | 10 | 74.5608 | 78.1357
2017-06-22 | 8:50 | 1.7007 | 7.0188 |  | 10
2017-06-22 | 8:55 | 1.7897 | 7.2437 |  | 10
2017-06-22 | 9:00 | 1.8123 | 6.6448 | 1 | 10 | 70.4664 | 77.5421
2017-06-22 | 9:05 | 1.7904 | 6.8952 |  | 10
2017-06-22 | 9:10 | 1.8123 | 6.3243 |  | 10
2017-06-22 | 9:15 | 1.8092 | 6.1596 | 1 | 10 | 65.938 | 76.0722
2017-06-22 | 9:20 | 1.7756 | 5.7669 |  | 10
2017-06-22 | 9:25 | 1.7304 | 6.5345 |  | 10
2017-06-22 | 9:30 | 1.7062 | 6.7465 | 1 | 10 | 70.9219 | 76.3033
2017-06-22 | 9:35 | 1.7491 | 6.3636 |  | 10
2017-06-22 | 9:40 | 1.7343 | 6.4534 |  | 10
2017-06-22 | 9:45 | 1.6992 | 6.6924 | 1 | 10 | 70.4782 | 77.0077
2017-06-22 | 9:50 | 1.7366 | 6.2129 |  | 10
2017-06-22 | 9:55 | 1.6953 | 6.9351 |  | 10
2017-06-22 | 10:00 | 1.707 | 7.3113 | 1 | 10 | 75.5862 | 77.839
2017-06-22 | 10:05 | 1.7257 | 7.3545 |  | 10
2017-06-22 | 10:10 | 1.7093 | 7.8396 |  | 10
2017-06-22 | 10:15 | 1.7343 | 7.5321 | 1 | 10 | 78.9278 | 78.6218
2017-06-22 | 10:20 | 1.7819 | 5.9043 |  | 10
2017-06-22 | 10:25 | 1.7725 | 3.6039 |  | 10
2017-06-22 | 10:30 | 1.6126 | 2.3766 | 0 | 1.5 | 29.02 | 78.3579
2017-06-22 | 10:35 | 1.6337 | 0 |  | 1.5
2017-06-22 | 10:40 | 1.6469 | 0 |  | 1.5
2017-06-22 | 10:45 | 1.6851 | 0 | 0 | 1.5 | 25 | 80.7501
2017-06-22 | 10:50 | 1.6555 | 0 |  | 1.5
2017-06-22 | 10:55 | 1.7031 | 0 |  | 1.5
2017-06-22 | 11:00 | 1.7499 | 0 | 0 | 1.5 | 25 | 82.1179
2017-06-22 | 11:05 | 1.6929 | 0 |  | 1.5
2017-06-22 | 11:10 | 1.6532 | 0 |  | 1.5
2017-06-22 | 11:15 | 1.6875 | 0 | 0 | 1.5 | 25 | 83.6229
2017-06-22 | 11:20 | 1.7187 | 0 |  | 1.5
2017-06-22 | 11:25 | 1.7234 | 0 |  | 1.5
2017-06-22 | 11:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 84.0242
2017-06-22 | 11:35 | 1.7351 | 0 |  | 1.5
2017-06-22 | 11:40 | 1.6953 | 0 |  | 1.5
2017-06-22 | 11:45 | 1.6376 | 0 | 0 | 1.5 | 25 | 85.0235
2017-06-22 | 11:50 | 1.714 | 0 |  | 1.5
2017-06-22 | 11:55 | 1.6461 | 0 |  | 1.5
2017-06-22 | 12:00 | 1.7397 | 0 | 0 | 1.5 | 25 | 86.4217
2017-06-22 | 12:05 | 1.7397 | 0 |  | 1.5
2017-06-22 | 12:10 | 1.7647 | 0 |  | 1.5
2017-06-22 | 12:15 | 1.746 | 0 | 0 | 1.5 | 25 | 86.4789
2017-06-22 | 12:20 | 1.7452 | 0 |  | 1.5
2017-06-22 | 12:25 | 1.7507 | 0 |  | 1.5
2017-06-22 | 12:30 | 1.6875 | 0 | 0 | 1.5 | 25 | 86.9962
2017-06-22 | 12:35 | 1.7405 | 0 |  | 1.5
2017-06-22 | 12:40 | 1.7163 | 0 |  | 1.5
2017-06-22 | 12:45 | 1.7585 | 0 | 0 | 1.5 | 25 | 87.4325
2017-06-22 | 12:50 | 1.7546 | 0 |  | 1.5
2017-06-22 | 12:55 | 1.7655 | 0 |  | 1.5
2017-06-22 | 13:00 | 1.746 | 0 | 0 | 1.5 | 25 | 87.4897
2017-06-22 | 13:05 | 1.7343 | 0 |  | 1.5
2017-06-22 | 13:10 | 1.7429 | 0 |  | 1.5
2017-06-22 | 13:15 | 1.7436 | 0 | 0 | 1.5 | 25 | 87.657
2017-06-22 | 13:20 | 1.7577 | 0 |  | 1.5
2017-06-22 | 13:25 | 1.7803 | 0 |  | 1.5
2017-06-22 | 13:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 87.2736
2017-06-22 | 13:35 | 1.7483 | 0 |  | 1.5
2017-06-22 | 13:40 | 1.799 | 0 |  | 1.5
2017-06-22 | 13:45 | 1.7608 | 0 | 0 | 1.5 | 25 | 86.8247
2017-06-22 | 13:50 | 1.7249 | 0 |  | 1.5
2017-06-22 | 13:55 | 1.7249 | 0 |  | 1.5
2017-06-22 | 14:00 | 1.6929 | 0 | 0 | 1.5 | 25 | 87.7029
2017-06-22 | 14:05 | 1.6805 | 0 |  | 1.5
2017-06-22 | 14:10 | 1.7561 | 0 |  | 1.5
2017-06-22 | 14:15 | 1.7694 | 0 | 0 | 1.5 | 25 | 88.1235
2017-06-22 | 14:20 | 1.7709 | 0 |  | 1.5
2017-06-22 | 14:25 | 1.7499 | 0 |  | 1.5
2017-06-22 | 14:30 | 1.6883 | 0 | 0 | 1.5 | 25 | 88.0118
2017-06-22 | 14:35 | 1.7202 | 0 |  | 1.5
2017-06-22 | 14:40 | 1.6719 | 0 |  | 1.5
2017-06-22 | 14:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 89.099
2017-06-22 | 14:50 | 1.7265 | 0 |  | 1.5
2017-06-22 | 14:55 | 1.7686 | 0 |  | 1.5
2017-06-22 | 15:00 | 1.753 | 0 | 0 | 1.5 | 25 | 89.2968
2017-06-22 | 15:05 | 1.7787 | 0 |  | 1.5
2017-06-22 | 15:10 | 1.7374 | 0 |  | 1.5
2017-06-22 | 15:15 | 1.7218 | 0 | 0 | 1.5 | 25 | 89.4771
2017-06-22 | 15:20 | 1.7171 | 0 |  | 1.5
2017-06-22 | 15:25 | 1.7436 | 0 |  | 1.5
2017-06-22 | 15:30 | 1.7741 | 0 | 0 | 1.5 | 25 | 89.7851
2017-06-22 | 15:35 | 1.7928 | 0 |  | 1.5
2017-06-22 | 15:40 | 1.7475 | 0 |  | 1.5
2017-06-22 | 15:45 | 1.7741 | 0 | 0 | 1.5 | 25 | 89.1182
2017-06-22 | 15:50 | 1.7538 | 0 |  | 1.5
2017-06-22 | 15:55 | 1.7585 | 0 |  | 1.5
2017-06-22 | 16:00 | 1.7865 | 0 | 0 | 1.5 | 25 | 88.8567
2017-06-22 | 16:05 | 1.8146 | 0 |  | 1.5
2017-06-22 | 16:10 | 1.792 | 0 |  | 1.5
2017-06-22 | 16:15 | 1.7803 | 0 | 0 | 1.5 | 25 | 87.6527
2017-06-22 | 16:20 | 1.8029 | 0 |  | 1.5
2017-06-22 | 16:25 | 1.8099 | 0 |  | 1.5
2017-06-22 | 16:30 | 1.7912 | 0 | 0 | 1.5 | 25 | 86.5611
2017-06-22 | 16:35 | 1.7655 | 0 |  | 1.5
2017-06-22 | 16:40 | 1.7897 | 0 |  | 1.5
2017-06-22 | 16:45 | 1.778 | 0 | 0 | 1.5 | 25 | 85.7668
2017-06-22 | 16:50 | 1.7538 | 0 |  | 1.5
2017-06-22 | 16:55 | 1.7608 | 0 |  | 1.5
2017-06-22 | 17:00 | 1.7686 | 0 | 0 | 1.5 | 25 | 85.1121
2017-06-22 | 17:05 | 1.778 | 0 |  | 1.5
2017-06-22 | 17:10 | 1.7475 | 0 |  | 1.5
2017-06-22 | 17:15 | 1.7647 | 0 | 0 | 1.5 | 25 | 84.4495
2017-06-22 | 17:20 | 1.7834 | 0.023753 |  | 1.5
2017-06-22 | 17:25 | 1.7858 | 0 |  | 1.5
2017-06-22 | 17:30 | 1.7483 | 0 | 0 | 1.5 | 25 | 83.909
2017-06-22 | 17:35 | 1.7741 | 0 |  | 1.5
2017-06-22 | 17:40 | 1.7569 | 0 |  | 1.5
2017-06-22 | 17:45 | 1.7819 | 0 | 0 | 1.5 | 25 | 83.434
2017-06-22 | 17:50 | 1.7475 | 0 |  | 1.5
2017-06-22 | 17:55 | 1.7873 | 0 |  | 1.5
2017-06-22 | 18:00 | 1.7546 | 0 | 0 | 1.5 | 25 | 83.0416
2017-06-22 | 18:05 | 1.767 | 0 |  | 1.5
2017-06-22 | 18:10 | 1.7725 | 0 |  | 1.5
2017-06-22 | 18:15 | 1.785 | 0 | 0 | 1.5 | 25 | 82.5865
2017-06-22 | 18:20 | 1.7826 | 0 |  | 1.5
2017-06-22 | 18:25 | 1.767 | 0 |  | 1.5
2017-06-22 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 25 | 82.2232
2017-06-22 | 18:35 | 1.7468 | 0 |  | 1.5
2017-06-22 | 18:40 | 1.7561 | 0 |  | 1.5
2017-06-22 | 18:45 | 1.7655 | 0 | 0 | 1.5 | 25 | 81.7284
2017-06-22 | 18:50 | 1.7569 | 0 |  | 1.5
2017-06-22 | 18:55 | 1.7959 | 0 |  | 1.5
2017-06-22 | 19:00 | 1.7764 | 0 | 0 | 1.5 | 25 | 81.3818
2017-06-22 | 19:05 | 1.7522 | 0.067973 |  | 1.5
2017-06-22 | 19:10 | 1.7624 | 0.058185 |  | 1.5
2017-06-22 | 19:15 | 1.7561 | 0 | 0 | 1.5 | 25 | 81.0398
2017-06-22 | 19:20 | 1.7702 | 0 |  | 1.5
2017-06-22 | 19:25 | 1.7257 | 0 |  | 1.5
2017-06-22 | 19:30 | 1.7288 | 0 | 0 | 1.5 | 25 | 80.817
2017-06-22 | 19:35 | 1.7748 | 0 |  | 1.5
2017-06-22 | 19:40 | 1.739 | 0 |  | 1.5
2017-06-22 | 19:45 | 1.76 | 0 | 0 | 1.5 | 25 | 80.613
2017-06-22 | 19:50 | 1.7452 | 0 |  | 1.5
2017-06-22 | 19:55 | 1.7366 | 0 |  | 1.5
2017-06-22 | 20:00 | 1.7421 | 0 | 0 | 1.5 | 25 | 80.7193
2017-06-22 | 20:05 | 1.7163 | 0 |  | 1.5
2017-06-22 | 20:10 | 1.7397 | 0 |  | 1.5
2017-06-22 | 20:15 | 1.7319 | 0 | 0 | 1.5 | 25 | 81.2033
2017-06-22 | 20:20 | 1.6992 | 0 |  | 1.5
2017-06-22 | 20:25 | 1.7444 | 0 |  | 1.5
2017-06-22 | 20:30 | 1.767 | 0 | 0 | 1.5 | 25 | 81.4189
2017-06-22 | 20:35 | 1.7405 | 0 |  | 1.5
2017-06-22 | 20:40 | 1.7694 | 0 |  | 1.5
2017-06-22 | 20:45 | 1.7296 | 0 | 0 | 1.5 | 25 | 81.258
2017-06-22 | 20:50 | 1.7631 | 0 |  | 1.5
2017-06-22 | 20:55 | 1.7405 | 0 |  | 1.5
2017-06-22 | 21:00 | 1.7374 | 0 | 0 | 1.5 | 25 | 80.9103
2017-06-22 | 21:05 | -0.1073 | 0 |  | 1.5
2017-06-22 | 21:10 | -0.11042 | 0 |  | 1.5
2017-06-22 | 21:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 21:20 | -0.10808 | 0 |  | 1.5
2017-06-22 | 21:25 | -0.10886 | 0 |  | 1.5
2017-06-22 | 21:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 21:35 | -0.10886 | 0 |  | 1.5
2017-06-22 | 21:40 | -0.10808 | 0 |  | 1.5
2017-06-22 | 21:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 21:50 | -0.10886 | 0 |  | 1.5
2017-06-22 | 21:55 | -0.10886 | 0 |  | 1.5
2017-06-22 | 22:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 22:05 | -0.10886 | 0 |  | 1.5
2017-06-22 | 22:10 | -0.10964 | 0 |  | 1.5
2017-06-22 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 22:20 | -0.10964 | 0 |  | 1.5
2017-06-22 | 22:25 | -0.10964 | 0 |  | 1.5
2017-06-22 | 22:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 22:35 | -0.10886 | 0 |  | 1.5
2017-06-22 | 22:40 | -0.10886 | 0 |  | 1.5
2017-06-22 | 22:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 22:50 | -0.10964 | 0 |  | 1.5
2017-06-22 | 22:55 | -0.10886 | 0 |  | 1.5
2017-06-22 | 23:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 23:05 | -0.10886 | 0 |  | 1.5
2017-06-22 | 23:10 | -0.11354 | 0 |  | 1.5
2017-06-22 | 23:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 23:20 | -0.10886 | 0 |  | 1.5
2017-06-22 | 23:25 | -0.10808 | 0 |  | 1.5
2017-06-22 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 23:35 | -0.10886 | 0 |  | 1.5
2017-06-22 | 23:40 | -0.10886 | 0 |  | 1.5
2017-06-22 | 23:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-22 | 23:50 | -0.10808 | 0 |  | 1.5
2017-06-22 | 23:55 | -0.10886 | 0 |  | 1.5
2017-06-23 | 0:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 0:05 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:10 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 0:20 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:25 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 0:35 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:40 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 0:50 | -0.10808 | 0 |  | 1.5
2017-06-23 | 0:55 | -0.10808 | 0 |  | 1.5
2017-06-23 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 1:05 | -0.1073 | 0 |  | 1.5
2017-06-23 | 1:10 | -0.1073 | 0 |  | 1.5
2017-06-23 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 1:20 | -0.1073 | 0 |  | 1.5
2017-06-23 | 1:25 | -0.11042 | 0 |  | 1.5
2017-06-23 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 1:35 | -0.11042 | 0 |  | 1.5
2017-06-23 | 1:40 | -0.10808 | 0 |  | 1.5
2017-06-23 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 1:50 | -0.11042 | 0 |  | 1.5
2017-06-23 | 1:55 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:00 | -0.1151 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 2:05 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:10 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 2:20 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:25 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 2:35 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:40 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 2:50 | -0.11042 | 0 |  | 1.5
2017-06-23 | 2:55 | -0.11042 | 0 |  | 1.5
2017-06-23 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 3:05 | -0.11042 | 0 |  | 1.5
2017-06-23 | 3:10 | -0.11042 | 0 |  | 1.5
2017-06-23 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 3:20 | -0.11042 | 0 |  | 1.5
2017-06-23 | 3:25 | -0.11042 | 0 |  | 1.5
2017-06-23 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 3:35 | -0.1112 | 0 |  | 1.5
2017-06-23 | 3:40 | -0.1112 | 0 |  | 1.5
2017-06-23 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 3:50 | -0.1112 | 0 |  | 1.5
2017-06-23 | 3:55 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 4:05 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:10 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 4:20 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:25 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 4:35 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:40 | -0.11042 | 0 |  | 1.5
2017-06-23 | 4:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 4:50 | -0.1112 | 0 |  | 1.5
2017-06-23 | 4:55 | -0.1112 | 0 |  | 1.5
2017-06-23 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 5:05 | 2.4729 | 6.0404 |  | 10
2017-06-23 | 5:10 | 2.1976 | 10 |  | 10
2017-06-23 | 5:15 | 2.0822 | 10 | 1 | 10 | 100 | 87.6088
2017-06-23 | 5:20 | 1.9987 | 9.5425 |  | 10
2017-06-23 | 5:25 | 1.923 | 9.038 |  | 10
2017-06-23 | 5:30 | 1.8739 | 8.4998 | 1 | 10 | 85.9586 | 82.1593
2017-06-23 | 5:35 | 1.8544 | 8.1097 |  | 10
2017-06-23 | 5:40 | 1.8466 | 7.6834 |  | 10
2017-06-23 | 5:45 | 1.8458 | 7.2665 | 1 | 10 | 73.7478 | 79.5205
2017-06-23 | 5:50 | 1.7982 | 7.3518 |  | 10
2017-06-23 | 5:55 | 1.7889 | 7.0643 |  | 10
2017-06-23 | 6:00 | 1.7756 | 7.0931 | 1 | 10 | 71.5179 | 78.5099
2017-06-23 | 6:05 | 1.7912 | 7.4189 |  | 10
2017-06-23 | 6:10 | 1.753 | 7.4426 |  | 10
2017-06-23 | 6:15 | 1.7312 | 7.6227 | 1 | 10 | 77.0649 | 78.2125
2017-06-23 | 6:20 | 1.7499 | 7.2067 |  | 10
2017-06-23 | 6:25 | 1.7772 | 7.35 |  | 10
2017-06-23 | 6:30 | 1.7241 | 7.0048 | 1 | 10 | 71.4328 | 77.9173
2017-06-23 | 6:35 | 1.7756 | 7.0241 |  | 10
2017-06-23 | 6:40 | 1.7748 | 6.8789 |  | 10
2017-06-23 | 6:45 | 1.7491 | 6.4078 | 1 | 10 | 65.9246 | 77.4274
2017-06-23 | 6:50 | 1.6477 | 3.0162 |  | 1.5
2017-06-23 | 6:55 | 1.707 | 0 |  | 1.5
2017-06-23 | 7:00 | 1.7553 | 0 | 1 | 10 | 25 | 79.2589
2017-06-23 | 7:05 | 1.9152 | 2.469 |  | 10
2017-06-23 | 7:10 | 1.8505 | 3.9229 |  | 10
2017-06-23 | 7:15 | 1.7943 | 4.385 | 1 | 10 | 65.8243 | 76.0749
2017-06-23 | 7:20 | 1.785 | 4.5941 |  | 10
2017-06-23 | 7:25 | 1.7561 | 4.6126 |  | 10
2017-06-23 | 7:30 | 1.767 | 4.7827 | 1 | 10 | 69.5993 | 75.5086
2017-06-23 | 7:35 | 1.7491 | 4.7324 |  | 10
2017-06-23 | 7:40 | 1.7522 | 4.937 |  | 10
2017-06-23 | 7:45 | 1.7499 | 5.2299 | 1 | 10 | 74.7341 | 75.6569
2017-06-23 | 7:50 | 1.7452 | 5.0286 |  | 10
2017-06-23 | 7:55 | 1.7499 | 4.7126 |  | 10
2017-06-23 | 8:00 | 1.7538 | 4.2833 | 1 | 10 | 65.2927 | 75.7312
2017-06-23 | 8:05 | 1.7499 | 4.4934 |  | 10
2017-06-23 | 8:10 | 1.7436 | 4.5777 |  | 10
2017-06-23 | 8:15 | 1.7319 | 4.8205 | 1 | 10 | 69.8012 | 75.8514
2017-06-23 | 8:20 | 1.7366 | 4.8162 |  | 10
2017-06-23 | 8:25 | 1.7561 | 5.4092 |  | 10
2017-06-23 | 8:30 | 1.7351 | 5.5636 | 1 | 10 | 77.7807 | 76.2815
2017-06-23 | 8:35 | 1.7202 | 5.2325 |  | 10
2017-06-23 | 8:40 | 1.7819 | 3.0817 |  | 10
2017-06-23 | 8:45 | 1.7865 | 1.4016 | 1 | 10 | 38.1358 | 76.0201
2017-06-23 | 8:50 | 1.6282 | 0 |  | 1.5
2017-06-23 | 8:55 | 1.6742 | 0 |  | 1.5
2017-06-23 | 9:00 | 1.6945 | 0 | 0 | 1.5 | 25 | 78.3992
2017-06-23 | 9:05 | 1.7234 | 0 |  | 1.5
2017-06-23 | 9:10 | 1.7288 | 0 |  | 1.5
2017-06-23 | 9:15 | 1.7241 | 0 | 0 | 1.5 | 25 | 79.325
2017-06-23 | 9:20 | 1.7296 | 0 |  | 1.5
2017-06-23 | 9:25 | 1.7452 | 0 |  | 1.5
2017-06-23 | 9:30 | 1.7109 | 0 | 0 | 1.5 | 25 | 79.7814
2017-06-23 | 9:35 | 1.7093 | 0 |  | 1.5
2017-06-23 | 9:40 | 1.7382 | 0 |  | 1.5
2017-06-23 | 9:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 80.3067
2017-06-23 | 9:50 | 1.728 | 0 |  | 1.5
2017-06-23 | 9:55 | 1.6914 | 0 |  | 1.5
2017-06-23 | 10:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 81.4754
2017-06-23 | 10:05 | 1.7491 | 0 |  | 1.5
2017-06-23 | 10:10 | 1.7366 | 0 |  | 1.5
2017-06-23 | 10:15 | 1.7374 | 0 | 0 | 1.5 | 25 | 81.5948
2017-06-23 | 10:20 | 1.7265 | 0 |  | 1.5
2017-06-23 | 10:25 | 1.7312 | 0 |  | 1.5
2017-06-23 | 10:30 | 1.7117 | 0 | 0 | 1.5 | 25 | 82.0953
2017-06-23 | 10:35 | 1.7374 | 0 |  | 1.5
2017-06-23 | 10:40 | 1.7312 | 0 |  | 1.5
2017-06-23 | 10:45 | 1.7093 | 0 | 0 | 1.5 | 25 | 82.9055
2017-06-23 | 10:50 | 1.7078 | 0 |  | 1.5
2017-06-23 | 10:55 | 1.739 | 0 |  | 1.5
2017-06-23 | 11:00 | 1.7062 | 0 | 0 | 1.5 | 25 | 83.4527
2017-06-23 | 11:05 | 1.682 | 0 |  | 1.5
2017-06-23 | 11:10 | 1.661 | 0 |  | 1.5
2017-06-23 | 11:15 | 1.7171 | 0 | 0 | 1.5 | 25 | 85.1867
2017-06-23 | 11:20 | 1.6797 | 0 |  | 1.5
2017-06-23 | 11:25 | 1.7179 | 0 |  | 1.5
2017-06-23 | 11:30 | 1.7288 | 0 | 0 | 1.5 | 25 | 85.8687
2017-06-23 | 11:35 | 1.7507 | 0 |  | 1.5
2017-06-23 | 11:40 | 1.7663 | 0 |  | 1.5
2017-06-23 | 11:45 | 1.8115 | 0 | 0 | 1.5 | 25 | 85.4126
2017-06-23 | 11:50 | 1.7319 | 0 |  | 1.5
2017-06-23 | 11:55 | 1.7132 | 0 |  | 1.5
2017-06-23 | 12:00 | 1.7241 | 0 | 0 | 1.5 | 25 | 85.7815
2017-06-23 | 12:05 | 1.7483 | 0 |  | 1.5
2017-06-23 | 12:10 | 1.7569 | 0 |  | 1.5
2017-06-23 | 12:15 | 1.7499 | 0 | 0 | 1.5 | 25 | 85.9952
2017-06-23 | 12:20 | 1.7241 | 0 |  | 1.5
2017-06-23 | 12:25 | 1.7429 | 0 |  | 1.5
2017-06-23 | 12:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 86.125
2017-06-23 | 12:35 | 1.7195 | 0 |  | 1.5
2017-06-23 | 12:40 | 1.7358 | 0 |  | 1.5
2017-06-23 | 12:45 | 1.7304 | 0 | 0 | 1.5 | 25 | 86.3706
2017-06-23 | 12:50 | 1.7499 | 0 |  | 1.5
2017-06-23 | 12:55 | 1.7343 | 0 |  | 1.5
2017-06-23 | 13:00 | 1.7546 | 0 | 0 | 1.5 | 25 | 86.5239
2017-06-23 | 13:05 | 1.7397 | 0 |  | 1.5
2017-06-23 | 13:10 | 1.7397 | 0 |  | 1.5
2017-06-23 | 13:15 | 1.7631 | 0 | 0 | 1.5 | 25 | 86.4482
2017-06-23 | 13:20 | 1.7179 | 0 |  | 1.5
2017-06-23 | 13:25 | 1.7663 | 0 |  | 1.5
2017-06-23 | 13:30 | 1.7234 | 0 | 0 | 1.5 | 25 | 86.9231
2017-06-23 | 13:35 | 1.7241 | 0 |  | 1.5
2017-06-23 | 13:40 | 1.7015 | 0 |  | 1.5
2017-06-23 | 13:45 | 1.7491 | 0 | 0 | 1.5 | 25 | 87.3292
2017-06-23 | 13:50 | 1.746 | 0 |  | 1.5
2017-06-23 | 13:55 | 1.7694 | 0 |  | 1.5
2017-06-23 | 14:00 | 1.714 | 0 | 0 | 1.5 | 25 | 87.552
2017-06-23 | 14:05 | 1.7397 | 0 |  | 1.5
2017-06-23 | 14:10 | 1.7054 | 0 |  | 1.5
2017-06-23 | 14:15 | 1.7241 | 0 | 0 | 1.5 | 25 | 87.9416
2017-06-23 | 14:20 | 1.7374 | 0 |  | 1.5
2017-06-23 | 14:25 | 1.7397 | 0 |  | 1.5
2017-06-23 | 14:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 88.3183
2017-06-23 | 14:35 | 1.6976 | 0 |  | 1.5
2017-06-23 | 14:40 | 1.7179 | 0 |  | 1.5
2017-06-23 | 14:45 | 1.7093 | 0 | 0 | 1.5 | 25 | 89.3008
2017-06-23 | 14:50 | 1.7312 | 0 |  | 1.5
2017-06-23 | 14:55 | 1.7265 | 0 |  | 1.5
2017-06-23 | 15:00 | 1.721 | 0 | 0 | 1.5 | 25 | 89.8873
2017-06-23 | 15:05 | 1.739 | 0 |  | 1.5
2017-06-23 | 15:10 | 1.7296 | 0 |  | 1.5
2017-06-23 | 15:15 | 1.7624 | 0 | 0 | 1.5 | 25 | 90.0153
2017-06-23 | 15:20 | 1.7202 | 0 |  | 1.5
2017-06-23 | 15:25 | 1.721 | 0.019677 |  | 1.5
2017-06-23 | 15:30 | 1.7787 | 0 | 0 | 1.5 | 25 | 90.5112
2017-06-23 | 15:35 | 1.7631 | 0 |  | 1.5
2017-06-23 | 15:40 | 1.7538 | 0 |  | 1.5
2017-06-23 | 15:45 | 1.7483 | 0 | 0 | 1.5 | 25 | 89.8351
2017-06-23 | 15:50 | 1.7616 | 0 |  | 1.5
2017-06-23 | 15:55 | 1.728 | 0 |  | 1.5
2017-06-23 | 16:00 | 1.739 | 0 | 0 | 1.5 | 25 | 89.8553
2017-06-23 | 16:05 | 1.7709 | 0 |  | 1.5
2017-06-23 | 16:10 | 1.7327 | 0 |  | 1.5
2017-06-23 | 16:15 | 1.76 | 0 | 0 | 1.5 | 25 | 89.8025
2017-06-23 | 16:20 | 1.7444 | 0 |  | 1.5
2017-06-23 | 16:25 | 1.7538 | 0 |  | 1.5
2017-06-23 | 16:30 | 1.7436 | 0 | 0 | 1.5 | 25 | 89.8125
2017-06-23 | 16:35 | 1.7546 | 0 |  | 1.5
2017-06-23 | 16:40 | 1.7358 | 0 |  | 1.5
2017-06-23 | 16:45 | 1.7382 | 0 | 0 | 1.5 | 25 | 89.9296
2017-06-23 | 16:50 | 1.7397 | 0 |  | 1.5
2017-06-23 | 16:55 | 1.7499 | 0 |  | 1.5
2017-06-23 | 17:00 | 1.767 | 0 | 0 | 1.5 | 25 | 89.6184
2017-06-23 | 17:05 | 1.7631 | 0 |  | 1.5
2017-06-23 | 17:10 | 1.7366 | 0 |  | 1.5
2017-06-23 | 17:15 | 1.7702 | 0 | 0 | 1.5 | 25 | 89.1522
2017-06-23 | 17:20 | 1.7514 | 0 |  | 1.5
2017-06-23 | 17:25 | 1.799 | 0 |  | 1.5
2017-06-23 | 17:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 88.4414
2017-06-23 | 17:35 | 1.7616 | 0 |  | 1.5
2017-06-23 | 17:40 | 1.7826 | 0 |  | 1.5
2017-06-23 | 17:45 | 1.7725 | 0 | 0 | 1.5 | 25 | 87.6503
2017-06-23 | 17:50 | 1.7709 | 0 |  | 1.5
2017-06-23 | 17:55 | 1.7702 | 0 |  | 1.5
2017-06-23 | 18:00 | 1.8045 | 0 | 0 | 1.5 | 25 | 86.8133
2017-06-23 | 18:05 | 1.792 | 0 |  | 1.5
2017-06-23 | 18:10 | 1.7858 | 0 |  | 1.5
2017-06-23 | 18:15 | 1.7858 | 0 | 0 | 1.5 | 25 | 86.0637
2017-06-23 | 18:20 | 1.8053 | 0 |  | 1.5
2017-06-23 | 18:25 | 1.7912 | 0 |  | 1.5
2017-06-23 | 18:30 | 1.8076 | 0 | 0 | 1.5 | 25 | 85.0808
2017-06-23 | 18:35 | 1.7858 | 0 |  | 1.5
2017-06-23 | 18:40 | 1.7577 | 0 |  | 1.5
2017-06-23 | 18:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 84.4441
2017-06-23 | 18:50 | 1.7717 | 0 |  | 1.5
2017-06-23 | 18:55 | 1.7655 | 0 |  | 1.5
2017-06-23 | 19:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 84.0781
2017-06-23 | 19:05 | 1.7639 | 0 |  | 1.5
2017-06-23 | 19:10 | 1.7444 | 0 |  | 1.5
2017-06-23 | 19:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 83.5998
2017-06-23 | 19:20 | 1.7421 | 0 |  | 1.5
2017-06-23 | 19:25 | 1.7366 | 0 |  | 1.5
2017-06-23 | 19:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 83.6761
2017-06-23 | 19:35 | 1.7397 | 0 |  | 1.5
2017-06-23 | 19:40 | 1.7218 | 0 |  | 1.5
2017-06-23 | 19:45 | 1.7725 | 0 | 0 | 1.5 | 25 | 83.747
2017-06-23 | 19:50 | 1.7577 | 0 |  | 1.5
2017-06-23 | 19:55 | 1.7694 | 0 |  | 1.5
2017-06-23 | 20:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 83.2421
2017-06-23 | 20:05 | 1.7631 | 0 |  | 1.5
2017-06-23 | 20:10 | 1.7444 | 0 |  | 1.5
2017-06-23 | 20:15 | 1.7756 | 0 | 0 | 1.5 | 25 | 82.9116
2017-06-23 | 20:20 | 1.7444 | 0 |  | 1.5
2017-06-23 | 20:25 | 1.7569 | 0 |  | 1.5
2017-06-23 | 20:30 | 1.7764 | 0 | 0 | 1.5 | 25 | 82.9417
2017-06-23 | 20:35 | 1.753 | 0 |  | 1.5
2017-06-23 | 20:40 | 1.7514 | 0 |  | 1.5
2017-06-23 | 20:45 | 1.7764 | 0 | 0 | 1.5 | 25 | 82.5468
2017-06-23 | 20:50 | 1.7959 | 0 |  | 1.5
2017-06-23 | 20:55 | 1.7686 | 0 |  | 1.5
2017-06-23 | 21:00 | 1.8146 | 0 | 0 | 1.5 | 25 | 81.767
2017-06-23 | 21:05 | -0.10652 | 0 |  | 1.5
2017-06-23 | 21:10 | -0.1073 | 0 |  | 1.5
2017-06-23 | 21:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 21:20 | -0.1073 | 0 |  | 1.5
2017-06-23 | 21:25 | -0.10808 | 0 |  | 1.5
2017-06-23 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 21:35 | -0.10886 | 0 |  | 1.5
2017-06-23 | 21:40 | -0.10886 | 0 |  | 1.5
2017-06-23 | 21:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 21:50 | -0.1112 | 0 |  | 1.5
2017-06-23 | 21:55 | -0.10964 | 0 |  | 1.5
2017-06-23 | 22:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 22:05 | -0.11042 | 0 |  | 1.5
2017-06-23 | 22:10 | -0.10964 | 0 |  | 1.5
2017-06-23 | 22:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 22:20 | -0.11042 | 0 |  | 1.5
2017-06-23 | 22:25 | -0.10964 | 0 |  | 1.5
2017-06-23 | 22:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 22:35 | -0.11042 | 0 |  | 1.5
2017-06-23 | 22:40 | -0.11042 | 0 |  | 1.5
2017-06-23 | 22:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 22:50 | -0.10964 | 0 |  | 1.5
2017-06-23 | 22:55 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 23:05 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:10 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 23:20 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:25 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 23:35 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:40 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-23 | 23:50 | -0.10964 | 0 |  | 1.5
2017-06-23 | 23:55 | -0.10886 | 0 |  | 1.5
2017-06-24 | 0:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-24 | 0:05 | -0.10886 | 0 |  | 1.5
2017-06-24 | 0:10 | -0.10886 | 0 |  | 1.5
2017-06-24 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-24 | 0:15 |  |  |  | 1.5 |  | 0
2017-06-24 | 0:20 | -0.10808 | 0 |  | 1.5
2017-06-24 | 0:25 | -0.10808 | 0 |  | 1.5
2017-06-24 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-24 | 0:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 0:35 | -0.10808 | 0 |  | 1.5
2017-06-24 | 0:40 | -0.10808 | 0 |  | 1.5
2017-06-24 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-24 | 0:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 0:50 | -0.10808 | 0 |  | 1.5
2017-06-24 | 0:55 | -0.10808 | 0 |  | 1.5
2017-06-24 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-24 | 1:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 1:05 | -0.10808 | 0 |  | 1.5
2017-06-24 | 1:10 | -0.10808 | 0 |  | 1.5
2017-06-24 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-24 | 1:15 | [5 empty] | 0
2017-06-24 | 1:20 | -0.10808 | 0 |  | 1.5
2017-06-24 | 1:25 | -0.11042 | 0 |  | 1.5
2017-06-24 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 1:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 1:35 | -0.1112 | 0 |  | 1.5
2017-06-24 | 1:40 | -0.1112 | 0 |  | 1.5
2017-06-24 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 1:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 1:50 | -0.1112 | 0 |  | 1.5
2017-06-24 | 1:55 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 2:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 2:05 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:10 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 2:15 |  |  |  | 1.5 |  | 0
2017-06-24 | 2:20 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:25 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 2:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 2:35 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:40 | -0.1112 | 0 |  | 1.5
2017-06-24 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 2:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 2:50 | -0.11198 | 0 |  | 1.5
2017-06-24 | 2:55 | -0.1112 | 0 |  | 1.5
2017-06-24 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 3:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 3:05 | -0.1112 | 0 |  | 1.5
2017-06-24 | 3:10 | -0.1112 | 0 |  | 1.5
2017-06-24 | 3:15 | -0.119 | 0 | 0 | 1.5 | 0
2017-06-24 | 3:15 |  |  |  | 1.5 |  | 0
2017-06-24 | 3:20 | -0.11354 | 0 |  | 1.5
2017-06-24 | 3:25 | -0.11354 | 0 |  | 1.5
2017-06-24 | 3:30 | -0.11354 | 0 | 0 | 1.5 | 0
2017-06-24 | 3:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 3:35 | -0.11354 | 0 |  | 1.5
2017-06-24 | 3:40 | -0.11432 | 0 |  | 1.5
2017-06-24 | 3:45 | -0.11354 | 0 | 0 | 1.5 | 0
2017-06-24 | 3:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 3:50 | -0.11354 | 0 |  | 1.5
2017-06-24 | 3:55 | -0.11354 | 0 |  | 1.5
2017-06-24 | 4:00 | -0.11354 | 0 | 0 | 1.5 | 0
2017-06-24 | 4:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 4:05 | -0.11354 | 0 |  | 1.5
2017-06-24 | 4:10 | -0.11276 | 0 |  | 1.5
2017-06-24 | 4:15 | -0.11354 | 0 | 0 | 1.5 | 0
2017-06-24 | 4:15 |  |  |  | 1.5 |  | 0
2017-06-24 | 4:20 | -0.11354 | 0 |  | 1.5
2017-06-24 | 4:25 | -0.11354 | 0 |  | 1.5
2017-06-24 | 4:30 | -0.11354 | 0 | 0 | 1.5 | 0
2017-06-24 | 4:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 4:35 | -0.11354 | 0 |  | 1.5
2017-06-24 | 4:40 | -0.11354 | 0 |  | 1.5
2017-06-24 | 4:45 | -0.11354 | 0 | 0 | 1.5 | 0
2017-06-24 | 4:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 4:50 | -0.11276 | 0 |  | 1.5
2017-06-24 | 4:55 | -0.11276 | 0 |  | 1.5
2017-06-24 | 5:00 | -0.11276 | 0 | 1 | 0 | 0
2017-06-24 | 5:00 |  |  |  | 0 |  | 25
2017-06-24 | 5:05 | 2.1594 | 6.2605 |  | 10
2017-06-24 | 5:10 | 1.9831 | 10 |  | 10
2017-06-24 | 5:15 | 1.9878 | 9.9964 | 1 | 10 | 100
2017-06-24 | 5:15 |  |  |  | 10 |  | 92.2803
2017-06-24 | 5:20 | 1.9613 | 10 |  | 10
2017-06-24 | 5:25 | 1.9402 | 10 |  | 10
2017-06-24 | 5:30 | 1.9262 | 9.8106 | 1 | 10 | 98.446
2017-06-24 | 5:30 |  |  |  | 10 |  | 86.9405
2017-06-24 | 5:35 | 1.9371 | 9.3227 |  | 10
2017-06-24 | 5:40 | 1.8965 | 8.7997 |  | 10
2017-06-24 | 5:45 | 1.8981 | 8.3121 | 1 | 10 | 83.943
2017-06-24 | 5:45 |  |  |  | 10 |  | 82.64
2017-06-24 | 5:50 | 1.8216 | 7.8698 |  | 10
2017-06-24 | 5:55 | 1.8302 | 7.4967 |  | 10
2017-06-24 | 6:00 | 1.8006 | 7.2729 | 1 | 10 | 73.6145
2017-06-24 | 6:00 |  |  |  | 10 |  | 80.3106
2017-06-24 | 6:05 | 1.7881 | 7.2702 |  | 10
2017-06-24 | 6:10 | 1.7709 | 7.5921 |  | 10
2017-06-24 | 6:15 | 1.7631 | 7.4809 | 1 | 10 | 75.6142
2017-06-24 | 6:15 |  |  |  | 10 |  | 79.441
2017-06-24 | 6:20 | 1.7982 | 7.5568 |  | 10
2017-06-24 | 6:25 | 1.7663 | 7.4658 |  | 10
2017-06-24 | 6:30 | 1.7936 | 7.3079 | 1 | 10 | 73.7378
2017-06-24 | 6:30 |  |  |  | 10 |  | 78.9964
2017-06-24 | 6:35 | 1.7624 | 7.3271 |  | 10
2017-06-24 | 6:40 | 1.6064 | 3.6196 |  | 1.5
2017-06-24 | 6:45 | 1.7241 | 0 | 0 | 1.5 | 25
2017-06-24 | 6:45 |  |  |  | 1.5 |  | 79.8204
2017-06-24 | 6:50 | 1.7304 | 0 |  | 1.5
2017-06-24 | 6:55 | 1.7382 | 0 |  | 1.5
2017-06-24 | 7:00 | 1.7483 | 0 | 0 | 1.5 | 25
2017-06-24 | 7:00 |  |  |  | 1.5 |  | 80.1553
2017-06-24 | 7:05 | 1.9714 | 0 |  | 10
2017-06-24 | 7:10 | 1.8957 | 0 |  | 10
2017-06-24 | 7:15 | 1.7007 | 0 | 0 | 1.5 | 25
2017-06-24 | 7:15 |  |  |  | 1.5 |  | 77.3974
2017-06-24 | 7:20 | 1.6711 | 0 |  | 1.5
2017-06-24 | 7:25 | 1.7249 | 0 |  | 1.5
2017-06-24 | 7:30 | 1.7179 | 0 | 0 | 1.5 | 25
2017-06-24 | 7:30 |  |  |  | 1.5 |  | 79.1577
2017-06-24 | 7:35 | 1.7296 | 0 |  | 1.5
2017-06-24 | 7:40 | 1.7413 | 0 |  | 1.5
2017-06-24 | 7:45 | 1.746 | 0 | 0 | 1.5 | 25
2017-06-24 | 7:45 |  |  |  | 1.5 |  | 79.8541
2017-06-24 | 7:50 | 1.7608 | 0 |  | 1.5
2017-06-24 | 7:55 | 1.7655 | 0 |  | 1.5
2017-06-24 | 8:00 | 1.7577 | 0 | 0 | 1.5 | 25
2017-06-24 | 8:00 |  |  |  | 1.5 |  | 79.8707
2017-06-24 | 8:05 | 1.7491 | 0 |  | 1.5
2017-06-24 | 8:10 | 1.7319 | 0 |  | 1.5
2017-06-24 | 8:15 | 1.746 | 0 | 0 | 1.5 | 25
2017-06-24 | 8:15 |  |  |  | 1.5 |  | 79.8126
2017-06-24 | 8:20 | 1.7429 | 0 |  | 1.5
2017-06-24 | 8:25 | 1.7569 | 0 |  | 1.5
2017-06-24 | 8:30 | 1.7514 | 0 | 0 | 1.5 | 25
2017-06-24 | 8:30 |  |  |  | 1.5 |  | 79.7571
2017-06-24 | 8:35 | 1.7249 | 0 |  | 1.5
2017-06-24 | 8:40 | 1.7475 | 0 |  | 1.5
2017-06-24 | 8:45 | 1.7483 | 0 | 0 | 1.5 | 25
2017-06-24 | 8:45 |  |  |  | 1.5 |  | 79.8073
2017-06-24 | 8:50 | 1.7374 | 0 |  | 1.5
2017-06-24 | 8:55 | 1.7319 | 0 |  | 1.5
2017-06-24 | 9:00 | 1.7304 | 0 | 0 | 1.5 | 25
2017-06-24 | 9:00 |  |  |  | 1.5 |  | 79.9109
2017-06-24 | 9:05 | 1.7514 | 0 |  | 1.5
2017-06-24 | 9:10 | 1.7452 | 0 |  | 1.5
2017-06-24 | 9:15 | 1.7265 | 0 | 0 | 1.5 | 25
2017-06-24 | 9:15 |  |  |  | 1.5 |  | 80.1647
2017-06-24 | 9:20 | 1.7452 | 0 |  | 1.5
2017-06-24 | 9:25 | 1.7343 | 0 |  | 1.5
2017-06-24 | 9:30 | 1.7577 | 0 | 0 | 1.5 | 25
2017-06-24 | 9:30 |  |  |  | 1.5 |  | 80.3622
2017-06-24 | 9:35 | 1.7382 | 0 |  | 1.5
2017-06-24 | 9:40 | 1.6992 | 0 |  | 1.5
2017-06-24 | 9:45 | 1.7468 | 0 | 0 | 1.5 | 25
2017-06-24 | 9:45 |  |  |  | 1.5 |  | 80.6876
2017-06-24 | 9:50 | 1.7585 | 0 |  | 1.5
2017-06-24 | 9:55 | 1.7265 | 0 |  | 1.5
2017-06-24 | 10:00 | 1.7702 | 0 | 0 | 1.5 | 25
2017-06-24 | 10:00 |  |  |  | 1.5 |  | 81.0337
2017-06-24 | 10:05 | 1.7686 | 0 |  | 1.5
2017-06-24 | 10:10 | 1.7538 | 0 |  | 1.5
2017-06-24 | 10:15 | 1.7538 | 0 | 0 | 1.5 | 25
2017-06-24 | 10:15 |  |  |  | 1.5 |  | 81.2484
2017-06-24 | 10:20 | 1.7413 | 0 |  | 1.5
2017-06-24 | 10:25 | 1.7273 | 0 |  | 1.5
2017-06-24 | 10:30 | 1.7405 | 0 | 0 | 1.5 | 25
2017-06-24 | 10:30 |  |  |  | 1.5 |  | 81.5405
2017-06-24 | 10:35 | 1.7241 | 0 |  | 1.5
2017-06-24 | 10:40 | 1.7592 | 0 |  | 1.5
2017-06-24 | 10:45 | 1.753 | 0 | 0 | 1.5 | 25
2017-06-24 | 10:45 |  |  |  | 1.5 |  | 81.8056
2017-06-24 | 10:50 | 1.7366 | 0 |  | 1.5
2017-06-24 | 10:55 | 1.7483 | 0 |  | 1.5
2017-06-24 | 11:00 | 1.739 | 0 | 0 | 1.5 | 25
2017-06-24 | 11:00 |  |  |  | 1.5 |  | 82.2225
2017-06-24 | 11:05 | 1.7023 | 0 |  | 1.5
2017-06-24 | 11:10 | 1.7507 | 0 |  | 1.5
2017-06-24 | 11:15 | 1.7148 | 0 | 0 | 1.5 | 25
2017-06-24 | 11:15 |  |  |  | 1.5 |  | 83.0727
2017-06-24 | 11:20 | 1.7015 | 0 |  | 1.5
2017-06-24 | 11:25 | 1.7382 | 0 |  | 1.5
2017-06-24 | 11:30 | 1.7468 | 0 | 0 | 1.5 | 25
2017-06-24 | 11:30 |  |  |  | 1.5 |  | 83.6756
2017-06-24 | 11:35 | 1.7382 | 0 |  | 1.5
2017-06-24 | 11:40 | 1.7343 | 0 |  | 1.5
2017-06-24 | 11:45 | 1.7351 | 0 | 0 | 1.5 | 25
2017-06-24 | 11:45 |  |  |  | 1.5 |  | 84.105
2017-06-24 | 11:50 | 1.7429 | 0 |  | 1.5
2017-06-24 | 11:55 | 1.7452 | 0 |  | 1.5
2017-06-24 | 12:00 | 1.7608 | 0 | 0 | 1.5 | 25
2017-06-24 | 12:00 |  |  |  | 1.5 |  | 84.4349
2017-06-24 | 12:05 | 1.7319 | 0 |  | 1.5
2017-06-24 | 12:10 | 1.7514 | 0 |  | 1.5
2017-06-24 | 12:15 | 1.7374 | 0 | 0 | 1.5 | 25
2017-06-24 | 12:15 |  |  |  | 1.5 |  | 84.6792
2017-06-24 | 12:20 | 1.7616 | 0 |  | 1.5
2017-06-24 | 12:25 | 1.7351 | 0 |  | 1.5
2017-06-24 | 12:30 | 1.7335 | 0 | 0 | 1.5 | 25
2017-06-24 | 12:30 |  |  |  | 1.5 |  | 84.877
2017-06-24 | 12:35 | 1.7647 | 0 |  | 1.5
2017-06-24 | 12:40 | 1.7397 | 0 |  | 1.5
2017-06-24 | 12:45 | 1.7514 | 0 | 0 | 1.5 | 25
2017-06-24 | 12:45 |  |  |  | 1.5 |  | 85.1003
2017-06-24 | 12:50 | 1.7374 | 0 |  | 1.5
2017-06-24 | 12:55 | 1.7468 | 0 |  | 1.5
2017-06-24 | 13:00 | 1.7296 | 0 | 0 | 1.5 | 25
2017-06-24 | 13:00 |  |  |  | 1.5 |  | 85.2705
2017-06-24 | 13:05 | 1.7327 | 0 |  | 1.5
2017-06-24 | 13:10 | 1.7468 | 0 |  | 1.5
2017-06-24 | 13:15 | 1.7374 | 0 | 0 | 1.5 | 25
2017-06-24 | 13:15 |  |  |  | 1.5 |  | 85.3789
2017-06-24 | 13:20 | 1.7351 | 0 |  | 1.5
2017-06-24 | 13:25 | 1.7624 | 0 |  | 1.5
2017-06-24 | 13:30 | 1.7522 | 0 | 0 | 1.5 | 25
2017-06-24 | 13:30 |  |  |  | 1.5 |  | 85.4596
2017-06-24 | 13:35 | 1.7616 | 0 |  | 1.5
2017-06-24 | 13:40 | 1.7444 | 0 |  | 1.5
2017-06-24 | 13:45 | 1.7553 | 0 | 0 | 1.5 | 25
2017-06-24 | 13:45 | [5 empty] | 85.6673
2017-06-24 | 13:50 | 1.7569 | 0 |  | 1.5
2017-06-24 | 13:55 | 1.7475 | 0 |  | 1.5
2017-06-24 | 14:00 | 1.7288 | 0 | 0 | 1.5 | 25
2017-06-24 | 14:00 |  |  |  | 1.5 |  | 85.899
2017-06-24 | 14:05 | 1.7468 | 0 |  | 1.5
2017-06-24 | 14:10 | 1.7382 | 0 |  | 1.5
2017-06-24 | 14:15 | 1.7296 | 0 | 0 | 1.5 | 25
2017-06-24 | 14:15 |  |  |  | 1.5 |  | 86.159
2017-06-24 | 14:20 | 1.7413 | 0 |  | 1.5
2017-06-24 | 14:25 | 1.7273 | 0 |  | 1.5
2017-06-24 | 14:30 | 1.7195 | 0 | 0 | 1.5 | 25
2017-06-24 | 14:30 |  |  |  | 1.5 |  | 86.5732
2017-06-24 | 14:35 | 1.7078 | 0 |  | 1.5
2017-06-24 | 14:40 | 1.7538 | 0 |  | 1.5
2017-06-24 | 14:45 | 1.7577 | 0 | 0 | 1.5 | 25
2017-06-24 | 14:45 | [5 empty] | 86.8771
2017-06-24 | 14:50 | 1.7171 | 0 |  | 1.5
2017-06-24 | 14:55 | 1.7335 | 0 |  | 1.5
2017-06-24 | 15:00 | 1.7234 | 0 | 0 | 1.5 | 25
2017-06-24 | 15:00 |  |  |  | 1.5 |  | 87.317
2017-06-24 | 15:05 | 1.7491 | 0 |  | 1.5
2017-06-24 | 15:10 | 1.7288 | 0 |  | 1.5
2017-06-24 | 15:15 | 1.7265 | 0 | 0 | 1.5 | 25
2017-06-24 | 15:15 |  |  |  | 1.5 |  | 87.6007
2017-06-24 | 15:20 | 1.7553 | 0 |  | 1.5
2017-06-24 | 15:25 | 1.7374 | 0 |  | 1.5
2017-06-24 | 15:30 | 1.7319 | 0 | 0 | 1.5 | 25
2017-06-24 | 15:30 |  |  |  | 1.5 |  | 87.7308
2017-06-24 | 15:35 | 1.7514 | 0 |  | 1.5
2017-06-24 | 15:40 | 1.7319 | 0 |  | 1.5
2017-06-24 | 15:45 | 1.7795 | 0 | 0 | 1.5 | 25
2017-06-24 | 15:45 |  |  |  | 1.5 |  | 87.8278
2017-06-24 | 15:50 | 1.7358 | 0 |  | 1.5
2017-06-24 | 15:55 | 1.7694 | 0 |  | 1.5
2017-06-24 | 16:00 | 1.7616 | 0 | 0 | 1.5 | 25
2017-06-24 | 16:00 |  |  |  | 1.5 |  | 87.9187
2017-06-24 | 16:05 | 1.7514 | 0 |  | 1.5
2017-06-24 | 16:10 | 1.7452 | 0 |  | 1.5
2017-06-24 | 16:15 | 1.7592 | 0 | 0 | 1.5 | 25
2017-06-24 | 16:15 |  |  |  | 1.5 |  | 87.8398
2017-06-24 | 16:20 | 1.7577 | 0 |  | 1.5
2017-06-24 | 16:25 | 1.739 | 0 |  | 1.5
2017-06-24 | 16:30 | 1.7499 | 0 | 0 | 1.5 | 25
2017-06-24 | 16:30 |  |  |  | 1.5 |  | 87.8306
2017-06-24 | 16:35 | 1.7468 | 0 |  | 1.5
2017-06-24 | 16:40 | 1.7686 | 0 |  | 1.5
2017-06-24 | 16:45 | 1.7429 | 0 | 0 | 1.5 | 25
2017-06-24 | 16:45 |  |  |  | 1.5 |  | 87.5801
2017-06-24 | 16:50 | 1.7678 | 0 |  | 1.5
2017-06-24 | 16:55 | 1.7514 | 0 |  | 1.5
2017-06-24 | 17:00 | 1.7413 | 0 | 0 | 1.5 | 25
2017-06-24 | 17:00 |  |  |  | 1.5 |  | 87.41
2017-06-24 | 17:05 | 1.7616 | 0 |  | 1.5
2017-06-24 | 17:10 | 1.7343 | 0 |  | 1.5
2017-06-24 | 17:15 | 1.7748 | 0 | 0 | 1.5 | 25
2017-06-24 | 17:15 | [5 empty] | 87.2968
2017-06-24 | 17:20 | 1.746 | 0 |  | 1.5
2017-06-24 | 17:25 | 1.7663 | 0 |  | 1.5
2017-06-24 | 17:30 | 1.7538 | 0 | 0 | 1.5 | 25
2017-06-24 | 17:30 |  |  |  | 1.5 |  | 87.2252
2017-06-24 | 17:35 | 1.7592 | 0 |  | 1.5
2017-06-24 | 17:40 | 1.7569 | 0 |  | 1.5
2017-06-24 | 17:45 | 1.7265 | 0 | 0 | 1.5 | 25
2017-06-24 | 17:45 |  |  |  | 1.5 |  | 87.0436
2017-06-24 | 17:50 | 1.7943 | 0 |  | 1.5
2017-06-24 | 17:55 | 1.7585 | 0 |  | 1.5
2017-06-24 | 18:00 | 1.76 | 0 | 0 | 1.5 | 25
2017-06-24 | 18:00 |  |  |  | 1.5 |  | 86.5113
2017-06-24 | 18:05 | 1.7507 | 0 |  | 1.5
2017-06-24 | 18:10 | 1.7553 | 0 |  | 1.5
2017-06-24 | 18:15 | 1.7585 | 0 | 0 | 1.5 | 25
2017-06-24 | 18:15 |  |  |  | 1.5 |  | 86.0765
2017-06-24 | 18:20 | 1.7694 | 0 |  | 1.5
2017-06-24 | 18:25 | 1.7686 | 0 |  | 1.5
2017-06-24 | 18:30 | 1.7748 | 0 | 0 | 1.5 | 25
2017-06-24 | 18:30 |  |  |  | 1.5 |  | 85.5232
2017-06-24 | 18:35 | 1.7616 | 0 |  | 1.5
2017-06-24 | 18:40 | 1.7678 | 0 |  | 1.5
2017-06-24 | 18:45 | 1.7811 | 0 | 0 | 1.5 | 25
2017-06-24 | 18:45 |  |  |  | 1.5 |  | 84.9858
2017-06-24 | 18:50 | 1.7538 | 0 |  | 1.5
2017-06-24 | 18:55 | 1.7702 | 0 |  | 1.5
2017-06-24 | 19:00 | 1.8006 | 0 | 0 | 1.5 | 25
2017-06-24 | 19:00 |  |  |  | 1.5 |  | 84.3984
2017-06-24 | 19:05 | 1.7561 | 0 |  | 1.5
2017-06-24 | 19:10 | 1.7553 | 0 |  | 1.5
2017-06-24 | 19:15 | 1.7561 | 0 | 0 | 1.5 | 25
2017-06-24 | 19:15 |  |  |  | 1.5 |  | 84.0611
2017-06-24 | 19:20 | 1.7616 | 0 |  | 1.5
2017-06-24 | 19:25 | 1.7195 | 0 |  | 1.5
2017-06-24 | 19:30 | 1.7382 | 0 | 0 | 1.5 | 25
2017-06-24 | 19:30 |  |  |  | 1.5 |  | 84.0858
2017-06-24 | 19:35 | 1.7507 | 0 |  | 1.5
2017-06-24 | 19:40 | 1.7444 | 0 |  | 1.5
2017-06-24 | 19:45 | 1.7741 | 0 | 0 | 1.5 | 25
2017-06-24 | 19:45 |  |  |  | 1.5 |  | 84.1041
2017-06-24 | 19:50 | 1.7608 | 0 |  | 1.5
2017-06-24 | 19:55 | 1.753 | 0 |  | 1.5
2017-06-24 | 20:00 | 1.7764 | 0 | 0 | 1.5 | 25
2017-06-24 | 20:00 |  |  |  | 1.5 |  | 83.944
2017-06-24 | 20:05 | 1.7678 | 0 |  | 1.5
2017-06-24 | 20:10 | 1.7335 | 0 |  | 1.5
2017-06-24 | 20:15 | 1.7452 | 0 | 0 | 1.5 | 25
2017-06-24 | 20:15 |  |  |  | 1.5 |  | 83.3632
2017-06-24 | 20:20 | 1.7639 | 0 |  | 1.5
2017-06-24 | 20:25 | 1.7514 | 0 |  | 1.5
2017-06-24 | 20:30 | 1.7444 | 0 | 0 | 1.5 | 25
2017-06-24 | 20:30 |  |  |  | 1.5 |  | 83.2415
2017-06-24 | 20:35 | 1.7725 | 0 |  | 1.5
2017-06-24 | 20:40 | 1.7725 | 0 |  | 1.5
2017-06-24 | 20:45 | 1.7678 | 0 | 0 | 1.5 | 25
2017-06-24 | 20:45 |  |  |  | 1.5 |  | 82.826
2017-06-24 | 20:50 | 1.7834 | 0 |  | 1.5
2017-06-24 | 20:55 | 1.7717 | 0 |  | 1.5
2017-06-24 | 21:00 | 1.7787 | 0 | 0 | 1.5 | 25
2017-06-24 | 21:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 21:05 | -0.10574 | 0 |  | 1.5
2017-06-24 | 21:10 | -0.10574 | 0 |  | 1.5
2017-06-24 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-06-24 | 21:15 |  |  |  | 1.5 |  | 0
2017-06-24 | 21:20 | -0.1073 | 0 |  | 1.5
2017-06-24 | 21:25 | -0.1073 | 0 |  | 1.5
2017-06-24 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-24 | 21:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 21:35 | -0.10886 | 0 |  | 1.5
2017-06-24 | 21:40 | -0.10808 | 0 |  | 1.5
2017-06-24 | 21:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-24 | 21:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 21:50 | -0.10808 | 0 |  | 1.5
2017-06-24 | 21:55 | -0.10964 | 0 |  | 1.5
2017-06-24 | 22:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-24 | 22:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 22:05 | -0.10964 | 0 |  | 1.5
2017-06-24 | 22:10 | -0.10964 | 0 |  | 1.5
2017-06-24 | 22:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-06-24 | 22:15 | [5 empty] | 0
2017-06-24 | 22:20 | -0.11042 | 0 |  | 1.5
2017-06-24 | 22:25 | -0.11042 | 0 |  | 1.5
2017-06-24 | 22:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-24 | 22:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 22:35 | -0.10964 | 0 |  | 1.5
2017-06-24 | 22:40 | -0.10964 | 0 |  | 1.5
2017-06-24 | 22:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-06-24 | 22:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 22:50 | -0.11042 | 0 |  | 1.5
2017-06-24 | 22:55 | -0.11042 | 0 |  | 1.5
2017-06-24 | 23:00 | -0.11042 | 0 | 0 | 1.5 | 0
2017-06-24 | 23:00 |  |  |  | 1.5 |  | 0
2017-06-24 | 23:05 | -0.11042 | 0 |  | 1.5
2017-06-24 | 23:10 | -0.11042 | 0 |  | 1.5
2017-06-24 | 23:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-06-24 | 23:15 | [5 empty] | 0
2017-06-24 | 23:20 | -0.10886 | 0 |  | 1.5
2017-06-24 | 23:25 | -0.10964 | 0 |  | 1.5
2017-06-24 | 23:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-24 | 23:30 |  |  |  | 1.5 |  | 0
2017-06-24 | 23:35 | -0.10886 | 0 |  | 1.5
2017-06-24 | 23:40 | -0.10886 | 0 |  | 1.5
2017-06-24 | 23:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-24 | 23:45 |  |  |  | 1.5 |  | 0
2017-06-24 | 23:50 | -0.10886 | 0 |  | 1.5
2017-06-24 | 23:55 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-25 | 0:00 |  |  |  | 1.5 |  | 0
2017-06-25 | 0:05 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:10 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 0:20 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:25 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 0:35 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:40 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 0:50 | -0.10886 | 0 |  | 1.5
2017-06-25 | 0:55 | -0.10886 | 0 |  | 1.5
2017-06-25 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 1:05 | -0.10886 | 0 |  | 1.5
2017-06-25 | 1:10 | -0.10886 | 0 |  | 1.5
2017-06-25 | 1:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 1:20 | -0.10886 | 0 |  | 1.5
2017-06-25 | 1:25 | -0.1112 | 0 |  | 1.5
2017-06-25 | 1:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 1:35 | -0.1112 | 0 |  | 1.5
2017-06-25 | 1:40 | -0.1112 | 0 |  | 1.5
2017-06-25 | 1:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 1:50 | -0.1112 | 0 |  | 1.5
2017-06-25 | 1:55 | -0.1112 | 0 |  | 1.5
2017-06-25 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 2:05 | -0.1112 | 0 |  | 1.5
2017-06-25 | 2:10 | -0.11042 | 0 |  | 1.5
2017-06-25 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 2:20 | -0.11042 | 0 |  | 1.5
2017-06-25 | 2:25 | -0.11042 | 0 |  | 1.5
2017-06-25 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 2:35 | -0.11042 | 0 |  | 1.5
2017-06-25 | 2:40 | -0.11042 | 0 |  | 1.5
2017-06-25 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 2:50 | -0.11042 | 0 |  | 1.5
2017-06-25 | 2:55 | -0.11042 | 0 |  | 1.5
2017-06-25 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 3:05 | -0.11042 | 0 |  | 1.5
2017-06-25 | 3:10 | -0.11042 | 0 |  | 1.5
2017-06-25 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 3:20 | -0.11042 | 0 |  | 1.5
2017-06-25 | 3:25 | -0.10964 | 0 |  | 1.5
2017-06-25 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 3:35 | -0.10964 | 0 |  | 1.5
2017-06-25 | 3:40 | -0.10964 | 0 |  | 1.5
2017-06-25 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 3:50 | -0.10964 | 0 |  | 1.5
2017-06-25 | 3:55 | -0.11042 | 0 |  | 1.5
2017-06-25 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 4:05 | -0.10964 | 0 |  | 1.5
2017-06-25 | 4:10 | -0.10964 | 0 |  | 1.5
2017-06-25 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 4:20 | -0.10964 | 0 |  | 1.5
2017-06-25 | 4:25 | -0.10964 | 0 |  | 1.5
2017-06-25 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 4:35 | -0.11042 | 0 |  | 1.5
2017-06-25 | 4:40 | -0.10964 | 0 |  | 1.5
2017-06-25 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 4:50 | -0.11042 | 0 |  | 1.5
2017-06-25 | 4:55 | -0.11042 | 0 |  | 1.5
2017-06-25 | 5:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 5:05 | 2.0205 | 6.0169 |  | 10
2017-06-25 | 5:10 | 1.9574 | 10 |  | 10
2017-06-25 | 5:15 | 1.9285 | 10 | 1 | 10 | 100 | 93.983
2017-06-25 | 5:20 | 1.9558 | 10 |  | 10
2017-06-25 | 5:25 | 1.8778 | 10 |  | 10
2017-06-25 | 5:30 | 1.8903 | 10 | 1 | 10 | 100 | 89.486
2017-06-25 | 5:35 | 1.8739 | 9.9962 |  | 10
2017-06-25 | 5:40 | 1.8989 | 9.7059 |  | 10
2017-06-25 | 5:45 | 1.8942 | 9.1564 | 1 | 10 | 92.2398 | 85.8157
2017-06-25 | 5:50 | 1.8926 | 8.6235 |  | 10
2017-06-25 | 5:55 | 1.8864 | 8.1506 |  | 10
2017-06-25 | 6:00 | 1.8583 | 7.6393 | 1 | 10 | 77.4746 | 82.081
2017-06-25 | 6:05 | 1.8404 | 7.3077 |  | 10
2017-06-25 | 6:10 | 1.8209 | 7.1096 |  | 10
2017-06-25 | 6:15 | 1.7912 | 6.8566 | 1 | 10 | 69.6738 | 79.9798
2017-06-25 | 6:20 | 1.7858 | 6.6747 |  | 10
2017-06-25 | 6:25 | 1.7826 | 6.6344 |  | 10
2017-06-25 | 6:30 | 1.7943 | 6.379 | 1 | 10 | 65.0368 | 78.8213
2017-06-25 | 6:35 | 1.6165 | 3.7543 |  | 1.5
2017-06-25 | 6:40 | 1.7218 | 0 |  | 1.5
2017-06-25 | 6:45 | 1.7499 | 0 | 0 | 1.5 | 25 | 80.5275
2017-06-25 | 6:50 | 1.7553 | 0 |  | 1.5
2017-06-25 | 6:55 | 1.7436 | 0 |  | 1.5
2017-06-25 | 7:00 | 1.7663 | 0 | 0 | 1.5 | 25 | 80.6074
2017-06-25 | 7:05 | 1.7631 | 0 |  | 1.5
2017-06-25 | 7:10 | 1.7756 | 0 |  | 1.5
2017-06-25 | 7:15 | 1.767 | 0 | 0 | 1.5 | 25 | 80.384
2017-06-25 | 7:20 | 1.76 | 0 |  | 1.5
2017-06-25 | 7:25 | 1.7787 | 0 |  | 1.5
2017-06-25 | 7:30 | 1.7717 | 0 | 0 | 1.5 | 25 | 80.1626
2017-06-25 | 7:35 | 1.7327 | 0 |  | 1.5
2017-06-25 | 7:40 | 1.7647 | 0 |  | 1.5
2017-06-25 | 7:45 | 1.7483 | 0 | 0 | 1.5 | 25 | 80.0444
2017-06-25 | 7:50 | 1.7569 | 0 |  | 1.5
2017-06-25 | 7:55 | 1.7499 | 0 |  | 1.5
2017-06-25 | 8:00 | 1.7647 | 0 | 0 | 1.5 | 25 | 79.8184
2017-06-25 | 8:05 | 1.767 | 0 |  | 1.5
2017-06-25 | 8:10 | 1.7655 | 0 |  | 1.5
2017-06-25 | 8:15 | 1.7319 | 0 | 0 | 1.5 | 25 | 79.8095
2017-06-25 | 8:20 | 1.7343 | 0 |  | 1.5
2017-06-25 | 8:25 | 1.7538 | 0 |  | 1.5
2017-06-25 | 8:30 | 1.7273 | 0 | 0 | 1.5 | 25 | 79.8837
2017-06-25 | 8:35 | 1.7374 | 0 |  | 1.5
2017-06-25 | 8:40 | 1.7335 | 0 |  | 1.5
2017-06-25 | 8:45 | 1.7265 | 0 | 0 | 1.5 | 25 | 80.1656
2017-06-25 | 8:50 | 1.7023 | 0 |  | 1.5
2017-06-25 | 8:55 | 1.7132 | 0 |  | 1.5
2017-06-25 | 9:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 80.8535
2017-06-25 | 9:05 | 1.7358 | 0 |  | 1.5
2017-06-25 | 9:10 | 1.7397 | 0 |  | 1.5
2017-06-25 | 9:15 | 1.7226 | 0 | 0 | 1.5 | 25 | 81.384
2017-06-25 | 9:20 | 1.714 | 0 |  | 1.5
2017-06-25 | 9:25 | 1.7273 | 0 |  | 1.5
2017-06-25 | 9:30 | 1.7374 | 0 | 0 | 1.5 | 25 | 81.8452
2017-06-25 | 9:35 | 1.7444 | 0 |  | 1.5
2017-06-25 | 9:40 | 1.7358 | 0 |  | 1.5
2017-06-25 | 9:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 82.3258
2017-06-25 | 9:50 | 1.7374 | 0 |  | 1.5
2017-06-25 | 9:55 | 1.7304 | 0 |  | 1.5
2017-06-25 | 10:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 82.7984
2017-06-25 | 10:05 | 1.7273 | 0 |  | 1.5
2017-06-25 | 10:10 | 1.7585 | 0 |  | 1.5
2017-06-25 | 10:15 | 1.7429 | 0 | 0 | 1.5 | 25 | 82.964
2017-06-25 | 10:20 | 1.7709 | 0 |  | 1.5
2017-06-25 | 10:25 | 1.7592 | 0 |  | 1.5
2017-06-25 | 10:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 82.6149
2017-06-25 | 10:35 | 1.7499 | 0 |  | 1.5
2017-06-25 | 10:40 | 1.7686 | 0 |  | 1.5
2017-06-25 | 10:45 | 1.7624 | 0 | 0 | 1.5 | 25 | 82.4381
2017-06-25 | 10:50 | 1.7265 | 0 |  | 1.5
2017-06-25 | 10:55 | 1.7553 | 0 |  | 1.5
2017-06-25 | 11:00 | 1.746 | 0 | 0 | 1.5 | 25 | 82.5465
2017-06-25 | 11:05 | 1.7327 | 0 |  | 1.5
2017-06-25 | 11:10 | 1.7436 | 0 |  | 1.5
2017-06-25 | 11:15 | 1.7234 | 0 | 0 | 1.5 | 25 | 83.0136
2017-06-25 | 11:20 | 1.7234 | 0 |  | 1.5
2017-06-25 | 11:25 | 1.7343 | 0 |  | 1.5
2017-06-25 | 11:30 | 1.7101 | 0 | 0 | 1.5 | 25 | 83.826
2017-06-25 | 11:35 | 1.6953 | 0 |  | 1.5
2017-06-25 | 11:40 | 1.7304 | 0 |  | 1.5
2017-06-25 | 11:45 | 1.7156 | 0 | 0 | 1.5 | 25 | 84.6831
2017-06-25 | 11:50 | 1.7202 | 0 |  | 1.5
2017-06-25 | 11:55 | 1.7499 | 0 |  | 1.5
2017-06-25 | 12:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 85.2608
2017-06-25 | 12:05 | 1.7312 | 0 |  | 1.5
2017-06-25 | 12:10 | 1.7421 | 0 |  | 1.5
2017-06-25 | 12:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 85.5825
2017-06-25 | 12:20 | 1.7499 | 0 |  | 1.5
2017-06-25 | 12:25 | 1.7491 | 0 |  | 1.5
2017-06-25 | 12:30 | 1.7639 | 0 | 0 | 1.5 | 25 | 85.7911
2017-06-25 | 12:35 | 1.7624 | 0 |  | 1.5
2017-06-25 | 12:40 | 1.7358 | 0 |  | 1.5
2017-06-25 | 12:45 | 1.7288 | 0 | 0 | 1.5 | 25 | 85.9236
2017-06-25 | 12:50 | 1.7202 | 0 |  | 1.5
2017-06-25 | 12:55 | 1.7397 | 0 |  | 1.5
2017-06-25 | 13:00 | 1.7514 | 0 | 0 | 1.5 | 25 | 86.1406
2017-06-25 | 13:05 | 1.7429 | 0 |  | 1.5
2017-06-25 | 13:10 | 1.7218 | 0 |  | 1.5
2017-06-25 | 13:15 | 1.7468 | 0 | 0 | 1.5 | 25 | 86.25
2017-06-25 | 13:20 | 1.7257 | 0 |  | 1.5
2017-06-25 | 13:25 | 1.7624 | 0 |  | 1.5
2017-06-25 | 13:30 | 1.7351 | 0 | 0 | 1.5 | 25 | 86.391
2017-06-25 | 13:35 | 1.7156 | 0 |  | 1.5
2017-06-25 | 13:40 | 1.7702 | 0 |  | 1.5
2017-06-25 | 13:45 | 1.7304 | 0 | 0 | 1.5 | 25 | 86.5674
2017-06-25 | 13:50 | 1.7514 | 0 |  | 1.5
2017-06-25 | 13:55 | 1.7366 | 0 |  | 1.5
2017-06-25 | 14:00 | 1.7195 | 0 | 0 | 1.5 | 25 | 86.9003
2017-06-25 | 14:05 | 1.7405 | 0 |  | 1.5
2017-06-25 | 14:10 | 1.7085 | 0 |  | 1.5
2017-06-25 | 14:15 | 1.721 | 0 | 0 | 1.5 | 25 | 87.4581
2017-06-25 | 14:20 | 1.7148 | 0 |  | 1.5
2017-06-25 | 14:25 | 1.7452 | 0 |  | 1.5
2017-06-25 | 14:30 | 1.746 | 0 | 0 | 1.5 | 25 | 87.8656
2017-06-25 | 14:35 | 1.7507 | 0 |  | 1.5
2017-06-25 | 14:40 | 1.7429 | 0 |  | 1.5
2017-06-25 | 14:45 | 1.7507 | 0 | 0 | 1.5 | 25 | 88.0016
2017-06-25 | 14:50 | 1.7452 | 0 |  | 1.5
2017-06-25 | 14:55 | 1.7475 | 0 |  | 1.5
2017-06-25 | 15:00 | 1.7499 | 0 | 0 | 1.5 | 25 | 88.1242
2017-06-25 | 15:05 | 1.7546 | 0 |  | 1.5
2017-06-25 | 15:10 | 1.7569 | 0 |  | 1.5
2017-06-25 | 15:15 | 1.7756 | 0 | 0 | 1.5 | 25 | 88.2521
2017-06-25 | 15:20 | 1.7421 | 0 |  | 1.5
2017-06-25 | 15:25 | 1.7647 | 0 |  | 1.5
2017-06-25 | 15:30 | 1.753 | 0 | 0 | 1.5 | 25 | 88.2509
2017-06-25 | 15:35 | 1.7475 | 0 |  | 1.5
2017-06-25 | 15:40 | 1.7538 | 0 |  | 1.5
2017-06-25 | 15:45 | 1.7616 | 0 | 0 | 1.5 | 25 | 88.3128
2017-06-25 | 15:50 | 1.7374 | 0 |  | 1.5
2017-06-25 | 15:55 | 1.7436 | 0 |  | 1.5
2017-06-25 | 16:00 | 1.7436 | 0 | 0 | 1.5 | 25 | 88.3176
2017-06-25 | 16:05 | 1.7826 | 0 |  | 1.5
2017-06-25 | 16:10 | 1.7304 | 0 |  | 1.5
2017-06-25 | 16:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 88.2116
2017-06-25 | 16:20 | 1.7561 | 0 |  | 1.5
2017-06-25 | 16:25 | 1.7335 | 0 |  | 1.5
2017-06-25 | 16:30 | 1.7647 | 0 | 0 | 1.5 | 25 | 88.1639
2017-06-25 | 16:35 | 1.7608 | 0 |  | 1.5
2017-06-25 | 16:40 | 1.7343 | 0 |  | 1.5
2017-06-25 | 16:45 | 1.7499 | 0 | 0 | 1.5 | 25 | 88.3629
2017-06-25 | 16:50 | 1.739 | 0 |  | 1.5
2017-06-25 | 16:55 | 1.7639 | 0 |  | 1.5
2017-06-25 | 17:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 88.4568
2017-06-25 | 17:05 | 1.7491 | 0 |  | 1.5
2017-06-25 | 17:10 | 1.7499 | 0 |  | 1.5
2017-06-25 | 17:15 | 1.7592 | 0 | 0 | 1.5 | 25 | 88.5542
2017-06-25 | 17:20 | 1.7694 | 0 |  | 1.5
2017-06-25 | 17:25 | 1.7491 | 0 |  | 1.5
2017-06-25 | 17:30 | 1.7577 | 0 | 0 | 1.5 | 25 | 88.4282
2017-06-25 | 17:35 | 1.746 | 0 |  | 1.5
2017-06-25 | 17:40 | 1.7585 | 0 |  | 1.5
2017-06-25 | 17:45 | 1.7483 | 0 | 0 | 1.5 | 25 | 88.3275
2017-06-25 | 17:50 | 1.753 | 0 |  | 1.5
2017-06-25 | 17:55 | 1.7834 | 0 |  | 1.5
2017-06-25 | 18:00 | 1.7725 | 0 | 0 | 1.5 | 25 | 87.8338
2017-06-25 | 18:05 | 1.7764 | 0 |  | 1.5
2017-06-25 | 18:10 | 1.7772 | 0 |  | 1.5
2017-06-25 | 18:15 | 1.76 | 0 | 0 | 1.5 | 25 | 87.2144
2017-06-25 | 18:20 | 1.7585 | 0 |  | 1.5
2017-06-25 | 18:25 | 1.7639 | 0 |  | 1.5
2017-06-25 | 18:30 | 1.7842 | 0 | 0 | 1.5 | 25 | 86.8139
2017-06-25 | 18:35 | 1.7678 | 0 |  | 1.5
2017-06-25 | 18:40 | 1.7803 | 0 |  | 1.5
2017-06-25 | 18:45 | 1.7873 | 0 | 0 | 1.5 | 25 | 86.2528
2017-06-25 | 18:50 | 1.8037 | 0 |  | 1.5
2017-06-25 | 18:55 | 1.7647 | 0 |  | 1.5
2017-06-25 | 19:00 | 1.7975 | 0 | 0 | 1.5 | 25 | 85.4943
2017-06-25 | 19:05 | 1.7616 | 0 |  | 1.5
2017-06-25 | 19:10 | 1.8084 | 0 |  | 1.5
2017-06-25 | 19:15 | 1.8123 | 0 | 0 | 1.5 | 25 | 84.3702
2017-06-25 | 19:20 | 1.7834 | 0 |  | 1.5
2017-06-25 | 19:25 | 1.8107 | 0 |  | 1.5
2017-06-25 | 19:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 83.3425
2017-06-25 | 19:35 | 1.778 | 0 |  | 1.5
2017-06-25 | 19:40 | 1.767 | 0 |  | 1.5
2017-06-25 | 19:45 | 1.7647 | 0 | 0 | 1.5 | 25 | 82.7187
2017-06-25 | 19:50 | 1.7889 | 0 |  | 1.5
2017-06-25 | 19:55 | 1.785 | 0 |  | 1.5
2017-06-25 | 20:00 | 1.7709 | 0 | 0 | 1.5 | 25 | 82.0277
2017-06-25 | 20:05 | 1.7826 | 0 |  | 1.5
2017-06-25 | 20:10 | 1.7811 | 0 |  | 1.5
2017-06-25 | 20:15 | 1.7748 | 0 | 0 | 1.5 | 25 | 81.4951
2017-06-25 | 20:20 | 1.778 | 0 |  | 1.5
2017-06-25 | 20:25 | 1.7569 | 0 |  | 1.5
2017-06-25 | 20:30 | 1.7741 | 0 | 0 | 1.5 | 25 | 81.0298
2017-06-25 | 20:35 | 1.7475 | 0 |  | 1.5
2017-06-25 | 20:40 | 1.7561 | 0 |  | 1.5
2017-06-25 | 20:45 | 1.7725 | 0 | 0 | 1.5 | 25 | 80.684
2017-06-25 | 20:50 | 1.7553 | 0 |  | 1.5
2017-06-25 | 20:55 | 1.7514 | 0 |  | 1.5
2017-06-25 | 21:00 | 1.7795 | 0 | 0 | 1.5 | 25 | 80.4276
2017-06-25 | 21:05 | -0.10652 | 0 |  | 1.5
2017-06-25 | 21:10 | -0.1073 | 0 |  | 1.5
2017-06-25 | 21:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 21:20 | -0.10808 | 0 |  | 1.5
2017-06-25 | 21:25 | -0.10808 | 0 |  | 1.5
2017-06-25 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 21:35 | -0.10886 | 0 |  | 1.5
2017-06-25 | 21:40 | -0.10886 | 0 |  | 1.5
2017-06-25 | 21:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 21:50 | -0.11042 | 0 |  | 1.5
2017-06-25 | 21:55 | -0.10886 | 0 |  | 1.5
2017-06-25 | 22:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 22:05 | -0.10886 | 0 |  | 1.5
2017-06-25 | 22:10 | -0.10886 | 0 |  | 1.5
2017-06-25 | 22:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 22:20 | -0.10886 | 0 |  | 1.5
2017-06-25 | 22:25 | -0.10886 | 0 |  | 1.5
2017-06-25 | 22:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 22:35 | -0.10886 | 0 |  | 1.5
2017-06-25 | 22:40 | -0.10964 | 0 |  | 1.5
2017-06-25 | 22:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 22:50 | -0.10964 | 0 |  | 1.5
2017-06-25 | 22:55 | -0.10964 | 0 |  | 1.5
2017-06-25 | 23:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 23:05 | -0.10964 | 0 |  | 1.5
2017-06-25 | 23:10 | -0.10964 | 0 |  | 1.5
2017-06-25 | 23:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 23:20 | -0.10964 | 0 |  | 1.5
2017-06-25 | 23:25 | -0.10964 | 0 |  | 1.5
2017-06-25 | 23:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 23:35 | -0.10964 | 0 |  | 1.5
2017-06-25 | 23:40 | -0.11042 | 0 |  | 1.5
2017-06-25 | 23:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-25 | 23:50 | -0.11042 | 0 |  | 1.5
2017-06-25 | 23:55 | -0.11042 | 0 |  | 1.5
2017-06-26 | 0:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 0:05 | -0.10964 | 0 |  | 1.5
2017-06-26 | 0:10 | -0.10964 | 0 |  | 1.5
2017-06-26 | 0:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 0:20 | -0.10964 | 0 |  | 1.5
2017-06-26 | 0:25 | -0.10886 | 0 |  | 1.5
2017-06-26 | 0:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 0:35 | -0.10886 | 0 |  | 1.5
2017-06-26 | 0:40 | -0.10886 | 0 |  | 1.5
2017-06-26 | 0:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 0:50 | -0.10808 | 0 |  | 1.5
2017-06-26 | 0:55 | -0.10808 | 0 |  | 1.5
2017-06-26 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 1:05 | -0.10808 | 0 |  | 1.5
2017-06-26 | 1:10 | -0.10808 | 0 |  | 1.5
2017-06-26 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 1:20 | -0.10886 | 0 |  | 1.5
2017-06-26 | 1:25 | -0.11198 | 0 |  | 1.5
2017-06-26 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 1:35 | -0.1112 | 0 |  | 1.5
2017-06-26 | 1:40 | -0.11198 | 0 |  | 1.5
2017-06-26 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 1:50 | -0.11198 | 0 |  | 1.5
2017-06-26 | 1:55 | -0.11198 | 0 |  | 1.5
2017-06-26 | 2:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 2:05 | -0.11198 | 0 |  | 1.5
2017-06-26 | 2:10 | -0.11198 | 0 |  | 1.5
2017-06-26 | 2:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 2:20 | -0.11198 | 0 |  | 1.5
2017-06-26 | 2:25 | -0.11198 | 0 |  | 1.5
2017-06-26 | 2:30 | -0.1151 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 2:35 | -0.11354 | 0 |  | 1.5
2017-06-26 | 2:40 | -0.11432 | 0 |  | 1.5
2017-06-26 | 2:45 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 2:50 | -0.11432 | 0 |  | 1.5
2017-06-26 | 2:55 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:00 | -0.1151 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 3:05 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:10 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:15 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 3:20 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:25 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:30 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 3:35 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:40 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:45 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 3:50 | -0.11432 | 0 |  | 1.5
2017-06-26 | 3:55 | -0.11432 | 0 |  | 1.5
2017-06-26 | 4:00 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 4:05 | -0.11432 | 0 |  | 1.5
2017-06-26 | 4:10 | -0.11354 | 0 |  | 1.5
2017-06-26 | 4:15 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 4:20 | -0.11744 | 0 |  | 1.5
2017-06-26 | 4:25 | -0.11354 | 0 |  | 1.5
2017-06-26 | 4:30 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 4:35 | -0.11354 | 0 |  | 1.5
2017-06-26 | 4:40 | -0.11354 | 0 |  | 1.5
2017-06-26 | 4:45 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 4:50 | -0.11276 | 0 |  | 1.5
2017-06-26 | 4:55 | -0.11276 | 0 |  | 1.5
2017-06-26 | 5:00 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 5:05 | 2.1711 | 6.3545 |  | 10
2017-06-26 | 5:10 | 1.9581 | 10 |  | 10
2017-06-26 | 5:15 | 1.9402 | 10 | 1 | 10 | 100 | 92.8371
2017-06-26 | 5:20 | 1.8989 | 10 |  | 10
2017-06-26 | 5:25 | 1.8887 | 10 |  | 10
2017-06-26 | 5:30 | 1.8817 | 10 | 1 | 10 | 99.98 | 88.6147
2017-06-26 | 5:35 | 1.8638 | 9.9601 |  | 10
2017-06-26 | 5:40 | 1.8762 | 9.6422 |  | 10
2017-06-26 | 5:45 | 1.8411 | 9.0565 | 1 | 10 | 91.3507 | 85.386
2017-06-26 | 5:50 | 1.8341 | 8.7057 |  | 10
2017-06-26 | 5:55 | 1.8739 | 8.3993 |  | 10
2017-06-26 | 6:00 | 1.8326 | 7.9341 | 1 | 10 | 80.7419 | 82.5199
2017-06-26 | 6:05 | 1.8341 | 7.9216 |  | 10
2017-06-26 | 6:10 | 1.7733 | 8.1289 |  | 10
2017-06-26 | 6:15 | 1.7647 | 8.2769 | 1 | 10 | 83.414 | 81.152
2017-06-26 | 6:20 | 1.7577 | 8.3026 |  | 10
2017-06-26 | 6:25 | 1.7608 | 7.8436 |  | 10
2017-06-26 | 6:30 | 1.7686 | 7.8964 | 1 | 10 | 79.8463 | 80.552
2017-06-26 | 6:35 | 1.7585 | 7.7847 |  | 10
2017-06-26 | 6:40 | 1.7327 | 7.8204 |  | 10
2017-06-26 | 6:45 | 1.8053 | 7.5027 | 1 | 10 | 76.0126 | 80.0849
2017-06-26 | 6:50 | 1.799 | 6.955 |  | 10
2017-06-26 | 6:55 | 1.7468 | 7.3402 |  | 10
2017-06-26 | 7:00 | 1.7795 | 7.0757 | 1 | 10 | 71.7371 | 79.368
2017-06-26 | 7:05 | 1.7631 | 6.7044 |  | 10
2017-06-26 | 7:10 | 1.7608 | 6.8531 |  | 10
2017-06-26 | 7:15 | 1.7429 | 6.5793 | 1 | 10 | 67.1778 | 78.7676
2017-06-26 | 7:20 | 1.7631 | 6.5425 |  | 10
2017-06-26 | 7:25 | 1.7241 | 6.0607 |  | 10
2017-06-26 | 7:30 | 1.7327 | 5.6867 | 1 | 10 | 58.168 | 78.8634
2017-06-26 | 7:35 | 1.7522 | 6.3128 |  | 10
2017-06-26 | 7:40 | 1.7397 | 6.5828 |  | 10
2017-06-26 | 7:45 | 1.7873 | 6.5725 | 1 | 10 | 66.4958 | 79.0299
2017-06-26 | 7:50 | 1.7514 | 6.2105 |  | 10
2017-06-26 | 7:55 | 1.7218 | 5.7691 |  | 10
2017-06-26 | 8:00 | 1.7655 | 5.5143 | 1 | 10 | 56.6416 | 78.9153
2017-06-26 | 8:05 | 1.7569 | 5.3137 |  | 10
2017-06-26 | 8:10 | 1.767 | 5.0093 |  | 10
2017-06-26 | 8:15 | 1.7709 | 5.3997 | 1 | 10 | 55.7492 | 78.7063
2017-06-26 | 8:20 | 1.7444 | 4.7267 |  | 10
2017-06-26 | 8:25 | 1.7686 | 4.4009 |  | 10
2017-06-26 | 8:30 | 1.7655 | 4.1715 | 1 | 10 | 44.3575 | 78.5309
2017-06-26 | 8:35 | 1.7273 | 4.2778 |  | 10
2017-06-26 | 8:40 | 1.7733 | 5.1372 |  | 10
2017-06-26 | 8:45 | 1.7429 | 5.4332 | 1 | 10 | 55.3 | 78.2091
2017-06-26 | 8:50 | 1.7803 | 5.2575 |  | 10
2017-06-26 | 8:55 | 1.7507 | 4.9604 |  | 10
2017-06-26 | 9:00 | 1.7507 | 4.6266 | 1 | 10 | 48.2886 | 77.9267
2017-06-26 | 9:05 | 1.7803 | 4.3736 |  | 10
2017-06-26 | 9:10 | 1.7421 | 4.7387 |  | 10
2017-06-26 | 9:15 | 1.7522 | 4.4914 | 1 | 10 | 46.9366 | 78.0003
2017-06-26 | 9:20 | 1.7218 | 4.7666 |  | 10
2017-06-26 | 9:25 | 1.7171 | 4.863 |  | 10
2017-06-26 | 9:30 | 1.6851 | 5.2404 | 1 | 10 | 53.3983 | 78.9585
2017-06-26 | 9:35 | 1.7202 | 5.39 |  | 10
2017-06-26 | 9:40 | 1.7741 | 4.806 |  | 10
2017-06-26 | 9:45 | 1.7475 | 4.4899 | 1 | 10 | 47.149 | 78.9314
2017-06-26 | 9:50 | 1.7741 | 4.2441 |  | 10
2017-06-26 | 9:55 | 1.7803 | 4.4533 |  | 10
2017-06-26 | 10:00 | 1.8053 | 3.7164 | 1 | 10 | 39.4877 | 78.3105
2017-06-26 | 10:05 | 1.7514 | 3.4325 |  | 10
2017-06-26 | 10:10 | 1.7007 | 3.5677 |  | 10
2017-06-26 | 10:15 | 1.746 | 3.7152 | 1 | 10 | 39.5192 | 78.6915
2017-06-26 | 10:20 | 1.7764 | 4.0079 |  | 10
2017-06-26 | 10:25 | 1.7795 | 4.2857 |  | 10
2017-06-26 | 10:30 | 1.7366 | 4.708 | 1 | 10 | 48.7294 | 79.0442
2017-06-26 | 10:35 | 1.5986 | 1.2619 |  | 1.5
2017-06-26 | 10:40 | 1.8162 | 0.34715 |  | 10
2017-06-26 | 10:45 | 1.8131 | 1.444 | 1 | 10 | 37.374 | 79.739
2017-06-26 | 10:50 | 1.8053 | 2.5601 |  | 10
2017-06-26 | 10:55 | 1.6446 | 0.30849 |  | 1.5
2017-06-26 | 11:00 | 1.6766 | 0 | 0 | 1.5 | 25 | 82.0333
2017-06-26 | 11:05 | 1.7101 | 0 |  | 1.5
2017-06-26 | 11:10 | 1.7132 | 0 |  | 1.5
2017-06-26 | 11:15 | 1.7273 | 0 | 0 | 1.5 | 25 | 83.4002
2017-06-26 | 11:20 | 1.6875 | 0 |  | 1.5
2017-06-26 | 11:25 | 1.6976 | 0 |  | 1.5
2017-06-26 | 11:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 84.5787
2017-06-26 | 11:35 | 1.7226 | 0 |  | 1.5
2017-06-26 | 11:40 | 1.7436 | 0 |  | 1.5
2017-06-26 | 11:45 | 1.7436 | 0 | 0 | 1.5 | 25 | 85.3
2017-06-26 | 11:50 | 1.7475 | 0 |  | 1.5
2017-06-26 | 11:55 | 1.7062 | 0 |  | 1.5
2017-06-26 | 12:00 | 1.7132 | 0 | 0 | 1.5 | 25 | 86.3039
2017-06-26 | 12:05 | 1.6727 | 0 |  | 1.5
2017-06-26 | 12:10 | 1.7156 | 0 |  | 1.5
2017-06-26 | 12:15 | 1.7163 | 0 | 0 | 1.5 | 25 | 87.3605
2017-06-26 | 12:20 | 1.8248 | 0 |  | 1.5
2017-06-26 | 12:25 | 1.799 | 0 |  | 1.5
2017-06-26 | 12:30 | 1.8045 | 0 | 0 | 1.5 | 25 | 86.1043
2017-06-26 | 12:35 | 1.8029 | 0 |  | 1.5
2017-06-26 | 12:40 | 1.7803 | 0 |  | 1.5
2017-06-26 | 12:45 | 1.746 | 0 | 0 | 1.5 | 25 | 85.3187
2017-06-26 | 12:50 | 1.7834 | 0 |  | 1.5
2017-06-26 | 12:55 | 1.7483 | 0 |  | 1.5
2017-06-26 | 13:00 | 1.7132 | 0 | 0 | 1.5 | 25 | 85.6685
2017-06-26 | 13:05 | 1.7273 | 0 |  | 1.5
2017-06-26 | 13:10 | 1.7522 | 0 |  | 1.5
2017-06-26 | 13:15 | 1.7553 | 0 | 0 | 1.5 | 25 | 86.2555
2017-06-26 | 13:20 | 1.7475 | 0 |  | 1.5
2017-06-26 | 13:25 | 1.7304 | 0 |  | 1.5
2017-06-26 | 13:30 | 1.7327 | 0 | 0 | 1.5 | 25 | 86.5522
2017-06-26 | 13:35 | 1.7117 | 0 |  | 1.5
2017-06-26 | 13:40 | 1.7499 | 0 |  | 1.5
2017-06-26 | 13:45 | 1.7351 | 0 | 0 | 1.5 | 25 | 86.9656
2017-06-26 | 13:50 | 1.7358 | 0 |  | 1.5
2017-06-26 | 13:55 | 1.7577 | 0 |  | 1.5
2017-06-26 | 14:00 | 1.707 | 0 | 0 | 1.5 | 25 | 87.3676
2017-06-26 | 14:05 | 1.7179 | 0 |  | 1.5
2017-06-26 | 14:10 | 1.7156 | 0 |  | 1.5
2017-06-26 | 14:15 | 1.7046 | 0 | 0 | 1.5 | 25 | 88.114
2017-06-26 | 14:20 | 1.7709 | 0 |  | 1.5
2017-06-26 | 14:25 | 1.714 | 0 |  | 1.5
2017-06-26 | 14:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 88.078
2017-06-26 | 14:35 | 1.7117 | 0 |  | 1.5
2017-06-26 | 14:40 | 1.7577 | 0 |  | 1.5
2017-06-26 | 14:45 | 1.7694 | 0 | 0 | 1.5 | 25 | 88.0211
2017-06-26 | 14:50 | 1.7366 | 0 |  | 1.5
2017-06-26 | 14:55 | 1.7109 | 0 |  | 1.5
2017-06-26 | 15:00 | 1.739 | 0 | 0 | 1.5 | 25 | 88.4474
2017-06-26 | 15:05 | 1.7452 | 0 |  | 1.5
2017-06-26 | 15:10 | 1.7514 | 0 |  | 1.5
2017-06-26 | 15:15 | 1.7335 | 0 | 0 | 1.5 | 25 | 88.9346
2017-06-26 | 15:20 | 1.7171 | 0 |  | 1.5
2017-06-26 | 15:25 | 1.7273 | 0 |  | 1.5
2017-06-26 | 15:30 | 1.7304 | 0 | 0 | 1.5 | 25 | 89.5492
2017-06-26 | 15:35 | 1.7694 | 0 |  | 1.5
2017-06-26 | 15:40 | 1.7592 | 0 |  | 1.5
2017-06-26 | 15:45 | 1.7756 | 0 | 0 | 1.5 | 25 | 89.6024
2017-06-26 | 15:50 | 1.746 | 0 |  | 1.5
2017-06-26 | 15:55 | 1.7608 | 0 |  | 1.5
2017-06-26 | 16:00 | 1.7577 | 0 | 0 | 1.5 | 25 | 89.631
2017-06-26 | 16:05 | 1.7171 | 0 |  | 1.5
2017-06-26 | 16:10 | 1.7538 | 0 |  | 1.5
2017-06-26 | 16:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 89.8765
2017-06-26 | 16:20 | 1.7265 | 0 |  | 1.5
2017-06-26 | 16:25 | 1.7553 | 0 |  | 1.5
2017-06-26 | 16:30 | 1.7429 | 0 | 0 | 1.5 | 25 | 90.0694
2017-06-26 | 16:35 | 1.7616 | 0 |  | 1.5
2017-06-26 | 16:40 | 1.753 | 0 |  | 1.5
2017-06-26 | 16:45 | 1.7507 | 0 | 0 | 1.5 | 25 | 89.7892
2017-06-26 | 16:50 | 1.7358 | 0 |  | 1.5
2017-06-26 | 16:55 | 1.7444 | 0 |  | 1.5
2017-06-26 | 17:00 | 1.7717 | 0 | 0 | 1.5 | 25 | 89.7482
2017-06-26 | 17:05 | 1.7663 | 0 |  | 1.5
2017-06-26 | 17:10 | 1.7772 | 0 |  | 1.5
2017-06-26 | 17:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 88.9744
2017-06-26 | 17:20 | 1.8107 | 0 |  | 1.5
2017-06-26 | 17:25 | 1.8396 | 0 |  | 1.5
2017-06-26 | 17:30 | 1.8138 | 0 | 0 | 1.5 | 25 | 87.3211
2017-06-26 | 17:35 | 1.8302 | 0 |  | 1.5
2017-06-26 | 17:40 | 1.831 | 0 |  | 1.5
2017-06-26 | 17:45 | 1.8115 | 0 | 0 | 1.5 | 25 | 85.4167
2017-06-26 | 17:50 | 1.7616 | 0 |  | 1.5
2017-06-26 | 17:55 | 1.8201 | 0 |  | 1.5
2017-06-26 | 18:00 | 1.8146 | 0 | 0 | 1.5 | 25 | 83.7764
2017-06-26 | 18:05 | 1.8014 | 0 |  | 1.5
2017-06-26 | 18:10 | 1.8068 | 0 |  | 1.5
2017-06-26 | 18:15 | 1.7873 | 0 | 0 | 1.5 | 25 | 82.7268
2017-06-26 | 18:20 | 1.7865 | 0 |  | 1.5
2017-06-26 | 18:25 | 1.7803 | 0 |  | 1.5
2017-06-26 | 18:30 | 1.806 | 0 | 0 | 1.5 | 25 | 81.857
2017-06-26 | 18:35 | 1.7709 | 0 |  | 1.5
2017-06-26 | 18:40 | 1.7327 | 0 |  | 1.5
2017-06-26 | 18:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 81.1853
2017-06-26 | 18:50 | 1.7717 | 0 |  | 1.5
2017-06-26 | 18:55 | 1.7561 | 0 |  | 1.5
2017-06-26 | 19:00 | 1.7819 | 0 | 0 | 1.5 | 25 | 80.7318
2017-06-26 | 19:05 | 1.7538 | 0 |  | 1.5
2017-06-26 | 19:10 | 1.7546 | 0 |  | 1.5
2017-06-26 | 19:15 | 1.7397 | 0 | 0 | 1.5 | 25 | 80.3604
2017-06-26 | 19:20 | 1.7616 | 0 |  | 1.5
2017-06-26 | 19:25 | 1.7717 | 0 |  | 1.5
2017-06-26 | 19:30 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.8332
2017-06-26 | 19:35 | 1.7897 | 0 |  | 1.5
2017-06-26 | 19:40 | 1.7819 | 0 |  | 1.5
2017-06-26 | 19:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 79.3666
2017-06-26 | 19:50 | 1.7522 | 0 |  | 1.5
2017-06-26 | 19:55 | 1.7631 | 0 |  | 1.5
2017-06-26 | 20:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 79.3286
2017-06-26 | 20:05 | 1.7327 | 0 |  | 1.5
2017-06-26 | 20:10 | 1.7561 | 0 |  | 1.5
2017-06-26 | 20:15 | 1.7249 | 0 | 0 | 1.5 | 25 | 79.5279
2017-06-26 | 20:20 | 1.746 | 0 |  | 1.5
2017-06-26 | 20:25 | 1.7436 | 0 |  | 1.5
2017-06-26 | 20:30 | 1.7421 | 0 | 0 | 1.5 | 25 | 79.5684
2017-06-26 | 20:35 | 1.7327 | 0 |  | 1.5
2017-06-26 | 20:40 | 1.7475 | 0 |  | 1.5
2017-06-26 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 25 | 79.5214
2017-06-26 | 20:50 | 1.7163 | 0 |  | 1.5
2017-06-26 | 20:55 | 1.7842 | 0 |  | 1.5
2017-06-26 | 21:00 | 1.7631 | 0 | 0 | 1.5 | 25 | 79.494
2017-06-26 | 21:05 | -0.10652 | 0 |  | 1.5
2017-06-26 | 21:10 | -0.10808 | 0 |  | 1.5
2017-06-26 | 21:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 21:20 | -0.10808 | 0 |  | 1.5
2017-06-26 | 21:25 | -0.10886 | 0 |  | 1.5
2017-06-26 | 21:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 21:35 | -0.10886 | 0 |  | 1.5
2017-06-26 | 21:40 | -0.10964 | 0 |  | 1.5
2017-06-26 | 21:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 21:50 | -0.10964 | 0 |  | 1.5
2017-06-26 | 21:55 | -0.11042 | 0 |  | 1.5
2017-06-26 | 22:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 22:05 | -0.11042 | 0 |  | 1.5
2017-06-26 | 22:10 | -0.11042 | 0 |  | 1.5
2017-06-26 | 22:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 22:20 | -0.11042 | 0 |  | 1.5
2017-06-26 | 22:25 | -0.11042 | 0 |  | 1.5
2017-06-26 | 22:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 22:35 | -0.10964 | 0 |  | 1.5
2017-06-26 | 22:40 | -0.11042 | 0 |  | 1.5
2017-06-26 | 22:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 22:50 | -0.10964 | 0 |  | 1.5
2017-06-26 | 22:55 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 23:05 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:10 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 23:20 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:25 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 23:35 | -0.11042 | 0 |  | 1.5
2017-06-26 | 23:40 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-26 | 23:50 | -0.10964 | 0 |  | 1.5
2017-06-26 | 23:55 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 0:05 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:10 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 0:20 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:25 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 0:35 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:40 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 0:50 | -0.10964 | 0 |  | 1.5
2017-06-27 | 0:55 | -0.10886 | 0 |  | 1.5
2017-06-27 | 1:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 1:05 | -0.10964 | 0 |  | 1.5
2017-06-27 | 1:10 | -0.10964 | 0 |  | 1.5
2017-06-27 | 1:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 1:20 | -0.10886 | 0 |  | 1.5
2017-06-27 | 1:25 | -0.11198 | 0 |  | 1.5
2017-06-27 | 1:30 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 1:35 | -0.11198 | 0 |  | 1.5
2017-06-27 | 1:40 | -0.11276 | 0 |  | 1.5
2017-06-27 | 1:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 1:50 | -0.11198 | 0 |  | 1.5
2017-06-27 | 1:55 | -0.11198 | 0 |  | 1.5
2017-06-27 | 2:00 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 2:05 | -0.11198 | 0 |  | 1.5
2017-06-27 | 2:10 | -0.1112 | 0 |  | 1.5
2017-06-27 | 2:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 2:20 | -0.11198 | 0 |  | 1.5
2017-06-27 | 2:25 | -0.11198 | 0 |  | 1.5
2017-06-27 | 2:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 2:35 | -0.11198 | 0 |  | 1.5
2017-06-27 | 2:40 | -0.1112 | 0 |  | 1.5
2017-06-27 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 2:50 | -0.11198 | 0 |  | 1.5
2017-06-27 | 2:55 | -0.11198 | 0 |  | 1.5
2017-06-27 | 3:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 3:05 | -0.11198 | 0 |  | 1.5
2017-06-27 | 3:10 | -0.11198 | 0 |  | 1.5
2017-06-27 | 3:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 3:20 | -0.11198 | 0 |  | 1.5
2017-06-27 | 3:25 | -0.11198 | 0 |  | 1.5
2017-06-27 | 3:30 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 3:35 | -0.11276 | 0 |  | 1.5
2017-06-27 | 3:40 | -0.11198 | 0 |  | 1.5
2017-06-27 | 3:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 3:50 | -0.11276 | 0 |  | 1.5
2017-06-27 | 3:55 | -0.11198 | 0 |  | 1.5
2017-06-27 | 4:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 4:05 | -0.11198 | 0 |  | 1.5
2017-06-27 | 4:10 | -0.1112 | 0 |  | 1.5
2017-06-27 | 4:15 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 4:20 | -0.11276 | 0 |  | 1.5
2017-06-27 | 4:25 | -0.11198 | 0 |  | 1.5
2017-06-27 | 4:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 4:35 | -0.11198 | 0 |  | 1.5
2017-06-27 | 4:40 | -0.11198 | 0 |  | 1.5
2017-06-27 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 4:50 | -0.11198 | 0 |  | 1.5
2017-06-27 | 4:55 | -0.11198 | 0 |  | 1.5
2017-06-27 | 5:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 5:05 | 2.2912 | 6.4514 |  | 10
2017-06-27 | 5:10 | 2.0244 | 10 |  | 10
2017-06-27 | 5:15 | 2.0486 | 10 | 1 | 10 | 100 | 90.9448
2017-06-27 | 5:20 | 2.0369 | 10 |  | 10
2017-06-27 | 5:25 | 2.012 | 9.805 |  | 10
2017-06-27 | 5:30 | 1.934 | 9.499 | 1 | 10 | 95.3195 | 84.0589
2017-06-27 | 5:35 | 1.9113 | 9.015 |  | 10
2017-06-27 | 5:40 | 1.8614 | 8.3017 |  | 10
2017-06-27 | 5:45 | 1.8435 | 8.1055 | 1 | 10 | 81.7387 | 80.6147
2017-06-27 | 5:50 | 1.8318 | 7.7743 |  | 10
2017-06-27 | 5:55 | 1.817 | 7.6107 |  | 10
2017-06-27 | 6:00 | 1.7889 | 7.1313 | 1 | 10 | 72.6781 | 78.79
2017-06-27 | 6:05 | 1.8138 | 7.1689 |  | 10
2017-06-27 | 6:10 | 1.7725 | 7.4995 |  | 10
2017-06-27 | 6:15 | 1.7764 | 7.4013 | 1 | 10 | 75.0558 | 77.9477
2017-06-27 | 6:20 | 1.7226 | 7.3801 |  | 10
2017-06-27 | 6:25 | 1.7811 | 7.0054 |  | 10
2017-06-27 | 6:30 | 1.7717 | 6.9136 | 1 | 10 | 69.9369 | 77.5514
2017-06-27 | 6:35 | 1.7647 | 6.7028 |  | 10
2017-06-27 | 6:40 | 1.7834 | 6.3427 |  | 10
2017-06-27 | 6:45 | 1.7374 | 6.3917 | 1 | 10 | 65.1704 | 77.0375
2017-06-27 | 6:50 | 1.7413 | 5.9783 |  | 10
2017-06-27 | 6:55 | 1.785 | 5.7965 |  | 10
2017-06-27 | 7:00 | 1.7678 | 5.965 | 1 | 10 | 60.9202 | 76.5407
2017-06-27 | 7:05 | 1.7655 | 5.8884 |  | 10
2017-06-27 | 7:10 | 1.7312 | 6.7426 |  | 10
2017-06-27 | 7:15 | 1.7546 | 6.8113 | 1 | 10 | 69.628 | 76.5502
2017-06-27 | 7:20 | 1.7561 | 6.4193 |  | 10
2017-06-27 | 7:25 | 1.7413 | 6.1898 |  | 10
2017-06-27 | 7:30 | 1.7686 | 5.8705 | 1 | 10 | 59.5098 | 76.4886
2017-06-27 | 7:35 | 1.7709 | 5.7384 |  | 10
2017-06-27 | 7:40 | 1.7499 | 5.8108 |  | 10
2017-06-27 | 7:45 | 1.7577 | 5.7597 | 1 | 10 | 58.6819 | 76.2448
2017-06-27 | 7:50 | 1.7686 | 5.3992 |  | 10
2017-06-27 | 7:55 | 1.7569 | 5.2248 |  | 10
2017-06-27 | 8:00 | 1.7514 | 4.6969 | 1 | 10 | 48.1385 | 76.056
2017-06-27 | 8:05 | 1.7608 | 5.212 |  | 10
2017-06-27 | 8:10 | 1.7273 | 5.0516 |  | 10
2017-06-27 | 8:15 | 1.7741 | 5.1827 | 1 | 10 | 52.7787 | 76.0893
2017-06-27 | 8:20 | 1.746 | 5.1851 |  | 10
2017-06-27 | 8:25 | 1.7304 | 5.2998 |  | 10
2017-06-27 | 8:30 | 1.728 | 4.978 | 1 | 10 | 51.0637 | 76.3368
2017-06-27 | 8:35 | 1.7663 | 5.8919 |  | 10
2017-06-27 | 8:40 | 1.7608 | 5.7201 |  | 10
2017-06-27 | 8:45 | 1.7491 | 5.6422 | 1 | 10 | 57.5853 | 75.9349
2017-06-27 | 8:50 | 1.7491 | 5.4801 |  | 10
2017-06-27 | 8:55 | 1.7491 | 5.7491 |  | 10
2017-06-27 | 9:00 | 1.7741 | 5.4632 | 1 | 10 | 56.1806 | 75.8657
2017-06-27 | 9:05 | 1.7078 | 5.9127 |  | 10
2017-06-27 | 9:10 | 1.7335 | 6.5698 |  | 10
2017-06-27 | 9:15 | 1.7273 | 6.5422 | 1 | 10 | 66.6556 | 76.2209
2017-06-27 | 9:20 | 1.7507 | 7.0141 |  | 10
2017-06-27 | 9:25 | 1.7156 | 7.2762 |  | 10
2017-06-27 | 9:30 | 1.7101 | 7.0455 | 1 | 10 | 71.7256 | 76.9119
2017-06-27 | 9:35 | 1.7132 | 6.8694 |  | 10
2017-06-27 | 9:40 | 1.746 | 6.3315 |  | 10
2017-06-27 | 9:45 | 1.7343 | 6.351 | 1 | 10 | 64.1832 | 77.5069
2017-06-27 | 9:50 | 1.7374 | 6.1058 |  | 10
2017-06-27 | 9:55 | 1.7702 | 5.9052 |  | 10
2017-06-27 | 10:00 | 1.7366 | 5.7797 | 1 | 10 | 59.2413 | 77.868
2017-06-27 | 10:05 | 1.7569 | 6.1589 |  | 10
2017-06-27 | 10:10 | 1.7514 | 6.5273 |  | 10
2017-06-27 | 10:15 | 1.6953 | 7.1208 | 1 | 10 | 71.7239 | 78.4896
2017-06-27 | 10:20 | 1.7101 | 7.343 |  | 10
2017-06-27 | 10:25 | 1.7296 | 7.3701 |  | 10
2017-06-27 | 10:30 | 1.7 | 7.8273 | 1 | 10 | 79.4018 | 80.0143
2017-06-27 | 10:35 | 1.7296 | 7.7841 |  | 10
2017-06-27 | 10:40 | 1.7265 | 7.3529 |  | 10
2017-06-27 | 10:45 | 1.7475 | 8.0507 | 1 | 10 | 79.9567 | 80.5743
2017-06-27 | 10:50 | 1.767 | 7.8401 |  | 10
2017-06-27 | 10:55 | 1.7382 | 7.6313 |  | 10
2017-06-27 | 11:00 | 1.7273 | 7.8134 | 1 | 10 | 78.6 | 80.5271
2017-06-27 | 11:05 | 1.7514 | 7.7841 |  | 10
2017-06-27 | 11:10 | 1.7569 | 8.3218 |  | 10
2017-06-27 | 11:15 | 1.7507 | 7.7657 | 1 | 10 | 78.5766 | 80.1759
2017-06-27 | 11:20 | 1.7647 | 7.8262 |  | 10
2017-06-27 | 11:25 | 1.7452 | 7.9964 |  | 10
2017-06-27 | 11:30 | 1.7413 | 7.7972 | 1 | 10 | 79.1019 | 79.9334
2017-06-27 | 11:35 | 1.7444 | 7.7618 |  | 10
2017-06-27 | 11:40 | 1.7226 | 7.6559 |  | 10
2017-06-27 | 11:45 | 1.6968 | 8.1512 | 1 | 10 | 82.0365 | 80.3411
2017-06-27 | 11:50 | 1.4831 | 5.2555 |  | 1.5
2017-06-27 | 11:55 | 1.6945 | 2.6459 |  | 1.5
2017-06-27 | 12:00 | 1.6922 | 0 | 0 | 1.5 | 25 | 84.2608
2017-06-27 | 12:05 | 1.7023 | 0 |  | 1.5
2017-06-27 | 12:10 | 1.6851 | 0 |  | 1.5
2017-06-27 | 12:15 | 1.7374 | 0 | 0 | 1.5 | 25 | 85.4922
2017-06-27 | 12:20 | 1.7249 | 0 |  | 1.5
2017-06-27 | 12:25 | 1.7397 | 0 |  | 1.5
2017-06-27 | 12:30 | 1.7413 | 0 | 0 | 1.5 | 25 | 85.8307
2017-06-27 | 12:35 | 1.6633 | 0 |  | 1.5
2017-06-27 | 12:40 | 1.7062 | 0 |  | 1.5
2017-06-27 | 12:45 | 1.7351 | 0 | 0 | 1.5 | 25 | 87.3484
2017-06-27 | 12:50 | 1.7117 | 0 |  | 1.5
2017-06-27 | 12:55 | 1.7296 | 0 |  | 1.5
2017-06-27 | 13:00 | 1.7304 | 0 | 0 | 1.5 | 25 | 87.8919
2017-06-27 | 13:05 | 1.7241 | 0 |  | 1.5
2017-06-27 | 13:10 | 1.7179 | 0 |  | 1.5
2017-06-27 | 13:15 | 1.707 | 0 | 0 | 1.5 | 25 | 88.7655
2017-06-27 | 13:20 | 1.7296 | 0 |  | 1.5
2017-06-27 | 13:25 | 1.7475 | 0 |  | 1.5
2017-06-27 | 13:30 | 1.7452 | 0 | 0 | 1.5 | 25 | 89.0484
2017-06-27 | 13:35 | 1.7585 | 0 |  | 1.5
2017-06-27 | 13:40 | 1.7741 | 0 |  | 1.5
2017-06-27 | 13:45 | 1.7881 | 0 | 0 | 1.5 | 25 | 88.52
2017-06-27 | 13:50 | 1.7748 | 0 |  | 1.5
2017-06-27 | 13:55 | 1.7491 | 0 |  | 1.5
2017-06-27 | 14:00 | 1.7195 | 0 | 0 | 1.5 | 25 | 88.4966
2017-06-27 | 14:05 | 1.8006 | 0 |  | 1.5
2017-06-27 | 14:10 | 1.8404 | 0 |  | 1.5
2017-06-27 | 14:15 | 1.8185 | 0 | 0 | 1.5 | 25 | 87.2289
2017-06-27 | 14:20 | 1.7842 | 0 |  | 1.5
2017-06-27 | 14:25 | 1.7787 | 0 |  | 1.5
2017-06-27 | 14:30 | 1.785 | 0 | 0 | 1.5 | 25 | 86.5286
2017-06-27 | 14:35 | 1.8193 | 0 |  | 1.5
2017-06-27 | 14:40 | 1.8014 | 0 |  | 1.5
2017-06-27 | 14:45 | 1.7624 | 0 | 0 | 1.5 | 25 | 85.33
2017-06-27 | 14:50 | 1.7904 | 0 |  | 1.5
2017-06-27 | 14:55 | 1.7678 | 0 |  | 1.5
2017-06-27 | 15:00 | 1.7889 | 0 | 0 | 1.5 | 25 | 85.1888
2017-06-27 | 15:05 | 1.7826 | 0 |  | 1.5
2017-06-27 | 15:10 | 1.7725 | 0 |  | 1.5
2017-06-27 | 15:15 | 1.7483 | 0 | 0 | 1.5 | 25 | 84.6257
2017-06-27 | 15:20 | 1.7639 | 0 |  | 1.5
2017-06-27 | 15:25 | 1.7694 | 0 |  | 1.5
2017-06-27 | 15:30 | 1.7429 | 0 | 0 | 1.5 | 25 | 84.4319
2017-06-27 | 15:35 | 1.778 | 0 |  | 1.5
2017-06-27 | 15:40 | 1.7468 | 0 |  | 1.5
2017-06-27 | 15:45 | 1.7678 | 0 | 0 | 1.5 | 25 | 84.2874
2017-06-27 | 15:50 | 1.7842 | 0 |  | 1.5
2017-06-27 | 15:55 | 1.7569 | 0 |  | 1.5
2017-06-27 | 16:00 | 1.7436 | 0 | 0 | 1.5 | 25 | 83.7601
2017-06-27 | 16:05 | 1.7366 | 0 |  | 1.5
2017-06-27 | 16:10 | 1.7304 | 0 |  | 1.5
2017-06-27 | 16:15 | 1.7538 | 0 | 0 | 1.5 | 25 | 83.9624
2017-06-27 | 16:20 | 1.7507 | 0 |  | 1.5
2017-06-27 | 16:25 | 1.7468 | 0 |  | 1.5
2017-06-27 | 16:30 | 1.7429 | 0 | 0 | 1.5 | 25 | 83.9842
2017-06-27 | 16:35 | 1.7733 | 0 |  | 1.5
2017-06-27 | 16:40 | 1.7585 | 0 |  | 1.5
2017-06-27 | 16:45 | 1.7756 | 0 | 0 | 1.5 | 25 | 83.5428
2017-06-27 | 16:50 | 1.76 | 0 |  | 1.5
2017-06-27 | 16:55 | 1.7803 | 0 |  | 1.5
2017-06-27 | 17:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 83.214
2017-06-27 | 17:05 | 1.7444 | 0 |  | 1.5
2017-06-27 | 17:10 | 1.753 | 0 |  | 1.5
2017-06-27 | 17:15 | 1.7772 | 0 | 0 | 1.5 | 25 | 82.9193
2017-06-27 | 17:20 | 1.7585 | 0 |  | 1.5
2017-06-27 | 17:25 | 1.7772 | 0 |  | 1.5
2017-06-27 | 17:30 | 1.7756 | 0 | 0 | 1.5 | 25 | 82.3233
2017-06-27 | 17:35 | 1.767 | 0 |  | 1.5
2017-06-27 | 17:40 | 1.7834 | 0 |  | 1.5
2017-06-27 | 17:45 | 1.767 | 0 | 0 | 1.5 | 25 | 81.7542
2017-06-27 | 17:50 | 1.7686 | 0 |  | 1.5
2017-06-27 | 17:55 | 1.7694 | 0 |  | 1.5
2017-06-27 | 18:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 81.2775
2017-06-27 | 18:05 | 1.7577 | 0 |  | 1.5
2017-06-27 | 18:10 | 1.7803 | 0 |  | 1.5
2017-06-27 | 18:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 81.0726
2017-06-27 | 18:20 | 1.7569 | 0 |  | 1.5
2017-06-27 | 18:25 | 1.7436 | 0 |  | 1.5
2017-06-27 | 18:30 | 1.7608 | 0 | 0 | 1.5 | 25 | 80.8349
2017-06-27 | 18:35 | 1.7358 | 0 |  | 1.5
2017-06-27 | 18:40 | 1.7483 | 0 |  | 1.5
2017-06-27 | 18:45 | 1.7241 | 0 | 0 | 1.5 | 25 | 80.5808
2017-06-27 | 18:50 | 1.7499 | 0 |  | 1.5
2017-06-27 | 18:55 | 1.7897 | 0 |  | 1.5
2017-06-27 | 19:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 80.4363
2017-06-27 | 19:05 | 1.7327 | 0 |  | 1.5
2017-06-27 | 19:10 | 1.7514 | 0 |  | 1.5
2017-06-27 | 19:15 | 1.7343 | 0 | 0 | 1.5 | 25 | 80.448
2017-06-27 | 19:20 | 1.7686 | 0 |  | 1.5
2017-06-27 | 19:25 | 1.7546 | 0 |  | 1.5
2017-06-27 | 19:30 | 1.7561 | 0 | 0 | 1.5 | 25 | 80.2491
2017-06-27 | 19:35 | 1.7577 | 0 |  | 1.5
2017-06-27 | 19:40 | 1.7647 | 0 |  | 1.5
2017-06-27 | 19:45 | 1.7351 | 0 | 0 | 1.5 | 25 | 80.0791
2017-06-27 | 19:50 | 1.7397 | 0 |  | 1.5
2017-06-27 | 19:55 | 1.7499 | 0 |  | 1.5
2017-06-27 | 20:00 | 1.7179 | 0 | 0 | 1.5 | 25 | 80.3498
2017-06-27 | 20:05 | 1.7288 | 0 |  | 1.5
2017-06-27 | 20:10 | 1.7538 | 0 |  | 1.5
2017-06-27 | 20:15 | 1.7296 | 0 | 0 | 1.5 | 25 | 80.6957
2017-06-27 | 20:20 | 1.7709 | 0 |  | 1.5
2017-06-27 | 20:25 | 1.7507 | 0 |  | 1.5
2017-06-27 | 20:30 | 1.7358 | 0 | 0 | 1.5 | 25 | 80.7429
2017-06-27 | 20:35 | 1.7717 | 0 |  | 1.5
2017-06-27 | 20:40 | 1.7569 | 0 |  | 1.5
2017-06-27 | 20:45 | 1.753 | 0 | 0 | 1.5 | 25 | 80.6491
2017-06-27 | 20:50 | 1.7273 | 0 |  | 1.5
2017-06-27 | 20:55 | 1.7483 | 0 |  | 1.5
2017-06-27 | 21:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 80.4726
2017-06-27 | 21:05 | -0.1073 | 0 |  | 1.5
2017-06-27 | 21:10 | -0.1073 | 0 |  | 1.5
2017-06-27 | 21:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 21:20 | -0.10808 | 0 |  | 1.5
2017-06-27 | 21:25 | -0.10808 | 0 |  | 1.5
2017-06-27 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 21:35 | -0.10808 | 0 |  | 1.5
2017-06-27 | 21:40 | -0.10808 | 0 |  | 1.5
2017-06-27 | 21:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 21:50 | -0.10808 | 0 |  | 1.5
2017-06-27 | 21:55 | -0.10808 | 0 |  | 1.5
2017-06-27 | 22:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 22:05 | -0.10808 | 0 |  | 1.5
2017-06-27 | 22:10 | -0.10808 | 0 |  | 1.5
2017-06-27 | 22:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 22:20 | -0.10886 | 0 |  | 1.5
2017-06-27 | 22:25 | -0.10886 | 0 |  | 1.5
2017-06-27 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 22:35 | -0.10808 | 0 |  | 1.5
2017-06-27 | 22:40 | -0.10808 | 0 |  | 1.5
2017-06-27 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 22:50 | -0.10808 | 0 |  | 1.5
2017-06-27 | 22:55 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 23:05 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:10 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 23:20 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:25 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 23:35 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:40 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-27 | 23:50 | -0.1073 | 0 |  | 1.5
2017-06-27 | 23:55 | -0.1073 | 0 |  | 1.5
2017-06-28 | 0:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-28 | 0:05 | -0.10652 | 0 |  | 1.5
2017-06-28 | 0:10 | -0.11042 | 0 |  | 1.5
2017-06-28 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-28 | 0:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 0:20 | -0.10886 | 0 |  | 1.5
2017-06-28 | 0:25 | -0.10808 | 0 |  | 1.5
2017-06-28 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 0:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 0:35 | -0.10886 | 0 |  | 1.5
2017-06-28 | 0:40 | -0.10886 | 0 |  | 1.5
2017-06-28 | 0:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-28 | 0:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 0:50 | -0.10808 | 0 |  | 1.5
2017-06-28 | 0:55 | -0.10886 | 0 |  | 1.5
2017-06-28 | 1:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-06-28 | 1:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 1:05 | -0.10886 | 0 |  | 1.5
2017-06-28 | 1:10 | -0.10886 | 0 |  | 1.5
2017-06-28 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 1:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 1:20 | -0.10886 | 0 |  | 1.5
2017-06-28 | 1:25 | -0.1112 | 0 |  | 1.5
2017-06-28 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-28 | 1:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 1:35 | -0.1112 | 0 |  | 1.5
2017-06-28 | 1:40 | -0.10964 | 0 |  | 1.5
2017-06-28 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-28 | 1:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 1:50 | -0.11198 | 0 |  | 1.5
2017-06-28 | 1:55 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-28 | 2:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 2:05 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:10 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-28 | 2:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 2:20 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:25 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:30 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 2:30 |  | 0 |  | 1.5 |  | 0
2017-06-28 | 2:35 | -0.11198 | 0 |  | 1.5
2017-06-28 | 2:40 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:45 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 2:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 2:50 | -0.1112 | 0 |  | 1.5
2017-06-28 | 2:55 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:00 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 3:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 3:05 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:10 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:15 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 3:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 3:20 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:25 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:30 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 3:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 3:35 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:40 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0
2017-06-28 | 3:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 3:50 | -0.11198 | 0 |  | 1.5
2017-06-28 | 3:55 | -0.11198 | 0 |  | 1.5
2017-06-28 | 4:00 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 4:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 4:05 | -0.11198 | 0 |  | 1.5
2017-06-28 | 4:10 | -0.11198 | 0 |  | 1.5
2017-06-28 | 4:15 | -0.11276 | 0 | 0 | 1.5 | 0
2017-06-28 | 4:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 4:20 | -0.11198 | 0 |  | 1.5
2017-06-28 | 4:25 | -0.11276 | 0 |  | 1.5
2017-06-28 | 4:30 | -0.11276 | 0 | 0 | 1.5 | 0
2017-06-28 | 4:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 4:35 | -0.11198 | 0 |  | 1.5
2017-06-28 | 4:40 | -0.11276 | 0 |  | 1.5
2017-06-28 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0
2017-06-28 | 4:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 4:50 | -0.11276 | 0 |  | 1.5
2017-06-28 | 4:55 | -0.11276 | 0 |  | 1.5
2017-06-28 | 5:00 | -0.11276 | 0 | 1 | 0 | 0
2017-06-28 | 5:00 |  |  |  | 0 |  | 25
2017-06-28 | 5:05 | 2.4269 | 6.1419 |  | 10
2017-06-28 | 5:10 | 2.1672 | 10 |  | 10
2017-06-28 | 5:15 | 2.0751 | 10 | 1 | 10 | 100
2017-06-28 | 5:15 |  |  |  | 10 |  | 87.8108
2017-06-28 | 5:20 | 2.0393 | 9.6537 |  | 10
2017-06-28 | 5:25 | 1.9371 | 9.1594 |  | 10
2017-06-28 | 5:30 | 1.8583 | 8.5333 | 1 | 10 | 86.1236
2017-06-28 | 5:30 |  |  |  | 10 |  | 81.8941
2017-06-28 | 5:35 | 1.8365 | 8.2557 |  | 10
2017-06-28 | 5:40 | 1.7998 | 8.0038 |  | 10
2017-06-28 | 5:45 | 1.8099 | 7.7527 | 1 | 10 | 78.1801
2017-06-28 | 5:45 |  |  |  | 10 |  | 79.5122
2017-06-28 | 5:50 | 1.799 | 7.5308 |  | 10
2017-06-28 | 5:55 | 1.7912 | 6.9924 |  | 10
2017-06-28 | 6:00 | 1.7873 | 6.9364 | 1 | 10 | 70.1651
2017-06-28 | 6:00 |  |  |  | 10 |  | 78.0664
2017-06-28 | 6:05 | 1.7694 | 6.9521 |  | 10
2017-06-28 | 6:10 | 1.7819 | 7.0754 |  | 10
2017-06-28 | 6:15 | 1.7343 | 7.2002 | 1 | 10 | 72.7303
2017-06-28 | 6:15 |  |  |  | 10 |  | 77.4645
2017-06-28 | 6:20 | 1.7694 | 7.0211 |  | 10
2017-06-28 | 6:25 | 1.767 | 6.7562 |  | 10
2017-06-28 | 6:30 | 1.7811 | 6.5641 | 1 | 10 | 66.594
2017-06-28 | 6:30 |  |  |  | 10 |  | 76.8532
2017-06-28 | 6:35 | 1.7787 | 6.6396 |  | 10
2017-06-28 | 6:40 | 1.7733 | 6.5374 |  | 10
2017-06-28 | 6:45 | 1.7569 | 6.5935 | 1 | 10 | 66.7202
2017-06-28 | 6:45 |  |  |  | 10 |  | 76.3278
2017-06-28 | 6:50 | 1.7546 | 6.45 |  | 10
2017-06-28 | 6:55 | 1.7647 | 5.9292 |  | 10
2017-06-28 | 7:00 | 1.7577 | 5.8998 | 1 | 10 | 60.2229
2017-06-28 | 7:00 |  |  |  | 10 |  | 75.9862
2017-06-28 | 7:05 | 1.7694 | 6.0543 |  | 10
2017-06-28 | 7:10 | 1.7429 | 5.9891 |  | 10
2017-06-28 | 7:15 | 1.7522 | 6.6133 | 1 | 10 | 66.9011
2017-06-28 | 7:15 |  |  |  | 10 |  | 75.7265
2017-06-28 | 7:20 | 1.7663 | 6.0417 |  | 10
2017-06-28 | 7:25 | 1.7514 | 5.3508 |  | 10
2017-06-28 | 7:30 | 1.753 | 4.9876 | 1 | 10 | 51.8417
2017-06-28 | 7:30 |  |  |  | 10 |  | 75.4813
2017-06-28 | 7:35 | 1.7514 | 5.4492 |  | 10
2017-06-28 | 7:40 | 1.7686 | 5.6687 |  | 10
2017-06-28 | 7:45 | 1.7819 | 4.8357 | 1 | 10 | 50.3782
2017-06-28 | 7:45 |  |  |  | 10 |  | 75.2691
2017-06-28 | 7:50 | 1.7405 | 4.7775 |  | 10
2017-06-28 | 7:55 | 1.739 | 4.5254 |  | 10
2017-06-28 | 8:00 | 1.7468 | 4.0972 | 1 | 10 | 43.0836
2017-06-28 | 8:00 |  |  |  | 10 |  | 75.3412
2017-06-28 | 8:05 | 1.7499 | 4.5691 |  | 10
2017-06-28 | 8:10 | 1.7452 | 4.8927 |  | 10
2017-06-28 | 8:15 | 1.7343 | 4.8025 | 1 | 10 | 49.7163
2017-06-28 | 8:15 |  |  |  | 10 |  | 75.4988
2017-06-28 | 8:20 | 1.7405 | 5.2138 |  | 10
2017-06-28 | 8:25 | 1.739 | 5.054 |  | 10
2017-06-28 | 8:30 | 1.7491 | 4.7883 | 1 | 10 | 49.4
2017-06-28 | 8:30 |  |  |  | 10 |  | 75.5386
2017-06-28 | 8:35 | 1.7491 | 5.1555 |  | 10
2017-06-28 | 8:40 | 1.7522 | 5.6008 |  | 10
2017-06-28 | 8:45 | 1.7507 | 5.5899 | 1 | 10 | 56.974
2017-06-28 | 8:45 |  |  |  | 10 |  | 75.4207
2017-06-28 | 8:50 | 1.7444 | 6.1124 |  | 10
2017-06-28 | 8:55 | 1.7507 | 5.7532 |  | 10
2017-06-28 | 9:00 | 1.739 | 5.4282 | 1 | 10 | 55.6071
2017-06-28 | 9:00 |  |  |  | 10 |  | 75.4884
2017-06-28 | 9:05 | 1.753 | 5.2577 |  | 10
2017-06-28 | 9:10 | 1.7327 | 5.268 |  | 10
2017-06-28 | 9:15 | 1.7733 | 4.976 | 1 | 10 | 51.8028
2017-06-28 | 9:15 | 1.7733 | 4.976 |  | 10 |  | 75.693
2017-06-28 | 9:20 | 1.7468 | 5.0123 |  | 10
2017-06-28 | 9:25 | 1.7382 | 5.1525 |  | 10
2017-06-28 | 9:30 | 1.7624 | 5.6133 | 1 | 10 | 56.7921
2017-06-28 | 9:30 |  |  |  | 10 |  | 75.7396
2017-06-28 | 9:35 | 1.7413 | 5.8225 |  | 10
2017-06-28 | 9:40 | 1.739 | 5.969 |  | 10
2017-06-28 | 9:45 | 1.7507 | 5.5905 | 1 | 10 | 57.8
2017-06-28 | 9:45 |  |  |  | 10 |  | 75.7897
2017-06-28 | 9:50 | 1.7631 | 5.347 |  | 10
2017-06-28 | 9:55 | 1.7374 | 5.2116 |  | 10
2017-06-28 | 10:00 | 1.7577 | 5.0577 | 1 | 10 | 52.0034
2017-06-28 | 10:00 |  |  |  | 10 |  | 75.7404
2017-06-28 | 10:05 | 1.7499 | 5.5787 |  | 10
2017-06-28 | 10:10 | 1.7374 | 5.7613 |  | 10
2017-06-28 | 10:15 | 1.7304 | 5.9415 | 1 | 10 | 60.2202
2017-06-28 | 10:15 | 1.7304 | 5.9415 |  | 10 |  | 75.955
2017-06-28 | 10:20 | 1.7834 | 5.7672 |  | 10
2017-06-28 | 10:25 | 1.7881 | 5.9883 |  | 10
2017-06-28 | 10:30 | 1.7507 | 5.9471 | 1 | 10 | 60.6666
2017-06-28 | 10:30 |  |  |  | 10 |  | 75.3333
2017-06-28 | 10:35 | 1.7468 | 5.5282 |  | 10
2017-06-28 | 10:40 | 1.7288 | 5.9581 |  | 10
2017-06-28 | 10:45 | 1.746 | 5.7152 | 1 | 10 | 58.6759
2017-06-28 | 10:45 |  |  |  | 10 |  | 75.4199
2017-06-28 | 10:50 | 1.7296 | 6.257 |  | 10
2017-06-28 | 10:55 | 1.7421 | 6.1948 |  | 10
2017-06-28 | 11:00 | 1.799 | 5.8438 | 1 | 10 | 59.9175
2017-06-28 | 11:00 |  |  |  | 10 |  | 75.6631
2017-06-28 | 11:05 | 1.7631 | 5.5678 |  | 10
2017-06-28 | 11:10 | 1.7912 | 5.6789 |  | 10
2017-06-28 | 11:15 | 1.7296 | 5.6501 | 1 | 10 | 57.0571
2017-06-28 | 11:15 |  |  |  | 10 |  | 75.7563
2017-06-28 | 11:20 | 1.753 | 5.1873 |  | 10
2017-06-28 | 11:25 | 1.7483 | 5.5493 |  | 10
2017-06-28 | 11:30 | 1.7374 | 6.1633 | 1 | 10 | 62.5214
2017-06-28 | 11:30 |  |  |  | 10 |  | 76.2
2017-06-28 | 11:35 | 1.7249 | 6.2809 |  | 10
2017-06-28 | 11:40 | 1.7374 | 6.1905 |  | 10
2017-06-28 | 11:45 | 1.7663 | 6.019 | 1 | 10 | 60.4618
2017-06-28 | 11:45 |  |  |  | 10 |  | 76.4234
2017-06-28 | 11:50 | 1.7117 | 6.5348 |  | 10
2017-06-28 | 11:55 | 1.7156 | 6.5656 |  | 10
2017-06-28 | 12:00 | 1.7234 | 6.2134 | 1 | 10 | 63.1066
2017-06-28 | 12:00 |  |  |  | 10 |  | 77.2567
2017-06-28 | 12:05 | 1.7273 | 5.7986 |  | 10
2017-06-28 | 12:10 | 1.7499 | 5.3008 |  | 10
2017-06-28 | 12:15 | 1.746 | 5.8441 | 1 | 10 | 58.5423
2017-06-28 | 12:15 |  |  |  | 10 |  | 77.7375
2017-06-28 | 12:20 | 1.5213 | 4.6455 |  | 1.5
2017-06-28 | 12:25 | 1.6898 | 1.0323 |  | 1.5
2017-06-28 | 12:30 | 1.7179 | 0 | 0 | 1.5 | 25
2017-06-28 | 12:30 |  |  |  | 1.5 |  | 80.946
2017-06-28 | 12:35 | 1.7257 | 0 |  | 1.5
2017-06-28 | 12:40 | 1.7452 | 0 |  | 1.5
2017-06-28 | 12:45 | 1.7241 | 0 | 0 | 1.5 | 25
2017-06-28 | 12:45 |  |  |  | 1.5 |  | 81.3058
2017-06-28 | 12:50 | 1.7717 | 0 |  | 1.5
2017-06-28 | 12:55 | 1.7156 | 0 |  | 1.5
2017-06-28 | 13:00 | 1.7054 | 0 | 0 | 1.5 | 25
2017-06-28 | 13:00 |  |  |  | 1.5 |  | 81.8794
2017-06-28 | 13:05 | 1.7132 | 0 |  | 1.5
2017-06-28 | 13:10 | 1.7218 | 0 |  | 1.5
2017-06-28 | 13:15 | 1.7039 | 0 | 0 | 1.5 | 25
2017-06-28 | 13:15 |  |  |  | 1.5 |  | 82.7785
2017-06-28 | 13:20 | 1.7117 | 0 |  | 1.5
2017-06-28 | 13:25 | 1.6649 | 0 |  | 1.5
2017-06-28 | 13:30 | 1.7234 | 0 | 0 | 1.5 | 25
2017-06-28 | 13:30 |  |  |  | 1.5 |  | 83.9684
2017-06-28 | 13:35 | 1.7405 | 0 |  | 1.5
2017-06-28 | 13:40 | 1.7241 | 0 |  | 1.5
2017-06-28 | 13:45 | 1.7514 | 0 | 0 | 1.5 | 25
2017-06-28 | 13:45 |  |  |  | 1.5 |  | 84.6569
2017-06-28 | 13:50 | 1.728 | 0 |  | 1.5
2017-06-28 | 13:55 | 1.7444 | 0 |  | 1.5
2017-06-28 | 14:00 | 1.7507 | 0 | 0 | 1.5 | 25
2017-06-28 | 14:00 |  |  |  | 1.5 |  | 84.9152
2017-06-28 | 14:05 | 1.746 | 0 |  | 1.5
2017-06-28 | 14:10 | 1.7678 | 0 |  | 1.5
2017-06-28 | 14:15 | 1.7444 | 0 | 0 | 1.5 | 25
2017-06-28 | 14:15 |  |  |  | 1.5 |  | 84.8292
2017-06-28 | 14:20 | 1.7616 | 0 |  | 1.5
2017-06-28 | 14:25 | 1.7795 | 0 |  | 1.5
2017-06-28 | 14:30 | 1.7561 | 0 | 0 | 1.5 | 25
2017-06-28 | 14:30 |  |  |  | 1.5 |  | 84.4355
2017-06-28 | 14:35 | 1.7592 | 0 |  | 1.5
2017-06-28 | 14:40 | 1.7187 | 0 |  | 1.5
2017-06-28 | 14:45 | 1.7522 | 0 | 0 | 1.5 | 25
2017-06-28 | 14:45 |  |  |  | 1.5 |  | 84.5395
2017-06-28 | 14:50 | 1.7514 | 0 |  | 1.5
2017-06-28 | 14:55 | 1.7546 | 0 |  | 1.5
2017-06-28 | 15:00 | 1.7366 | 0 | 0 | 1.5 | 25
2017-06-28 | 15:00 |  |  |  | 1.5 |  | 84.596
2017-06-28 | 15:05 | 1.7444 | 0 |  | 1.5
2017-06-28 | 15:10 | 1.7304 | 0 |  | 1.5
2017-06-28 | 15:15 | 1.7358 | 0 | 0 | 1.5 | 25
2017-06-28 | 15:15 |  |  |  | 1.5 |  | 84.9438
2017-06-28 | 15:20 | 1.7546 | 0 |  | 1.5
2017-06-28 | 15:25 | 1.7522 | 0 |  | 1.5
2017-06-28 | 15:30 | 1.739 | 0 | 0 | 1.5 | 25
2017-06-28 | 15:30 |  |  |  | 1.5 |  | 85.0917
2017-06-28 | 15:35 | 1.7234 | 0 |  | 1.5
2017-06-28 | 15:40 | 1.7421 | 0 |  | 1.5
2017-06-28 | 15:45 | 1.7514 | 0 | 0 | 1.5 | 25
2017-06-28 | 15:45 |  |  |  | 1.5 |  | 85.5015
2017-06-28 | 15:50 | 1.7569 | 0 |  | 1.5
2017-06-28 | 15:55 | 1.7631 | 0 |  | 1.5
2017-06-28 | 16:00 | 1.7351 | 0 | 0 | 1.5 | 25
2017-06-28 | 16:00 |  |  |  | 1.5 |  | 85.6921
2017-06-28 | 16:05 | 1.7405 | 0 |  | 1.5
2017-06-28 | 16:10 | 1.7717 | 0 |  | 1.5
2017-06-28 | 16:15 | 1.721 | 0 | 0 | 1.5 | 25
2017-06-28 | 16:15 |  |  |  | 1.5 |  | 85.6957
2017-06-28 | 16:20 | 1.746 | 0 |  | 1.5
2017-06-28 | 16:25 | 1.7304 | 0 |  | 1.5
2017-06-28 | 16:30 | 1.7397 | 0 | 0 | 1.5 | 25
2017-06-28 | 16:30 |  |  |  | 1.5 |  | 85.7786
2017-06-28 | 16:35 | 1.7616 | 0 |  | 1.5
2017-06-28 | 16:40 | 1.7335 | 0 |  | 1.5
2017-06-28 | 16:45 | 1.7514 | 0 | 0 | 1.5 | 25
2017-06-28 | 16:45 |  |  |  | 1.5 |  | 85.8631
2017-06-28 | 16:50 | 1.7358 | 0 |  | 1.5
2017-06-28 | 16:55 | 1.7452 | 0 |  | 1.5
2017-06-28 | 17:00 | 1.7858 | 0 | 0 | 1.5 | 25
2017-06-28 | 17:00 |  |  |  | 1.5 |  | 85.7139
2017-06-28 | 17:05 | 1.7319 | 0 |  | 1.5
2017-06-28 | 17:10 | 1.7577 | 0 |  | 1.5
2017-06-28 | 17:15 | 1.7561 | 0 | 0 | 1.5 | 25
2017-06-28 | 17:15 |  |  |  | 1.5 |  | 85.6122
2017-06-28 | 17:20 | 1.7366 | 0 |  | 1.5
2017-06-28 | 17:25 | 1.7655 | 0 |  | 1.5
2017-06-28 | 17:30 | 1.7569 | 0 | 0 | 1.5 | 25
2017-06-28 | 17:30 |  |  |  | 1.5 |  | 85.4038
2017-06-28 | 17:35 | 1.7468 | 0 |  | 1.5
2017-06-28 | 17:40 | 1.7639 | 0 |  | 1.5
2017-06-28 | 17:45 | 1.7538 | 0 | 0 | 1.5 | 25
2017-06-28 | 17:45 |  |  |  | 1.5 |  | 84.959
2017-06-28 | 17:50 | 1.7452 | 0 |  | 1.5
2017-06-28 | 17:55 | 1.7873 | 0 |  | 1.5
2017-06-28 | 18:00 | 1.7702 | 0 | 0 | 1.5 | 25
2017-06-28 | 18:00 |  |  |  | 1.5 |  | 84.4572
2017-06-28 | 18:05 | 1.7834 | 0 |  | 1.5
2017-06-28 | 18:10 | 1.7772 | 0 |  | 1.5
2017-06-28 | 18:15 | 1.753 | 0 | 0 | 1.5 | 25
2017-06-28 | 18:15 |  |  |  | 1.5 |  | 83.5387
2017-06-28 | 18:20 | 1.785 | 0 |  | 1.5
2017-06-28 | 18:25 | 1.7491 | 0 |  | 1.5
2017-06-28 | 18:30 | 1.7803 | 0 | 0 | 1.5 | 25
2017-06-28 | 18:30 |  |  |  | 1.5 |  | 82.9688
2017-06-28 | 18:35 | 1.7553 | 0 |  | 1.5
2017-06-28 | 18:40 | 1.7943 | 0 |  | 1.5
2017-06-28 | 18:45 | 1.7663 | 0 | 0 | 1.5 | 25
2017-06-28 | 18:45 |  |  |  | 1.5 |  | 82.4908
2017-06-28 | 18:50 | 1.7553 | 0 |  | 1.5
2017-06-28 | 18:55 | 1.767 | 0 |  | 1.5
2017-06-28 | 19:00 | 1.7709 | 0 | 0 | 1.5 | 25
2017-06-28 | 19:00 |  |  |  | 1.5 |  | 82.122
2017-06-28 | 19:05 | 1.7982 | 0 |  | 1.5
2017-06-28 | 19:10 | 1.7538 | 0 |  | 1.5
2017-06-28 | 19:15 | 1.7655 | 0 | 0 | 1.5 | 25
2017-06-28 | 19:15 |  |  |  | 1.5 |  | 81.7005
2017-06-28 | 19:20 | 1.7631 | 0 |  | 1.5
2017-06-28 | 19:25 | 1.7483 | 0 |  | 1.5
2017-06-28 | 19:30 | 1.7444 | 0 | 0 | 1.5 | 25
2017-06-28 | 19:30 |  | 0 |  | 1.5 |  | 81.6696
2017-06-28 | 19:35 | 1.7499 | 0 |  | 1.5
2017-06-28 | 19:40 | 1.7366 | 0 |  | 1.5
2017-06-28 | 19:45 | 1.7397 | 0 | 0 | 1.5 | 25
2017-06-28 | 19:45 |  |  |  | 1.5 |  | 81.7534
2017-06-28 | 19:50 | 1.7514 | 0 |  | 1.5
2017-06-28 | 19:55 | 1.7616 | 0 |  | 1.5
2017-06-28 | 20:00 | 1.7163 | 0 | 0 | 1.5 | 25
2017-06-28 | 20:00 |  |  |  | 1.5 |  | 81.4966
2017-06-28 | 20:05 | 1.7546 | 0 |  | 1.5
2017-06-28 | 20:10 | 1.7709 | 0 |  | 1.5
2017-06-28 | 20:15 | 1.7514 | 0 | 0 | 1.5 | 25
2017-06-28 | 20:15 |  |  |  | 1.5 |  | 81.0392
2017-06-28 | 20:20 | 1.7507 | 0 |  | 1.5
2017-06-28 | 20:25 | 1.7748 | 0.085456 |  | 1.5
2017-06-28 | 20:30 | 1.7421 | 0.47368 | 0 | 1.5 | 29.2833
2017-06-28 | 20:30 |  |  |  | 1.5 |  | 80.9117
2017-06-28 | 20:35 | 1.7343 | 0.57185 |  | 1.5
2017-06-28 | 20:40 | 1.7702 | 0.75929 |  | 1.5
2017-06-28 | 20:45 | 1.9402 | 1.3607 | 1 | 10 | 36.1067
2017-06-28 | 20:45 |  |  |  | 10 |  | 80.2692
2017-06-28 | 20:50 | 1.8942 | 4.2896 |  | 10
2017-06-28 | 20:55 | 1.7982 | 6.1709 |  | 10
2017-06-28 | 21:00 | 1.7811 | 6.4307 | 0 | 1.5 | 87.1076
2017-06-28 | 21:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 21:05 | -0.10496 | 0 |  | 1.5
2017-06-28 | 21:10 | -0.10652 | 0 |  | 1.5
2017-06-28 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-06-28 | 21:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 21:20 | -0.10652 | 0 |  | 1.5
2017-06-28 | 21:25 | -0.1073 | 0 |  | 1.5
2017-06-28 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-06-28 | 21:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 21:35 | -0.1073 | 0 |  | 1.5
2017-06-28 | 21:40 | -0.1073 | 0 |  | 1.5
2017-06-28 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-06-28 | 21:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 21:50 | -0.1073 | 0 |  | 1.5
2017-06-28 | 21:55 | -0.1073 | 0 |  | 1.5
2017-06-28 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-06-28 | 22:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 22:05 | -0.1073 | 0 |  | 1.5
2017-06-28 | 22:10 | -0.10808 | 0 |  | 1.5
2017-06-28 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 22:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 22:20 | -0.10808 | 0 |  | 1.5
2017-06-28 | 22:25 | -0.10808 | 0 |  | 1.5
2017-06-28 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 22:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 22:35 | -0.10808 | 0 |  | 1.5
2017-06-28 | 22:40 | -0.10808 | 0 |  | 1.5
2017-06-28 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 22:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 22:50 | -0.10808 | 0 |  | 1.5
2017-06-28 | 22:55 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 23:00 |  |  |  | 1.5 |  | 0
2017-06-28 | 23:05 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:10 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 23:15 |  |  |  | 1.5 |  | 0
2017-06-28 | 23:20 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:25 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 23:30 |  |  |  | 1.5 |  | 0
2017-06-28 | 23:35 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:40 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-28 | 23:45 |  |  |  | 1.5 |  | 0
2017-06-28 | 23:50 | -0.10808 | 0 |  | 1.5
2017-06-28 | 23:55 | -0.1073 | 0 |  | 1.5
2017-06-29 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-06-29 | 0:00 |  |  |  | 1.5 |  | 0
2017-06-29 | 0:05 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:10 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 0:20 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:25 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 0:35 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:40 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 0:50 | -0.10808 | 0 |  | 1.5
2017-06-29 | 0:55 | -0.10808 | 0 |  | 1.5
2017-06-29 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 1:05 | -0.10808 | 0 |  | 1.5
2017-06-29 | 1:10 | -0.10808 | 0 |  | 1.5
2017-06-29 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 1:20 | -0.10808 | 0 |  | 1.5
2017-06-29 | 1:25 | -0.11042 | 0 |  | 1.5
2017-06-29 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 1:35 | -0.1112 | 0 |  | 1.5
2017-06-29 | 1:40 | -0.10964 | 0 |  | 1.5
2017-06-29 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 1:50 | -0.11042 | 0 |  | 1.5
2017-06-29 | 1:55 | -0.10964 | 0 |  | 1.5
2017-06-29 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 2:05 | -0.11042 | 0 |  | 1.5
2017-06-29 | 2:10 | -0.11042 | 0 |  | 1.5
2017-06-29 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 2:20 | -0.11042 | 0 |  | 1.5
2017-06-29 | 2:25 | -0.11042 | 0 |  | 1.5
2017-06-29 | 2:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 2:35 | -0.11042 | 0 |  | 1.5
2017-06-29 | 2:40 | -0.1112 | 0 |  | 1.5
2017-06-29 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 2:50 | -0.11042 | 0 |  | 1.5
2017-06-29 | 2:55 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 3:05 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:10 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 3:20 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:25 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 3:35 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:40 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 3:50 | -0.1112 | 0 |  | 1.5
2017-06-29 | 3:55 | -0.1112 | 0 |  | 1.5
2017-06-29 | 4:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 4:05 | -0.11198 | 0 |  | 1.5
2017-06-29 | 4:10 | -0.11198 | 0 |  | 1.5
2017-06-29 | 4:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 4:20 | -0.11198 | 0 |  | 1.5
2017-06-29 | 4:25 | -0.11276 | 0 |  | 1.5
2017-06-29 | 4:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 4:35 | -0.11198 | 0 |  | 1.5
2017-06-29 | 4:40 | -0.11198 | 0 |  | 1.5
2017-06-29 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 4:50 | -0.11198 | 0 |  | 1.5
2017-06-29 | 4:55 | -0.11198 | 0 |  | 1.5
2017-06-29 | 5:00 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 5:05 | 2.5572 | 5.9486 |  | 10
2017-06-29 | 5:10 | 2.2374 | 9.7197 |  | 10
2017-06-29 | 5:15 | 2.1134 | 8.9919 | 1 | 10 | 92.131 | 86.467
2017-06-29 | 5:20 | 2.0127 | 8.5461 |  | 10
2017-06-29 | 5:25 | 1.9402 | 7.8084 |  | 10
2017-06-29 | 5:30 | 1.8684 | 7.4595 | 1 | 10 | 76.9021 | 80.6933
2017-06-29 | 5:35 | 1.8567 | 7.1691 |  | 10
2017-06-29 | 5:40 | 1.7865 | 6.6543 |  | 10
2017-06-29 | 5:45 | 1.7904 | 6.6628 | 1 | 10 | 69.0597 | 78.6487
2017-06-29 | 5:50 | 1.7967 | 6.2911 |  | 10
2017-06-29 | 5:55 | 1.7795 | 6.2389 |  | 10
2017-06-29 | 6:00 | 1.7803 | 6.1414 | 1 | 10 | 64.1566 | 77.8444
2017-06-29 | 6:05 | 1.7444 | 6.3791 |  | 10
2017-06-29 | 6:10 | 1.7483 | 6.9275 |  | 10
2017-06-29 | 6:15 | 1.7577 | 6.9876 | 1 | 10 | 72.1808 | 77.6404
2017-06-29 | 6:20 | 1.7335 | 7.266 |  | 10
2017-06-29 | 6:25 | 1.7655 | 7.1428 |  | 10
2017-06-29 | 6:30 | 1.7514 | 7.1992 | 1 | 10 | 74.0813 | 77.7577
2017-06-29 | 6:35 | 1.7452 | 7.2027 |  | 10
2017-06-29 | 6:40 | 1.7756 | 6.8036 |  | 10
2017-06-29 | 6:45 | 1.7585 | 6.9375 | 1 | 10 | 72.0363 | 77.3028
2017-06-29 | 6:50 | 1.7936 | 6.5563 |  | 10
2017-06-29 | 6:55 | 1.7678 | 6.3627 |  | 10
2017-06-29 | 7:00 | 1.7483 | 5.9321 | 1 | 10 | 62.3283 | 76.7464
2017-06-29 | 7:05 | 1.7678 | 5.9622 |  | 10
2017-06-29 | 7:10 | 1.7538 | 6.221 |  | 10
2017-06-29 | 7:15 | 1.7483 | 6.3822 | 1 | 10 | 66.3952 | 76.3755
2017-06-29 | 7:20 | 1.7631 | 6.0044 |  | 10
2017-06-29 | 7:25 | 1.7639 | 5.9771 |  | 10
2017-06-29 | 7:30 | 1.7561 | 5.7522 | 1 | 10 | 60.7216 | 76.1706
2017-06-29 | 7:35 | 1.7522 | 6.0606 |  | 10
2017-06-29 | 7:40 | 1.7483 | 5.5862 |  | 10
2017-06-29 | 7:45 | 1.7468 | 5.852 | 1 | 10 | 60.7811 | 76.1148
2017-06-29 | 7:50 | 1.7592 | 5.5118 |  | 10
2017-06-29 | 7:55 | 1.7234 | 5.0712 |  | 10
2017-06-29 | 8:00 | 1.7241 | 5.0095 | 1 | 10 | 53.4296 | 76.4148
2017-06-29 | 8:05 | 1.7163 | 5.5804 |  | 10
2017-06-29 | 8:10 | 1.689 | 6.5779 |  | 10
2017-06-29 | 8:15 | 1.7132 | 7.1445 | 1 | 10 | 73.7118 | 77.2108
2017-06-29 | 8:20 | 1.7179 | 7.2451 |  | 10
2017-06-29 | 8:25 | 1.7327 | 6.8042 |  | 10
2017-06-29 | 8:30 | 1.7429 | 6.427 | 1 | 10 | 66.4 | 77.6473
2017-06-29 | 8:35 | 1.7741 | 6.0713 |  | 10
2017-06-29 | 8:40 | 1.7046 | 6.607 |  | 10
2017-06-29 | 8:45 | 1.7772 | 6.3999 | 1 | 10 | 66.0109 | 77.5776
2017-06-29 | 8:50 | 1.7335 | 6.6505 |  | 10
2017-06-29 | 8:55 | 1.746 | 7.2616 |  | 10
2017-06-29 | 9:00 | 1.7483 | 7.1499 | 1 | 10 | 73.461 | 77.9221
2017-06-29 | 9:05 | 1.7304 | 6.84 |  | 10
2017-06-29 | 9:10 | 1.7273 | 7.2096 |  | 10
2017-06-29 | 9:15 | 1.7382 | 6.7019 | 1 | 10 | 70.0488 | 78.3033
2017-06-29 | 9:20 | 1.7304 | 6.9188 |  | 10
2017-06-29 | 9:25 | 1.7148 | 7.5048 |  | 10
2017-06-29 | 9:30 | 1.7709 | 6.8349 | 1 | 10 | 71.4999 | 78.7279
2017-06-29 | 9:35 | 1.7787 | 6.2949 |  | 10
2017-06-29 | 9:40 | 1.7569 | 6.6535 |  | 10
2017-06-29 | 9:45 | 1.6836 | 7.5413 | 1 | 10 | 77.1564 | 78.8536
2017-06-29 | 9:50 | 1.7031 | 7.3277 |  | 10
2017-06-29 | 9:55 | 1.668 | 7.3318 |  | 10
2017-06-29 | 10:00 | 1.7039 | 7.2938 | 1 | 10 | 75.5834 | 79.8714
2017-06-29 | 10:05 | 1.6922 | 6.9124 |  | 10
2017-06-29 | 10:10 | 1.7085 | 7.1094 |  | 10
2017-06-29 | 10:15 | 1.7234 | 7.1248 | 1 | 10 | 73.1016 | 80.5966
2017-06-29 | 10:20 | 1.7585 | 7.3555 |  | 10
2017-06-29 | 10:25 | 1.7296 | 7.6078 |  | 10
2017-06-29 | 10:30 | 1.7475 | 7.7181 | 1 | 10 | 80.2636 | 80.4754
2017-06-29 | 10:35 | 1.7756 | 7.7571 |  | 10
2017-06-29 | 10:40 | 1.7928 | 6.8244 |  | 10
2017-06-29 | 10:45 | 1.7585 | 6.8533 | 1 | 10 | 71.1279 | 80.0599
2017-06-29 | 10:50 | 1.7374 | 6.7874 |  | 10
2017-06-29 | 10:55 | 1.7312 | 6.0628 |  | 10
2017-06-29 | 11:00 | 1.7444 | 6.0329 | 1 | 10 | 63.3425 | 80.2999
2017-06-29 | 11:05 | 1.7483 | 5.6416 |  | 10
2017-06-29 | 11:10 | 1.6282 | 2.2789 |  | 1.5
2017-06-29 | 11:15 | 1.6243 | 0 | 0 | 1.5 | 25 | 82.0961
2017-06-29 | 11:20 | 1.7062 | 0 |  | 1.5
2017-06-29 | 11:25 | 1.7085 | 0 |  | 1.5
2017-06-29 | 11:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 83.5461
2017-06-29 | 11:35 | 1.6773 | 0 |  | 1.5
2017-06-29 | 11:40 | 1.7023 | 0 |  | 1.5
2017-06-29 | 11:45 | 1.7031 | 0 | 0 | 1.5 | 25 | 85.0916
2017-06-29 | 11:50 | 1.6984 | 0 |  | 1.5
2017-06-29 | 11:55 | 1.7085 | 0 |  | 1.5
2017-06-29 | 12:00 | 1.6945 | 0 | 0 | 1.5 | 25 | 86.5829
2017-06-29 | 12:05 | 1.728 | 0 |  | 1.5
2017-06-29 | 12:10 | 1.707 | 0 |  | 1.5
2017-06-29 | 12:15 | 1.7007 | 0 | 0 | 1.5 | 25 | 87.6086
2017-06-29 | 12:20 | 1.7195 | 0 |  | 1.5
2017-06-29 | 12:25 | 1.7452 | 0 |  | 1.5
2017-06-29 | 12:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 88.3813
2017-06-29 | 12:35 | 1.7616 | 0 |  | 1.5
2017-06-29 | 12:40 | 1.7405 | 0 |  | 1.5
2017-06-29 | 12:45 | 1.7351 | 0 | 0 | 1.5 | 25 | 88.4087
2017-06-29 | 12:50 | 1.7577 | 0 |  | 1.5
2017-06-29 | 12:55 | 1.7413 | 0 |  | 1.5
2017-06-29 | 13:00 | 1.767 | 0 | 0 | 1.5 | 25 | 88.3471
2017-06-29 | 13:05 | 1.7452 | 0 |  | 1.5
2017-06-29 | 13:10 | 1.7538 | 0 |  | 1.5
2017-06-29 | 13:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 88.2027
2017-06-29 | 13:20 | 1.7468 | 0 |  | 1.5
2017-06-29 | 13:25 | 1.7288 | 0 |  | 1.5
2017-06-29 | 13:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 88.3388
2017-06-29 | 13:35 | 1.7538 | 0 |  | 1.5
2017-06-29 | 13:40 | 1.7366 | 0 |  | 1.5
2017-06-29 | 13:45 | 1.7148 | 0 | 0 | 1.5 | 25 | 88.2404
2017-06-29 | 13:50 | 1.7202 | 0 |  | 1.5
2017-06-29 | 13:55 | 1.7826 | 0 |  | 1.5
2017-06-29 | 14:00 | 1.7764 | 0 | 0 | 1.5 | 25 | 87.8408
2017-06-29 | 14:05 | 1.7312 | 0 |  | 1.5
2017-06-29 | 14:10 | 1.7452 | 0 |  | 1.5
2017-06-29 | 14:15 | 1.7163 | 0 | 0 | 1.5 | 25 | 88.4192
2017-06-29 | 14:20 | 1.7374 | 0 |  | 1.5
2017-06-29 | 14:25 | 1.7296 | 0 |  | 1.5
2017-06-29 | 14:30 | 1.7452 | 0 | 0 | 1.5 | 25 | 88.4442
2017-06-29 | 14:35 | 1.7468 | 0 |  | 1.5
2017-06-29 | 14:40 | 1.7522 | 0 |  | 1.5
2017-06-29 | 14:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 88.3953
2017-06-29 | 14:50 | 1.7561 | 0 |  | 1.5
2017-06-29 | 14:55 | 1.7709 | 0 |  | 1.5
2017-06-29 | 15:00 | 1.7725 | 0 | 0 | 1.5 | 25 | 88.3114
2017-06-29 | 15:05 | 1.7967 | 0 |  | 1.5
2017-06-29 | 15:10 | 1.7561 | 0 |  | 1.5
2017-06-29 | 15:15 | 1.7366 | 0 | 0 | 1.5 | 25 | 87.8134
2017-06-29 | 15:20 | 1.7569 | 0 |  | 1.5
2017-06-29 | 15:25 | 1.7561 | 0 |  | 1.5
2017-06-29 | 15:30 | 1.7616 | 0 | 0 | 1.5 | 25 | 87.528
2017-06-29 | 15:35 | 1.7163 | 0 |  | 1.5
2017-06-29 | 15:40 | 1.7514 | 0 |  | 1.5
2017-06-29 | 15:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 88.0604
2017-06-29 | 15:50 | 1.7436 | 0 |  | 1.5
2017-06-29 | 15:55 | 1.7319 | 0 |  | 1.5
2017-06-29 | 16:00 | 1.7686 | 0 | 0 | 1.5 | 25 | 88.0454
2017-06-29 | 16:05 | 1.7585 | 0 |  | 1.5
2017-06-29 | 16:10 | 1.7585 | 0 |  | 1.5
2017-06-29 | 16:15 | 1.7592 | 0 | 0 | 1.5 | 25 | 87.7897
2017-06-29 | 16:20 | 1.767 | 0 |  | 1.5
2017-06-29 | 16:25 | 1.8099 | 0 |  | 1.5
2017-06-29 | 16:30 | 1.7748 | 0 | 0 | 1.5 | 25 | 87.0297
2017-06-29 | 16:35 | 1.7889 | 0 |  | 1.5
2017-06-29 | 16:40 | 1.7811 | 0 |  | 1.5
2017-06-29 | 16:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 86.42
2017-06-29 | 16:50 | 1.7561 | 0 |  | 1.5
2017-06-29 | 16:55 | 1.7351 | 0 |  | 1.5
2017-06-29 | 17:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 86.3184
2017-06-29 | 17:05 | 1.7655 | 0 |  | 1.5
2017-06-29 | 17:10 | 1.7631 | 0 |  | 1.5
2017-06-29 | 17:15 | 1.792 | 0 | 0 | 1.5 | 25 | 85.6866
2017-06-29 | 17:20 | 1.7491 | 0 |  | 1.5
2017-06-29 | 17:25 | 1.7904 | 0 |  | 1.5
2017-06-29 | 17:30 | 1.8396 | 0 | 0 | 1.5 | 25 | 84.9941
2017-06-29 | 17:35 | 1.8333 | 0 |  | 1.5
2017-06-29 | 17:40 | 1.824 | 0 |  | 1.5
2017-06-29 | 17:45 | 1.7764 | 0 | 0 | 1.5 | 25 | 83.3114
2017-06-29 | 17:50 | 1.7756 | 0 |  | 1.5
2017-06-29 | 17:55 | 1.7795 | 0 |  | 1.5
2017-06-29 | 18:00 | 1.7694 | 0 | 0 | 1.5 | 25 | 82.5397
2017-06-29 | 18:05 | 1.7639 | 0 |  | 1.5
2017-06-29 | 18:10 | 1.7499 | 0 |  | 1.5
2017-06-29 | 18:15 | 1.746 | 0 | 0 | 1.5 | 25 | 82.2019
2017-06-29 | 18:20 | 1.7475 | 0 |  | 1.5
2017-06-29 | 18:25 | 1.7741 | 0 |  | 1.5
2017-06-29 | 18:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 81.9326
2017-06-29 | 18:35 | 1.7553 | 0 |  | 1.5
2017-06-29 | 18:40 | 1.7514 | 0 |  | 1.5
2017-06-29 | 18:45 | 1.7249 | 0 | 0 | 1.5 | 25 | 81.8442
2017-06-29 | 18:50 | 1.7811 | 0 |  | 1.5
2017-06-29 | 18:55 | 1.7647 | 0 |  | 1.5
2017-06-29 | 19:00 | 1.7592 | 0 | 0 | 1.5 | 25 | 81.7231
2017-06-29 | 19:05 | 1.7694 | 0 |  | 1.5
2017-06-29 | 19:10 | 1.7725 | 0 |  | 1.5
2017-06-29 | 19:15 | 1.739 | 0 | 0 | 1.5 | 25 | 81.5367
2017-06-29 | 19:20 | 1.7514 | 0 |  | 1.5
2017-06-29 | 19:25 | 1.7546 | 0 |  | 1.5
2017-06-29 | 19:30 | 1.7374 | 0 | 0 | 1.5 | 25 | 81.4781
2017-06-29 | 19:35 | 1.7436 | 0 |  | 1.5
2017-06-29 | 19:40 | 1.7241 | 0 |  | 1.5
2017-06-29 | 19:45 | 1.7608 | 0 | 0 | 1.5 | 25 | 81.4625
2017-06-29 | 19:50 | 1.7889 | 0 |  | 1.5
2017-06-29 | 19:55 | 1.778 | 0 |  | 1.5
2017-06-29 | 20:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 81.0265
2017-06-29 | 20:05 | 1.753 | 0 |  | 1.5
2017-06-29 | 20:10 | 1.7577 | 0 |  | 1.5
2017-06-29 | 20:15 | 1.7741 | 0 | 0 | 1.5 | 25 | 80.7549
2017-06-29 | 20:20 | 1.753 | 0 |  | 1.5
2017-06-29 | 20:25 | 1.7631 | 0 |  | 1.5
2017-06-29 | 20:30 | 1.7709 | 0 | 0 | 1.5 | 25 | 80.3647
2017-06-29 | 20:35 | 1.7569 | 0 |  | 1.5
2017-06-29 | 20:40 | 1.7787 | 0 |  | 1.5
2017-06-29 | 20:45 | 1.7717 | 0 | 0 | 1.5 | 25 | 79.8729
2017-06-29 | 20:50 | 1.7881 | 0 |  | 1.5
2017-06-29 | 20:55 | 1.799 | 0 |  | 1.5
2017-06-29 | 21:00 | 1.7717 | 0 | 0 | 1.5 | 25 | 79.3618
2017-06-29 | 21:05 | -0.10652 | 0 |  | 1.5
2017-06-29 | 21:10 | -0.1073 | 0 |  | 1.5
2017-06-29 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 21:20 | -0.10652 | 0 |  | 1.5
2017-06-29 | 21:25 | -0.10808 | 0 |  | 1.5
2017-06-29 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 21:35 | -0.1073 | 0 |  | 1.5
2017-06-29 | 21:40 | -0.1073 | 0 |  | 1.5
2017-06-29 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 21:50 | -0.1073 | 0 |  | 1.5
2017-06-29 | 21:55 | -0.1073 | 0 |  | 1.5
2017-06-29 | 22:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 22:05 | -0.10808 | 0 |  | 1.5
2017-06-29 | 22:10 | -0.1073 | 0 |  | 1.5
2017-06-29 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 22:20 | -0.10808 | 0 |  | 1.5
2017-06-29 | 22:25 | -0.11042 | 0 |  | 1.5
2017-06-29 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 22:35 | -0.10808 | 0 |  | 1.5
2017-06-29 | 22:40 | -0.1073 | 0 |  | 1.5
2017-06-29 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 22:50 | -0.1073 | 0 |  | 1.5
2017-06-29 | 22:55 | -0.1073 | 0 |  | 1.5
2017-06-29 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 23:05 | -0.1073 | 0 |  | 1.5
2017-06-29 | 23:10 | -0.1073 | 0 |  | 1.5
2017-06-29 | 23:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 23:20 | -0.10652 | 0 |  | 1.5
2017-06-29 | 23:25 | -0.10652 | 0 |  | 1.5
2017-06-29 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 23:35 | -0.10652 | 0 |  | 1.5
2017-06-29 | 23:40 | -0.10652 | 0 |  | 1.5
2017-06-29 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-29 | 23:50 | -0.10652 | 0 |  | 1.5
2017-06-29 | 23:55 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 0:05 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:10 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 0:20 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:25 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 0:35 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:40 | -0.10652 | 0 |  | 1.5
2017-06-30 | 0:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 0:50 | -0.10574 | 0 |  | 1.5
2017-06-30 | 0:55 | -0.10652 | 0 |  | 1.5
2017-06-30 | 1:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 1:05 | -0.10808 | 0 |  | 1.5
2017-06-30 | 1:10 | -0.10652 | 0 |  | 1.5
2017-06-30 | 1:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 1:20 | -0.10652 | 0 |  | 1.5
2017-06-30 | 1:25 | -0.10964 | 0 |  | 1.5
2017-06-30 | 1:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 1:35 | -0.10964 | 0 |  | 1.5
2017-06-30 | 1:40 | -0.10886 | 0 |  | 1.5
2017-06-30 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 1:50 | -0.10964 | 0 |  | 1.5
2017-06-30 | 1:55 | -0.10964 | 0 |  | 1.5
2017-06-30 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 2:05 | -0.10964 | 0 |  | 1.5
2017-06-30 | 2:10 | -0.10886 | 0 |  | 1.5
2017-06-30 | 2:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 2:20 | -0.11042 | 0 |  | 1.5
2017-06-30 | 2:25 | -0.11042 | 0 |  | 1.5
2017-06-30 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 2:35 | -0.11042 | 0 |  | 1.5
2017-06-30 | 2:40 | -0.11042 | 0 |  | 1.5
2017-06-30 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 2:50 | -0.11042 | 0 |  | 1.5
2017-06-30 | 2:55 | -0.1112 | 0 |  | 1.5
2017-06-30 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 3:05 | -0.1112 | 0 |  | 1.5
2017-06-30 | 3:10 | -0.1112 | 0 |  | 1.5
2017-06-30 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 3:20 | -0.1112 | 0 |  | 1.5
2017-06-30 | 3:25 | -0.1112 | 0 |  | 1.5
2017-06-30 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 3:35 | -0.11042 | 0 |  | 1.5
2017-06-30 | 3:40 | -0.1112 | 0 |  | 1.5
2017-06-30 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 3:50 | -0.11042 | 0 |  | 1.5
2017-06-30 | 3:55 | -0.1112 | 0 |  | 1.5
2017-06-30 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 4:05 | -0.1112 | 0 |  | 1.5
2017-06-30 | 4:10 | -0.11042 | 0 |  | 1.5
2017-06-30 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 4:20 | -0.1112 | 0 |  | 1.5
2017-06-30 | 4:25 | -0.1112 | 0 |  | 1.5
2017-06-30 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 4:35 | -0.1112 | 0 |  | 1.5
2017-06-30 | 4:40 | -0.1112 | 0 |  | 1.5
2017-06-30 | 4:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 4:50 | -0.11042 | 0 |  | 1.5
2017-06-30 | 4:55 | -0.1112 | 0 |  | 1.5
2017-06-30 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 5:05 | 2.1734 | 6.3228 |  | 10
2017-06-30 | 5:10 | 2.0003 | 10 |  | 10
2017-06-30 | 5:15 | 2.012 | 10 | 1 | 10 | 100 | 91.4185
2017-06-30 | 5:20 | 1.9792 | 10 |  | 10
2017-06-30 | 5:25 | 1.9285 | 9.9855 |  | 10
2017-06-30 | 5:30 | 1.9285 | 9.593 | 1 | 10 | 96.4506 | 85.9725
2017-06-30 | 5:35 | 1.8973 | 8.7898 |  | 10
2017-06-30 | 5:40 | 1.8817 | 8.3329 |  | 10
2017-06-30 | 5:45 | 1.8544 | 8.1576 | 1 | 10 | 82.3998 | 82.211
2017-06-30 | 5:50 | 1.8255 | 8.0288 |  | 10
2017-06-30 | 5:55 | 1.7967 | 8.033 |  | 10
2017-06-30 | 6:00 | 1.8115 | 7.6278 | 1 | 10 | 77.0011 | 80.4221
2017-06-30 | 6:05 | 1.7444 | 7.8534 |  | 10
2017-06-30 | 6:10 | 1.7491 | 7.8111 |  | 10
2017-06-30 | 6:15 | 1.7842 | 7.5445 | 1 | 10 | 76.1224 | 79.6254
2017-06-30 | 6:20 | 1.7881 | 7.7787 |  | 10
2017-06-30 | 6:25 | 1.7741 | 7.5666 |  | 10
2017-06-30 | 6:30 | 1.7694 | 7.5785 | 1 | 10 | 76.7 | 79.1799
2017-06-30 | 6:35 | 1.7826 | 7.3805 |  | 10
2017-06-30 | 6:40 | 1.7663 | 7.4506 |  | 10
2017-06-30 | 6:45 | 1.7561 | 7.2466 | 1 | 10 | 73.4533 | 78.8637
2017-06-30 | 6:50 | 1.778 | 6.69 |  | 10
2017-06-30 | 6:55 | 1.377 | 6.4169 |  | 1.5
2017-06-30 | 7:00 | 1.707 | 1.8661 | 0 | 1.5 | 25 | 80.0521
2017-06-30 | 7:05 | 1.8528 | 3.4943 |  | 10
2017-06-30 | 7:10 | 1.8123 | 4.7524 |  | 10
2017-06-30 | 7:15 | 1.8099 | 5.6401 | 1 | 10 | 67.4088 | 77.9046
2017-06-30 | 7:20 | 1.7452 | 6.2988 |  | 10
2017-06-30 | 7:25 | 1.7678 | 5.4984 |  | 10
2017-06-30 | 7:30 | 1.7499 | 5.3772 | 1 | 10 | 64.9285 | 77.5961
2017-06-30 | 7:35 | 1.7444 | 5.185 |  | 10
2017-06-30 | 7:40 | 1.7553 | 5.235 |  | 10
2017-06-30 | 7:45 | 1.7663 | 5.1087 | 1 | 10 | 63.4271 | 77.627
2017-06-30 | 7:50 | 1.7577 | 4.6879 |  | 10
2017-06-30 | 7:55 | 1.7491 | 4.3202 |  | 10
2017-06-30 | 8:00 | 1.7522 | 3.6002 | 1 | 10 | 48.4552 | 77.5027
2017-06-30 | 8:05 | 1.7351 | 3.7453 |  | 10
2017-06-30 | 8:10 | 1.7257 | 3.812 |  | 10
2017-06-30 | 8:15 | 1.7249 | 4.1866 | 1 | 10 | 52.9366 | 77.6076
2017-06-30 | 8:20 | 1.7397 | 4.9907 |  | 10
2017-06-30 | 8:25 | 1.7569 | 4.2321 |  | 10
2017-06-30 | 8:30 | 1.7499 | 3.9899 | 1 | 10 | 51.6315 | 77.8601
2017-06-30 | 8:35 | 1.7624 | 3.4787 |  | 10
2017-06-30 | 8:40 | 1.7366 | 3.9128 |  | 10
2017-06-30 | 8:45 | 1.7694 | 4.3597 | 1 | 10 | 54.5975 | 78.0161
2017-06-30 | 8:50 | 1.7304 | 4.1256 |  | 10
2017-06-30 | 8:55 | 1.746 | 5.6206 |  | 10
2017-06-30 | 9:00 | 1.7319 | 5.3119 | 1 | 10 | 65.2296 | 78.2589
2017-06-30 | 9:05 | 1.7702 | 2.3904 |  | 10
2017-06-30 | 9:10 | 1.5533 | 0 |  | 1.5
2017-06-30 | 9:15 | 1.6188 | 0 | 0 | 1.5 | 25 | 79.9137
2017-06-30 | 9:20 | 1.6672 | 0 |  | 1.5
2017-06-30 | 9:25 | 1.7015 | 0 |  | 1.5
2017-06-30 | 9:30 | 1.7023 | 0 | 0 | 1.5 | 25 | 81.6028
2017-06-30 | 9:35 | 1.7351 | 0 |  | 1.5
2017-06-30 | 9:40 | 1.7296 | 0 |  | 1.5
2017-06-30 | 9:45 | 1.7257 | 0 | 0 | 1.5 | 25 | 82.3386
2017-06-30 | 9:50 | 1.7015 | 0 |  | 1.5
2017-06-30 | 9:55 | 1.6797 | 0 |  | 1.5
2017-06-30 | 10:00 | 1.7444 | 0 | 0 | 1.5 | 25 | 83.5124
2017-06-30 | 10:05 | 1.7795 | 0 |  | 1.5
2017-06-30 | 10:10 | 1.7507 | 0 |  | 1.5
2017-06-30 | 10:15 | 1.7195 | 0 | 0 | 1.5 | 25 | 83.6858
2017-06-30 | 10:20 | 1.7078 | 0 |  | 1.5
2017-06-30 | 10:25 | 1.7171 | 0 |  | 1.5
2017-06-30 | 10:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 84.0951
2017-06-30 | 10:35 | 1.7553 | 0 |  | 1.5
2017-06-30 | 10:40 | 1.7444 | 0 |  | 1.5
2017-06-30 | 10:45 | 1.7569 | 0 | 0 | 1.5 | 25 | 84.2293
2017-06-30 | 10:50 | 1.7327 | 0 |  | 1.5
2017-06-30 | 10:55 | 1.7265 | 0 |  | 1.5
2017-06-30 | 11:00 | 1.7273 | 0 | 0 | 1.5 | 25 | 84.8066
2017-06-30 | 11:05 | 1.6929 | 0 |  | 1.5
2017-06-30 | 11:10 | 1.6851 | 0 |  | 1.5
2017-06-30 | 11:15 | 1.7319 | 0 | 0 | 1.5 | 25 | 86.1029
2017-06-30 | 11:20 | 1.7655 | 0 |  | 1.5
2017-06-30 | 11:25 | 1.792 | 0 |  | 1.5
2017-06-30 | 11:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 86.0702
2017-06-30 | 11:35 | 1.7585 | 0 |  | 1.5
2017-06-30 | 11:40 | 1.682 | 0 |  | 1.5
2017-06-30 | 11:45 | 1.7171 | 0 | 0 | 1.5 | 25 | 86.8159
2017-06-30 | 11:50 | 1.6992 | 0 |  | 1.5
2017-06-30 | 11:55 | 1.7655 | 0 |  | 1.5
2017-06-30 | 12:00 | 1.714 | 0 | 0 | 1.5 | 25 | 87.6056
2017-06-30 | 12:05 | 1.7163 | 0 |  | 1.5
2017-06-30 | 12:10 | 1.6953 | 0 |  | 1.5
2017-06-30 | 12:15 | 1.7156 | 0 | 0 | 1.5 | 25 | 88.6298
2017-06-30 | 12:20 | 1.7335 | 0 |  | 1.5
2017-06-30 | 12:25 | 1.7265 | 0 |  | 1.5
2017-06-30 | 12:30 | 1.7351 | 0 | 0 | 1.5 | 25 | 88.7726
2017-06-30 | 12:35 | 1.7483 | 0 |  | 1.5
2017-06-30 | 12:40 | 1.7444 | 0 |  | 1.5
2017-06-30 | 12:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 88.8333
2017-06-30 | 12:50 | 1.76 | 0 |  | 1.5
2017-06-30 | 12:55 | 1.7592 | 0 |  | 1.5
2017-06-30 | 13:00 | 1.7343 | 0 | 0 | 1.5 | 25 | 88.7681
2017-06-30 | 13:05 | 1.7397 | 0 |  | 1.5
2017-06-30 | 13:10 | 1.7351 | 0 |  | 1.5
2017-06-30 | 13:15 | 1.7413 | 0 | 0 | 1.5 | 25 | 88.922
2017-06-30 | 13:20 | 1.7413 | 0 |  | 1.5
2017-06-30 | 13:25 | 1.7577 | 0 |  | 1.5
2017-06-30 | 13:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 89.2147
2017-06-30 | 13:35 | 1.7397 | 0 |  | 1.5
2017-06-30 | 13:40 | 1.7374 | 0 |  | 1.5
2017-06-30 | 13:45 | 1.7569 | 0 | 0 | 1.5 | 25 | 89.2362
2017-06-30 | 13:50 | 1.7397 | 0 |  | 1.5
2017-06-30 | 13:55 | 1.7304 | 0 |  | 1.5
2017-06-30 | 14:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 89.4924
2017-06-30 | 14:05 | 1.7304 | 0 |  | 1.5
2017-06-30 | 14:10 | 1.7577 | 0 |  | 1.5
2017-06-30 | 14:15 | 1.7265 | 0 | 0 | 1.5 | 25 | 89.6614
2017-06-30 | 14:20 | 1.7655 | 0 |  | 1.5
2017-06-30 | 14:25 | 1.7296 | 0 |  | 1.5
2017-06-30 | 14:30 | 1.7756 | 0 | 0 | 1.5 | 25 | 90.0806
2017-06-30 | 14:35 | 1.7382 | 0 |  | 1.5
2017-06-30 | 14:40 | 1.7444 | 0 |  | 1.5
2017-06-30 | 14:45 | 1.7507 | 0 | 0 | 1.5 | 25 | 90.2507
2017-06-30 | 14:50 | 1.7631 | 0 |  | 1.5
2017-06-30 | 14:55 | 1.7507 | 0 |  | 1.5
2017-06-30 | 15:00 | 1.7382 | 0 | 0 | 1.5 | 25 | 90.4714
2017-06-30 | 15:05 | 1.7553 | 0 |  | 1.5
2017-06-30 | 15:10 | 1.7514 | 0 |  | 1.5
2017-06-30 | 15:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 90.511
2017-06-30 | 15:20 | 1.7538 | 0 |  | 1.5
2017-06-30 | 15:25 | 1.7335 | 0 |  | 1.5
2017-06-30 | 15:30 | 1.7468 | 0 | 0 | 1.5 | 25 | 90.6846
2017-06-30 | 15:35 | 1.7616 | 0 |  | 1.5
2017-06-30 | 15:40 | 1.7078 | 0 |  | 1.5
2017-06-30 | 15:45 | 1.7538 | 0 | 0 | 1.5 | 25 | 90.7512
2017-06-30 | 15:50 | 1.7343 | 0 |  | 1.5
2017-06-30 | 15:55 | 1.721 | 0 |  | 1.5
2017-06-30 | 16:00 | 1.746 | 0 | 0 | 1.5 | 25 | 90.9665
2017-06-30 | 16:05 | 1.7577 | 0 |  | 1.5
2017-06-30 | 16:10 | 1.778 | 0 |  | 1.5
2017-06-30 | 16:15 | 1.7296 | 0 | 0 | 1.5 | 25 | 90.7818
2017-06-30 | 16:20 | 1.778 | 0 |  | 1.5
2017-06-30 | 16:25 | 1.728 | 0 |  | 1.5
2017-06-30 | 16:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 90.727
2017-06-30 | 16:35 | 1.7803 | 0 |  | 1.5
2017-06-30 | 16:40 | 1.7358 | 0 |  | 1.5
2017-06-30 | 16:45 | 1.7686 | 0 | 0 | 1.5 | 25 | 90.2774
2017-06-30 | 16:50 | 1.7834 | 0 |  | 1.5
2017-06-30 | 16:55 | 1.7772 | 0 |  | 1.5
2017-06-30 | 17:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 89.7592
2017-06-30 | 17:05 | 1.7616 | 0 |  | 1.5
2017-06-30 | 17:10 | 1.785 | 0 |  | 1.5
2017-06-30 | 17:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 89.0884
2017-06-30 | 17:20 | 1.8084 | 0 |  | 1.5
2017-06-30 | 17:25 | 1.8138 | 0 |  | 1.5
2017-06-30 | 17:30 | 1.8341 | 0 | 0 | 1.5 | 25 | 87.4756
2017-06-30 | 17:35 | 1.8263 | 0 |  | 1.5
2017-06-30 | 17:40 | 1.8006 | 0 |  | 1.5
2017-06-30 | 17:45 | 1.8099 | 0 | 0 | 1.5 | 25 | 85.6577
2017-06-30 | 17:50 | 1.8084 | 0 |  | 1.5
2017-06-30 | 17:55 | 1.7741 | 0 |  | 1.5
2017-06-30 | 18:00 | 1.7912 | 0 | 0 | 1.5 | 25 | 84.3718
2017-06-30 | 18:05 | 1.7889 | 0 |  | 1.5
2017-06-30 | 18:10 | 1.7748 | 0 |  | 1.5
2017-06-30 | 18:15 | 1.7787 | 0 | 0 | 1.5 | 25 | 83.4901
2017-06-30 | 18:20 | 1.7702 | 0 |  | 1.5
2017-06-30 | 18:25 | 1.7748 | 0 |  | 1.5
2017-06-30 | 18:30 | 1.767 | 0 | 0 | 1.5 | 25 | 82.7283
2017-06-30 | 18:35 | 1.7624 | 0 |  | 1.5
2017-06-30 | 18:40 | 1.7608 | 0 |  | 1.5
2017-06-30 | 18:45 | 1.7865 | 0 | 0 | 1.5 | 25 | 82.0819
2017-06-30 | 18:50 | 1.7787 | 0 |  | 1.5
2017-06-30 | 18:55 | 1.7709 | 0 |  | 1.5
2017-06-30 | 19:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 81.5949
2017-06-30 | 19:05 | 1.7764 | 0 |  | 1.5
2017-06-30 | 19:10 | 1.7522 | 0 |  | 1.5
2017-06-30 | 19:15 | 1.7499 | 0 | 0 | 1.5 | 25 | 81.2745
2017-06-30 | 19:20 | 1.7725 | 0 |  | 1.5
2017-06-30 | 19:25 | 1.7655 | 0 |  | 1.5
2017-06-30 | 19:30 | 1.7608 | 0 | 0 | 1.5 | 25 | 80.9315
2017-06-30 | 19:35 | 1.7741 | 0 |  | 1.5
2017-06-30 | 19:40 | 1.7538 | 0 |  | 1.5
2017-06-30 | 19:45 | 1.7436 | 0 | 0 | 1.5 | 25 | 80.6115
2017-06-30 | 19:50 | 1.7881 | 0 |  | 1.5
2017-06-30 | 19:55 | 1.7826 | 0 |  | 1.5
2017-06-30 | 20:00 | 1.7663 | 0 | 0 | 1.5 | 25 | 80.2091
2017-06-30 | 20:05 | 1.7483 | 0 |  | 1.5
2017-06-30 | 20:10 | 1.7553 | 0 |  | 1.5
2017-06-30 | 20:15 | 1.7647 | 0 | 0 | 1.5 | 25 | 79.7351
2017-06-30 | 20:20 | 1.7374 | 0 |  | 1.5
2017-06-30 | 20:25 | 1.7499 | 0 |  | 1.5
2017-06-30 | 20:30 | 1.7608 | 0 | 0 | 1.5 | 25 | 79.8957
2017-06-30 | 20:35 | 1.767 | 0 |  | 1.5
2017-06-30 | 20:40 | 1.7234 | 0 |  | 1.5
2017-06-30 | 20:45 | 1.7553 | 0 | 0 | 1.5 | 25 | 79.9138
2017-06-30 | 20:50 | 1.7397 | 0 |  | 1.5
2017-06-30 | 20:55 | 1.7686 | 0 |  | 1.5
2017-06-30 | 21:00 | 1.7374 | 0 | 0 | 1.5 | 25 | 79.7683
2017-06-30 | 21:05 | -0.1073 | 0 |  | 1.5
2017-06-30 | 21:10 | -0.10808 | 0 |  | 1.5
2017-06-30 | 21:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 21:20 | -0.10964 | 0 |  | 1.5
2017-06-30 | 21:25 | -0.10964 | 0 |  | 1.5
2017-06-30 | 21:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 21:35 | -0.11042 | 0 |  | 1.5
2017-06-30 | 21:40 | -0.10964 | 0 |  | 1.5
2017-06-30 | 21:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 21:50 | -0.11042 | 0 |  | 1.5
2017-06-30 | 21:55 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 22:05 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:10 | -0.10808 | 0 |  | 1.5
2017-06-30 | 22:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 22:20 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:25 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 22:35 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:40 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 22:50 | -0.10886 | 0 |  | 1.5
2017-06-30 | 22:55 | -0.10886 | 0 |  | 1.5
2017-06-30 | 23:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 23:05 | -0.10886 | 0 |  | 1.5
2017-06-30 | 23:10 | -0.10808 | 0 |  | 1.5
2017-06-30 | 23:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 23:20 | -0.10886 | 0 |  | 1.5
2017-06-30 | 23:25 | -0.10808 | 0 |  | 1.5
2017-06-30 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 23:35 | -0.10886 | 0 |  | 1.5
2017-06-30 | 23:40 | -0.10808 | 0 |  | 1.5
2017-06-30 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-06-30 | 23:50 | -0.10808 | 0 |  | 1.5
2017-06-30 | 23:55 | -0.10808 | 0 |  | 1.5
2017-07-01 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-01 | 0:05 | -0.10808 | 0 |  | 1.5
2017-07-01 | 0:10 | -0.10808 | 0 |  | 1.5
2017-07-01 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 0:15 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 0:20 | -0.10886 | 0 |  | 1.5
2017-07-01 | 0:25 | -0.10964 | 0 |  | 1.5
2017-07-01 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-01 | 0:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-01 | 0:35 | -0.10808 | 0 |  | 1.5
2017-07-01 | 0:40 | -0.10886 | 0 |  | 1.5
2017-07-01 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-01 | 0:45 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-01 | 0:50 | -0.10808 | 0 |  | 1.5
2017-07-01 | 0:55 | -0.10808 | 0 |  | 1.5
2017-07-01 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-01 | 1:00 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-01 | 1:05 | -0.10808 | 0 |  | 1.5
2017-07-01 | 1:10 | -0.10886 | 0 |  | 1.5
2017-07-01 | 1:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 1:15 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-01 | 1:25 | -0.1112 | 0 |  | 1.5
2017-07-01 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-07-01 | 1:30 | -0.1112 | 0 |  | 1.5 |  | 0
2017-07-01 | 1:35 | -0.1112 | 0 |  | 1.5
2017-07-01 | 1:40 | -0.1112 | 0 |  | 1.5
2017-07-01 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0
2017-07-01 | 1:45 | -0.1112 | 0 |  | 1.5 |  | 0
2017-07-01 | 1:50 | -0.1112 | 0 |  | 1.5
2017-07-01 | 1:55 | -0.1112 | 0 |  | 1.5
2017-07-01 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0
2017-07-01 | 2:00 | -0.1112 | 0 |  | 1.5 |  | 0
2017-07-01 | 2:05 | -0.1112 | 0 |  | 1.5
2017-07-01 | 2:10 | -0.11198 | 0 |  | 1.5
2017-07-01 | 2:15 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 2:15 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 2:20 | -0.11198 | 0 |  | 1.5
2017-07-01 | 2:25 | -0.11198 | 0 |  | 1.5
2017-07-01 | 2:30 | -0.11276 | 0 | 0 | 1.5 | 0
2017-07-01 | 2:30 | -0.11276 | 0 |  | 1.5 |  | 0
2017-07-01 | 2:35 | -0.11198 | 0 |  | 1.5
2017-07-01 | 2:40 | -0.11198 | 0 |  | 1.5
2017-07-01 | 2:45 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 2:45 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-01 | 2:55 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:00 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 3:00 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 3:05 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:10 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:15 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 3:15 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 3:20 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:25 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:30 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 3:30 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 3:35 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:40 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:45 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 3:45 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 3:50 | -0.11198 | 0 |  | 1.5
2017-07-01 | 3:55 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0
2017-07-01 | 4:00 | -0.1112 | 0 |  | 1.5 |  | 0
2017-07-01 | 4:05 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:10 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:15 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 4:15 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 4:20 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:25 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:30 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 4:30 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 4:35 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-01 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-01 | 4:45 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-01 | 4:50 | -0.11198 | 0 |  | 1.5
2017-07-01 | 4:55 | -0.11198 | 0 |  | 1.5
2017-07-01 | 5:00 | -0.11198 | 0 | 1 | 0 | 0
2017-07-01 | 5:00 | -0.11198 | 0 |  | 0 |  | 25
2017-07-01 | 5:05 | 2.2499 | 6.3291 |  | 10
2017-07-01 | 5:10 | 2.0424 | 10 |  | 10
2017-07-01 | 5:15 | 2.0112 | 10 | 1 | 10 | 100
2017-07-01 | 5:15 | 2.0112 | 10 |  | 10 |  | 90.8387
2017-07-01 | 5:20 | 1.9737 | 10 |  | 10
2017-07-01 | 5:25 | 1.9457 | 9.9242 |  | 10
2017-07-01 | 5:30 | 1.9207 | 9.3425 | 1 | 10 | 94.0211
2017-07-01 | 5:30 | 1.9207 | 9.3425 |  | 10 |  | 85.1743
2017-07-01 | 5:35 | 1.8856 | 8.8971 |  | 10
2017-07-01 | 5:40 | 1.8716 | 8.3587 |  | 10
2017-07-01 | 5:45 | 1.8653 | 8.2713 | 1 | 10 | 83.3258
2017-07-01 | 5:45 | 1.8653 | 8.2713 |  | 10 |  | 81.5542
2017-07-01 | 5:50 | 1.8232 | 8.0741 |  | 10
2017-07-01 | 5:55 | 1.8053 | 7.9137 |  | 10
2017-07-01 | 6:00 | 1.7889 | 7.7134 | 1 | 10 | 78.0529
2017-07-01 | 6:00 | 1.7889 | 7.7134 |  | 10 |  | 80.0341
2017-07-01 | 6:05 | 1.7889 | 7.5903 |  | 10
2017-07-01 | 6:10 | 1.7889 | 7.8834 |  | 10
2017-07-01 | 6:15 | 1.7998 | 7.6914 | 1 | 10 | 77.9594
2017-07-01 | 6:15 | 1.7998 | 7.6914 |  | 10 |  | 79.3013
2017-07-01 | 6:20 | 1.7678 | 7.6087 |  | 10
2017-07-01 | 6:25 | 1.7834 | 7.6806 |  | 10
2017-07-01 | 6:30 | 1.792 | 7.4295 | 1 | 10 | 75.2254
2017-07-01 | 6:30 | 1.792 | 7.4295 |  | 10 |  | 78.7554
2017-07-01 | 6:35 | 1.7811 | 7.3699 |  | 10
2017-07-01 | 6:40 | 1.76 | 7.1073 |  | 10
2017-07-01 | 6:45 | 1.7787 | 7.0649 | 1 | 10 | 71.4318
2017-07-01 | 6:45 | 1.7787 | 7.0649 |  | 10 |  | 78.1839
2017-07-01 | 6:50 | 1.8029 | 7.0573 |  | 10
2017-07-01 | 6:55 | 1.7452 | 6.8475 |  | 10
2017-07-01 | 7:00 | 1.7655 | 6.9936 | 1 | 10 | 70.8291
2017-07-01 | 7:00 | 1.7655 | 6.9936 |  | 10 |  | 77.6727
2017-07-01 | 7:05 | 1.7748 | 6.7827 |  | 10
2017-07-01 | 7:10 | 1.7514 | 6.8438 |  | 10
2017-07-01 | 7:15 | 1.7546 | 6.7267 | 1 | 10 | 68.4231
2017-07-01 | 7:15 | 1.7546 | 6.7267 |  | 10 |  | 77.3482
2017-07-01 | 7:20 | 1.7553 | 6.7442 |  | 10
2017-07-01 | 7:25 | 1.7639 | 6.7648 |  | 10
2017-07-01 | 7:30 | 1.7397 | 6.6995 | 1 | 10 | 68.0906
2017-07-01 | 7:30 | 1.7397 | 6.6995 |  | 10 |  | 77.0378
2017-07-01 | 7:35 | 1.7725 | 6.8741 |  | 10
2017-07-01 | 7:40 | 1.7538 | 6.7706 |  | 10
2017-07-01 | 7:45 | 1.7382 | 6.718 | 1 | 10 | 68.1618
2017-07-01 | 7:45 | 1.7382 | 6.718 |  | 10 |  | 76.8879
2017-07-01 | 7:50 | 1.7561 | 6.6519 |  | 10
2017-07-01 | 7:55 | 1.7507 | 6.5152 |  | 10
2017-07-01 | 8:00 | 1.7631 | 6.3327 | 1 | 10 | 64.676
2017-07-01 | 8:00 | 1.7631 | 6.3327 |  | 10 |  | 76.5576
2017-07-01 | 8:05 | 1.7436 | 6.1575 |  | 10
2017-07-01 | 8:10 | 1.7413 | 6.16 |  | 10
2017-07-01 | 8:15 | 1.739 | 6.0941 | 1 | 10 | 62.1606
2017-07-01 | 8:15 | 1.739 | 6.0941 |  | 10 |  | 76.3297
2017-07-01 | 8:20 | 1.7522 | 6.127 |  | 10
2017-07-01 | 8:25 | 1.7452 | 6.0743 |  | 10
2017-07-01 | 8:30 | 1.7655 | 6.195 | 1 | 10 | 62.909
2017-07-01 | 8:30 | 1.7655 | 6.195 |  | 10 |  | 76.1288
2017-07-01 | 8:35 | 1.7304 | 6.5473 |  | 10
2017-07-01 | 8:40 | 1.7273 | 6.6897 |  | 10
2017-07-01 | 8:45 | 1.7241 | 6.6882 | 1 | 10 | 67.8969
2017-07-01 | 8:45 | 1.7241 | 6.6882 |  | 10 |  | 76.1495
2017-07-01 | 8:50 | 1.7748 | 6.5937 |  | 10
2017-07-01 | 8:55 | 1.7865 | 6.445 |  | 10
2017-07-01 | 9:00 | 1.7265 | 6.6649 | 1 | 10 | 67.4823
2017-07-01 | 9:00 | 1.7265 | 6.6649 |  | 10 |  | 76.1886
2017-07-01 | 9:05 | 1.7592 | 6.8153 |  | 10
2017-07-01 | 9:10 | 1.7577 | 6.6669 |  | 10
2017-07-01 | 9:15 | 1.7655 | 6.5889 | 1 | 10 | 66.952
2017-07-01 | 9:15 | 1.7655 | 6.5889 |  | 10 |  | 76.0744
2017-07-01 | 9:20 | 1.7577 | 6.6887 |  | 10
2017-07-01 | 9:25 | 1.728 | 6.7049 |  | 10
2017-07-01 | 9:30 | 1.7374 | 6.7746 | 1 | 10 | 68.9091
2017-07-01 | 9:30 | 1.7374 | 6.7746 |  | 10 |  | 76.0433
2017-07-01 | 9:35 | 1.7436 | 6.7204 |  | 10
2017-07-01 | 9:40 | 1.739 | 6.7364 |  | 10
2017-07-01 | 9:45 | 1.7522 | 6.5105 | 1 | 10 | 66.5021
2017-07-01 | 9:45 | 1.7522 | 6.5105 |  | 10 |  | 76.0006
2017-07-01 | 9:50 | 1.7546 | 6.4059 |  | 10
2017-07-01 | 9:55 | 1.7741 | 6.183 |  | 10
2017-07-01 | 10:00 | 1.7702 | 6.2748 | 1 | 10 | 63.9644
2017-07-01 | 10:00 | 1.7702 | 6.2748 |  | 10 |  | 75.8717
2017-07-01 | 10:05 | 1.7717 | 6.4076 |  | 10
2017-07-01 | 10:10 | 1.7327 | 6.3625 |  | 10
2017-07-01 | 10:15 | 1.7499 | 6.464 | 1 | 10 | 65.6722
2017-07-01 | 10:15 | 1.7499 | 6.464 |  | 10 |  | 75.8277
2017-07-01 | 10:20 | 1.76 | 6.6149 |  | 10
2017-07-01 | 10:25 | 1.7499 | 6.7244 |  | 10
2017-07-01 | 10:30 | 1.7647 | 6.7164 | 1 | 10 | 68.2184
2017-07-01 | 10:30 | 1.7647 | 6.7164 |  | 10 |  | 75.8834
2017-07-01 | 10:35 | 1.7429 | 6.6799 |  | 10
2017-07-01 | 10:40 | 1.7561 | 6.6094 |  | 10
2017-07-01 | 10:45 | 1.7429 | 6.6448 | 1 | 10 | 67.4149
2017-07-01 | 10:45 | 1.7429 | 6.6448 |  | 10 |  | 75.9335
2017-07-01 | 10:50 | 1.7444 | 6.491 |  | 10
2017-07-01 | 10:55 | 1.7468 | 6.2158 |  | 10
2017-07-01 | 11:00 | 1.7335 | 6.2034 | 1 | 10 | 63.0018
2017-07-01 | 11:00 | 1.7335 | 6.2034 |  | 10 |  | 75.946
2017-07-01 | 11:05 | 1.7491 | 6.3735 |  | 10
2017-07-01 | 11:10 | 1.7421 | 6.4468 |  | 10
2017-07-01 | 11:15 | 1.7436 | 6.3791 | 1 | 10 | 64.8508
2017-07-01 | 11:15 | 1.7436 | 6.3791 |  | 10 |  | 75.9783
2017-07-01 | 11:20 | 1.7592 | 6.4362 |  | 10
2017-07-01 | 11:25 | 1.7538 | 6.5264 |  | 10
2017-07-01 | 11:30 | 1.7202 | 6.5898 | 1 | 10 | 66.9508
2017-07-01 | 11:30 | 1.7202 | 6.5898 |  | 10 |  | 76.1787
2017-07-01 | 11:35 | 1.7288 | 6.5356 |  | 10
2017-07-01 | 11:40 | 1.746 | 6.5243 |  | 10
2017-07-01 | 11:45 | 1.7663 | 6.3948 | 1 | 10 | 65.0964
2017-07-01 | 11:45 | 1.7663 | 6.3948 |  | 10 |  | 76.3603
2017-07-01 | 11:50 | 1.7436 | 5.9795 |  | 10
2017-07-01 | 11:55 | 1.7421 | 5.9615 |  | 10
2017-07-01 | 12:00 | 1.7514 | 6.2386 | 1 | 10 | 63.4522
2017-07-01 | 12:00 | 1.7514 | 6.2386 |  | 10 |  | 76.3694
2017-07-01 | 12:05 | 1.767 | 3.7234 |  | 10
2017-07-01 | 12:10 | 1.7514 | 4.4959 |  | 10
2017-07-01 | 12:15 | 1.7507 | 4.551 | 1 | 10 | 48.804
2017-07-01 | 12:15 | 1.7507 | 4.551 |  | 10 |  | 76.0996
2017-07-01 | 12:20 | 1.675 | 1.287 |  | 1.5
2017-07-01 | 12:25 | 1.6781 | 0 |  | 1.5
2017-07-01 | 12:30 | 1.6727 | 0 | 0 | 1.5 | 25
2017-07-01 | 12:30 | 1.6727 | 0 |  | 1.5 |  | 78.3242
2017-07-01 | 12:35 | 1.689 | 0 |  | 1.5
2017-07-01 | 12:40 | 1.6672 | 0 |  | 1.5
2017-07-01 | 12:45 | 1.7273 | 0 | 0 | 1.5 | 25
2017-07-01 | 12:45 | 1.7273 | 0 |  | 1.5 |  | 78.6519
2017-07-01 | 12:50 | 1.7226 | 0 |  | 1.5
2017-07-01 | 12:55 | 1.7 | 0 |  | 1.5
2017-07-01 | 13:00 | 1.7304 | 0 | 0 | 1.5 | 25
2017-07-01 | 13:00 | 1.7304 | 0 |  | 1.5 |  | 79.2155
2017-07-01 | 13:05 | 1.7436 | 0 |  | 1.5
2017-07-01 | 13:10 | 1.7249 | 0 |  | 1.5
2017-07-01 | 13:15 | 1.7553 | 0 | 0 | 1.5 | 25
2017-07-01 | 13:15 | 1.7553 | 0 |  | 1.5 |  | 79.4223
2017-07-01 | 13:20 | 1.7522 | 0 |  | 1.5
2017-07-01 | 13:25 | 1.7678 | 0 |  | 1.5
2017-07-01 | 13:30 | 1.7522 | 0 | 0 | 1.5 | 25
2017-07-01 | 13:30 | 1.7522 | 0 |  | 1.5 |  | 79.36
2017-07-01 | 13:35 | 1.767 | 0 |  | 1.5
2017-07-01 | 13:40 | 1.7319 | 0 |  | 1.5
2017-07-01 | 13:45 | 1.7546 | 0 | 0 | 1.5 | 25
2017-07-01 | 13:45 | 1.7546 | 0 |  | 1.5 |  | 79.6085
2017-07-01 | 13:50 | 1.7468 | 0 |  | 1.5
2017-07-01 | 13:55 | 1.7202 | 0 |  | 1.5
2017-07-01 | 14:00 | 1.7179 | 0 | 0 | 1.5 | 25
2017-07-01 | 14:00 | 1.7179 | 0 |  | 1.5 |  | 79.9809
2017-07-01 | 14:05 | 1.7405 | 0 |  | 1.5
2017-07-01 | 14:10 | 1.7358 | 0 |  | 1.5
2017-07-01 | 14:15 | 1.7444 | 0 | 0 | 1.5 | 25
2017-07-01 | 14:15 | 1.7444 | 0 |  | 1.5 |  | 80.414
2017-07-01 | 14:20 | 1.7195 | 0 |  | 1.5
2017-07-01 | 14:25 | 1.7491 | 0 |  | 1.5
2017-07-01 | 14:30 | 1.7468 | 0 | 0 | 1.5 | 25
2017-07-01 | 14:30 | 1.7468 | 0 |  | 1.5 |  | 80.8306
2017-07-01 | 14:35 | 1.7444 | 0 |  | 1.5
2017-07-01 | 14:40 | 1.7561 | 0 |  | 1.5
2017-07-01 | 14:45 | 1.7187 | 0 | 0 | 1.5 | 25
2017-07-01 | 14:45 | 1.7187 | 0 |  | 1.5 |  | 81.2751
2017-07-01 | 14:50 | 1.7312 | 0 |  | 1.5
2017-07-01 | 14:55 | 1.7093 | 0 |  | 1.5
2017-07-01 | 15:00 | 1.7475 | 0 | 0 | 1.5 | 25
2017-07-01 | 15:00 | 1.7475 | 0 |  | 1.5 |  | 81.7538
2017-07-01 | 15:05 | 1.7546 | 0 |  | 1.5
2017-07-01 | 15:10 | 1.7655 | 0 |  | 1.5
2017-07-01 | 15:15 | 1.7725 | 0 | 0 | 1.5 | 25
2017-07-01 | 15:15 | 1.7725 | 0 |  | 1.5 |  | 81.908
2017-07-01 | 15:20 | 1.7148 | 0 |  | 1.5
2017-07-01 | 15:25 | 1.7483 | 0 |  | 1.5
2017-07-01 | 15:30 | 1.7834 | 0 | 0 | 1.5 | 25
2017-07-01 | 15:30 | 1.7834 | 0 |  | 1.5 |  | 81.8845
2017-07-01 | 15:35 | 1.7608 | 0 |  | 1.5
2017-07-01 | 15:40 | 1.7491 | 0 |  | 1.5
2017-07-01 | 15:45 | 1.7514 | 0 | 0 | 1.5 | 25
2017-07-01 | 15:45 | 1.7514 | 0 |  | 1.5 |  | 81.774
2017-07-01 | 15:50 | 1.7413 | 0 |  | 1.5
2017-07-01 | 15:55 | 1.7319 | 0 |  | 1.5
2017-07-01 | 16:00 | 1.7881 | 0 | 0 | 1.5 | 25
2017-07-01 | 16:00 | 1.7881 | 0 |  | 1.5 |  | 81.5498
2017-07-01 | 16:05 | 1.7725 | 0 |  | 1.5
2017-07-01 | 16:10 | 1.753 | 0 |  | 1.5
2017-07-01 | 16:15 | 1.7733 | 0 | 0 | 1.5 | 25
2017-07-01 | 16:15 | 1.7733 | 0 |  | 1.5 |  | 81.2961
2017-07-01 | 16:20 | 1.7585 | 0 |  | 1.5
2017-07-01 | 16:25 | 1.7538 | 0 |  | 1.5
2017-07-01 | 16:30 | 1.7499 | 0 | 0 | 1.5 | 25
2017-07-01 | 16:30 | 1.7499 | 0 |  | 1.5 |  | 81.2115
2017-07-01 | 16:35 | 1.7741 | 0 |  | 1.5
2017-07-01 | 16:40 | 1.7608 | 0 |  | 1.5
2017-07-01 | 16:45 | 1.7616 | 0 | 0 | 1.5 | 25
2017-07-01 | 16:45 | 1.7616 | 0 |  | 1.5 |  | 81.2948
2017-07-01 | 16:50 | 1.7546 | 0 |  | 1.5
2017-07-01 | 16:55 | 1.7319 | 0 |  | 1.5
2017-07-01 | 17:00 | 1.7507 | 0 | 0 | 1.5 | 25
2017-07-01 | 17:00 | 1.7507 | 0 |  | 1.5 |  | 81.2778
2017-07-01 | 17:05 | 1.7741 | 0 |  | 1.5
2017-07-01 | 17:10 | 1.7538 | 0 |  | 1.5
2017-07-01 | 17:15 | 1.7725 | 0 | 0 | 1.5 | 25
2017-07-01 | 17:15 | 1.7725 | 0 |  | 1.5 |  | 80.9794
2017-07-01 | 17:20 | 1.7655 | 0 |  | 1.5
2017-07-01 | 17:25 | 1.7725 | 0 |  | 1.5
2017-07-01 | 17:30 | 1.7631 | 0 | 0 | 1.5 | 25
2017-07-01 | 17:30 | 1.7631 | 0 |  | 1.5 |  | 80.4376
2017-07-01 | 17:35 | 1.7616 | 0 |  | 1.5
2017-07-01 | 17:40 | 1.7585 | 0 |  | 1.5
2017-07-01 | 17:45 | 1.7249 | 0 | 0 | 1.5 | 25
2017-07-01 | 17:45 | 1.7249 | 0 |  | 1.5 |  | 80.1922
2017-07-01 | 17:50 | 1.7491 | 0 |  | 1.5
2017-07-01 | 17:55 | 1.7202 | 0 |  | 1.5
2017-07-01 | 18:00 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-01 | 18:00 | 1.7585 | 0 |  | 1.5 |  | 80.1027
2017-07-01 | 18:05 | 1.7842 | 0 |  | 1.5
2017-07-01 | 18:10 | 1.7585 | 0 |  | 1.5
2017-07-01 | 18:15 | 1.7421 | 0 | 0 | 1.5 | 25
2017-07-01 | 18:15 | 1.7421 | 0 |  | 1.5 |  | 80.0844
2017-07-01 | 18:20 | 1.7546 | 0 |  | 1.5
2017-07-01 | 18:25 | 1.7491 | 0 |  | 1.5
2017-07-01 | 18:30 | 1.7787 | 0 | 0 | 1.5 | 25
2017-07-01 | 18:30 | 1.7787 | 0 |  | 1.5 |  | 80.0233
2017-07-01 | 18:35 | 1.7553 | 0 |  | 1.5
2017-07-01 | 18:40 | 1.7772 | 0 |  | 1.5
2017-07-01 | 18:45 | 1.7124 | 0 | 0 | 1.5 | 25
2017-07-01 | 18:45 | 1.7124 | 0 |  | 1.5 |  | 79.9872
2017-07-01 | 18:50 | 1.7639 | 0 |  | 1.5
2017-07-01 | 18:55 | 1.7577 | 0 |  | 1.5
2017-07-01 | 19:00 | 1.728 | 0 | 0 | 1.5 | 25
2017-07-01 | 19:00 | 1.728 | 0 |  | 1.5 |  | 79.8721
2017-07-01 | 19:05 | 1.753 | 0 |  | 1.5
2017-07-01 | 19:10 | 1.7273 | 0 |  | 1.5
2017-07-01 | 19:15 | 1.778 | 0 | 0 | 1.5 | 25
2017-07-01 | 19:15 | 1.778 | 0 |  | 1.5 |  | 79.7545
2017-07-01 | 19:20 | 1.7569 | 0 |  | 1.5
2017-07-01 | 19:25 | 1.739 | 0 |  | 1.5
2017-07-01 | 19:30 | 1.7319 | 0 | 0 | 1.5 | 25
2017-07-01 | 19:30 | 1.7319 | 0 |  | 1.5 |  | 79.8847
2017-07-01 | 19:35 | 1.6953 | 0 |  | 1.5
2017-07-01 | 19:40 | 1.7226 | 0 |  | 1.5
2017-07-01 | 19:45 | 1.7741 | 0 | 0 | 1.5 | 25
2017-07-01 | 19:45 | 1.7741 | 0 |  | 1.5 |  | 80.3416
2017-07-01 | 19:50 | 1.76 | 0 |  | 1.5
2017-07-01 | 19:55 | 1.7569 | 0 |  | 1.5
2017-07-01 | 20:00 | 1.7608 | 0 | 0 | 1.5 | 25
2017-07-01 | 20:00 | 1.7608 | 0 |  | 1.5 |  | 79.9481
2017-07-01 | 20:05 | 1.7702 | 0 |  | 1.5
2017-07-01 | 20:10 | 1.7585 | 0 |  | 1.5
2017-07-01 | 20:15 | 1.7764 | 0 | 0 | 1.5 | 25
2017-07-01 | 20:15 | 1.7764 | 0 |  | 1.5 |  | 79.8264
2017-07-01 | 20:20 | 1.7655 | 0 |  | 1.5
2017-07-01 | 20:25 | 1.728 | 0 |  | 1.5
2017-07-01 | 20:30 | 1.7483 | 0 | 0 | 1.5 | 25
2017-07-01 | 20:30 | 1.7483 | 0 |  | 1.5 |  | 79.7557
2017-07-01 | 20:35 | 1.7249 | 0 |  | 1.5
2017-07-01 | 20:40 | 1.7694 | 0 |  | 1.5
2017-07-01 | 20:45 | 1.7444 | 0 | 0 | 1.5 | 25
2017-07-01 | 20:45 | 1.7444 | 0 |  | 1.5 |  | 79.7199
2017-07-01 | 20:50 | 1.7624 | 0 |  | 1.5
2017-07-01 | 20:55 | 1.746 | 0 |  | 1.5
2017-07-01 | 21:00 | 1.7429 | 0 | 0 | 1.5 | 25
2017-07-01 | 21:00 | 1.7429 | 0 |  | 1.5 |  | 0
2017-07-01 | 21:05 | -0.10652 | 0 |  | 1.5
2017-07-01 | 21:10 | -0.1073 | 0 |  | 1.5
2017-07-01 | 21:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-01 | 21:15 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-01 | 21:20 | -0.10808 | 0 |  | 1.5
2017-07-01 | 21:25 | -0.10808 | 0 |  | 1.5
2017-07-01 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-01 | 21:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-01 | 21:35 | -0.10808 | 0 |  | 1.5
2017-07-01 | 21:40 | -0.10886 | 0 |  | 1.5
2017-07-01 | 21:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 21:45 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 21:50 | -0.10886 | 0 |  | 1.5
2017-07-01 | 21:55 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 22:00 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 22:05 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:10 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 22:15 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 22:20 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:25 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 22:30 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 22:35 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:40 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 22:45 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 22:50 | -0.10886 | 0 |  | 1.5
2017-07-01 | 22:55 | -0.10886 | 0 |  | 1.5
2017-07-01 | 23:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-01 | 23:00 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-01 | 23:05 | -0.10886 | 0 |  | 1.5
2017-07-01 | 23:10 | -0.1112 | 0 |  | 1.5
2017-07-01 | 23:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-01 | 23:15 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-01 | 23:20 | -0.10964 | 0 |  | 1.5
2017-07-01 | 23:25 | -0.10886 | 0 |  | 1.5
2017-07-01 | 23:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 23:30 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 23:35 | -0.10886 | 0 |  | 1.5
2017-07-01 | 23:40 | -0.10964 | 0 |  | 1.5
2017-07-01 | 23:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-01 | 23:45 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-01 | 23:50 | -0.10886 | 0 |  | 1.5
2017-07-01 | 23:55 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-02 | 0:00 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-02 | 0:05 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:10 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 0:20 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:25 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 0:35 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:40 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 0:50 | -0.10886 | 0 |  | 1.5
2017-07-02 | 0:55 | -0.10886 | 0 |  | 1.5
2017-07-02 | 1:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 1:05 | -0.10886 | 0 |  | 1.5
2017-07-02 | 1:10 | -0.10886 | 0 |  | 1.5
2017-07-02 | 1:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-02 | 1:25 | -0.11198 | 0 |  | 1.5
2017-07-02 | 1:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 1:35 | -0.11198 | 0 |  | 1.5
2017-07-02 | 1:40 | -0.1112 | 0 |  | 1.5
2017-07-02 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 1:50 | -0.1112 | 0 |  | 1.5
2017-07-02 | 1:55 | -0.1112 | 0 |  | 1.5
2017-07-02 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 2:05 | -0.1112 | 0 |  | 1.5
2017-07-02 | 2:10 | -0.11198 | 0 |  | 1.5
2017-07-02 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 2:20 | -0.1112 | 0 |  | 1.5
2017-07-02 | 2:25 | -0.1112 | 0 |  | 1.5
2017-07-02 | 2:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 2:35 | -0.1112 | 0 |  | 1.5
2017-07-02 | 2:40 | -0.11198 | 0 |  | 1.5
2017-07-02 | 2:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-02 | 2:55 | -0.1112 | 0 |  | 1.5
2017-07-02 | 3:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 3:05 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:10 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 3:20 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:25 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 3:35 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:40 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 3:50 | -0.11198 | 0 |  | 1.5
2017-07-02 | 3:55 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 4:05 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:10 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:15 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 4:20 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:25 | -0.11276 | 0 |  | 1.5
2017-07-02 | 4:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 4:35 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:40 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 4:50 | -0.11198 | 0 |  | 1.5
2017-07-02 | 4:55 | -0.11276 | 0 |  | 1.5
2017-07-02 | 5:00 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 5:05 | 2.3832 | 6.0435 |  | 10
2017-07-02 | 5:10 | 2.1664 | 9.677 |  | 10
2017-07-02 | 5:15 | 2.0689 | 9.3847 | 1 | 10 | 95.9161 | 88.4995
2017-07-02 | 5:20 | 1.9971 | 8.8518 |  | 10
2017-07-02 | 5:25 | 1.9558 | 8.2373 |  | 10
2017-07-02 | 5:30 | 1.8926 | 7.9525 | 1 | 10 | 81.9652 | 82.6482
2017-07-02 | 5:35 | 1.8497 | 7.4224 |  | 10
2017-07-02 | 5:40 | 1.856 | 7.2162 |  | 10
2017-07-02 | 5:45 | 1.8154 | 7.0003 | 1 | 10 | 72.7057 | 79.9845
2017-07-02 | 5:50 | 1.8107 | 6.7389 |  | 10
2017-07-02 | 5:55 | 1.7624 | 6.7768 |  | 10
2017-07-02 | 6:00 | 1.7647 | 6.4804 | 1 | 10 | 67.5399 | 78.972
2017-07-02 | 6:05 | 1.7405 | 6.92 |  | 10
2017-07-02 | 6:10 | 1.753 | 6.9403 |  | 10
2017-07-02 | 6:15 | 1.739 | 6.915 | 1 | 10 | 71.5754 | 78.4402
2017-07-02 | 6:20 | 1.7647 | 6.9383 |  | 10
2017-07-02 | 6:25 | 1.7616 | 6.746 |  | 10
2017-07-02 | 6:30 | 1.7522 | 6.8133 | 1 | 10 | 70.698 | 78.1158
2017-07-02 | 6:35 | 1.7514 | 6.6732 |  | 10
2017-07-02 | 6:40 | 1.7436 | 6.6151 |  | 10
2017-07-02 | 6:45 | 1.7943 | 6.7583 | 1 | 10 | 70.1327 | 77.7003
2017-07-02 | 6:50 | 1.7546 | 6.5195 |  | 10
2017-07-02 | 6:55 | 1.7912 | 6.4324 |  | 10
2017-07-02 | 7:00 | 1.7639 | 6.3248 | 1 | 10 | 66.0711 | 77.1906
2017-07-02 | 7:05 | 1.7499 | 6.3595 |  | 10
2017-07-02 | 7:10 | 1.7741 | 6.3417 |  | 10
2017-07-02 | 7:15 | 1.7522 | 6.2328 | 1 | 10 | 64.9167 | 76.9177
2017-07-02 | 7:20 | 1.7475 | 6.4352 |  | 10
2017-07-02 | 7:25 | 1.7694 | 6.2662 |  | 10
2017-07-02 | 7:30 | 1.7475 | 6.3484 | 1 | 10 | 66.2733 | 76.7583
2017-07-02 | 7:35 | 1.7826 | 6.2688 |  | 10
2017-07-02 | 7:40 | 1.7546 | 6.1061 |  | 10
2017-07-02 | 7:45 | 1.7608 | 6.155 | 1 | 10 | 64.2336 | 76.4474
2017-07-02 | 7:50 | 1.7429 | 6.068 |  | 10
2017-07-02 | 7:55 | 1.7709 | 6.0592 |  | 10
2017-07-02 | 8:00 | 1.7655 | 6.1038 | 1 | 10 | 63.7528 | 76.2377
2017-07-02 | 8:05 | 1.7468 | 6.3191 |  | 10
2017-07-02 | 8:10 | 1.7483 | 6.5984 |  | 10
2017-07-02 | 8:15 | 1.7538 | 6.4709 | 1 | 10 | 67.1875 | 76.146
2017-07-02 | 8:20 | 1.7319 | 6.8596 |  | 10
2017-07-02 | 8:25 | 1.7538 | 6.9309 |  | 10
2017-07-02 | 8:30 | 1.7085 | 6.8565 | 1 | 10 | 70.9653 | 76.3413
2017-07-02 | 8:35 | 1.7452 | 7.1669 |  | 10
2017-07-02 | 8:40 | 1.7522 | 7.2621 |  | 10
2017-07-02 | 8:45 | 1.7569 | 7.3706 | 1 | 10 | 76.4272 | 76.5078
2017-07-02 | 8:50 | 1.7444 | 7.2224 |  | 10
2017-07-02 | 8:55 | 1.7429 | 7.2798 |  | 10
2017-07-02 | 9:00 | 1.7538 | 7.0995 | 1 | 10 | 73.5307 | 76.6397
2017-07-02 | 9:05 | 1.7452 | 7.1026 |  | 10
2017-07-02 | 9:10 | 1.7507 | 6.9747 |  | 10
2017-07-02 | 9:15 | 1.7694 | 6.7215 | 1 | 10 | 69.8654 | 76.5931
2017-07-02 | 9:20 | 1.7405 | 6.7965 |  | 10
2017-07-02 | 9:25 | 1.7296 | 6.8663 |  | 10
2017-07-02 | 9:30 | 1.7499 | 6.7315 | 1 | 10 | 69.6925 | 76.6084
2017-07-02 | 9:35 | 1.7553 | 6.7513 |  | 10
2017-07-02 | 9:40 | 1.7522 | 6.625 |  | 10
2017-07-02 | 9:45 | 1.7491 | 6.9915 | 1 | 10 | 72.0456 | 76.7415
2017-07-02 | 9:50 | 1.7273 | 6.8459 |  | 10
2017-07-02 | 9:55 | 1.728 | 6.9955 |  | 10
2017-07-02 | 10:00 | 1.7335 | 7.1178 | 1 | 10 | 73.6882 | 77.0869
2017-07-02 | 10:05 | 1.7507 | 7.1869 |  | 10
2017-07-02 | 10:10 | 1.7553 | 6.2207 |  | 10
2017-07-02 | 10:15 | 1.8076 | 3.5791 | 1 | 10 | 40.5747 | 76.898
2017-07-02 | 10:20 | 1.6149 | 1.647 |  | 1.5
2017-07-02 | 10:25 | 1.8209 | 0.81387 |  | 10
2017-07-02 | 10:30 | 1.7678 | 3.0309 | 0 | 1.5 | 52.2 | 76.9479
2017-07-02 | 10:35 | 1.6422 | 0 |  | 1.5
2017-07-02 | 10:40 | 1.7124 | 0 |  | 1.5
2017-07-02 | 10:45 | 1.7187 | 0 | 0 | 1.5 | 25 | 79.2581
2017-07-02 | 10:50 | 1.739 | 0 |  | 1.5
2017-07-02 | 10:55 | 1.7444 | 0 |  | 1.5
2017-07-02 | 11:00 | 1.7351 | 0 | 0 | 1.5 | 25 | 79.4824
2017-07-02 | 11:05 | 1.7421 | 0 |  | 1.5
2017-07-02 | 11:10 | 1.7475 | 0 |  | 1.5
2017-07-02 | 11:15 | 1.728 | 0 | 0 | 1.5 | 25 | 79.694
2017-07-02 | 11:20 | 1.7436 | 0 |  | 1.5
2017-07-02 | 11:25 | 1.746 | 0 |  | 1.5
2017-07-02 | 11:30 | 1.7304 | 0 | 0 | 1.5 | 25 | 80.0098
2017-07-02 | 11:35 | 1.7522 | 0 |  | 1.5
2017-07-02 | 11:40 | 1.739 | 0 |  | 1.5
2017-07-02 | 11:45 | 1.7257 | 0 | 0 | 1.5 | 25 | 80.3668
2017-07-02 | 11:50 | 1.7483 | 0 |  | 1.5
2017-07-02 | 11:55 | 1.7226 | 0 |  | 1.5
2017-07-02 | 12:00 | 1.7335 | 0 | 0 | 1.5 | 25 | 80.8755
2017-07-02 | 12:05 | 1.714 | 0 |  | 1.5
2017-07-02 | 12:10 | 1.7179 | 0 |  | 1.5
2017-07-02 | 12:15 | 1.7436 | 0 | 0 | 1.5 | 25 | 81.5389
2017-07-02 | 12:20 | 1.7187 | 0 |  | 1.5
2017-07-02 | 12:25 | 1.7468 | 0 |  | 1.5
2017-07-02 | 12:30 | 1.7078 | 0 | 0 | 1.5 | 25 | 82.434
2017-07-02 | 12:35 | 1.707 | 0 |  | 1.5
2017-07-02 | 12:40 | 1.7327 | 0 |  | 1.5
2017-07-02 | 12:45 | 1.7101 | 0 | 0 | 1.5 | 25 | 83.27
2017-07-02 | 12:50 | 1.7234 | 0 |  | 1.5
2017-07-02 | 12:55 | 1.7101 | 0 |  | 1.5
2017-07-02 | 13:00 | 1.7124 | 0 | 0 | 1.5 | 25 | 83.8557
2017-07-02 | 13:05 | 1.7429 | 0 |  | 1.5
2017-07-02 | 13:10 | 1.7265 | 0 |  | 1.5
2017-07-02 | 13:15 | 1.7156 | 0 | 0 | 1.5 | 25 | 84.3628
2017-07-02 | 13:20 | 1.7218 | 0 |  | 1.5
2017-07-02 | 13:25 | 1.7491 | 0 |  | 1.5
2017-07-02 | 13:30 | 1.7296 | 0 | 0 | 1.5 | 25 | 84.7463
2017-07-02 | 13:35 | 1.7358 | 0 |  | 1.5
2017-07-02 | 13:40 | 1.7319 | 0 |  | 1.5
2017-07-02 | 13:45 | 1.7312 | 0 | 0 | 1.5 | 25 | 85.2012
2017-07-02 | 13:50 | 1.7179 | 0 |  | 1.5
2017-07-02 | 13:55 | 1.7436 | 0 |  | 1.5
2017-07-02 | 14:00 | 1.7475 | 0 | 0 | 1.5 | 25 | 85.6531
2017-07-02 | 14:05 | 1.7561 | 0 |  | 1.5
2017-07-02 | 14:10 | 1.7421 | 0 |  | 1.5
2017-07-02 | 14:15 | 1.7631 | 0 | 0 | 1.5 | 25 | 85.8192
2017-07-02 | 14:20 | 1.7553 | 0 |  | 1.5
2017-07-02 | 14:25 | 1.7343 | 0 |  | 1.5
2017-07-02 | 14:30 | 1.7702 | 0 | 0 | 1.5 | 25 | 85.7234
2017-07-02 | 14:35 | 1.76 | 0 |  | 1.5
2017-07-02 | 14:40 | 1.7592 | 0 |  | 1.5
2017-07-02 | 14:45 | 1.7741 | 0 | 0 | 1.5 | 25 | 85.6384
2017-07-02 | 14:50 | 1.7452 | 0 |  | 1.5
2017-07-02 | 14:55 | 1.7265 | 0 |  | 1.5
2017-07-02 | 15:00 | 1.767 | 0 | 0 | 1.5 | 25 | 85.5745
2017-07-02 | 15:05 | 1.7374 | 0 |  | 1.5
2017-07-02 | 15:10 | 1.7413 | 0 |  | 1.5
2017-07-02 | 15:15 | 1.7546 | 0 | 0 | 1.5 | 25 | 85.502
2017-07-02 | 15:20 | 1.7366 | 0 |  | 1.5
2017-07-02 | 15:25 | 1.7725 | 0 |  | 1.5
2017-07-02 | 15:30 | 1.7717 | 0 | 0 | 1.5 | 25 | 85.0249
2017-07-02 | 15:35 | 1.7608 | 0 |  | 1.5
2017-07-02 | 15:40 | 1.7826 | 0 |  | 1.5
2017-07-02 | 15:45 | 1.7881 | 0 | 0 | 1.5 | 25 | 84.4775
2017-07-02 | 15:50 | 1.7694 | 0 |  | 1.5
2017-07-02 | 15:55 | 1.7709 | 0 |  | 1.5
2017-07-02 | 16:00 | 1.7803 | 0 | 0 | 1.5 | 25 | 83.7152
2017-07-02 | 16:05 | 1.7951 | 0 |  | 1.5
2017-07-02 | 16:10 | 1.7842 | 0 |  | 1.5
2017-07-02 | 16:15 | 1.7772 | 0 | 0 | 1.5 | 25 | 82.7356
2017-07-02 | 16:20 | 1.7928 | 0 |  | 1.5
2017-07-02 | 16:25 | 1.7928 | 0 |  | 1.5
2017-07-02 | 16:30 | 1.7686 | 0 | 0 | 1.5 | 25 | 81.919
2017-07-02 | 16:35 | 1.7678 | 0 |  | 1.5
2017-07-02 | 16:40 | 1.7585 | 0 |  | 1.5
2017-07-02 | 16:45 | 1.7444 | 0 | 0 | 1.5 | 25 | 81.3809
2017-07-02 | 16:50 | 1.7351 | 0 |  | 1.5
2017-07-02 | 16:55 | 1.7702 | 0 |  | 1.5
2017-07-02 | 17:00 | 1.7795 | 0 | 0 | 1.5 | 25 | 81.0953
2017-07-02 | 17:05 | 1.7663 | 0 |  | 1.5
2017-07-02 | 17:10 | 1.7709 | 0 |  | 1.5
2017-07-02 | 17:15 | 1.7413 | 0 | 0 | 1.5 | 25 | 80.7514
2017-07-02 | 17:20 | 1.7483 | 0 |  | 1.5
2017-07-02 | 17:25 | 1.7858 | 0 |  | 1.5
2017-07-02 | 17:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 80.1351
2017-07-02 | 17:35 | 1.7663 | 0 |  | 1.5
2017-07-02 | 17:40 | 1.7569 | 0 |  | 1.5
2017-07-02 | 17:45 | 1.7553 | 0 | 0 | 1.5 | 25 | 79.768
2017-07-02 | 17:50 | 1.7702 | 0 |  | 1.5
2017-07-02 | 17:55 | 1.7483 | 0 |  | 1.5
2017-07-02 | 18:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 79.5102
2017-07-02 | 18:05 | 1.778 | 0 |  | 1.5
2017-07-02 | 18:10 | 1.7436 | 0 |  | 1.5
2017-07-02 | 18:15 | 1.7429 | 0 | 0 | 1.5 | 25 | 79.3463
2017-07-02 | 18:20 | 1.7405 | 0 |  | 1.5
2017-07-02 | 18:25 | 1.7546 | 0 |  | 1.5
2017-07-02 | 18:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 79.2811
2017-07-02 | 18:35 | 1.7787 | 0 |  | 1.5
2017-07-02 | 18:40 | 1.7592 | 0 |  | 1.5
2017-07-02 | 18:45 | 1.7273 | 0 | 0 | 1.5 | 25 | 79.1213
2017-07-02 | 18:50 | 1.7499 | 0 |  | 1.5
2017-07-02 | 18:55 | 1.7413 | 0 |  | 1.5
2017-07-02 | 19:00 | 1.7413 | 0 | 0 | 1.5 | 25 | 78.8962
2017-07-02 | 19:05 | 1.7499 | 0 |  | 1.5
2017-07-02 | 19:10 | 1.778 | 0 |  | 1.5
2017-07-02 | 19:15 | 1.7218 | 0 | 0 | 1.5 | 25 | 78.7047
2017-07-02 | 19:20 | 1.7569 | 0 |  | 1.5
2017-07-02 | 19:25 | 1.7382 | 0 |  | 1.5
2017-07-02 | 19:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 78.5669
2017-07-02 | 19:35 | 1.7405 | 0 |  | 1.5
2017-07-02 | 19:40 | 1.7577 | 0 |  | 1.5
2017-07-02 | 19:45 | 1.7452 | 0 | 0 | 1.5 | 25 | 78.7425
2017-07-02 | 19:50 | 1.7678 | 0 |  | 1.5
2017-07-02 | 19:55 | 1.7304 | 0 |  | 1.5
2017-07-02 | 20:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 79.0563
2017-07-02 | 20:05 | 1.7429 | 0 |  | 1.5
2017-07-02 | 20:10 | 1.7124 | 0 |  | 1.5
2017-07-02 | 20:15 | 1.7335 | 0 | 0 | 1.5 | 25 | 79.3562
2017-07-02 | 20:20 | 1.739 | 0 |  | 1.5
2017-07-02 | 20:25 | 1.7366 | 0 |  | 1.5
2017-07-02 | 20:30 | 1.7101 | 0 | 0 | 1.5 | 25 | 79.867
2017-07-02 | 20:35 | 1.7522 | 0 |  | 1.5
2017-07-02 | 20:40 | 1.7382 | 0 |  | 1.5
2017-07-02 | 20:45 | 1.7811 | 0 | 0 | 1.5 | 25 | 79.921
2017-07-02 | 20:50 | 1.7787 | 0 |  | 1.5
2017-07-02 | 20:55 | 1.7811 | 0 |  | 1.5
2017-07-02 | 21:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 79.5786
2017-07-02 | 21:05 | -0.10574 | 0 |  | 1.5
2017-07-02 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-02 | 21:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 21:20 | -0.10808 | 0 |  | 1.5
2017-07-02 | 21:25 | -0.10808 | 0 |  | 1.5
2017-07-02 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 21:35 | -0.10886 | 0 |  | 1.5
2017-07-02 | 21:40 | -0.10808 | 0 |  | 1.5
2017-07-02 | 21:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 21:50 | -0.10964 | 0 |  | 1.5
2017-07-02 | 21:55 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 22:05 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:10 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 22:20 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:25 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 22:35 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:40 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 22:50 | -0.10886 | 0 |  | 1.5
2017-07-02 | 22:55 | -0.10886 | 0 |  | 1.5
2017-07-02 | 23:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 23:05 | -0.10886 | 0 |  | 1.5
2017-07-02 | 23:10 | -0.10886 | 0 |  | 1.5
2017-07-02 | 23:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 23:20 | -0.10886 | 0 |  | 1.5
2017-07-02 | 23:25 | -0.10808 | 0 |  | 1.5
2017-07-02 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 23:35 | -0.10808 | 0 |  | 1.5
2017-07-02 | 23:40 | -0.10886 | 0 |  | 1.5
2017-07-02 | 23:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-02 | 23:50 | -0.10886 | 0 |  | 1.5
2017-07-02 | 23:55 | -0.10886 | 0 |  | 1.5
2017-07-03 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 0:05 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:10 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 0:20 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:25 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 0:35 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:40 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 0:50 | -0.10808 | 0 |  | 1.5
2017-07-03 | 0:55 | -0.10808 | 0 |  | 1.5
2017-07-03 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 1:05 | -0.10808 | 0 |  | 1.5
2017-07-03 | 1:10 | -0.10808 | 0 |  | 1.5
2017-07-03 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-03 | 1:25 | -0.11042 | 0 |  | 1.5
2017-07-03 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 1:35 | -0.11042 | 0 |  | 1.5
2017-07-03 | 1:40 | -0.11042 | 0 |  | 1.5
2017-07-03 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-03 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-03 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-03 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-03 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 2:20 | -0.1112 | 0 |  | 1.5
2017-07-03 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-03 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-03 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-03 | 2:45 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-03 | 2:55 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 3:05 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-03 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 3:20 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:25 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:40 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 3:50 | -0.1112 | 0 |  | 1.5
2017-07-03 | 3:55 | -0.1112 | 0 |  | 1.5
2017-07-03 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 4:05 | -0.11198 | 0 |  | 1.5
2017-07-03 | 4:10 | -0.1112 | 0 |  | 1.5
2017-07-03 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 4:20 | -0.11198 | 0 |  | 1.5
2017-07-03 | 4:25 | -0.119 | 0 |  | 1.5
2017-07-03 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 4:35 | -0.1112 | 0 |  | 1.5
2017-07-03 | 4:40 | -0.11198 | 0 |  | 1.5
2017-07-03 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 4:50 | -0.11198 | 0 |  | 1.5
2017-07-03 | 4:55 | -0.1112 | 0 |  | 1.5
2017-07-03 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 5:05 | 2.3224 | 5.9865 |  | 10
2017-07-03 | 5:10 | 2.0861 | 10 |  | 10
2017-07-03 | 5:15 | 2.0252 | 10 | 1 | 10 | 100 | 89.3522
2017-07-03 | 5:20 | 1.9628 | 9.9278 |  | 10
2017-07-03 | 5:25 | 1.9605 | 9.4877 |  | 10
2017-07-03 | 5:30 | 1.941 | 9.1056 | 1 | 10 | 91.0842 | 83.5343
2017-07-03 | 5:35 | 1.8614 | 9.0314 |  | 10
2017-07-03 | 5:40 | 1.8747 | 8.2659 |  | 10
2017-07-03 | 5:45 | 1.8435 | 7.7501 | 1 | 10 | 78.5263 | 80.391
2017-07-03 | 5:50 | 1.831 | 7.473 |  | 10
2017-07-03 | 5:55 | 1.7967 | 7.4776 |  | 10
2017-07-03 | 6:00 | 1.7975 | 7.1029 | 1 | 10 | 72.0656 | 78.8476
2017-07-03 | 6:05 | 1.7865 | 6.9222 |  | 10
2017-07-03 | 6:10 | 1.7655 | 6.9535 |  | 10
2017-07-03 | 6:15 | 1.7795 | 7.1607 | 1 | 10 | 72.3936 | 77.9221
2017-07-03 | 6:20 | 1.7655 | 7.2745 |  | 10
2017-07-03 | 6:25 | 1.7694 | 7.062 |  | 10
2017-07-03 | 6:30 | 1.8006 | 6.6431 | 1 | 10 | 67.7346 | 77.3893
2017-07-03 | 6:35 | 1.7507 | 7.4068 |  | 10
2017-07-03 | 6:40 | 1.7522 | 7.1588 |  | 10
2017-07-03 | 6:45 | 1.7538 | 7.2453 | 1 | 10 | 73.1628 | 77.2266
2017-07-03 | 6:50 | 1.7499 | 7.2863 |  | 10
2017-07-03 | 6:55 | 1.7928 | 6.7768 |  | 10
2017-07-03 | 7:00 | 1.7795 | 6.8097 | 1 | 10 | 69.2391 | 76.6222
2017-07-03 | 7:05 | 1.7725 | 6.9888 |  | 10
2017-07-03 | 7:10 | 1.7772 | 6.5702 |  | 10
2017-07-03 | 7:15 | 1.7678 | 6.1899 | 1 | 10 | 63.4476 | 76.0194
2017-07-03 | 7:20 | 1.7538 | 6.2283 |  | 10
2017-07-03 | 7:25 | 1.7725 | 6.2482 |  | 10
2017-07-03 | 7:30 | 1.7546 | 6.1996 | 1 | 10 | 63.5951 | 75.5394
2017-07-03 | 7:35 | 1.7522 | 6.7503 |  | 10
2017-07-03 | 7:40 | 1.7444 | 6.5534 |  | 10
2017-07-03 | 7:45 | 1.7561 | 6.6442 | 1 | 10 | 67.3508 | 75.3714
2017-07-03 | 7:50 | 1.7319 | 6.4837 |  | 10
2017-07-03 | 7:55 | 1.7655 | 6.1217 |  | 10
2017-07-03 | 8:00 | 1.7351 | 6.1665 | 1 | 10 | 62.8633 | 75.2531
2017-07-03 | 8:05 | 1.7491 | 6.7018 |  | 10
2017-07-03 | 8:10 | 1.7483 | 6.7174 |  | 10
2017-07-03 | 8:15 | 1.7335 | 6.6078 | 1 | 10 | 66.8008 | 75.4156
2017-07-03 | 8:20 | 1.7366 | 6.2383 |  | 10
2017-07-03 | 8:25 | 1.7366 | 6.1471 |  | 10
2017-07-03 | 8:30 | 1.7312 | 6.0053 | 1 | 10 | 61.1796 | 75.5746
2017-07-03 | 8:35 | 1.7366 | 6.5234 |  | 10
2017-07-03 | 8:40 | 1.7343 | 6.6859 |  | 10
2017-07-03 | 8:45 | 1.8232 | 6.3637 | 1 | 10 | 65.132 | 75.3624
2017-07-03 | 8:50 | 1.8092 | 6.1662 |  | 10
2017-07-03 | 8:55 | 1.7795 | 5.2256 |  | 10
2017-07-03 | 9:00 | 1.7756 | 5.1594 | 1 | 10 | 52.6764 | 73.8313
2017-07-03 | 9:05 | 1.7748 | 4.7435 |  | 10
2017-07-03 | 9:10 | 1.7522 | 4.8165 |  | 10
2017-07-03 | 9:15 | 1.7413 | 5.3009 | 1 | 10 | 54.1054 | 73.2247
2017-07-03 | 9:20 | 1.7522 | 4.8864 |  | 10
2017-07-03 | 9:25 | 1.7483 | 5.0518 |  | 10
2017-07-03 | 9:30 | 1.7819 | 4.6118 | 1 | 10 | 48.1779 | 72.9434
2017-07-03 | 9:35 | 1.7561 | 4.8582 |  | 10
2017-07-03 | 9:40 | 1.7148 | 5.0106 |  | 10
2017-07-03 | 9:45 | 1.7382 | 4.6099 | 1 | 10 | 48.0273 | 73.1625
2017-07-03 | 9:50 | 1.7109 | 4.9435 |  | 10
2017-07-03 | 9:55 | 1.7499 | 5.0628 |  | 10
2017-07-03 | 10:00 | 1.7327 | 4.9005 | 1 | 10 | 50.3254 | 73.4919
2017-07-03 | 10:05 | 1.7397 | 4.5372 |  | 10
2017-07-03 | 10:10 | 1.7397 | 4.8292 |  | 10
2017-07-03 | 10:15 | 1.7405 | 5.4714 | 1 | 10 | 55.3464 | 73.8304
2017-07-03 | 10:20 | 1.7171 | 6.4051 |  | 10
2017-07-03 | 10:25 | 1.7382 | 6.0012 |  | 10
2017-07-03 | 10:30 | 1.7413 | 5.6985 | 1 | 10 | 58.4065 | 74.1767
2017-07-03 | 10:35 | 1.7538 | 5.5103 |  | 10
2017-07-03 | 10:40 | 1.7358 | 5.1819 |  | 10
2017-07-03 | 10:45 | 1.7616 | 4.6778 | 1 | 10 | 48.9931 | 74.1354
2017-07-03 | 10:50 | 1.7522 | 4.5991 |  | 10
2017-07-03 | 10:55 | 1.7592 | 4.8842 |  | 10
2017-07-03 | 11:00 | 1.7288 | 5.2984 | 1 | 10 | 54.2537 | 74.3128
2017-07-03 | 11:05 | 1.7124 | 5.7274 |  | 10
2017-07-03 | 11:10 | 1.7405 | 4.8451 |  | 10
2017-07-03 | 11:15 | 1.7187 | 4.9614 | 1 | 10 | 50.8034 | 74.7567
2017-07-03 | 11:20 | 1.7195 | 5.1077 |  | 10
2017-07-03 | 11:25 | 1.7 | 5.4776 |  | 10
2017-07-03 | 11:30 | 1.739 | 4.917 | 1 | 10 | 50.464 | 75.4776
2017-07-03 | 11:35 | 1.7187 | 5.0889 |  | 10
2017-07-03 | 11:40 | 1.5042 | 5.3887 |  | 1.5
2017-07-03 | 11:45 | 1.6625 | 1.4087 | 0 | 1.5 | 25 | 77.785
2017-07-03 | 11:50 | 1.65 | 0.002618 |  | 1.5
2017-07-03 | 11:55 | 1.6937 | 0 |  | 1.5
2017-07-03 | 12:00 | 1.6984 | 0 | 0 | 1.5 | 25 | 79.7405
2017-07-03 | 12:05 | 1.7343 | 0 |  | 1.5
2017-07-03 | 12:10 | 1.7202 | 0 |  | 1.5
2017-07-03 | 12:15 | 1.7039 | 0 | 0 | 1.5 | 25 | 80.6761
2017-07-03 | 12:20 | 1.7156 | 0 |  | 1.5
2017-07-03 | 12:25 | 1.7187 | 0 |  | 1.5
2017-07-03 | 12:30 | 1.7241 | 0 | 0 | 1.5 | 25 | 81.2684
2017-07-03 | 12:35 | 1.7351 | 0 |  | 1.5
2017-07-03 | 12:40 | 1.6742 | 0 |  | 1.5
2017-07-03 | 12:45 | 1.7171 | 0 | 0 | 1.5 | 25 | 81.781
2017-07-03 | 12:50 | 1.721 | 0 |  | 1.5
2017-07-03 | 12:55 | 1.7187 | 0 |  | 1.5
2017-07-03 | 13:00 | 1.746 | 0 | 0 | 1.5 | 25 | 82.2756
2017-07-03 | 13:05 | 1.7101 | 0 |  | 1.5
2017-07-03 | 13:10 | 1.7491 | 0 |  | 1.5
2017-07-03 | 13:15 | 1.7195 | 0 | 0 | 1.5 | 25 | 82.629
2017-07-03 | 13:20 | 1.7577 | 0 |  | 1.5
2017-07-03 | 13:25 | 1.7514 | 0 |  | 1.5
2017-07-03 | 13:30 | 1.7218 | 0 | 0 | 1.5 | 25 | 82.697
2017-07-03 | 13:35 | 1.7413 | 0 |  | 1.5
2017-07-03 | 13:40 | 1.7351 | 0 |  | 1.5
2017-07-03 | 13:45 | 1.6844 | 0 | 0 | 1.5 | 25 | 83.2761
2017-07-03 | 13:50 | 1.714 | 0 |  | 1.5
2017-07-03 | 13:55 | 1.7163 | 0 |  | 1.5
2017-07-03 | 14:00 | 1.6992 | 0 | 0 | 1.5 | 25 | 84.2687
2017-07-03 | 14:05 | 1.7709 | 0 |  | 1.5
2017-07-03 | 14:10 | 1.7561 | 0 |  | 1.5
2017-07-03 | 14:15 | 1.7234 | 0 | 0 | 1.5 | 25 | 84.4719
2017-07-03 | 14:20 | 1.7475 | 0 |  | 1.5
2017-07-03 | 14:25 | 1.7101 | 0 |  | 1.5
2017-07-03 | 14:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 84.8426
2017-07-03 | 14:35 | 1.7382 | 0 |  | 1.5
2017-07-03 | 14:40 | 1.7265 | 0 |  | 1.5
2017-07-03 | 14:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 85.1441
2017-07-03 | 14:50 | 1.7608 | 0 |  | 1.5
2017-07-03 | 14:55 | 1.7577 | 0 |  | 1.5
2017-07-03 | 15:00 | 1.7296 | 0 | 0 | 1.5 | 25 | 85.1506
2017-07-03 | 15:05 | 1.7202 | 0 |  | 1.5
2017-07-03 | 15:10 | 1.7117 | 0 |  | 1.5
2017-07-03 | 15:15 | 1.746 | 0 | 0 | 1.5 | 25 | 85.5507
2017-07-03 | 15:20 | 1.7639 | 0 |  | 1.5
2017-07-03 | 15:25 | 1.6953 | 0 |  | 1.5
2017-07-03 | 15:30 | 1.7296 | 0 | 0 | 1.5 | 25 | 86.4138
2017-07-03 | 15:35 | 1.6984 | 0 |  | 1.5
2017-07-03 | 15:40 | 1.6649 | 0 |  | 1.5
2017-07-03 | 15:45 | 1.7538 | 0 | 0 | 1.5 | 25 | 87.509
2017-07-03 | 15:50 | 1.8123 | 0 |  | 1.5
2017-07-03 | 15:55 | 1.8372 | 0 |  | 1.5
2017-07-03 | 16:00 | 1.8302 | 0 | 0 | 1.5 | 25 | 85.4468
2017-07-03 | 16:05 | 1.8138 | 0 |  | 1.5
2017-07-03 | 16:10 | 1.8021 | 0 |  | 1.5
2017-07-03 | 16:15 | 1.8115 | 0 | 0 | 1.5 | 25 | 83.6667
2017-07-03 | 16:20 | 1.7858 | 0 |  | 1.5
2017-07-03 | 16:25 | 1.8201 | 0 |  | 1.5
2017-07-03 | 16:30 | 1.7904 | 0 | 0 | 1.5 | 25 | 82.2997
2017-07-03 | 16:35 | 1.8084 | 0 |  | 1.5
2017-07-03 | 16:40 | 1.7967 | 0 |  | 1.5
2017-07-03 | 16:45 | 1.8123 | 0 | 0 | 1.5 | 25 | 81.0413
2017-07-03 | 16:50 | 1.7959 | 0 |  | 1.5
2017-07-03 | 16:55 | 1.8045 | 0 |  | 1.5
2017-07-03 | 17:00 | 1.8193 | 0 | 0 | 1.5 | 25 | 79.9637
2017-07-03 | 17:05 | 1.792 | 0 |  | 1.5
2017-07-03 | 17:10 | 1.7694 | 0 |  | 1.5
2017-07-03 | 17:15 | 1.7741 | 0 | 0 | 1.5 | 25 | 79.2037
2017-07-03 | 17:20 | 1.7553 | 0 |  | 1.5
2017-07-03 | 17:25 | 1.7624 | 0 |  | 1.5
2017-07-03 | 17:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 78.8094
2017-07-03 | 17:35 | 1.7475 | 0 |  | 1.5
2017-07-03 | 17:40 | 1.753 | 0 |  | 1.5
2017-07-03 | 17:45 | 1.7171 | 0 | 0 | 1.5 | 25 | 78.7264
2017-07-03 | 17:50 | 1.7819 | 0 |  | 1.5
2017-07-03 | 17:55 | 1.7631 | 0 |  | 1.5
2017-07-03 | 18:00 | 1.7327 | 0 | 0 | 1.5 | 25 | 78.6912
2017-07-03 | 18:05 | 1.7624 | 0 |  | 1.5
2017-07-03 | 18:10 | 1.7421 | 0 |  | 1.5
2017-07-03 | 18:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 78.6465
2017-07-03 | 18:20 | 1.7717 | 0 |  | 1.5
2017-07-03 | 18:25 | 1.7312 | 0 |  | 1.5
2017-07-03 | 18:30 | 1.7655 | 0 | 0 | 1.5 | 25 | 78.4987
2017-07-03 | 18:35 | 1.746 | 0 |  | 1.5
2017-07-03 | 18:40 | 1.7491 | 0 |  | 1.5
2017-07-03 | 18:45 | 1.7413 | 0 | 0 | 1.5 | 25 | 78.4672
2017-07-03 | 18:50 | 1.7475 | 0 |  | 1.5
2017-07-03 | 18:55 | 1.746 | 0 |  | 1.5
2017-07-03 | 19:00 | 1.739 | 0 | 0 | 1.5 | 25 | 78.4403
2017-07-03 | 19:05 | 1.778 | 0 |  | 1.5
2017-07-03 | 19:10 | 1.739 | 0 |  | 1.5
2017-07-03 | 19:15 | 1.7319 | 0 | 0 | 1.5 | 25 | 78.5595
2017-07-03 | 19:20 | 1.7265 | 0 |  | 1.5
2017-07-03 | 19:25 | 1.746 | 0 |  | 1.5
2017-07-03 | 19:30 | 1.7491 | 0 | 0 | 1.5 | 25 | 78.4597
2017-07-03 | 19:35 | 1.7522 | 0 |  | 1.5
2017-07-03 | 19:40 | 1.7795 | 0 |  | 1.5
2017-07-03 | 19:45 | 1.7624 | 0 | 0 | 1.5 | 25 | 78.2256
2017-07-03 | 19:50 | 1.7569 | 0 |  | 1.5
2017-07-03 | 19:55 | 1.7694 | 0 |  | 1.5
2017-07-03 | 20:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 78.0248
2017-07-03 | 20:05 | 1.7639 | 0 |  | 1.5
2017-07-03 | 20:10 | 1.76 | 0 |  | 1.5
2017-07-03 | 20:15 | 1.7546 | 0 | 0 | 1.5 | 25 | 77.6613
2017-07-03 | 20:20 | 1.7577 | 0 |  | 1.5
2017-07-03 | 20:25 | 1.7585 | 0 |  | 1.5
2017-07-03 | 20:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 77.363
2017-07-03 | 20:35 | 1.7491 | 0 |  | 1.5
2017-07-03 | 20:40 | 1.7429 | 0 |  | 1.5
2017-07-03 | 20:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 77.0315
2017-07-03 | 20:50 | 1.76 | 0 |  | 1.5
2017-07-03 | 20:55 | 1.7826 | 0 |  | 1.5
2017-07-03 | 21:00 | 1.7725 | 0 | 0 | 1.5 | 25 | 76.6445
2017-07-03 | 21:05 | -0.10652 | 0 |  | 1.5
2017-07-03 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-03 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 21:20 | -0.10652 | 0 |  | 1.5
2017-07-03 | 21:25 | -0.10652 | 0 |  | 1.5
2017-07-03 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 21:35 | -0.1073 | 0 |  | 1.5
2017-07-03 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-03 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-03 | 21:55 | -0.1073 | 0 |  | 1.5
2017-07-03 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 22:05 | -0.10808 | 0 |  | 1.5
2017-07-03 | 22:10 | -0.10808 | 0 |  | 1.5
2017-07-03 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 22:20 | -0.10808 | 0 |  | 1.5
2017-07-03 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-03 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 22:35 | -0.1073 | 0 |  | 1.5
2017-07-03 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-03 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-03 | 22:55 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 23:05 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:10 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 23:20 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:25 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 23:35 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:40 | -0.1073 | 0 |  | 1.5
2017-07-03 | 23:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-03 | 23:50 | -0.10652 | 0 |  | 1.5
2017-07-03 | 23:55 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 0:05 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:10 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 0:20 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:25 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 0:35 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:40 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 0:50 | -0.1073 | 0 |  | 1.5
2017-07-04 | 0:55 | -0.1073 | 0 |  | 1.5
2017-07-04 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 1:05 | -0.1073 | 0 |  | 1.5
2017-07-04 | 1:10 | -0.1073 | 0 |  | 1.5
2017-07-04 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 1:20 | -0.1073 | 0 |  | 1.5
2017-07-04 | 1:25 | -0.11042 | 0 |  | 1.5
2017-07-04 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 1:35 | -0.11042 | 0 |  | 1.5
2017-07-04 | 1:40 | -0.11042 | 0 |  | 1.5
2017-07-04 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 1:50 | -0.10886 | 0 |  | 1.5
2017-07-04 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-04 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-04 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 3:05 | -0.1112 | 0 |  | 1.5
2017-07-04 | 3:10 | -0.1112 | 0 |  | 1.5
2017-07-04 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 3:20 | -0.1112 | 0 |  | 1.5
2017-07-04 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-04 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 3:35 | -0.11042 | 0 |  | 1.5
2017-07-04 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-04 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-04 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-04 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 4:05 | -0.1112 | 0 |  | 1.5
2017-07-04 | 4:10 | -0.1112 | 0 |  | 1.5
2017-07-04 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 4:20 | -0.11432 | 0 |  | 1.5
2017-07-04 | 4:25 | -0.1112 | 0 |  | 1.5
2017-07-04 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-04 | 4:40 | -0.1112 | 0 |  | 1.5
2017-07-04 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 4:50 | -0.1112 | 0 |  | 1.5
2017-07-04 | 4:55 | -0.1112 | 0 |  | 1.5
2017-07-04 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 5:05 | 2.604 | 5.665 |  | 10
2017-07-04 | 5:10 | 2.2475 | 9.7788 |  | 10
2017-07-04 | 5:15 | 2.143 | 9.1462 | 1 | 10 | 93.6706 | 85.8695
2017-07-04 | 5:20 | 2.0549 | 8.6499 |  | 10
2017-07-04 | 5:25 | 1.9605 | 8.019 |  | 10
2017-07-04 | 5:30 | 1.8864 | 7.4102 | 1 | 10 | 76.5881 | 79.4293
2017-07-04 | 5:35 | 1.863 | 7.1167 |  | 10
2017-07-04 | 5:40 | 1.8489 | 6.6014 |  | 10
2017-07-04 | 5:45 | 1.8068 | 6.4968 | 1 | 10 | 67.5049 | 76.9148
2017-07-04 | 5:50 | 1.792 | 6.2415 |  | 10
2017-07-04 | 5:55 | 1.7904 | 6.0413 |  | 10
2017-07-04 | 6:00 | 1.7865 | 5.9728 | 1 | 10 | 62.558 | 75.9
2017-07-04 | 6:05 | 1.8045 | 6.3335 |  | 10
2017-07-04 | 6:10 | 1.7374 | 6.8244 |  | 10
2017-07-04 | 6:15 | 1.7631 | 6.7552 | 1 | 10 | 70.1162 | 75.5221
2017-07-04 | 6:20 | 1.7553 | 6.9062 |  | 10
2017-07-04 | 6:25 | 1.7624 | 6.8862 |  | 10
2017-07-04 | 6:30 | 1.7592 | 6.793 | 1 | 10 | 70.2791 | 75.4363
2017-07-04 | 6:35 | 1.7561 | 6.912 |  | 10
2017-07-04 | 6:40 | 1.7358 | 6.8095 |  | 10
2017-07-04 | 6:45 | 1.7374 | 6.8168 | 1 | 10 | 70.5 | 75.3213
2017-07-04 | 6:50 | 1.7452 | 6.8507 |  | 10
2017-07-04 | 6:55 | 1.7577 | 6.7493 |  | 10
2017-07-04 | 7:00 | 1.76 | 6.8424 | 1 | 10 | 70.7966 | 75.3117
2017-07-04 | 7:05 | 1.7561 | 6.6352 |  | 10
2017-07-04 | 7:10 | 1.7943 | 6.7771 |  | 10
2017-07-04 | 7:15 | 1.7647 | 6.6584 | 1 | 10 | 69.2412 | 74.9139
2017-07-04 | 7:20 | 1.739 | 6.6848 |  | 10
2017-07-04 | 7:25 | 1.7382 | 6.6755 |  | 10
2017-07-04 | 7:30 | 1.7312 | 6.3666 | 1 | 10 | 66.3773 | 75.1457
2017-07-04 | 7:35 | 1.7218 | 6.6428 |  | 10
2017-07-04 | 7:40 | 1.7811 | 6.8606 |  | 10
2017-07-04 | 7:45 | 1.7483 | 7.3886 | 1 | 10 | 76.2 | 75.2127
2017-07-04 | 7:50 | 1.7772 | 7.2619 |  | 10
2017-07-04 | 7:55 | 1.7413 | 7.2467 |  | 10
2017-07-04 | 8:00 | 1.7647 | 7.2842 | 1 | 10 | 75.1315 | 75.2042
2017-07-04 | 8:05 | 1.7156 | 7.4556 |  | 10
2017-07-04 | 8:10 | 1.7257 | 7.6887 |  | 10
2017-07-04 | 8:15 | 1.7616 | 7.6536 | 1 | 10 | 79.0214 | 75.3183
2017-07-04 | 8:20 | 1.7265 | 7.5993 |  | 10
2017-07-04 | 8:25 | 1.7374 | 7.6237 |  | 10
2017-07-04 | 8:30 | 1.7491 | 7.2431 | 1 | 10 | 75.0018 | 75.4722
2017-07-04 | 8:35 | 1.739 | 7.0085 |  | 10
2017-07-04 | 8:40 | 1.7616 | 7.0809 |  | 10
2017-07-04 | 8:45 | 1.7522 | 7.2562 | 1 | 10 | 74.9256 | 75.2779
2017-07-04 | 8:50 | 1.7819 | 7.6626 |  | 10
2017-07-04 | 8:55 | 1.7335 | 7.7023 |  | 10
2017-07-04 | 9:00 | 1.7366 | 7.8411 | 1 | 10 | 80.8139 | 75.3837
2017-07-04 | 9:05 | 1.7522 | 7.5307 |  | 10
2017-07-04 | 9:10 | 1.7546 | 7.3425 |  | 10
2017-07-04 | 9:15 | 1.7795 | 6.8596 | 1 | 10 | 71.2508 | 75.4152
2017-07-04 | 9:20 | 1.7741 | 7.0217 |  | 10
2017-07-04 | 9:25 | 1.739 | 7.2156 |  | 10
2017-07-04 | 9:30 | 1.7639 | 7.1109 | 1 | 10 | 73.7251 | 75.3869
2017-07-04 | 9:35 | 1.7241 | 7.3763 |  | 10
2017-07-04 | 9:40 | 1.753 | 7.6053 |  | 10
2017-07-04 | 9:45 | 1.7273 | 7.5044 | 1 | 10 | 77.2942 | 75.6434
2017-07-04 | 9:50 | 1.7569 | 7.4597 |  | 10
2017-07-04 | 9:55 | 1.7483 | 7.2938 |  | 10
2017-07-04 | 10:00 | 1.7483 | 7.1289 | 1 | 10 | 73.5721 | 75.7711
2017-07-04 | 10:05 | 1.7725 | 7.0011 |  | 10
2017-07-04 | 10:10 | 1.7569 | 6.7019 |  | 10
2017-07-04 | 10:15 | 1.7655 | 6.7173 | 1 | 10 | 69.7754 | 75.7289
2017-07-04 | 10:20 | 1.7436 | 6.44 |  | 10
2017-07-04 | 10:25 | 1.7686 | 3.4353 |  | 10
2017-07-04 | 10:30 | 1.6719 | 0 | 0 | 1.5 | 25 | 76.2668
2017-07-04 | 10:35 | 1.6805 | 0 |  | 1.5
2017-07-04 | 10:40 | 1.7124 | 0 |  | 1.5
2017-07-04 | 10:45 | 1.7078 | 0 | 0 | 1.5 | 25 | 77.7162
2017-07-04 | 10:50 | 1.7241 | 0 |  | 1.5
2017-07-04 | 10:55 | 1.7327 | 0 |  | 1.5
2017-07-04 | 11:00 | 1.7842 | 0 | 0 | 1.5 | 25 | 77.7013
2017-07-04 | 11:05 | 1.767 | 0 |  | 1.5
2017-07-04 | 11:10 | 1.767 | 0 |  | 1.5
2017-07-04 | 11:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 77.4498
2017-07-04 | 11:20 | 1.7312 | 0 |  | 1.5
2017-07-04 | 11:25 | 1.7265 | 0 |  | 1.5
2017-07-04 | 11:30 | 1.7312 | 0 | 0 | 1.5 | 25 | 77.5925
2017-07-04 | 11:35 | 1.7397 | 0 |  | 1.5
2017-07-04 | 11:40 | 1.7327 | 0 |  | 1.5
2017-07-04 | 11:45 | 1.7335 | 0 | 0 | 1.5 | 25 | 77.9719
2017-07-04 | 11:50 | 1.7553 | 0 |  | 1.5
2017-07-04 | 11:55 | 1.7468 | 0 |  | 1.5
2017-07-04 | 12:00 | 1.7312 | 0 | 0 | 1.5 | 25 | 78.4194
2017-07-04 | 12:05 | 1.7319 | 0 |  | 1.5
2017-07-04 | 12:10 | 1.7288 | 0 |  | 1.5
2017-07-04 | 12:15 | 1.7241 | 0 | 0 | 1.5 | 25 | 79.0703
2017-07-04 | 12:20 | 1.7093 | 0 |  | 1.5
2017-07-04 | 12:25 | 1.7218 | 0 |  | 1.5
2017-07-04 | 12:30 | 1.714 | 0 | 0 | 1.5 | 25 | 79.9094
2017-07-04 | 12:35 | 1.7093 | 0 |  | 1.5
2017-07-04 | 12:40 | 1.753 | 0 |  | 1.5
2017-07-04 | 12:45 | 1.7647 | 0 | 0 | 1.5 | 25 | 80.5196
2017-07-04 | 12:50 | 1.7296 | 0 |  | 1.5
2017-07-04 | 12:55 | 1.7163 | 0 |  | 1.5
2017-07-04 | 13:00 | 1.7241 | 0 | 0 | 1.5 | 25 | 81.0431
2017-07-04 | 13:05 | 1.739 | 0 |  | 1.5
2017-07-04 | 13:10 | 1.707 | 0 |  | 1.5
2017-07-04 | 13:15 | 1.721 | 0 | 0 | 1.5 | 25 | 81.5267
2017-07-04 | 13:20 | 1.7499 | 0 |  | 1.5
2017-07-04 | 13:25 | 1.7351 | 0 |  | 1.5
2017-07-04 | 13:30 | 1.721 | 0 | 0 | 1.5 | 25 | 81.8787
2017-07-04 | 13:35 | 1.7288 | 0 |  | 1.5
2017-07-04 | 13:40 | 1.7312 | 0 |  | 1.5
2017-07-04 | 13:45 | 1.7148 | 0 | 0 | 1.5 | 25 | 82.3647
2017-07-04 | 13:50 | 1.7538 | 0 |  | 1.5
2017-07-04 | 13:55 | 1.7358 | 0 |  | 1.5
2017-07-04 | 14:00 | 1.7179 | 0 | 0 | 1.5 | 25 | 82.6715
2017-07-04 | 14:05 | 1.7374 | 0 |  | 1.5
2017-07-04 | 14:10 | 1.7343 | 0 |  | 1.5
2017-07-04 | 14:15 | 1.753 | 0 | 0 | 1.5 | 25 | 83.0671
2017-07-04 | 14:20 | 1.76 | 0 |  | 1.5
2017-07-04 | 14:25 | 1.753 | 0 |  | 1.5
2017-07-04 | 14:30 | 1.7273 | 0 | 0 | 1.5 | 25 | 83.4468
2017-07-04 | 14:35 | 1.7452 | 0 |  | 1.5
2017-07-04 | 14:40 | 1.7085 | 0 |  | 1.5
2017-07-04 | 14:45 | 1.7444 | 0 | 0 | 1.5 | 25 | 83.8156
2017-07-04 | 14:50 | 1.7273 | 0 |  | 1.5
2017-07-04 | 14:55 | 1.739 | 0 |  | 1.5
2017-07-04 | 15:00 | 1.7343 | 0 | 0 | 1.5 | 25 | 84.2551
2017-07-04 | 15:05 | 1.7296 | 0 |  | 1.5
2017-07-04 | 15:10 | 1.7468 | 0 |  | 1.5
2017-07-04 | 15:15 | 1.7577 | 0 | 0 | 1.5 | 25 | 84.5568
2017-07-04 | 15:20 | 1.7304 | 0 |  | 1.5
2017-07-04 | 15:25 | 1.739 | 0 |  | 1.5
2017-07-04 | 15:30 | 1.7374 | 0 | 0 | 1.5 | 25 | 84.7371
2017-07-04 | 15:35 | 1.7709 | 0 |  | 1.5
2017-07-04 | 15:40 | 1.7312 | 0 |  | 1.5
2017-07-04 | 15:45 | 1.7585 | 0 | 0 | 1.5 | 25 | 84.6661
2017-07-04 | 15:50 | 1.7811 | 0 |  | 1.5
2017-07-04 | 15:55 | 1.778 | 0 |  | 1.5
2017-07-04 | 16:00 | 1.7546 | 0 | 0 | 1.5 | 25 | 84.2577
2017-07-04 | 16:05 | 1.7936 | 0 |  | 1.5
2017-07-04 | 16:10 | 1.7858 | 0 |  | 1.5
2017-07-04 | 16:15 | 1.7959 | 0 | 0 | 1.5 | 25 | 83.408
2017-07-04 | 16:20 | 1.7928 | 0 |  | 1.5
2017-07-04 | 16:25 | 1.7928 | 0 |  | 1.5
2017-07-04 | 16:30 | 1.7858 | 0 | 0 | 1.5 | 25 | 82.1698
2017-07-04 | 16:35 | 1.7764 | 0 |  | 1.5
2017-07-04 | 16:40 | 1.8131 | 0 |  | 1.5
2017-07-04 | 16:45 | 1.8084 | 0 | 0 | 1.5 | 25 | 80.7864
2017-07-04 | 16:50 | 1.7772 | 0 |  | 1.5
2017-07-04 | 16:55 | 1.8092 | 0 |  | 1.5
2017-07-04 | 17:00 | 1.7585 | 0 | 0 | 1.5 | 25 | 79.8303
2017-07-04 | 17:05 | 1.7764 | 0 |  | 1.5
2017-07-04 | 17:10 | 1.7889 | 0 |  | 1.5
2017-07-04 | 17:15 | 1.785 | 0 | 0 | 1.5 | 25 | 79.0009
2017-07-04 | 17:20 | 1.785 | 0 |  | 1.5
2017-07-04 | 17:25 | 1.7873 | 0 |  | 1.5
2017-07-04 | 17:30 | 1.7733 | 0 | 0 | 1.5 | 25 | 78.2665
2017-07-04 | 17:35 | 1.7748 | 0 |  | 1.5
2017-07-04 | 17:40 | 1.7546 | 0 |  | 1.5
2017-07-04 | 17:45 | 1.7468 | 0 | 0 | 1.5 | 25 | 77.6884
2017-07-04 | 17:50 | 1.7413 | 0 |  | 1.5
2017-07-04 | 17:55 | 1.7312 | 0 |  | 1.5
2017-07-04 | 18:00 | 1.7171 | 0 | 0 | 1.5 | 25 | 77.9574
2017-07-04 | 18:05 | 1.7382 | 0 |  | 1.5
2017-07-04 | 18:10 | 1.721 | 0 |  | 1.5
2017-07-04 | 18:15 | 1.7585 | 0 | 0 | 1.5 | 25 | 78.1733
2017-07-04 | 18:20 | 1.767 | 0 |  | 1.5
2017-07-04 | 18:25 | 1.728 | 0 |  | 1.5
2017-07-04 | 18:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 78.1445
2017-07-04 | 18:35 | 1.753 | 0 |  | 1.5
2017-07-04 | 18:40 | 1.7577 | 0 |  | 1.5
2017-07-04 | 18:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 78.1475
2017-07-04 | 18:50 | 1.7335 | 0 |  | 1.5
2017-07-04 | 18:55 | 1.7491 | 0 |  | 1.5
2017-07-04 | 19:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 78.1744
2017-07-04 | 19:05 | 1.7296 | 0 |  | 1.5
2017-07-04 | 19:10 | 1.7397 | 0 |  | 1.5
2017-07-04 | 19:15 | 1.7561 | 0 | 0 | 1.5 | 25 | 78.1963
2017-07-04 | 19:20 | 1.7382 | 0 |  | 1.5
2017-07-04 | 19:25 | 1.728 | 0 |  | 1.5
2017-07-04 | 19:30 | 1.7514 | 0 | 0 | 1.5 | 25 | 78.3973
2017-07-04 | 19:35 | 1.7148 | 0 |  | 1.5
2017-07-04 | 19:40 | 1.7093 | 0 |  | 1.5
2017-07-04 | 19:45 | 1.7655 | 0 | 0 | 1.5 | 25 | 78.9069
2017-07-04 | 19:50 | 1.746 | 0 |  | 1.5
2017-07-04 | 19:55 | 1.707 | 0 |  | 1.5
2017-07-04 | 20:00 | 1.7538 | 0 | 0 | 1.5 | 25 | 78.7605
2017-07-04 | 20:05 | 1.76 | 0 |  | 1.5
2017-07-04 | 20:10 | 1.7366 | 0 |  | 1.5
2017-07-04 | 20:15 | 1.7624 | 0 | 0 | 1.5 | 25 | 78.7532
2017-07-04 | 20:20 | 1.7491 | 0 |  | 1.5
2017-07-04 | 20:25 | 1.721 | 0 |  | 1.5
2017-07-04 | 20:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 78.9347
2017-07-04 | 20:35 | 1.7296 | 0 |  | 1.5
2017-07-04 | 20:40 | 1.7577 | 0 |  | 1.5
2017-07-04 | 20:45 | 1.7873 | 0 | 0 | 1.5 | 25 | 78.6584
2017-07-04 | 20:50 | 1.7826 | 0 |  | 1.5
2017-07-04 | 20:55 | 1.7413 | 0 |  | 1.5
2017-07-04 | 21:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 78.1604
2017-07-04 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-04 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-04 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 21:20 | -0.10652 | 0 |  | 1.5
2017-07-04 | 21:25 | -0.10652 | 0 |  | 1.5
2017-07-04 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-04 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-04 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-04 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 22:20 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:25 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:40 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-04 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-04 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-04 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-04 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 23:20 | -0.10574 | 0 |  | 1.5
2017-07-04 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-04 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 23:35 | -0.10574 | 0 |  | 1.5
2017-07-04 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-04 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-04 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-04 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-05 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-05 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-05 | 0:10 | -0.10574 | 0 |  | 1.5
2017-07-05 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-05 | 0:15 | -0.10574 | 0 |  | 1.5 |  | 0
2017-07-05 | 0:20 | -0.10808 | 0 |  | 1.5
2017-07-05 | 0:25 | -0.1073 | 0 |  | 1.5
2017-07-05 | 0:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 0:30 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 0:35 | -0.10652 | 0 |  | 1.5
2017-07-05 | 0:40 | -0.1073 | 0 |  | 1.5
2017-07-05 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 0:45 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 0:50 | -0.1073 | 0 |  | 1.5
2017-07-05 | 0:55 | -0.10652 | 0 |  | 1.5
2017-07-05 | 1:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 1:00 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 1:05 | -0.10652 | 0 |  | 1.5
2017-07-05 | 1:10 | -0.1073 | 0 |  | 1.5
2017-07-05 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 1:15 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 1:20 | -0.1073 | 0 |  | 1.5
2017-07-05 | 1:25 | -0.10964 | 0 |  | 1.5
2017-07-05 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 1:30 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 1:35 | -0.10964 | 0 |  | 1.5
2017-07-05 | 1:40 | -0.10964 | 0 |  | 1.5
2017-07-05 | 1:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-05 | 1:45 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-05 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-05 | 1:55 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-05 | 2:00 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-05 | 2:05 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:10 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 2:15 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 2:20 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:25 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-05 | 2:30 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-05 | 2:35 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-05 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-05 | 2:45 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-05 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-05 | 2:55 | -0.10964 | 0 |  | 1.5
2017-07-05 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-05 | 3:00 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-05 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-05 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-05 | 3:15 | -0.11198 | 0 | 0 | 1.5 | 0
2017-07-05 | 3:15 | -0.11198 | 0 |  | 1.5 |  | 0
2017-07-05 | 3:20 | -0.10964 | 0 |  | 1.5
2017-07-05 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-05 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 3:30 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 3:35 | -0.11042 | 0 |  | 1.5
2017-07-05 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-05 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 3:45 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-05 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 4:00 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 4:15 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-05 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-07-05 | 4:30 | -0.1112 | 0 |  | 1.5 |  | 0
2017-07-05 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-05 | 4:45 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-05 | 4:50 | -0.11042 | 0 |  | 1.5
2017-07-05 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-05 | 5:00 | -0.11042 | 0 | 1 | 0 | 0
2017-07-05 | 5:00 | -0.11042 | 0 |  | 0 |  | 25
2017-07-05 | 5:05 | 2.4324 | 5.8122 |  | 10
2017-07-05 | 5:10 | 2.1219 | 9.9307 |  | 10
2017-07-05 | 5:15 | 2.051 | 9.8172 | 1 | 10 | 98.5432
2017-07-05 | 5:15 | 2.051 | 9.8172 |  | 10 |  | 88.2452
2017-07-05 | 5:20 | 1.9964 | 9.565 |  | 10
2017-07-05 | 5:25 | 1.9792 | 8.9765 |  | 10
2017-07-05 | 5:30 | 1.9199 | 8.1431 | 1 | 10 | 82.3518
2017-07-05 | 5:30 | 1.9199 | 8.1431 |  | 10 |  | 81.949
2017-07-05 | 5:35 | 1.9067 | 7.7762 |  | 10
2017-07-05 | 5:40 | 1.8583 | 7.2814 |  | 10
2017-07-05 | 5:45 | 1.8248 | 7.0025 | 1 | 10 | 71.3943
2017-07-05 | 5:45 | 1.8248 | 7.0025 |  | 10 |  | 78.619
2017-07-05 | 5:50 | 1.8029 | 6.517 |  | 10
2017-07-05 | 5:55 | 1.8053 | 6.2787 |  | 10
2017-07-05 | 6:00 | 1.7733 | 6.2364 | 1 | 10 | 63.4877
2017-07-05 | 6:00 | 1.7733 | 6.2364 |  | 10 |  | 77.0094
2017-07-05 | 6:05 | 1.7865 | 6.2842 |  | 10
2017-07-05 | 6:10 | 1.7733 | 6.5033 |  | 10
2017-07-05 | 6:15 | 1.7639 | 6.2115 | 1 | 10 | 63.3059
2017-07-05 | 6:15 | 1.7639 | 6.2115 |  | 10 |  | 76.3413
2017-07-05 | 6:20 | 1.7819 | 6.2765 |  | 10
2017-07-05 | 6:25 | 1.7546 | 6.1438 |  | 10
2017-07-05 | 6:30 | 1.7585 | 5.7673 | 1 | 10 | 58.7123
2017-07-05 | 6:30 | 1.7585 | 5.7673 |  | 10 |  | 75.903
2017-07-05 | 6:35 | 1.7756 | 5.9501 |  | 10
2017-07-05 | 6:40 | 1.7631 | 5.6603 |  | 10
2017-07-05 | 6:45 | 1.7358 | 2.8693 | 0 | 1.5 | 32.0938
2017-07-05 | 6:45 | 1.7358 | 2.8693 |  | 1.5 |  | 75.4738
2017-07-05 | 6:50 | 1.6961 | 0 |  | 1.5
2017-07-05 | 6:55 | 1.6922 | 0 |  | 1.5
2017-07-05 | 7:00 | 1.7195 | 0 | 0 | 1.5 | 25
2017-07-05 | 7:00 | 1.7195 | 0 |  | 1.5 |  | 77.2026
2017-07-05 | 7:05 | 1.8489 | 0.64405 |  | 10
2017-07-05 | 7:10 | 1.8131 | 2.48 |  | 10
2017-07-05 | 7:15 | 1.778 | 3.4254 | 1 | 10 | 56.4483
2017-07-05 | 7:15 | 1.778 | 3.4254 |  | 10 |  | 75.5461
2017-07-05 | 7:20 | 1.7904 | 3.9237 |  | 10
2017-07-05 | 7:25 | 1.7592 | 4.1504 |  | 10
2017-07-05 | 7:30 | 1.7585 | 3.71 | 1 | 10 | 59.5502
2017-07-05 | 7:30 | 1.7585 | 3.71 |  | 10 |  | 74.9387
2017-07-05 | 7:35 | 1.7483 | 3.6965 |  | 10
2017-07-05 | 7:40 | 1.767 | 3.5422 |  | 10
2017-07-05 | 7:45 | 1.7546 | 3.1407 | 1 | 10 | 54.847
2017-07-05 | 7:45 | 1.7546 | 3.1407 |  | 10 |  | 74.8533
2017-07-05 | 7:50 | 1.7553 | 2.6314 |  | 10
2017-07-05 | 7:55 | 1.7452 | 2.4805 |  | 10
2017-07-05 | 8:00 | 1.7522 | 2.4956 | 1 | 10 | 47.6523
2017-07-05 | 8:00 | 1.7522 | 2.4956 |  | 10 |  | 74.9572
2017-07-05 | 8:05 | 1.7491 | 2.7821 |  | 10
2017-07-05 | 8:10 | 1.7218 | 3.4558 |  | 10
2017-07-05 | 8:15 | 1.7358 | 3.6535 | 1 | 10 | 59.1159
2017-07-05 | 8:15 | 1.7358 | 3.6535 |  | 10 |  | 75.1915
2017-07-05 | 8:20 | 1.7296 | 3.2163 |  | 10
2017-07-05 | 8:25 | 1.7085 | 3.1511 |  | 10
2017-07-05 | 8:30 | 1.7522 | 1.0134 | 1 | 10 | 35
2017-07-05 | 8:30 | 1.7522 | 1.0134 |  | 10 |  | 75.3372
2017-07-05 | 8:35 | 1.7382 | 0 |  | 10
2017-07-05 | 8:40 | 1.5619 | 0 |  | 1.5
2017-07-05 | 8:45 | 1.6383 | 0 | 0 | 1.5 | 25
2017-07-05 | 8:45 | 1.6383 | 0 |  | 1.5 |  | 77.7742
2017-07-05 | 8:50 | 1.6859 | 0 |  | 1.5
2017-07-05 | 8:55 | 1.7358 | 0 |  | 1.5
2017-07-05 | 9:00 | 1.7202 | 0 | 0 | 1.5 | 25
2017-07-05 | 9:00 | 1.7202 | 0 |  | 1.5 |  | 79.0797
2017-07-05 | 9:05 | 1.7327 | 0 |  | 1.5
2017-07-05 | 9:10 | 1.7678 | 0 |  | 1.5
2017-07-05 | 9:15 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-05 | 9:15 | 1.7639 | 0 |  | 1.5 |  | 79.1415
2017-07-05 | 9:20 | 1.7608 | 0 |  | 1.5
2017-07-05 | 9:25 | 1.7444 | 0 |  | 1.5
2017-07-05 | 9:30 | 1.7257 | 0 | 0 | 1.5 | 25
2017-07-05 | 9:30 | 1.7257 | 0 |  | 1.5 |  | 79.1775
2017-07-05 | 9:35 | 1.7343 | 0 |  | 1.5
2017-07-05 | 9:40 | 1.7296 | 0 |  | 1.5
2017-07-05 | 9:45 | 1.7499 | 0 | 0 | 1.5 | 25
2017-07-05 | 9:45 | 1.7499 | 0 |  | 1.5 |  | 79.2315
2017-07-05 | 9:50 | 1.721 | 0 |  | 1.5
2017-07-05 | 9:55 | 1.7569 | 0 |  | 1.5
2017-07-05 | 10:00 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-05 | 10:00 | 1.7639 | 0 |  | 1.5 |  | 79.2305
2017-07-05 | 10:05 | 1.7429 | 0 |  | 1.5
2017-07-05 | 10:10 | 1.7288 | 0 |  | 1.5
2017-07-05 | 10:15 | 1.7826 | 0 | 0 | 1.5 | 25
2017-07-05 | 10:15 | 1.7826 | 0 |  | 1.5 |  | 79.182
2017-07-05 | 10:20 | 1.7241 | 0 |  | 1.5
2017-07-05 | 10:25 | 1.7413 | 0 |  | 1.5
2017-07-05 | 10:30 | 1.7405 | 0 | 0 | 1.5 | 25
2017-07-05 | 10:30 | 1.7405 | 0 |  | 1.5 |  | 79.242
2017-07-05 | 10:35 | 1.7257 | 0 |  | 1.5
2017-07-05 | 10:40 | 1.7413 | 0 |  | 1.5
2017-07-05 | 10:45 | 1.7109 | 0 | 0 | 1.5 | 25
2017-07-05 | 10:45 | 1.7109 | 0 |  | 1.5 |  | 79.5431
2017-07-05 | 10:50 | 1.739 | 0 |  | 1.5
2017-07-05 | 10:55 | 1.7444 | 0 |  | 1.5
2017-07-05 | 11:00 | 1.7163 | 0 | 0 | 1.5 | 25
2017-07-05 | 11:00 | 1.7163 | 0 |  | 1.5 |  | 79.7309
2017-07-05 | 11:05 | 1.7358 | 0 |  | 1.5
2017-07-05 | 11:10 | 1.7171 | 0 |  | 1.5
2017-07-05 | 11:15 | 1.7226 | 0 | 0 | 1.5 | 25
2017-07-05 | 11:15 | 1.7226 | 0 |  | 1.5 |  | 80.5726
2017-07-05 | 11:20 | 1.721 | 0 |  | 1.5
2017-07-05 | 11:25 | 1.6844 | 0 |  | 1.5
2017-07-05 | 11:30 | 1.6649 | 0 | 0 | 1.5 | 25
2017-07-05 | 11:30 | 1.6649 | 0 |  | 1.5 |  | 81.91
2017-07-05 | 11:35 | 1.6953 | 0 |  | 1.5
2017-07-05 | 11:40 | 1.6781 | 0 |  | 1.5
2017-07-05 | 11:45 | 1.6844 | 0 | 0 | 1.5 | 25
2017-07-05 | 11:45 | 1.6844 | 0 |  | 1.5 |  | 83.746
2017-07-05 | 11:50 | 1.7288 | 0 |  | 1.5
2017-07-05 | 11:55 | 1.7273 | 0 |  | 1.5
2017-07-05 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 25
2017-07-05 | 12:00 | 1.7257 | 0 |  | 1.5 |  | 84.4724
2017-07-05 | 12:05 | 1.7429 | 0 |  | 1.5
2017-07-05 | 12:10 | 1.728 | 0 |  | 1.5
2017-07-05 | 12:15 | 1.721 | 0 | 0 | 1.5 | 25
2017-07-05 | 12:15 | 1.721 | 0 |  | 1.5 |  | 84.7539
2017-07-05 | 12:20 | 1.7436 | 0 |  | 1.5
2017-07-05 | 12:25 | 1.753 | 0 |  | 1.5
2017-07-05 | 12:30 | 1.7304 | 0 | 0 | 1.5 | 25
2017-07-05 | 12:30 | 1.7304 | 0 |  | 1.5 |  | 84.9833
2017-07-05 | 12:35 | 1.7288 | 0 |  | 1.5
2017-07-05 | 12:40 | 1.7436 | 0 |  | 1.5
2017-07-05 | 12:45 | 1.7163 | 0 | 0 | 1.5 | 25
2017-07-05 | 12:45 | 1.7163 | 0 |  | 1.5 |  | 85.3276
2017-07-05 | 12:50 | 1.7733 | 0 |  | 1.5
2017-07-05 | 12:55 | 1.7522 | 0 |  | 1.5
2017-07-05 | 13:00 | 1.767 | 0 | 0 | 1.5 | 25
2017-07-05 | 13:00 | 1.767 | 0 |  | 1.5 |  | 85.1882
2017-07-05 | 13:05 | 1.7195 | 0 |  | 1.5
2017-07-05 | 13:10 | 1.7421 | 0 |  | 1.5
2017-07-05 | 13:15 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-05 | 13:15 | 1.7639 | 0 |  | 1.5 |  | 85.2444
2017-07-05 | 13:20 | 1.7538 | 0 |  | 1.5
2017-07-05 | 13:25 | 1.7312 | 0 |  | 1.5
2017-07-05 | 13:30 | 1.7304 | 0 | 0 | 1.5 | 25
2017-07-05 | 13:30 | 1.7304 | 0 |  | 1.5 |  | 85.3393
2017-07-05 | 13:35 | 1.7296 | 0 |  | 1.5
2017-07-05 | 13:40 | 1.7265 | 0 |  | 1.5
2017-07-05 | 13:45 | 1.753 | 0 | 0 | 1.5 | 25
2017-07-05 | 13:45 | 1.753 | 0 |  | 1.5 |  | 85.6515
2017-07-05 | 13:50 | 1.6961 | 0 |  | 1.5
2017-07-05 | 13:55 | 1.7288 | 0 |  | 1.5
2017-07-05 | 14:00 | 1.7265 | 0 | 0 | 1.5 | 25
2017-07-05 | 14:00 | 1.7265 | 0 |  | 1.5 |  | 86.6924
2017-07-05 | 14:05 | 1.721 | 0 |  | 1.5
2017-07-05 | 14:10 | 1.746 | 0 |  | 1.5
2017-07-05 | 14:15 | 1.76 | 0 | 0 | 1.5 | 25
2017-07-05 | 14:15 | 1.76 | 0 |  | 1.5 |  | 87.1525
2017-07-05 | 14:20 | 1.7374 | 0 |  | 1.5
2017-07-05 | 14:25 | 1.7358 | 0 |  | 1.5
2017-07-05 | 14:30 | 1.7319 | 0 | 0 | 1.5 | 25
2017-07-05 | 14:30 | 1.7319 | 0 |  | 1.5 |  | 87.597
2017-07-05 | 14:35 | 1.7109 | 0 |  | 1.5
2017-07-05 | 14:40 | 1.7241 | 0 |  | 1.5
2017-07-05 | 14:45 | 1.7195 | 0 | 0 | 1.5 | 25
2017-07-05 | 14:45 | 1.7195 | 0 |  | 1.5 |  | 88.2507
2017-07-05 | 14:50 | 1.7218 | 0 |  | 1.5
2017-07-05 | 14:55 | 1.7218 | 0 |  | 1.5
2017-07-05 | 15:00 | 1.7382 | 0 | 0 | 1.5 | 25
2017-07-05 | 15:00 | 1.7382 | 0 |  | 1.5 |  | 88.6777
2017-07-05 | 15:05 | 1.7795 | 0 |  | 1.5
2017-07-05 | 15:10 | 1.7951 | 0 |  | 1.5
2017-07-05 | 15:15 | 1.7764 | 0 | 0 | 1.5 | 25
2017-07-05 | 15:15 | 1.7764 | 0 |  | 1.5 |  | 88.0096
2017-07-05 | 15:20 | 1.7702 | 0 |  | 1.5
2017-07-05 | 15:25 | 1.7982 | 0 |  | 1.5
2017-07-05 | 15:30 | 1.7764 | 0 | 0 | 1.5 | 25
2017-07-05 | 15:30 | 1.7764 | 0 |  | 1.5 |  | 87.5424
2017-07-05 | 15:35 | 1.7234 | 0 |  | 1.5
2017-07-05 | 15:40 | 1.7234 | 0 |  | 1.5
2017-07-05 | 15:45 | 1.7483 | 0 | 0 | 1.5 | 25
2017-07-05 | 15:45 | 1.7483 | 0 |  | 1.5 |  | 87.6529
2017-07-05 | 15:50 | 1.7397 | 0 |  | 1.5
2017-07-05 | 15:55 | 1.7475 | 0 |  | 1.5
2017-07-05 | 16:00 | 1.7397 | 0 | 0 | 1.5 | 25
2017-07-05 | 16:00 | 1.7397 | 0 |  | 1.5 |  | 87.6434
2017-07-05 | 16:05 | 1.7678 | 0 |  | 1.5
2017-07-05 | 16:10 | 1.7343 | 0 |  | 1.5
2017-07-05 | 16:15 | 1.7546 | 0 | 0 | 1.5 | 25
2017-07-05 | 16:15 | 1.7546 | 0 |  | 1.5 |  | 87.4356
2017-07-05 | 16:20 | 1.7288 | 0 |  | 1.5
2017-07-05 | 16:25 | 1.7561 | 0 |  | 1.5
2017-07-05 | 16:30 | 1.7382 | 0 | 0 | 1.5 | 25
2017-07-05 | 16:30 | 1.7382 | 0 |  | 1.5 |  | 87.6219
2017-07-05 | 16:35 | 1.7421 | 0 |  | 1.5
2017-07-05 | 16:40 | 1.7507 | 0 |  | 1.5
2017-07-05 | 16:45 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-05 | 16:45 | 1.7639 | 0 |  | 1.5 |  | 87.7517
2017-07-05 | 16:50 | 1.7413 | 0 |  | 1.5
2017-07-05 | 16:55 | 1.7483 | 0 |  | 1.5
2017-07-05 | 17:00 | 1.7663 | 0 | 0 | 1.5 | 25
2017-07-05 | 17:00 | 1.7663 | 0 |  | 1.5 |  | 87.6411
2017-07-05 | 17:05 | 1.7569 | 0 |  | 1.5
2017-07-05 | 17:10 | 1.7624 | 0 |  | 1.5
2017-07-05 | 17:15 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-05 | 17:15 | 1.7639 | 0 |  | 1.5 |  | 87.453
2017-07-05 | 17:20 | 1.7483 | 0 |  | 1.5
2017-07-05 | 17:25 | 1.778 | 0 |  | 1.5
2017-07-05 | 17:30 | 1.7787 | 0 | 0 | 1.5 | 25
2017-07-05 | 17:30 | 1.7787 | 0 |  | 1.5 |  | 86.9048
2017-07-05 | 17:35 | 1.7702 | 0 |  | 1.5
2017-07-05 | 17:40 | 1.7678 | 0 |  | 1.5
2017-07-05 | 17:45 | 1.7702 | 0 | 0 | 1.5 | 25
2017-07-05 | 17:45 | 1.7702 | 0 |  | 1.5 |  | 86.1419
2017-07-05 | 17:50 | 1.767 | 0 |  | 1.5
2017-07-05 | 17:55 | 1.7858 | 0 |  | 1.5
2017-07-05 | 18:00 | 1.7811 | 0 | 0 | 1.5 | 25
2017-07-05 | 18:00 | 1.7811 | 0 |  | 1.5 |  | 85.4701
2017-07-05 | 18:05 | 1.7491 | 0 |  | 1.5
2017-07-05 | 18:10 | 1.7764 | 0 |  | 1.5
2017-07-05 | 18:15 | 1.7764 | 0 | 0 | 1.5 | 25
2017-07-05 | 18:15 | 1.7764 | 0 |  | 1.5 |  | 85.049
2017-07-05 | 18:20 | 1.7522 | 0 |  | 1.5
2017-07-05 | 18:25 | 1.7522 | 0 |  | 1.5
2017-07-05 | 18:30 | 1.7717 | 0 | 0 | 1.5 | 25
2017-07-05 | 18:30 | 1.7717 | 0 |  | 1.5 |  | 84.5055
2017-07-05 | 18:35 | 1.7413 | 0 |  | 1.5
2017-07-05 | 18:40 | 1.7491 | 0 |  | 1.5
2017-07-05 | 18:45 | 1.7982 | 0 | 0 | 1.5 | 25
2017-07-05 | 18:45 | 1.7982 | 0 |  | 1.5 |  | 83.8802
2017-07-05 | 18:50 | 1.7865 | 0 |  | 1.5
2017-07-05 | 18:55 | 1.7702 | 0 |  | 1.5
2017-07-05 | 19:00 | 1.7647 | 0 | 0 | 1.5 | 25
2017-07-05 | 19:00 | 1.7647 | 0 |  | 1.5 |  | 83.1597
2017-07-05 | 19:05 | 1.7592 | 0 |  | 1.5
2017-07-05 | 19:10 | 1.7491 | 0 |  | 1.5
2017-07-05 | 19:15 | 1.7772 | 0 | 0 | 1.5 | 25
2017-07-05 | 19:15 | 1.7772 | 0 |  | 1.5 |  | 82.5607
2017-07-05 | 19:20 | 1.7795 | 0 |  | 1.5
2017-07-05 | 19:25 | 1.6243 | 0 |  | 1.5
2017-07-05 | 19:30 | 1.6851 | 0 | 0 | 1.5 | 25
2017-07-05 | 19:30 | 1.6851 | 0 |  | 1.5 |  | 83.5324
2017-07-05 | 19:35 | 1.7148 | 0 |  | 1.5
2017-07-05 | 19:40 | 1.7374 | 0 |  | 1.5
2017-07-05 | 19:45 | 1.7522 | 0 | 0 | 1.5 | 25
2017-07-05 | 19:45 | 1.7522 | 0 |  | 1.5 |  | 84.1667
2017-07-05 | 19:50 | 1.7444 | 0 |  | 1.5
2017-07-05 | 19:55 | 1.7826 | 0 |  | 1.5
2017-07-05 | 20:00 | 1.7717 | 0 | 0 | 1.5 | 25
2017-07-05 | 20:00 | 1.7717 | 0 |  | 1.5 |  | 83.9114
2017-07-05 | 20:05 | 1.7577 | 0 |  | 1.5
2017-07-05 | 20:10 | 1.7702 | 0 |  | 1.5
2017-07-05 | 20:15 | 1.7725 | 0 | 0 | 1.5 | 25
2017-07-05 | 20:15 | 1.7725 | 0 |  | 1.5 |  | 83.4091
2017-07-05 | 20:20 | 1.7694 | 0 |  | 1.5
2017-07-05 | 20:25 | 1.7452 | 0 |  | 1.5
2017-07-05 | 20:30 | 1.7631 | 0 | 0 | 1.5 | 25
2017-07-05 | 20:30 | 1.7631 | 0 |  | 1.5 |  | 82.9479
2017-07-05 | 20:35 | 1.7873 | 0 |  | 1.5
2017-07-05 | 20:40 | 1.7663 | 0 |  | 1.5
2017-07-05 | 20:45 | 1.7592 | 0 | 0 | 1.5 | 25
2017-07-05 | 20:45 | 1.7592 | 0 |  | 1.5 |  | 82.3489
2017-07-05 | 20:50 | 1.7686 | 0 |  | 1.5
2017-07-05 | 20:55 | 1.7873 | 0 |  | 1.5
2017-07-05 | 21:00 | 1.7873 | 0 | 0 | 1.5 | 25
2017-07-05 | 21:00 | 1.7873 | 0 |  | 1.5 |  | 0
2017-07-05 | 21:05 | -0.10652 | 0 |  | 1.5
2017-07-05 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-05 | 21:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 21:15 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 21:20 | -0.1073 | 0 |  | 1.5
2017-07-05 | 21:25 | -0.10808 | 0 |  | 1.5
2017-07-05 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 21:30 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 21:35 | -0.1073 | 0 |  | 1.5
2017-07-05 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-05 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 21:45 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-05 | 21:55 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 22:00 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 22:05 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:10 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 22:15 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 22:30 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 22:35 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 22:45 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-05 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-05 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 23:00 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 23:05 | -0.1073 | 0 |  | 1.5
2017-07-05 | 23:10 | -0.1073 | 0 |  | 1.5
2017-07-05 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 23:15 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-05 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-05 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-05 | 23:30 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-05 | 23:35 | -0.10964 | 0 |  | 1.5
2017-07-05 | 23:40 | -0.10652 | 0 |  | 1.5
2017-07-05 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-05 | 23:45 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-05 | 23:50 | -0.10652 | 0 |  | 1.5
2017-07-05 | 23:55 | -0.10652 | 0 |  | 1.5
2017-07-06 | 0:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-06 | 0:00 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-06 | 0:05 | -0.10652 | 0 |  | 1.5
2017-07-06 | 0:10 | -0.10652 | 0 |  | 1.5
2017-07-06 | 0:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 0:20 | -0.10574 | 0 |  | 1.5
2017-07-06 | 0:25 | -0.10652 | 0 |  | 1.5
2017-07-06 | 0:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 0:35 | -0.10652 | 0 |  | 1.5
2017-07-06 | 0:40 | -0.10652 | 0 |  | 1.5
2017-07-06 | 0:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 0:50 | -0.10574 | 0 |  | 1.5
2017-07-06 | 0:55 | -0.10574 | 0 |  | 1.5
2017-07-06 | 1:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 1:05 | -0.10652 | 0 |  | 1.5
2017-07-06 | 1:10 | -0.10652 | 0 |  | 1.5
2017-07-06 | 1:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-06 | 1:25 | -0.1112 | 0 |  | 1.5
2017-07-06 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 1:35 | -0.11042 | 0 |  | 1.5
2017-07-06 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-06 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-06 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-06 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-06 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-06 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-06 | 2:25 | -0.1112 | 0 |  | 1.5
2017-07-06 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-06 | 2:40 | -0.1112 | 0 |  | 1.5
2017-07-06 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-06 | 2:55 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 3:05 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-06 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 3:20 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:25 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:40 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 3:50 | -0.1112 | 0 |  | 1.5
2017-07-06 | 3:55 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 4:05 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:10 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:25 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:30 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 4:35 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:40 | -0.1112 | 0 |  | 1.5
2017-07-06 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 4:50 | -0.11198 | 0 |  | 1.5
2017-07-06 | 4:55 | -0.11198 | 0 |  | 1.5
2017-07-06 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 5:05 | 2.3583 | 6.0822 |  | 10
2017-07-06 | 5:10 | 2.072 | 10 |  | 10
2017-07-06 | 5:15 | 1.9901 | 9.9972 | 1 | 10 | 99.9793 | 89.8771
2017-07-06 | 5:20 | 1.9862 | 9.6935 |  | 10
2017-07-06 | 5:25 | 1.9589 | 9.1412 |  | 10
2017-07-06 | 5:30 | 1.9238 | 8.6906 | 1 | 10 | 87.6291 | 83.8745
2017-07-06 | 5:35 | 1.8747 | 8.2452 |  | 10
2017-07-06 | 5:40 | 1.8349 | 8.4216 |  | 10
2017-07-06 | 5:45 | 1.8029 | 8.1029 | 1 | 10 | 81.8426 | 81.2759
2017-07-06 | 5:50 | 1.8154 | 8.0194 |  | 10
2017-07-06 | 5:55 | 1.799 | 7.8329 |  | 10
2017-07-06 | 6:00 | 1.799 | 7.4463 | 1 | 10 | 75.3856 | 79.6059
2017-07-06 | 6:05 | 1.7998 | 7.1434 |  | 10
2017-07-06 | 6:10 | 1.8006 | 7.0557 |  | 10
2017-07-06 | 6:15 | 1.8099 | 7.1891 | 1 | 10 | 72.6612 | 78.2008
2017-07-06 | 6:20 | 1.7803 | 7.1505 |  | 10
2017-07-06 | 6:25 | 1.792 | 6.8181 |  | 10
2017-07-06 | 6:30 | 1.8302 | 6.1658 | 1 | 10 | 62.8837 | 77.1823
2017-07-06 | 6:35 | 1.7982 | 6.3648 |  | 10
2017-07-06 | 6:40 | 1.7873 | 6.3522 |  | 10
2017-07-06 | 6:45 | 1.785 | 6.1528 | 1 | 10 | 62.9926 | 76.1616
2017-07-06 | 6:50 | 1.767 | 5.8175 |  | 10
2017-07-06 | 6:55 | 1.7522 | 5.5809 |  | 10
2017-07-06 | 7:00 | 1.7717 | 5.2187 | 1 | 10 | 53.4066 | 75.5047
2017-07-06 | 7:05 | 1.7702 | 5.1568 |  | 10
2017-07-06 | 7:10 | 1.7382 | 5.4595 |  | 10
2017-07-06 | 7:15 | 1.7374 | 5.4816 | 1 | 10 | 55.907 | 75.5246
2017-07-06 | 7:20 | 1.7647 | 5.4544 |  | 10
2017-07-06 | 7:25 | 1.7405 | 5.3446 |  | 10
2017-07-06 | 7:30 | 1.76 | 4.9958 | 1 | 10 | 51.656 | 75.5448
2017-07-06 | 7:35 | 1.7358 | 4.8127 |  | 10
2017-07-06 | 7:40 | 1.7343 | 4.7566 |  | 10
2017-07-06 | 7:45 | 1.7163 | 4.609 | 1 | 10 | 47.65 | 76.144
2017-07-06 | 7:50 | 1.7787 | 4.5114 |  | 10
2017-07-06 | 7:55 | 1.7475 | 4.5064 |  | 10
2017-07-06 | 8:00 | 1.7499 | 3.9454 | 1 | 10 | 41.2673 | 75.7642
2017-07-06 | 8:05 | 1.7795 | 4.1613 |  | 10
2017-07-06 | 8:10 | 1.7296 | 4.5939 |  | 10
2017-07-06 | 8:15 | 1.7452 | 5.0969 | 1 | 10 | 51.0083 | 75.7491
2017-07-06 | 8:20 | 1.7483 | 5.3361 |  | 10
2017-07-06 | 8:25 | 1.7553 | 5.44 |  | 10
2017-07-06 | 8:30 | 1.7226 | 5.28 | 1 | 10 | 54.0035 | 76.0147
2017-07-06 | 8:35 | 1.7257 | 4.7255 |  | 10
2017-07-06 | 8:40 | 1.7647 | 5.3408 |  | 10
2017-07-06 | 8:45 | 1.7647 | 5.7418 | 1 | 10 | 58.5123 | 75.9651
2017-07-06 | 8:50 | 1.7436 | 5.0865 |  | 10
2017-07-06 | 8:55 | 1.7397 | 5.1564 |  | 10
2017-07-06 | 9:00 | 1.7374 | 5.3878 | 1 | 10 | 55.3378 | 76.2563
2017-07-06 | 9:05 | 1.7507 | 5.0122 |  | 10
2017-07-06 | 9:10 | 1.714 | 5.7585 |  | 10
2017-07-06 | 9:15 | 1.7124 | 5.7388 | 1 | 10 | 58.8761 | 76.7157
2017-07-06 | 9:20 | 1.7351 | 5.8392 |  | 10
2017-07-06 | 9:25 | 1.7351 | 6.0096 |  | 10
2017-07-06 | 9:30 | 1.6929 | 6.2073 | 1 | 10 | 63.8821 | 77.4604
2017-07-06 | 9:35 | 1.7039 | 6.4267 |  | 10
2017-07-06 | 9:40 | 1.6992 | 6.1439 |  | 10
2017-07-06 | 9:45 | 1.7195 | 4.9773 | 1 | 10 | 52.7803 | 78.6007
2017-07-06 | 9:50 | 1.5869 | 2.7935 |  | 1.5
2017-07-06 | 9:55 | 1.5728 | 0 |  | 1.5
2017-07-06 | 10:00 | 1.6485 | 0 | 0 | 1.5 | 25 | 81.482
2017-07-06 | 10:05 | 1.7218 | 0 |  | 1.5
2017-07-06 | 10:10 | 1.7257 | 0 |  | 1.5
2017-07-06 | 10:15 | 1.7483 | 0 | 0 | 1.5 | 25 | 82.2468
2017-07-06 | 10:20 | 1.7249 | 0 |  | 1.5
2017-07-06 | 10:25 | 1.7202 | 0 |  | 1.5
2017-07-06 | 10:30 | 1.6976 | 0 | 0 | 1.5 | 25 | 82.8915
2017-07-06 | 10:35 | 1.7202 | 0 |  | 1.5
2017-07-06 | 10:40 | 1.7639 | 0 |  | 1.5
2017-07-06 | 10:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 83.1788
2017-07-06 | 10:50 | 1.7015 | 0 |  | 1.5
2017-07-06 | 10:55 | 1.6945 | 0 |  | 1.5
2017-07-06 | 11:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 84.0053
2017-07-06 | 11:05 | 1.7787 | 0 |  | 1.5
2017-07-06 | 11:10 | 1.7663 | 0 |  | 1.5
2017-07-06 | 11:15 | 1.767 | 0 | 0 | 1.5 | 25 | 83.625
2017-07-06 | 11:20 | 1.7327 | 0 |  | 1.5
2017-07-06 | 11:25 | 1.739 | 0 |  | 1.5
2017-07-06 | 11:30 | 1.6922 | 0 | 0 | 1.5 | 25 | 84.2597
2017-07-06 | 11:35 | 1.7421 | 0 |  | 1.5
2017-07-06 | 11:40 | 1.7124 | 0 |  | 1.5
2017-07-06 | 11:45 | 1.7202 | 0 | 0 | 1.5 | 25 | 84.9295
2017-07-06 | 11:50 | 1.7226 | 0 |  | 1.5
2017-07-06 | 11:55 | 1.7296 | 0 |  | 1.5
2017-07-06 | 12:00 | 1.7741 | 0 | 0 | 1.5 | 25 | 85.4897
2017-07-06 | 12:05 | 1.7639 | 0 |  | 1.5
2017-07-06 | 12:10 | 1.7538 | 0 |  | 1.5
2017-07-06 | 12:15 | 1.7304 | 0 | 0 | 1.5 | 25 | 85.3864
2017-07-06 | 12:20 | 1.7421 | 0 |  | 1.5
2017-07-06 | 12:25 | 1.7288 | 0 |  | 1.5
2017-07-06 | 12:30 | 1.7327 | 0 | 0 | 1.5 | 25 | 85.6463
2017-07-06 | 12:35 | 1.7202 | 0 |  | 1.5
2017-07-06 | 12:40 | 1.8154 | 0 |  | 1.5
2017-07-06 | 12:45 | 1.7624 | 0 | 0 | 1.5 | 25 | 85.2658
2017-07-06 | 12:50 | 1.7748 | 0 |  | 1.5
2017-07-06 | 12:55 | 1.7553 | 0 |  | 1.5
2017-07-06 | 13:00 | 1.7772 | 0 | 0 | 1.5 | 25 | 84.9741
2017-07-06 | 13:05 | 1.7663 | 0 |  | 1.5
2017-07-06 | 13:10 | 1.7491 | 0 |  | 1.5
2017-07-06 | 13:15 | 1.7436 | 0 | 0 | 1.5 | 25 | 84.7474
2017-07-06 | 13:20 | 1.7436 | 0 |  | 1.5
2017-07-06 | 13:25 | 1.7156 | 0 |  | 1.5
2017-07-06 | 13:30 | 1.7015 | 0 | 0 | 1.5 | 25 | 85.5393
2017-07-06 | 13:35 | 1.7351 | 0 |  | 1.5
2017-07-06 | 13:40 | 1.6953 | 0 |  | 1.5
2017-07-06 | 13:45 | 1.6797 | 0 | 0 | 1.5 | 25 | 87.0561
2017-07-06 | 13:50 | 1.7007 | 0 |  | 1.5
2017-07-06 | 13:55 | 1.6851 | 0 |  | 1.5
2017-07-06 | 14:00 | 1.6805 | 0 | 0 | 1.5 | 25 | 88.6243
2017-07-06 | 14:05 | 1.7109 | 0 |  | 1.5
2017-07-06 | 14:10 | 1.714 | 0 |  | 1.5
2017-07-06 | 14:15 | 1.7405 | 0 | 0 | 1.5 | 25 | 89.4357
2017-07-06 | 14:20 | 1.7452 | 0 |  | 1.5
2017-07-06 | 14:25 | 1.7468 | 0 |  | 1.5
2017-07-06 | 14:30 | 1.728 | 0 | 0 | 1.5 | 25 | 90.0071
2017-07-06 | 14:35 | 1.7078 | 0 |  | 1.5
2017-07-06 | 14:40 | 1.7522 | 0 |  | 1.5
2017-07-06 | 14:45 | 1.7335 | 0 | 0 | 1.5 | 25 | 90.1375
2017-07-06 | 14:50 | 1.721 | 0 |  | 1.5
2017-07-06 | 14:55 | 1.6781 | 0 |  | 1.5
2017-07-06 | 15:00 | 1.7577 | 0 | 0 | 1.5 | 25 | 90.7738
2017-07-06 | 15:05 | 1.7647 | 0 |  | 1.5
2017-07-06 | 15:10 | 1.7569 | 0 |  | 1.5
2017-07-06 | 15:15 | 1.7889 | 0 | 0 | 1.5 | 25 | 90.441
2017-07-06 | 15:20 | 1.7897 | 0 |  | 1.5
2017-07-06 | 15:25 | 1.7499 | 0 |  | 1.5
2017-07-06 | 15:30 | 1.7148 | 0 | 0 | 1.5 | 25 | 90.143
2017-07-06 | 15:35 | 1.7421 | 0 |  | 1.5
2017-07-06 | 15:40 | 1.7546 | 0 |  | 1.5
2017-07-06 | 15:45 | 1.7015 | 0 | 0 | 1.5 | 25 | 90.3224
2017-07-06 | 15:50 | 1.7444 | 0 |  | 1.5
2017-07-06 | 15:55 | 1.7624 | 0 |  | 1.5
2017-07-06 | 16:00 | 1.7569 | 0 | 0 | 1.5 | 25 | 90.1794
2017-07-06 | 16:05 | 1.7608 | 0 |  | 1.5
2017-07-06 | 16:10 | 1.767 | 0 |  | 1.5
2017-07-06 | 16:15 | 1.7795 | 0 | 0 | 1.5 | 25 | 89.6915
2017-07-06 | 16:20 | 1.7702 | 0 |  | 1.5
2017-07-06 | 16:25 | 1.7897 | 0 |  | 1.5
2017-07-06 | 16:30 | 1.7936 | 0 | 0 | 1.5 | 25 | 88.8756
2017-07-06 | 16:35 | 1.7444 | 0 |  | 1.5
2017-07-06 | 16:40 | 1.7709 | 0 |  | 1.5
2017-07-06 | 16:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 88.7456
2017-07-06 | 16:50 | 1.7873 | 0 |  | 1.5
2017-07-06 | 16:55 | 1.7608 | 0 |  | 1.5
2017-07-06 | 17:00 | 1.76 | 0 | 0 | 1.5 | 25 | 88.3293
2017-07-06 | 17:05 | 1.7787 | 0 |  | 1.5
2017-07-06 | 17:10 | 1.7725 | 0 |  | 1.5
2017-07-06 | 17:15 | 1.7912 | 0 | 0 | 1.5 | 25 | 87.582
2017-07-06 | 17:20 | 1.7741 | 0 |  | 1.5
2017-07-06 | 17:25 | 1.7553 | 0 |  | 1.5
2017-07-06 | 17:30 | 1.8107 | 0 | 0 | 1.5 | 25 | 86.8206
2017-07-06 | 17:35 | 1.7936 | 0 |  | 1.5
2017-07-06 | 17:40 | 1.7803 | 0 |  | 1.5
2017-07-06 | 17:45 | 1.785 | 0 | 0 | 1.5 | 25 | 85.9206
2017-07-06 | 17:50 | 1.7834 | 0 |  | 1.5
2017-07-06 | 17:55 | 1.8123 | 0 |  | 1.5
2017-07-06 | 18:00 | 1.8014 | 0 | 0 | 1.5 | 25 | 84.9627
2017-07-06 | 18:05 | 1.7959 | 0 |  | 1.5
2017-07-06 | 18:10 | 1.792 | 0 |  | 1.5
2017-07-06 | 18:15 | 1.8099 | 0 | 0 | 1.5 | 25 | 83.7862
2017-07-06 | 18:20 | 1.7764 | 0 |  | 1.5
2017-07-06 | 18:25 | 1.7912 | 0 |  | 1.5
2017-07-06 | 18:30 | 1.7709 | 0 | 0 | 1.5 | 25 | 82.9642
2017-07-06 | 18:35 | 1.792 | 0 |  | 1.5
2017-07-06 | 18:40 | 1.7912 | 0 |  | 1.5
2017-07-06 | 18:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 82.5107
2017-07-06 | 18:50 | 1.7834 | 0 |  | 1.5
2017-07-06 | 18:55 | 1.7663 | 0 |  | 1.5
2017-07-06 | 19:00 | 1.7538 | 0 | 0 | 1.5 | 25 | 82.3247
2017-07-06 | 19:05 | 1.7655 | 0 |  | 1.5
2017-07-06 | 19:10 | 1.7655 | 0 |  | 1.5
2017-07-06 | 19:15 | 1.728 | 0 | 0 | 1.5 | 25 | 82.3272
2017-07-06 | 19:20 | 1.7241 | 0 |  | 1.5
2017-07-06 | 19:25 | 1.7405 | 0 |  | 1.5
2017-07-06 | 19:30 | 1.7132 | 0 | 0 | 1.5 | 25 | 82.9029
2017-07-06 | 19:35 | 1.7234 | 0 |  | 1.5
2017-07-06 | 19:40 | 1.7694 | 0 |  | 1.5
2017-07-06 | 19:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 82.7823
2017-07-06 | 19:50 | 1.7842 | 0 |  | 1.5
2017-07-06 | 19:55 | 1.7709 | 0 |  | 1.5
2017-07-06 | 20:00 | 1.7202 | 0 | 0 | 1.5 | 25 | 82.4211
2017-07-06 | 20:05 | 1.746 | 0 |  | 1.5
2017-07-06 | 20:10 | 1.7483 | 0 |  | 1.5
2017-07-06 | 20:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 82.4909
2017-07-06 | 20:20 | 1.7491 | 0 |  | 1.5
2017-07-06 | 20:25 | 1.7234 | 0 |  | 1.5
2017-07-06 | 20:30 | 1.753 | 0 | 0 | 1.5 | 25 | 82.472
2017-07-06 | 20:35 | 1.7709 | 0 |  | 1.5
2017-07-06 | 20:40 | 1.7444 | 0 |  | 1.5
2017-07-06 | 20:45 | 1.7756 | 0 | 0 | 1.5 | 25 | 82.0364
2017-07-06 | 20:50 | 1.7608 | 0 |  | 1.5
2017-07-06 | 20:55 | 1.7585 | 0 |  | 1.5
2017-07-06 | 21:00 | 1.7631 | 0 | 0 | 1.5 | 25 | 81.4955
2017-07-06 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-06 | 21:10 | -0.10496 | 0 |  | 1.5
2017-07-06 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-06 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-06 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-06 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-06 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-06 | 21:55 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-06 | 22:55 | -0.10574 | 0 |  | 1.5
2017-07-06 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-06 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-06 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 23:20 | -0.10574 | 0 |  | 1.5
2017-07-06 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-06 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-06 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-06 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-06 | 23:50 | -0.10496 | 0 |  | 1.5
2017-07-06 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 0:35 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 0:50 | -0.10496 | 0 |  | 1.5
2017-07-07 | 0:55 | -0.10496 | 0 |  | 1.5
2017-07-07 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-07 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-07 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 1:20 | -0.10496 | 0 |  | 1.5
2017-07-07 | 1:25 | -0.1073 | 0 |  | 1.5
2017-07-07 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 1:35 | -0.1073 | 0 |  | 1.5
2017-07-07 | 1:40 | -0.10652 | 0 |  | 1.5
2017-07-07 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 1:50 | -0.10808 | 0 |  | 1.5
2017-07-07 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:10 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 2:20 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:25 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 2:35 | -0.10808 | 0 |  | 1.5
2017-07-07 | 2:40 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 2:50 | -0.10886 | 0 |  | 1.5
2017-07-07 | 2:55 | -0.10886 | 0 |  | 1.5
2017-07-07 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 3:05 | -0.10886 | 0 |  | 1.5
2017-07-07 | 3:10 | -0.10886 | 0 |  | 1.5
2017-07-07 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 3:20 | -0.10886 | 0 |  | 1.5
2017-07-07 | 3:25 | -0.10886 | 0 |  | 1.5
2017-07-07 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-07 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-07 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-07 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-07 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-07 | 4:10 | -0.10964 | 0 |  | 1.5
2017-07-07 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-07 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-07 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 4:35 | -0.11588 | 0 |  | 1.5
2017-07-07 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-07 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 4:50 | -0.11042 | 0 |  | 1.5
2017-07-07 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-07 | 5:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 5:05 | 2.3208 | 6.228 |  | 10
2017-07-07 | 5:10 | 2.1134 | 10 |  | 10
2017-07-07 | 5:15 | 2.0252 | 10 | 1 | 10 | 100 | 89.2558
2017-07-07 | 5:20 | 1.9761 | 10 |  | 10
2017-07-07 | 5:25 | 1.9769 | 9.7587 |  | 10
2017-07-07 | 5:30 | 1.9301 | 9.2041 | 1 | 10 | 92.6199 | 83.5094
2017-07-07 | 5:35 | 1.8684 | 8.8519 |  | 10
2017-07-07 | 5:40 | 1.8544 | 8.5072 |  | 10
2017-07-07 | 5:45 | 1.8154 | 8.2222 | 1 | 10 | 83.0564 | 80.5391
2017-07-07 | 5:50 | 1.8372 | 7.9869 |  | 10
2017-07-07 | 5:55 | 1.7967 | 7.6601 |  | 10
2017-07-07 | 6:00 | 1.7982 | 7.4297 | 1 | 10 | 75.3962 | 78.9082
2017-07-07 | 6:05 | 1.8021 | 7.1279 |  | 10
2017-07-07 | 6:10 | 1.7858 | 7.1266 |  | 10
2017-07-07 | 6:15 | 1.7655 | 7.1088 | 1 | 10 | 72.0041 | 77.938
2017-07-07 | 6:20 | 1.7631 | 7.0009 |  | 10
2017-07-07 | 6:25 | 1.7655 | 6.926 |  | 10
2017-07-07 | 6:30 | 1.7507 | 6.8787 | 1 | 10 | 69.6288 | 77.248
2017-07-07 | 6:35 | 1.8006 | 6.723 |  | 10
2017-07-07 | 6:40 | 1.7702 | 6.7083 |  | 10
2017-07-07 | 6:45 | 1.7725 | 6.7289 | 1 | 10 | 68.5437 | 76.5938
2017-07-07 | 6:50 | 1.7842 | 6.4099 |  | 10
2017-07-07 | 6:55 | 1.7889 | 6.3768 |  | 10
2017-07-07 | 7:00 | 1.8021 | 6.0008 | 1 | 10 | 61.2332 | 75.73
2017-07-07 | 7:05 | 1.7959 | 5.9731 |  | 10
2017-07-07 | 7:10 | 1.7647 | 6.4699 |  | 10
2017-07-07 | 7:15 | 1.7881 | 5.7276 | 1 | 10 | 58.7043 | 75.0141
2017-07-07 | 7:20 | 1.7608 | 6.0781 |  | 10
2017-07-07 | 7:25 | 1.7709 | 5.9423 |  | 10
2017-07-07 | 7:30 | 1.7093 | 5.9196 | 1 | 10 | 59.9499 | 74.7874
2017-07-07 | 7:35 | 1.7452 | 5.6238 |  | 10
2017-07-07 | 7:40 | 1.7499 | 5.3408 |  | 10
2017-07-07 | 7:45 | 1.7452 | 4.914 | 1 | 10 | 50.834 | 74.3254
2017-07-07 | 7:50 | 1.7803 | 5.7076 |  | 10
2017-07-07 | 7:55 | 1.7631 | 4.9671 |  | 10
2017-07-07 | 8:00 | 1.7483 | 4.8683 | 1 | 10 | 50.2695 | 74.1538
2017-07-07 | 8:05 | 1.7507 | 4.9659 |  | 10
2017-07-07 | 8:10 | 1.7397 | 5.2794 |  | 10
2017-07-07 | 8:15 | 1.7514 | 5.1435 | 1 | 10 | 52.863 | 74.2022
2017-07-07 | 8:20 | 1.7374 | 5.2407 |  | 10
2017-07-07 | 8:25 | 1.7374 | 4.753 |  | 10
2017-07-07 | 8:30 | 1.7624 | 4.5006 | 1 | 10 | 46.0849 | 74.123
2017-07-07 | 8:35 | 1.7741 | 4.759 |  | 10
2017-07-07 | 8:40 | 1.7624 | 4.3142 |  | 10
2017-07-07 | 8:45 | 1.7444 | 4.3783 | 1 | 10 | 45.5862 | 74.1749
2017-07-07 | 8:50 | 1.7444 | 4.6035 |  | 10
2017-07-07 | 8:55 | 1.7374 | 4.3303 |  | 10
2017-07-07 | 9:00 | 1.7366 | 4.8148 | 1 | 10 | 49.5649 | 74.2995
2017-07-07 | 9:05 | 1.7639 | 4.7894 |  | 10
2017-07-07 | 9:10 | 1.7647 | 5.5768 |  | 10
2017-07-07 | 9:15 | 1.7491 | 5.9149 | 1 | 10 | 60.6713 | 74.3971
2017-07-07 | 9:20 | 1.7249 | 5.6824 |  | 10
2017-07-07 | 9:25 | 1.7156 | 5.537 |  | 10
2017-07-07 | 9:30 | 1.7413 | 5.3695 | 1 | 10 | 55.0965 | 74.5303
2017-07-07 | 9:35 | 1.7351 | 5.7789 |  | 10
2017-07-07 | 9:40 | 1.7382 | 5.768 |  | 10
2017-07-07 | 9:45 | 1.746 | 5.4934 | 1 | 10 | 56.92 | 74.9734
2017-07-07 | 9:50 | 1.7514 | 5.1018 |  | 10
2017-07-07 | 9:55 | 1.7959 | 4.91 |  | 10
2017-07-07 | 10:00 | 1.7421 | 4.9414 | 1 | 10 | 50.7203 | 74.8682
2017-07-07 | 10:05 | 1.7319 | 4.7575 |  | 10
2017-07-07 | 10:10 | 1.7577 | 4.6642 |  | 10
2017-07-07 | 10:15 | 1.728 | 4.6859 | 1 | 10 | 48.8757 | 75.1155
2017-07-07 | 10:20 | 1.7304 | 4.555 |  | 10
2017-07-07 | 10:25 | 1.7421 | 5.3679 |  | 10
2017-07-07 | 10:30 | 1.6851 | 5.3156 | 1 | 10 | 53.9509 | 75.5253
2017-07-07 | 10:35 | 1.7109 | 5.4365 |  | 10
2017-07-07 | 10:40 | 1.7273 | 4.8933 |  | 10
2017-07-07 | 10:45 | 1.7546 | 4.7766 | 1 | 10 | 49.4452 | 75.9735
2017-07-07 | 10:50 | 1.7912 | 4.9097 |  | 10
2017-07-07 | 10:55 | 1.739 | 4.7106 |  | 10
2017-07-07 | 11:00 | 1.739 | 4.457 | 1 | 10 | 46.3216 | 75.7168
2017-07-07 | 11:05 | 1.7319 | 4.7795 |  | 10
2017-07-07 | 11:10 | 1.7249 | 5.2781 |  | 10
2017-07-07 | 11:15 | 1.7343 | 5.1414 | 1 | 10 | 53.4273 | 76.177
2017-07-07 | 11:20 | 1.7553 | 4.7644 |  | 10
2017-07-07 | 11:25 | 1.7772 | 5.1777 |  | 10
2017-07-07 | 11:30 | 1.7678 | 6.2683 | 1 | 10 | 62.717 | 76.0402
2017-07-07 | 11:35 | 1.7327 | 6.2489 |  | 10
2017-07-07 | 11:40 | 1.767 | 5.9716 |  | 10
2017-07-07 | 11:45 | 1.7023 | 6.0727 | 1 | 10 | 61.8694 | 76.2595
2017-07-07 | 11:50 | 1.7148 | 6.43 |  | 10
2017-07-07 | 11:55 | 1.7234 | 6.6009 |  | 10
2017-07-07 | 12:00 | 1.7187 | 6.6587 | 1 | 10 | 67.086 | 77.3726
2017-07-07 | 12:05 | 1.7538 | 6.0207 |  | 10
2017-07-07 | 12:10 | 1.7546 | 5.8025 |  | 10
2017-07-07 | 12:15 | 1.7709 | 5.9331 | 1 | 10 | 60.2208 | 77.4395
2017-07-07 | 12:20 | 1.753 | 5.5532 |  | 10
2017-07-07 | 12:25 | 1.7725 | 5.8207 |  | 10
2017-07-07 | 12:30 | 1.7343 | 6.2414 | 1 | 10 | 62.6457 | 77.0812
2017-07-07 | 12:35 | 1.7686 | 6.206 |  | 10
2017-07-07 | 12:40 | 1.7585 | 6.2114 |  | 10
2017-07-07 | 12:45 | 1.7616 | 5.5914 | 1 | 10 | 57.5629 | 76.5714
2017-07-07 | 12:50 | 1.7507 | 5.5762 |  | 10
2017-07-07 | 12:55 | 1.7858 | 5.092 |  | 10
2017-07-07 | 13:00 | 1.7592 | 5.0809 | 1 | 10 | 50.8 | 76.1179
2017-07-07 | 13:05 | 1.7499 | 5.4118 |  | 10
2017-07-07 | 13:10 | 1.7413 | 6.2288 |  | 10
2017-07-07 | 13:15 | 1.7413 | 5.773 | 1 | 10 | 58.9239 | 76.0714
2017-07-07 | 13:20 | 1.7468 | 5.8083 |  | 10
2017-07-07 | 13:25 | 1.753 | 6.0006 |  | 10
2017-07-07 | 13:30 | 1.7678 | 6.1218 | 1 | 10 | 61.9306 | 75.9848
2017-07-07 | 13:35 | 1.7429 | 6.3754 |  | 10
2017-07-07 | 13:40 | 1.7296 | 6.5345 |  | 10
2017-07-07 | 13:45 | 1.7319 | 6.6614 | 1 | 10 | 67.0293 | 76.6356
2017-07-07 | 13:50 | 1.7312 | 6.4575 |  | 10
2017-07-07 | 13:55 | 1.728 | 6.2878 |  | 10
2017-07-07 | 14:00 | 1.5596 | 4.1107 | 0 | 1.5 | 45 | 79.1704
2017-07-07 | 14:05 | 1.6212 | 0.15869 |  | 1.5
2017-07-07 | 14:10 | 1.6789 | 0 |  | 1.5
2017-07-07 | 14:15 | 1.7109 | 0 | 0 | 1.5 | 25 | 81.2109
2017-07-07 | 14:20 | 1.7109 | 0 |  | 1.5
2017-07-07 | 14:25 | 1.7366 | 0 |  | 1.5
2017-07-07 | 14:30 | 1.7819 | 0 | 0 | 1.5 | 25 | 81.3377
2017-07-07 | 14:35 | 1.7608 | 0 |  | 1.5
2017-07-07 | 14:40 | 1.7546 | 0 |  | 1.5
2017-07-07 | 14:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 81.1085
2017-07-07 | 14:50 | 1.7062 | 0 |  | 1.5
2017-07-07 | 14:55 | 1.7366 | 0 |  | 1.5
2017-07-07 | 15:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 81.4638
2017-07-07 | 15:05 | 1.7218 | 0 |  | 1.5
2017-07-07 | 15:10 | 1.7631 | 0 |  | 1.5
2017-07-07 | 15:15 | 1.7397 | 0 | 0 | 1.5 | 25 | 81.7469
2017-07-07 | 15:20 | 1.7202 | 0 |  | 1.5
2017-07-07 | 15:25 | 1.746 | 0 |  | 1.5
2017-07-07 | 15:30 | 1.7202 | 0 | 0 | 1.5 | 25 | 82.1572
2017-07-07 | 15:35 | 1.7187 | 0 |  | 1.5
2017-07-07 | 15:40 | 1.7452 | 0 |  | 1.5
2017-07-07 | 15:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 82.5543
2017-07-07 | 15:50 | 1.7343 | 0 |  | 1.5
2017-07-07 | 15:55 | 1.7195 | 0 |  | 1.5
2017-07-07 | 16:00 | 1.7335 | 0 | 0 | 1.5 | 25 | 82.985
2017-07-07 | 16:05 | 1.7374 | 0 |  | 1.5
2017-07-07 | 16:10 | 1.7327 | 0 |  | 1.5
2017-07-07 | 16:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 83.2812
2017-07-07 | 16:20 | 1.746 | 0 |  | 1.5
2017-07-07 | 16:25 | 1.767 | 0 |  | 1.5
2017-07-07 | 16:30 | 1.7561 | 0 | 0 | 1.5 | 25 | 82.827
2017-07-07 | 16:35 | 1.7577 | 0 |  | 1.5
2017-07-07 | 16:40 | 1.7678 | 0 |  | 1.5
2017-07-07 | 16:45 | 1.767 | 0 | 0 | 1.5 | 25 | 82.4799
2017-07-07 | 16:50 | 1.7624 | 0 |  | 1.5
2017-07-07 | 16:55 | 1.7819 | 0 |  | 1.5
2017-07-07 | 17:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 82.1363
2017-07-07 | 17:05 | 1.7811 | 0 |  | 1.5
2017-07-07 | 17:10 | 1.7639 | 0 |  | 1.5
2017-07-07 | 17:15 | 1.7741 | 0 | 0 | 1.5 | 25 | 81.7517
2017-07-07 | 17:20 | 1.7764 | 0 |  | 1.5
2017-07-07 | 17:25 | 1.7694 | 0 |  | 1.5
2017-07-07 | 17:30 | 1.8037 | 0 | 0 | 1.5 | 25 | 80.9801
2017-07-07 | 17:35 | 1.7694 | 0 |  | 1.5
2017-07-07 | 17:40 | 1.7694 | 0 |  | 1.5
2017-07-07 | 17:45 | 1.778 | 0 | 0 | 1.5 | 25 | 80.0498
2017-07-07 | 17:50 | 1.7764 | 0 |  | 1.5
2017-07-07 | 17:55 | 1.7678 | 0 |  | 1.5
2017-07-07 | 18:00 | 1.7741 | 0 | 0 | 1.5 | 25 | 79.4981
2017-07-07 | 18:05 | 1.7741 | 0 |  | 1.5
2017-07-07 | 18:10 | 1.7842 | 0 |  | 1.5
2017-07-07 | 18:15 | 1.7702 | 0 | 0 | 1.5 | 25 | 79.0857
2017-07-07 | 18:20 | 1.7741 | 0 |  | 1.5
2017-07-07 | 18:25 | 1.7803 | 0 |  | 1.5
2017-07-07 | 18:30 | 1.7351 | 0 | 0 | 1.5 | 25 | 78.6995
2017-07-07 | 18:35 | 1.7764 | 0 |  | 1.5
2017-07-07 | 18:40 | 1.7702 | 0 |  | 1.5
2017-07-07 | 18:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 78.2608
2017-07-07 | 18:50 | 1.7787 | 0 |  | 1.5
2017-07-07 | 18:55 | 1.7569 | 0 |  | 1.5
2017-07-07 | 19:00 | 1.7577 | 0 | 0 | 1.5 | 25 | 77.7372
2017-07-07 | 19:05 | 1.7639 | 0 |  | 1.5
2017-07-07 | 19:10 | 1.7826 | 0 |  | 1.5
2017-07-07 | 19:15 | 1.7865 | 0 | 0 | 1.5 | 25 | 77.1218
2017-07-07 | 19:20 | 1.7553 | 0 |  | 1.5
2017-07-07 | 19:25 | 1.7795 | 0 |  | 1.5
2017-07-07 | 19:30 | 1.7616 | 0 | 0 | 1.5 | 25 | 76.5858
2017-07-07 | 19:35 | 1.7663 | 0 |  | 1.5
2017-07-07 | 19:40 | 1.7631 | 0 |  | 1.5
2017-07-07 | 19:45 | 1.7772 | 0 | 0 | 1.5 | 25 | 76.2041
2017-07-07 | 19:50 | 1.7834 | 0 |  | 1.5
2017-07-07 | 19:55 | 1.7647 | 0 |  | 1.5
2017-07-07 | 20:00 | 1.7491 | 0 | 0 | 1.5 | 25 | 75.9774
2017-07-07 | 20:05 | 1.7647 | 0 |  | 1.5
2017-07-07 | 20:10 | 1.7686 | 0 |  | 1.5
2017-07-07 | 20:15 | 1.7202 | 0 | 0 | 1.5 | 25 | 75.9506
2017-07-07 | 20:20 | 1.7663 | 0 |  | 1.5
2017-07-07 | 20:25 | 1.7499 | 0 |  | 1.5
2017-07-07 | 20:30 | 1.7577 | 0 | 0 | 1.5 | 25 | 75.5376
2017-07-07 | 20:35 | 1.7678 | 0 |  | 1.5
2017-07-07 | 20:40 | 1.7803 | 0 |  | 1.5
2017-07-07 | 20:45 | 1.7538 | 0.073931 | 0 | 1.5 | 25.7013 | 75.2243
2017-07-07 | 20:50 | 1.7624 | 0 |  | 1.5
2017-07-07 | 20:55 | 1.7678 | 0 |  | 1.5
2017-07-07 | 21:00 | 1.7491 | 0 | 0 | 1.5 | 25 | 74.7901
2017-07-07 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-07 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-07 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 21:20 | -0.1073 | 0 |  | 1.5
2017-07-07 | 21:25 | -0.1073 | 0 |  | 1.5
2017-07-07 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 21:35 | -0.10808 | 0 |  | 1.5
2017-07-07 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-07 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-07 | 21:55 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 22:05 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:10 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 22:35 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-07 | 22:55 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-07 | 23:10 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 23:20 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:25 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 23:35 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:40 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-07 | 23:50 | -0.1073 | 0 |  | 1.5
2017-07-07 | 23:55 | -0.10652 | 0 |  | 1.5
2017-07-08 | 0:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 0:05 | -0.1073 | 0 |  | 1.5
2017-07-08 | 0:10 | -0.10652 | 0 |  | 1.5
2017-07-08 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 0:20 | -0.10652 | 0 |  | 1.5
2017-07-08 | 0:25 | -0.10652 | 0 |  | 1.5
2017-07-08 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 0:35 | -0.1073 | 0 |  | 1.5
2017-07-08 | 0:40 | -0.10652 | 0 |  | 1.5
2017-07-08 | 0:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 0:50 | -0.10652 | 0 |  | 1.5
2017-07-08 | 0:55 | -0.10652 | 0 |  | 1.5
2017-07-08 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 1:05 | -0.1073 | 0 |  | 1.5
2017-07-08 | 1:10 | -0.1073 | 0 |  | 1.5
2017-07-08 | 1:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-08 | 1:25 | -0.1073 | 0 |  | 1.5
2017-07-08 | 1:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 1:35 | -0.10964 | 0 |  | 1.5
2017-07-08 | 1:40 | -0.10964 | 0 |  | 1.5
2017-07-08 | 1:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 1:50 | -0.10964 | 0 |  | 1.5
2017-07-08 | 1:55 | -0.10964 | 0 |  | 1.5
2017-07-08 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 2:05 | -0.10964 | 0 |  | 1.5
2017-07-08 | 2:10 | -0.10964 | 0 |  | 1.5
2017-07-08 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 2:20 | -0.10964 | 0 |  | 1.5
2017-07-08 | 2:25 | -0.10964 | 0 |  | 1.5
2017-07-08 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-08 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-08 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-08 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-08 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 3:35 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-08 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 4:20 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-08 | 4:45 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 4:50 | -0.11276 | 0 |  | 1.5
2017-07-08 | 4:55 | -0.11276 | 0 |  | 1.5
2017-07-08 | 5:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 5:05 | 2.735 | 5.2079 |  | 10
2017-07-08 | 5:10 | 2.4722 | 9.9131 |  | 10
2017-07-08 | 5:15 | 1.9808 | 8.1521 | 1 | 7.1738 | 85.2412 | 84.0337
2017-07-08 | 5:20 | 1.9925 | 6.6048 |  | 7.5384
2017-07-08 | 5:25 | 1.9792 | 5.7285 |  | 8.6367
2017-07-08 | 5:30 | 1.902 | 5.678 | 1 | 8.7763 | 60.0226 | 77.6704
2017-07-08 | 5:35 | 1.8294 | 5.3005 |  | 7.9672
2017-07-08 | 5:40 | 1.8263 | 5.0332 |  | 8.3702
2017-07-08 | 5:45 | 1.8123 | 4.9495 | 1 | 9.2458 | 52.9098 | 75.3573
2017-07-08 | 5:50 | 1.7678 | 4.6506 |  | 6.917
2017-07-08 | 5:55 | 1.7842 | 4.5295 |  | 8.675
2017-07-08 | 6:00 | 1.7826 | 4.2804 | 1 | 8.5014 | 46.512 | 74.4568
2017-07-08 | 6:05 | 1.7982 | 4.7966 |  | 10
2017-07-08 | 6:10 | 1.7616 | 5.0705 |  | 9.9693
2017-07-08 | 6:15 | 1.7702 | 5.2209 | 1 | 10 | 55.2931 | 73.6744
2017-07-08 | 6:20 | 1.7585 | 5.4772 |  | 10
2017-07-08 | 6:25 | 1.7608 | 5.3392 |  | 10
2017-07-08 | 6:30 | 1.7366 | 5.5389 | 1 | 10 | 58.3371 | 73.4595
2017-07-08 | 6:35 | 1.7507 | 5.4395 |  | 10
2017-07-08 | 6:40 | 1.7624 | 5.3575 |  | 10
2017-07-08 | 6:45 | 1.7764 | 5.3488 | 1 | 10 | 56.7618 | 73.3571
2017-07-08 | 6:50 | 1.7546 | 5.1376 |  | 10
2017-07-08 | 6:55 | 1.7631 | 5.2478 |  | 10
2017-07-08 | 7:00 | 1.7717 | 5.1033 | 1 | 10 | 54.4074 | 73.2176
2017-07-08 | 7:05 | 1.7889 | 5.239 |  | 10
2017-07-08 | 7:10 | 1.7663 | 5.4127 |  | 10
2017-07-08 | 7:15 | 1.7397 | 5.358 | 1 | 10 | 56.7554 | 72.9038
2017-07-08 | 7:20 | 1.7631 | 5.5802 |  | 10
2017-07-08 | 7:25 | 1.7179 | 5.4995 |  | 10
2017-07-08 | 7:30 | 1.7421 | 5.6686 | 1 | 10 | 59.7617 | 73.0991
2017-07-08 | 7:35 | 1.7842 | 5.58 |  | 10
2017-07-08 | 7:40 | 1.7881 | 5.4454 |  | 10
2017-07-08 | 7:45 | 1.76 | 5.6509 | 1 | 10 | 59.6226 | 72.7215
2017-07-08 | 7:50 | 1.7444 | 5.5046 |  | 10
2017-07-08 | 7:55 | 1.7187 | 5.738 |  | 10
2017-07-08 | 8:00 | 1.7468 | 5.6453 | 1 | 10 | 59.7391 | 72.6701
2017-07-08 | 8:05 | 1.7686 | 5.6284 |  | 10
2017-07-08 | 8:10 | 1.7538 | 5.7084 |  | 10
2017-07-08 | 8:15 | 1.7585 | 5.5789 | 1 | 10 | 58.9099 | 72.6725
2017-07-08 | 8:20 | 1.7382 | 5.5599 |  | 10
2017-07-08 | 8:25 | 1.7733 | 5.5046 |  | 10
2017-07-08 | 8:30 | 1.7483 | 5.5049 | 1 | 10 | 58.1314 | 72.6878
2017-07-08 | 8:35 | 1.7569 | 5.3842 |  | 10
2017-07-08 | 8:40 | 1.76 | 5.2267 |  | 10
2017-07-08 | 8:45 | 1.7444 | 5.493 | 1 | 10 | 58.0373 | 72.7338
2017-07-08 | 8:50 | 1.7569 | 5.3494 |  | 10
2017-07-08 | 8:55 | 1.7475 | 5.5158 |  | 10
2017-07-08 | 9:00 | 1.7132 | 5.6348 | 1 | 10 | 59.5847 | 72.7812
2017-07-08 | 9:05 | 1.7187 | 5.6177 |  | 10
2017-07-08 | 9:10 | 1.7452 | 5.8403 |  | 10
2017-07-08 | 9:15 | 1.7616 | 5.6616 | 1 | 10 | 59.8204 | 72.9226
2017-07-08 | 9:20 | 1.7577 | 5.9972 |  | 10
2017-07-08 | 9:25 | 1.7343 | 5.9615 |  | 10
2017-07-08 | 9:30 | 1.7366 | 6.0962 | 1 | 10 | 63.8478 | 73.1532
2017-07-08 | 9:35 | 1.739 | 5.8279 |  | 10
2017-07-08 | 9:40 | 1.7686 | 5.5689 |  | 10
2017-07-08 | 9:45 | 1.7475 | 5.7566 | 1 | 10 | 60.6115 | 73.1325
2017-07-08 | 9:50 | 1.753 | 5.4115 |  | 10
2017-07-08 | 9:55 | 1.4972 | 4.9131 |  | 1.5
2017-07-08 | 10:00 | 1.6485 | 3.4265 | 0 | 1.5 | 38.5811 | 75.5233
2017-07-08 | 10:05 | 1.9074 | 2.9827 |  | 10
2017-07-08 | 10:10 | 1.6235 | 3.5881 |  | 1.5
2017-07-08 | 10:15 | 1.7694 | 1.8475 | 0 | 1.5 | 25.166 | 75.7453
2017-07-08 | 10:20 | 1.7374 | 0 |  | 1.5
2017-07-08 | 10:25 | 1.7444 | 0 |  | 1.5
2017-07-08 | 10:30 | 1.7397 | 0 | 0 | 1.5 | 25 | 75.942
2017-07-08 | 10:35 | 1.7507 | 0 |  | 1.5
2017-07-08 | 10:40 | 1.7358 | 0 |  | 1.5
2017-07-08 | 10:45 | 1.7655 | 0 | 0 | 1.5 | 25 | 76.0283
2017-07-08 | 10:50 | 1.7475 | 0 |  | 1.5
2017-07-08 | 10:55 | 1.7639 | 0 |  | 1.5
2017-07-08 | 11:00 | 1.7327 | 0 | 0 | 1.5 | 25 | 76.0436
2017-07-08 | 11:05 | 1.7483 | 0 |  | 1.5
2017-07-08 | 11:10 | 1.7514 | 0 |  | 1.5
2017-07-08 | 11:15 | 1.746 | 0 | 0 | 1.5 | 25 | 75.9813
2017-07-08 | 11:20 | 1.7397 | 0 |  | 1.5
2017-07-08 | 11:25 | 1.753 | 0 |  | 1.5
2017-07-08 | 11:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 75.9288
2017-07-08 | 11:35 | 1.746 | 0 |  | 1.5
2017-07-08 | 11:40 | 1.7663 | 0 |  | 1.5
2017-07-08 | 11:45 | 1.7249 | 0 | 0 | 1.5 | 25 | 76.1047
2017-07-08 | 11:50 | 1.7054 | 0 |  | 1.5
2017-07-08 | 11:55 | 1.7273 | 0 |  | 1.5
2017-07-08 | 12:00 | 1.6945 | 0 | 0 | 1.5 | 25 | 76.7483
2017-07-08 | 12:05 | 1.7366 | 0 |  | 1.5
2017-07-08 | 12:10 | 1.7304 | 0 |  | 1.5
2017-07-08 | 12:15 | 1.7218 | 0 | 0 | 1.5 | 25 | 77.3491
2017-07-08 | 12:20 | 1.7015 | 0 |  | 1.5
2017-07-08 | 12:25 | 1.714 | 0 |  | 1.5
2017-07-08 | 12:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 78.0926
2017-07-08 | 12:35 | 1.7179 | 0 |  | 1.5
2017-07-08 | 12:40 | 1.721 | 0 |  | 1.5
2017-07-08 | 12:45 | 1.7156 | 0 | 0 | 1.5 | 25 | 78.9222
2017-07-08 | 12:50 | 1.7249 | 0 |  | 1.5
2017-07-08 | 12:55 | 1.721 | 0 |  | 1.5
2017-07-08 | 13:00 | 1.728 | 0 | 0 | 1.5 | 25 | 79.5213
2017-07-08 | 13:05 | 1.7483 | 0 |  | 1.5
2017-07-08 | 13:10 | 1.7304 | 0 |  | 1.5
2017-07-08 | 13:15 | 1.7343 | 0 | 0 | 1.5 | 25 | 80.0809
2017-07-08 | 13:20 | 1.728 | 0 |  | 1.5
2017-07-08 | 13:25 | 1.7351 | 0 |  | 1.5
2017-07-08 | 13:30 | 1.7304 | 0 | 0 | 1.5 | 25 | 80.6411
2017-07-08 | 13:35 | 1.7475 | 0 |  | 1.5
2017-07-08 | 13:40 | 1.7358 | 0 |  | 1.5
2017-07-08 | 13:45 | 1.7265 | 0 | 0 | 1.5 | 25 | 81.2878
2017-07-08 | 13:50 | 1.7405 | 0 |  | 1.5
2017-07-08 | 13:55 | 1.7265 | 0 |  | 1.5
2017-07-08 | 14:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 81.7549
2017-07-08 | 14:05 | 1.7124 | 0 |  | 1.5
2017-07-08 | 14:10 | 1.728 | 0 |  | 1.5
2017-07-08 | 14:15 | 1.7195 | 0 | 0 | 1.5 | 25 | 82.2873
2017-07-08 | 14:20 | 1.7483 | 0 |  | 1.5
2017-07-08 | 14:25 | 1.721 | 0 |  | 1.5
2017-07-08 | 14:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 82.7891
2017-07-08 | 14:35 | 1.7429 | 0 |  | 1.5
2017-07-08 | 14:40 | 1.7436 | 0 |  | 1.5
2017-07-08 | 14:45 | 1.7195 | 0 | 0 | 1.5 | 25 | 83.2787
2017-07-08 | 14:50 | 1.7023 | 0 |  | 1.5
2017-07-08 | 14:55 | 1.7694 | 0 |  | 1.5
2017-07-08 | 15:00 | 1.7265 | 0 | 0 | 1.5 | 25 | 83.7541
2017-07-08 | 15:05 | 1.7327 | 0 |  | 1.5
2017-07-08 | 15:10 | 1.7538 | 0 |  | 1.5
2017-07-08 | 15:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 83.6558
2017-07-08 | 15:20 | 1.7819 | 0 |  | 1.5
2017-07-08 | 15:25 | 1.767 | 0 |  | 1.5
2017-07-08 | 15:30 | 1.7811 | 0 | 0 | 1.5 | 25 | 82.9128
2017-07-08 | 15:35 | 1.7819 | 0 |  | 1.5
2017-07-08 | 15:40 | 1.7865 | 0 |  | 1.5
2017-07-08 | 15:45 | 1.8053 | 0 | 0 | 1.5 | 25 | 81.7768
2017-07-08 | 15:50 | 1.7928 | 0 |  | 1.5
2017-07-08 | 15:55 | 1.8138 | 0 |  | 1.5
2017-07-08 | 16:00 | 1.7889 | 0 | 0 | 1.5 | 25 | 80.7367
2017-07-08 | 16:05 | 1.7842 | 0 |  | 1.5
2017-07-08 | 16:10 | 1.7811 | 0 |  | 1.5
2017-07-08 | 16:15 | 1.8107 | 0 | 0 | 1.5 | 25 | 79.8502
2017-07-08 | 16:20 | 1.7967 | 0 |  | 1.5
2017-07-08 | 16:25 | 1.7873 | 0 |  | 1.5
2017-07-08 | 16:30 | 1.7803 | 0 | 0 | 1.5 | 25 | 78.7839
2017-07-08 | 16:35 | 1.7756 | 0 |  | 1.5
2017-07-08 | 16:40 | 1.7912 | 0 |  | 1.5
2017-07-08 | 16:45 | 1.7748 | 0 | 0 | 1.5 | 25 | 78.03
2017-07-08 | 16:50 | 1.7858 | 0 |  | 1.5
2017-07-08 | 16:55 | 1.7702 | 0 |  | 1.5
2017-07-08 | 17:00 | 1.7897 | 0 | 0 | 1.5 | 25 | 77.3646
2017-07-08 | 17:05 | 1.767 | 0 |  | 1.5
2017-07-08 | 17:10 | 1.7374 | 0 |  | 1.5
2017-07-08 | 17:15 | 1.7764 | 0 | 0 | 1.5 | 25 | 76.9716
2017-07-08 | 17:20 | 1.7561 | 0 |  | 1.5
2017-07-08 | 17:25 | 1.7514 | 0 |  | 1.5
2017-07-08 | 17:30 | 1.7748 | 0 | 0 | 1.5 | 25 | 76.5704
2017-07-08 | 17:35 | 1.7577 | 0 |  | 1.5
2017-07-08 | 17:40 | 1.7577 | 0 |  | 1.5
2017-07-08 | 17:45 | 1.7694 | 0 | 0 | 1.5 | 25 | 76.3345
2017-07-08 | 17:50 | 1.7374 | 0 |  | 1.5
2017-07-08 | 17:55 | 1.7085 | 0 |  | 1.5
2017-07-08 | 18:00 | 1.7249 | 0 | 0 | 1.5 | 25 | 76.563
2017-07-08 | 18:05 | 1.7288 | 0 |  | 1.5
2017-07-08 | 18:10 | 1.7483 | 0 |  | 1.5
2017-07-08 | 18:15 | 1.7374 | 0 | 0 | 1.5 | 25 | 76.7257
2017-07-08 | 18:20 | 1.7429 | 0 |  | 1.5
2017-07-08 | 18:25 | 1.7639 | 0 |  | 1.5
2017-07-08 | 18:30 | 1.7639 | 0 | 0 | 1.5 | 25 | 76.8145
2017-07-08 | 18:35 | 1.7413 | 0 |  | 1.5
2017-07-08 | 18:40 | 1.7288 | 0 |  | 1.5
2017-07-08 | 18:45 | 1.7678 | 0 | 0 | 1.5 | 25 | 76.9961
2017-07-08 | 18:50 | 1.7865 | 0 |  | 1.5
2017-07-08 | 18:55 | 1.7702 | 0 |  | 1.5
2017-07-08 | 19:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 76.968
2017-07-08 | 19:05 | 1.7397 | 0 |  | 1.5
2017-07-08 | 19:10 | 1.7592 | 0 |  | 1.5
2017-07-08 | 19:15 | 1.7592 | 0 | 0 | 1.5 | 25 | 76.8297
2017-07-08 | 19:20 | 1.7655 | 0 |  | 1.5
2017-07-08 | 19:25 | 1.7553 | 0 |  | 1.5
2017-07-08 | 19:30 | 1.7491 | 0 | 0 | 1.5 | 25 | 76.8258
2017-07-08 | 19:35 | 1.7686 | 0 |  | 1.5
2017-07-08 | 19:40 | 1.7405 | 0 |  | 1.5
2017-07-08 | 19:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 76.8704
2017-07-08 | 19:50 | 1.7475 | 0 |  | 1.5
2017-07-08 | 19:55 | 1.7312 | 0 |  | 1.5
2017-07-08 | 20:00 | 1.7452 | 0 | 0 | 1.5 | 25 | 76.9306
2017-07-08 | 20:05 | 1.7351 | 0 |  | 1.5
2017-07-08 | 20:10 | 1.7296 | 0 |  | 1.5
2017-07-08 | 20:15 | 1.7382 | 0 | 0 | 1.5 | 25 | 77.0351
2017-07-08 | 20:20 | 1.7429 | 0 |  | 1.5
2017-07-08 | 20:25 | 1.7343 | 0 |  | 1.5
2017-07-08 | 20:30 | 1.7436 | 0 | 0 | 1.5 | 25 | 77.0821
2017-07-08 | 20:35 | 1.7663 | 0 |  | 1.5
2017-07-08 | 20:40 | 1.7522 | 0 |  | 1.5
2017-07-08 | 20:45 | 1.7717 | 0 | 0 | 1.5 | 25 | 76.7837
2017-07-08 | 20:50 | 1.7319 | 0 |  | 1.5
2017-07-08 | 20:55 | 1.7764 | 0 |  | 1.5
2017-07-08 | 21:00 | 1.7733 | 0 | 0 | 1.5 | 25 | 76.5055
2017-07-08 | 21:05 | -0.10574 | 0 |  | 1.5
2017-07-08 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-08 | 21:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 21:20 | -0.1073 | 0 |  | 1.5
2017-07-08 | 21:25 | -0.10652 | 0 |  | 1.5
2017-07-08 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 21:35 | -0.1073 | 0 |  | 1.5
2017-07-08 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-08 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 21:50 | -0.10808 | 0 |  | 1.5
2017-07-08 | 21:55 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 22:05 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:10 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 22:20 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:25 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 22:35 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:40 | -0.10808 | 0 |  | 1.5
2017-07-08 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 22:50 | -0.10886 | 0 |  | 1.5
2017-07-08 | 22:55 | -0.10808 | 0 |  | 1.5
2017-07-08 | 23:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 23:05 | -0.10808 | 0 |  | 1.5
2017-07-08 | 23:10 | -0.10808 | 0 |  | 1.5
2017-07-08 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 23:20 | -0.10808 | 0 |  | 1.5
2017-07-08 | 23:25 | -0.10808 | 0 |  | 1.5
2017-07-08 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 23:35 | -0.1073 | 0 |  | 1.5
2017-07-08 | 23:40 | -0.10808 | 0 |  | 1.5
2017-07-08 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-08 | 23:50 | -0.1073 | 0 |  | 1.5
2017-07-08 | 23:55 | -0.10808 | 0 |  | 1.5
2017-07-09 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 0:05 | -0.10808 | 0 |  | 1.5
2017-07-09 | 0:10 | -0.10808 | 0 |  | 1.5
2017-07-09 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 0:20 | -0.1073 | 0 |  | 1.5
2017-07-09 | 0:25 | -0.1073 | 0 |  | 1.5
2017-07-09 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 0:35 | -0.1073 | 0 |  | 1.5
2017-07-09 | 0:40 | -0.1073 | 0 |  | 1.5
2017-07-09 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 0:50 | -0.1073 | 0 |  | 1.5
2017-07-09 | 0:55 | -0.1073 | 0 |  | 1.5
2017-07-09 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 1:05 | -0.1073 | 0 |  | 1.5
2017-07-09 | 1:10 | -0.1073 | 0 |  | 1.5
2017-07-09 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 1:20 | -0.11198 | 0 |  | 1.5
2017-07-09 | 1:25 | -0.11042 | 0 |  | 1.5
2017-07-09 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 1:35 | -0.11042 | 0 |  | 1.5
2017-07-09 | 1:40 | -0.11042 | 0 |  | 1.5
2017-07-09 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-09 | 1:55 | -0.10964 | 0 |  | 1.5
2017-07-09 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-09 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 3:35 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-09 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-09 | 4:00 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-09 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-09 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-09 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-09 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 4:35 | -0.1112 | 0 |  | 1.5
2017-07-09 | 4:40 | -0.1112 | 0 |  | 1.5
2017-07-09 | 4:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 4:50 | -0.1112 | 0 |  | 1.5
2017-07-09 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-09 | 5:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 5:05 | 2.6453 | 5.0459 |  | 10
2017-07-09 | 5:10 | 2.4144 | 9.9736 |  | 10
2017-07-09 | 5:15 | 2.1882 | 8.367 | 1 | 10 | 86.5186 | 84.3675
2017-07-09 | 5:20 | 2.0611 | 7.2753 |  | 10
2017-07-09 | 5:25 | 1.9831 | 6.7068 |  | 10
2017-07-09 | 5:30 | 1.9098 | 6.0906 | 1 | 10 | 64.0172 | 77.5003
2017-07-09 | 5:35 | 1.8263 | 5.9848 |  | 10
2017-07-09 | 5:40 | 1.8333 | 5.996 |  | 10
2017-07-09 | 5:45 | 1.7998 | 5.6993 | 1 | 10 | 59.7482 | 75.3084
2017-07-09 | 5:50 | 1.7834 | 5.7746 |  | 10
2017-07-09 | 5:55 | 1.7819 | 5.501 |  | 10
2017-07-09 | 6:00 | 1.7694 | 5.517 | 1 | 10 | 57.8867 | 74.5309
2017-07-09 | 6:05 | 1.7436 | 5.6124 |  | 10
2017-07-09 | 6:10 | 1.7639 | 5.7019 |  | 10
2017-07-09 | 6:15 | 1.7624 | 5.8906 | 1 | 10 | 61.5675 | 74.3437
2017-07-09 | 6:20 | 1.7452 | 5.7188 |  | 10
2017-07-09 | 6:25 | 1.7694 | 5.7984 |  | 10
2017-07-09 | 6:30 | 1.7694 | 5.664 | 1 | 10 | 59.5482 | 74.1502
2017-07-09 | 6:35 | 1.7748 | 5.626 |  | 10
2017-07-09 | 6:40 | 1.7756 | 5.6739 |  | 10
2017-07-09 | 6:45 | 1.7171 | 5.5837 | 1 | 10 | 58.6069 | 73.7946
2017-07-09 | 6:50 | 1.7811 | 5.5414 |  | 10
2017-07-09 | 6:55 | 1.7725 | 5.1771 |  | 10
2017-07-09 | 7:00 | 1.7538 | 5.1022 | 1 | 10 | 53.8249 | 73.1327
2017-07-09 | 7:05 | 1.785 | 5.1824 |  | 10
2017-07-09 | 7:10 | 1.7444 | 4.9047 |  | 10
2017-07-09 | 7:15 | 1.7764 | 4.9708 | 1 | 10 | 52.608 | 72.819
2017-07-09 | 7:20 | 1.76 | 4.7882 |  | 10
2017-07-09 | 7:25 | 1.7429 | 4.6001 |  | 10
2017-07-09 | 7:30 | 1.7709 | 4.4121 | 1 | 10 | 47.1957 | 72.6467
2017-07-09 | 7:35 | 1.7413 | 4.333 |  | 10
2017-07-09 | 7:40 | 1.7483 | 4.2006 |  | 10
2017-07-09 | 7:45 | 1.7514 | 4.147 | 1 | 10 | 44.6138 | 72.6046
2017-07-09 | 7:50 | 1.7577 | 4.1971 |  | 10
2017-07-09 | 7:55 | 1.7351 | 4.1728 |  | 10
2017-07-09 | 8:00 | 1.7561 | 4.206 | 1 | 10 | 45.1782 | 72.5997
2017-07-09 | 8:05 | 1.7678 | 4.3381 |  | 10
2017-07-09 | 8:10 | 1.7507 | 4.4224 |  | 10
2017-07-09 | 8:15 | 1.7475 | 4.4449 | 1 | 10 | 47.5782 | 72.6705
2017-07-09 | 8:20 | 1.7655 | 4.3672 |  | 10
2017-07-09 | 8:25 | 1.7491 | 4.5346 |  | 10
2017-07-09 | 8:30 | 1.7483 | 4.4389 | 1 | 10 | 47.5276 | 72.7416
2017-07-09 | 8:35 | 1.7452 | 4.28 |  | 10
2017-07-09 | 8:40 | 1.7538 | 4.3466 |  | 10
2017-07-09 | 8:45 | 1.7218 | 4.4103 | 1 | 10 | 47.0373 | 72.7912
2017-07-09 | 8:50 | 1.7694 | 4.4793 |  | 10
2017-07-09 | 8:55 | 1.7452 | 4.4987 |  | 10
2017-07-09 | 9:00 | 1.65 | 2.7399 | 0 | 1.5 | 32.0079 | 74.3536
2017-07-09 | 9:05 | 1.7413 | 1.8221 |  | 1.5
2017-07-09 | 9:10 | 1.7093 | 0.85763 |  | 1.5
2017-07-09 | 9:15 | 1.7273 | 0.00453 | 0 | 1.5 | 25 | 75.2069
2017-07-09 | 9:20 | 1.7444 | 0 |  | 1.5
2017-07-09 | 9:25 | 1.753 | 0 |  | 1.5
2017-07-09 | 9:30 | 1.7577 | 0 | 0 | 1.5 | 25 | 75.624
2017-07-09 | 9:35 | 1.7202 | 0 |  | 1.5
2017-07-09 | 9:40 | 1.7226 | 0 |  | 1.5
2017-07-09 | 9:45 | 1.753 | 0 | 0 | 1.5 | 25 | 75.8658
2017-07-09 | 9:50 | 1.7647 | 0 |  | 1.5
2017-07-09 | 9:55 | 1.7608 | 0 |  | 1.5
2017-07-09 | 10:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 75.6678
2017-07-09 | 10:05 | 1.7296 | 0 |  | 1.5
2017-07-09 | 10:10 | 1.7616 | 0 |  | 1.5
2017-07-09 | 10:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 75.6603
2017-07-09 | 10:20 | 1.7585 | 0 |  | 1.5
2017-07-09 | 10:25 | 1.7655 | 0 |  | 1.5
2017-07-09 | 10:30 | 1.753 | 0 | 0 | 1.5 | 25 | 75.5631
2017-07-09 | 10:35 | 1.7335 | 0 |  | 1.5
2017-07-09 | 10:40 | 1.7631 | 0 |  | 1.5
2017-07-09 | 10:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 75.5225
2017-07-09 | 10:50 | 1.7335 | 0 |  | 1.5
2017-07-09 | 10:55 | 1.7608 | 0 |  | 1.5
2017-07-09 | 11:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 75.5908
2017-07-09 | 11:05 | 1.7312 | 0 |  | 1.5
2017-07-09 | 11:10 | 1.7585 | 0 |  | 1.5
2017-07-09 | 11:15 | 1.76 | 0 | 0 | 1.5 | 25 | 75.6562
2017-07-09 | 11:20 | 1.7499 | 0 |  | 1.5
2017-07-09 | 11:25 | 1.739 | 0 |  | 1.5
2017-07-09 | 11:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 75.8976
2017-07-09 | 11:35 | 1.7491 | 0 |  | 1.5
2017-07-09 | 11:40 | 1.7319 | 0 |  | 1.5
2017-07-09 | 11:45 | 1.7358 | 0 | 0 | 1.5 | 25 | 76.2798
2017-07-09 | 11:50 | 1.7101 | 0 |  | 1.5
2017-07-09 | 11:55 | 1.7054 | 0 |  | 1.5
2017-07-09 | 12:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 77.065
2017-07-09 | 12:05 | 1.7343 | 0 |  | 1.5
2017-07-09 | 12:10 | 1.7085 | 0 |  | 1.5
2017-07-09 | 12:15 | 1.753 | 0 | 0 | 1.5 | 25 | 77.7835
2017-07-09 | 12:20 | 1.714 | 0 |  | 1.5
2017-07-09 | 12:25 | 1.7109 | 0 |  | 1.5
2017-07-09 | 12:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 78.4706
2017-07-09 | 12:35 | 1.7109 | 0 |  | 1.5
2017-07-09 | 12:40 | 1.7 | 0 |  | 1.5
2017-07-09 | 12:45 | 1.728 | 0 | 0 | 1.5 | 25 | 79.3834
2017-07-09 | 12:50 | 1.7156 | 0 |  | 1.5
2017-07-09 | 12:55 | 1.7078 | 0 |  | 1.5
2017-07-09 | 13:00 | 1.7296 | 0 | 0 | 1.5 | 25 | 80.2613
2017-07-09 | 13:05 | 1.7179 | 0 |  | 1.5
2017-07-09 | 13:10 | 1.7046 | 0 |  | 1.5
2017-07-09 | 13:15 | 1.7117 | 0 | 0 | 1.5 | 25 | 81.1679
2017-07-09 | 13:20 | 1.7351 | 0 |  | 1.5
2017-07-09 | 13:25 | 1.7031 | 0 |  | 1.5
2017-07-09 | 13:30 | 1.7234 | 0 | 0 | 1.5 | 25 | 81.7413
2017-07-09 | 13:35 | 1.7273 | 0 |  | 1.5
2017-07-09 | 13:40 | 1.7343 | 0 |  | 1.5
2017-07-09 | 13:45 | 1.6828 | 0 | 0 | 1.5 | 25 | 82.5193
2017-07-09 | 13:50 | 1.7015 | 0 |  | 1.5
2017-07-09 | 13:55 | 1.6968 | 0 |  | 1.5
2017-07-09 | 14:00 | 1.707 | 0 | 0 | 1.5 | 25 | 83.8387
2017-07-09 | 14:05 | 1.7366 | 0 |  | 1.5
2017-07-09 | 14:10 | 1.7616 | 0 |  | 1.5
2017-07-09 | 14:15 | 1.7834 | 0 | 0 | 1.5 | 25 | 83.5774
2017-07-09 | 14:20 | 1.7865 | 0 |  | 1.5
2017-07-09 | 14:25 | 1.7639 | 0 |  | 1.5
2017-07-09 | 14:30 | 1.7538 | 0 | 0 | 1.5 | 25 | 82.9395
2017-07-09 | 14:35 | 1.7514 | 0 |  | 1.5
2017-07-09 | 14:40 | 1.7826 | 0 |  | 1.5
2017-07-09 | 14:45 | 1.7608 | 0 | 0 | 1.5 | 25 | 82.6143
2017-07-09 | 14:50 | 1.7702 | 0 |  | 1.5
2017-07-09 | 14:55 | 1.7702 | 0 |  | 1.5
2017-07-09 | 15:00 | 1.7803 | 0 | 0 | 1.5 | 25 | 82.1904
2017-07-09 | 15:05 | 1.7694 | 0 |  | 1.5
2017-07-09 | 15:10 | 1.7507 | 0 |  | 1.5
2017-07-09 | 15:15 | 1.7608 | 0 | 0 | 1.5 | 25 | 81.6435
2017-07-09 | 15:20 | 1.7881 | 0 |  | 1.5
2017-07-09 | 15:25 | 1.7834 | 0 |  | 1.5
2017-07-09 | 15:30 | 1.7834 | 0 | 0 | 1.5 | 25 | 80.957
2017-07-09 | 15:35 | 1.7897 | 0 |  | 1.5
2017-07-09 | 15:40 | 1.7717 | 0 |  | 1.5
2017-07-09 | 15:45 | 1.7943 | 0 | 0 | 1.5 | 25 | 80.028
2017-07-09 | 15:50 | 1.7585 | 0 |  | 1.5
2017-07-09 | 15:55 | 1.7943 | 0 |  | 1.5
2017-07-09 | 16:00 | 1.7647 | 0 | 0 | 1.5 | 25 | 79.4932
2017-07-09 | 16:05 | 1.8014 | 0 |  | 1.5
2017-07-09 | 16:10 | 1.7561 | 0 |  | 1.5
2017-07-09 | 16:15 | 1.7959 | 0 | 0 | 1.5 | 25 | 78.9323
2017-07-09 | 16:20 | 1.753 | 0 |  | 1.5
2017-07-09 | 16:25 | 1.7733 | 0 |  | 1.5
2017-07-09 | 16:30 | 1.7569 | 0 | 0 | 1.5 | 25 | 78.4522
2017-07-09 | 16:35 | 1.7756 | 0 |  | 1.5
2017-07-09 | 16:40 | 1.7514 | 0 |  | 1.5
2017-07-09 | 16:45 | 1.7569 | 0 | 0 | 1.5 | 25 | 77.9611
2017-07-09 | 16:50 | 1.7858 | 0 |  | 1.5
2017-07-09 | 16:55 | 1.7889 | 0 |  | 1.5
2017-07-09 | 17:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 77.4838
2017-07-09 | 17:05 | 1.7351 | 0 |  | 1.5
2017-07-09 | 17:10 | 1.7928 | 0 |  | 1.5
2017-07-09 | 17:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 77.0782
2017-07-09 | 17:20 | 1.7382 | 0 |  | 1.5
2017-07-09 | 17:25 | 1.7811 | 0 |  | 1.5
2017-07-09 | 17:30 | 1.7663 | 0 | 0 | 1.5 | 25 | 76.5658
2017-07-09 | 17:35 | 1.7678 | 0 |  | 1.5
2017-07-09 | 17:40 | 1.7374 | 0 |  | 1.5
2017-07-09 | 17:45 | 1.76 | 0 | 0 | 1.5 | 25 | 76.3698
2017-07-09 | 17:50 | 1.7358 | 0 |  | 1.5
2017-07-09 | 17:55 | 1.7553 | 0 |  | 1.5
2017-07-09 | 18:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 76.5454
2017-07-09 | 18:05 | 1.753 | 0 |  | 1.5
2017-07-09 | 18:10 | 1.7468 | 0 |  | 1.5
2017-07-09 | 18:15 | 1.7546 | 0 | 0 | 1.5 | 25 | 76.7263
2017-07-09 | 18:20 | 1.7382 | 0 |  | 1.5
2017-07-09 | 18:25 | 1.7343 | 0 |  | 1.5
2017-07-09 | 18:30 | 1.746 | 0 | 0 | 1.5 | 25 | 76.8584
2017-07-09 | 18:35 | 1.7717 | 0 |  | 1.5
2017-07-09 | 18:40 | 1.7702 | 0 |  | 1.5
2017-07-09 | 18:45 | 1.7241 | 0 | 0 | 1.5 | 25 | 76.8072
2017-07-09 | 18:50 | 1.7413 | 0 |  | 1.5
2017-07-09 | 18:55 | 1.7507 | 0 |  | 1.5
2017-07-09 | 19:00 | 1.7631 | 0 | 0 | 1.5 | 25 | 76.7215
2017-07-09 | 19:05 | 1.7585 | 0 |  | 1.5
2017-07-09 | 19:10 | 1.7553 | 0 |  | 1.5
2017-07-09 | 19:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 76.6693
2017-07-09 | 19:20 | 1.753 | 0 |  | 1.5
2017-07-09 | 19:25 | 1.7585 | 0 |  | 1.5
2017-07-09 | 19:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 76.6127
2017-07-09 | 19:35 | 1.7312 | 0 |  | 1.5
2017-07-09 | 19:40 | 1.7709 | 0 |  | 1.5
2017-07-09 | 19:45 | 1.7468 | 0 | 0 | 1.5 | 25 | 76.6392
2017-07-09 | 19:50 | 1.7546 | 0 |  | 1.5
2017-07-09 | 19:55 | 1.7499 | 0 |  | 1.5
2017-07-09 | 20:00 | 1.7585 | 0 | 0 | 1.5 | 25 | 76.5907
2017-07-09 | 20:05 | 1.767 | 0 |  | 1.5
2017-07-09 | 20:10 | 1.7538 | 0 |  | 1.5
2017-07-09 | 20:15 | 1.7226 | 0 | 0 | 1.5 | 25 | 76.7064
2017-07-09 | 20:20 | 1.7522 | 0 |  | 1.5
2017-07-09 | 20:25 | 1.7569 | 0 |  | 1.5
2017-07-09 | 20:30 | 1.7382 | 0 | 0 | 1.5 | 25 | 76.6651
2017-07-09 | 20:35 | 1.7343 | 0 |  | 1.5
2017-07-09 | 20:40 | 1.7561 | 0 |  | 1.5
2017-07-09 | 20:45 | 1.7475 | 0 | 0 | 1.5 | 25 | 76.5127
2017-07-09 | 20:50 | 1.7834 | 0 |  | 1.5
2017-07-09 | 20:55 | 1.7483 | 0 |  | 1.5
2017-07-09 | 21:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 76.2299
2017-07-09 | 21:05 | -0.10652 | 0 |  | 1.5
2017-07-09 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-09 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 21:20 | -0.1073 | 0 |  | 1.5
2017-07-09 | 21:25 | -0.1073 | 0 |  | 1.5
2017-07-09 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 21:35 | -0.1073 | 0 |  | 1.5
2017-07-09 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-09 | 21:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-09 | 21:55 | -0.1073 | 0 |  | 1.5
2017-07-09 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 22:05 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:10 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 22:20 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:25 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 22:35 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:40 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 22:50 | -0.10808 | 0 |  | 1.5
2017-07-09 | 22:55 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 23:05 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:10 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 23:20 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:25 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 23:35 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:40 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-09 | 23:50 | -0.10808 | 0 |  | 1.5
2017-07-09 | 23:55 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 0:05 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:10 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 0:20 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:25 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 0:35 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:40 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 0:50 | -0.10808 | 0 |  | 1.5
2017-07-10 | 0:55 | -0.10808 | 0 |  | 1.5
2017-07-10 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 1:05 | -0.10808 | 0 |  | 1.5
2017-07-10 | 1:10 | -0.10808 | 0 |  | 1.5
2017-07-10 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 1:20 | -0.11198 | 0 |  | 1.5
2017-07-10 | 1:25 | -0.1112 | 0 |  | 1.5
2017-07-10 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 1:35 | -0.1112 | 0 |  | 1.5
2017-07-10 | 1:40 | -0.1112 | 0 |  | 1.5
2017-07-10 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 1:50 | -0.1112 | 0 |  | 1.5
2017-07-10 | 1:55 | -0.1112 | 0 |  | 1.5
2017-07-10 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-10 | 2:10 | -0.1112 | 0 |  | 1.5
2017-07-10 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-10 | 2:25 | -0.1112 | 0 |  | 1.5
2017-07-10 | 2:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 2:35 | -0.1112 | 0 |  | 1.5
2017-07-10 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-10 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-10 | 2:55 | -0.1112 | 0 |  | 1.5
2017-07-10 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-10 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-10 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 3:20 | -0.1112 | 0 |  | 1.5
2017-07-10 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-10 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-10 | 3:40 | -0.1112 | 0 |  | 1.5
2017-07-10 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 3:50 | -0.1112 | 0 |  | 1.5
2017-07-10 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-10 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-10 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-10 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-10 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-10 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-10 | 4:40 | -0.1112 | 0 |  | 1.5
2017-07-10 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 4:50 | -0.1112 | 0 |  | 1.5
2017-07-10 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-10 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 5:05 | 2.4729 | 5.2831 |  | 10
2017-07-10 | 5:10 | 2.2148 | 9.8659 |  | 10
2017-07-10 | 5:15 | 2.2062 | 9.1549 | 1 | 10 | 93.8304 | 86.0725
2017-07-10 | 5:20 | 2.104 | 8.0845 |  | 10
2017-07-10 | 5:25 | 2.0159 | 7.1369 |  | 10
2017-07-10 | 5:30 | 1.9012 | 6.5608 | 1 | 10 | 68.388 | 77.916
2017-07-10 | 5:35 | 1.8856 | 5.9368 |  | 10
2017-07-10 | 5:40 | 1.87 | 5.7042 |  | 10
2017-07-10 | 5:45 | 1.8255 | 5.4018 | 1 | 10 | 57.025 | 74.9558
2017-07-10 | 5:50 | 1.7858 | 5.0566 |  | 10
2017-07-10 | 5:55 | 1.7663 | 4.8924 |  | 10
2017-07-10 | 6:00 | 1.7756 | 4.4462 | 1 | 10 | 47.6622 | 73.7961
2017-07-10 | 6:05 | 1.7655 | 4.785 |  | 10
2017-07-10 | 6:10 | 1.7561 | 5.2154 |  | 10
2017-07-10 | 6:15 | 1.7343 | 5.2527 | 1 | 10 | 55.1885 | 73.4396
2017-07-10 | 6:20 | 1.7468 | 5.3613 |  | 10
2017-07-10 | 6:25 | 1.7405 | 5.2316 |  | 10
2017-07-10 | 6:30 | 1.7928 | 5.3883 | 1 | 10 | 56.4731 | 73.259
2017-07-10 | 6:35 | 1.7858 | 5.3853 |  | 10
2017-07-10 | 6:40 | 1.767 | 5.1109 |  | 10
2017-07-10 | 6:45 | 1.7865 | 5.1378 | 1 | 10 | 54.3198 | 72.7614
2017-07-10 | 6:50 | 1.5323 | 4.143 |  | 1.5
2017-07-10 | 6:55 | 1.8287 | 3.014 |  | 10
2017-07-10 | 7:00 | 1.7686 | 3.27 | 0 | 1.5 | 35.5971 | 72.8321
2017-07-10 | 7:05 | 1.7959 | 2.7766 |  | 10
2017-07-10 | 7:10 | 1.767 | 3.7717 |  | 10
2017-07-10 | 7:15 | 1.7819 | 4.2272 | 1 | 10 | 45.2812 | 72.2726
2017-07-10 | 7:20 | 1.7748 | 4.5529 |  | 10
2017-07-10 | 7:25 | 1.7655 | 4.3906 |  | 10
2017-07-10 | 7:30 | 1.7733 | 4.5046 | 1 | 10 | 47.7802 | 71.8005
2017-07-10 | 7:35 | 1.7748 | 4.3016 |  | 10
2017-07-10 | 7:40 | 1.767 | 3.9772 |  | 10
2017-07-10 | 7:45 | 1.7561 | 3.992 | 1 | 10 | 43.1061 | 71.5955
2017-07-10 | 7:50 | 1.7616 | 3.489 |  | 10
2017-07-10 | 7:55 | 1.7444 | 2.9601 |  | 10
2017-07-10 | 8:00 | 1.7475 | 2.135 | 1 | 10 | 25.6233 | 71.6286
2017-07-10 | 8:05 | 1.721 | 2.1458 |  | 10
2017-07-10 | 8:10 | 1.7124 | 2.2464 |  | 10
2017-07-10 | 8:15 | 1.7202 | 2.1573 | 1 | 10 | 26.3538 | 72.248
2017-07-10 | 8:20 | 1.7444 | 2.1841 |  | 10
2017-07-10 | 8:25 | 1.7616 | 1.9439 |  | 10
2017-07-10 | 8:30 | 1.7148 | 1.4715 | 1 | 10 | 25.8625 | 72.5393
2017-07-10 | 8:35 | 1.7351 | 1.123 |  | 10
2017-07-10 | 8:40 | 1.7343 | 0.61874 |  | 10
2017-07-10 | 8:45 | 1.7429 | 0.79277 | 1 | 10 | 28.8882 | 72.9357
2017-07-10 | 8:50 | 1.7366 | 1.1244 |  | 10
2017-07-10 | 8:55 | 1.7429 | 1.2374 |  | 10
2017-07-10 | 9:00 | 1.5908 | 0.25569 | 0 | 1.5 | 25 | 73.693
2017-07-10 | 9:05 | 1.7608 | 0.38361 |  | 10
2017-07-10 | 9:10 | 1.7881 | 0.64568 |  | 10
2017-07-10 | 9:15 | 1.7374 | 1.0712 | 1 | 10 | 33.439 | 73.417
2017-07-10 | 9:20 | 1.7507 | 1.8415 |  | 10
2017-07-10 | 9:25 | 1.785 | 2.2075 |  | 10
2017-07-10 | 9:30 | 1.7397 | 2.7816 | 1 | 10 | 50.749 | 73.272
2017-07-10 | 9:35 | 1.7335 | 3.2569 |  | 10
2017-07-10 | 9:40 | 1.7202 | 3.1405 |  | 10
2017-07-10 | 9:45 | 1.505 | 2.7145 | 0 | 1.5 | 51.3679 | 74.6517
2017-07-10 | 9:50 | 1.6571 | 0.76494 |  | 1.5
2017-07-10 | 9:55 | 1.6875 | 0 |  | 1.5
2017-07-10 | 10:00 | 1.7202 | 0 | 0 | 1.5 | 25 | 76.7132
2017-07-10 | 10:05 | 1.8341 | 0.4731 |  | 10
2017-07-10 | 10:10 | 1.7889 | 1.9469 |  | 10
2017-07-10 | 10:15 | 1.5057 | 1.5218 | 0 | 1.5 | 41.1245 | 75.7089
2017-07-10 | 10:20 | 1.6399 | 0.10542 |  | 1.5
2017-07-10 | 10:25 | 1.7093 | 0 |  | 1.5
2017-07-10 | 10:30 | 1.746 | 0 | 0 | 1.5 | 25 | 77.8151
2017-07-10 | 10:35 | 1.7163 | 0 |  | 1.5
2017-07-10 | 10:40 | 1.7522 | 0 |  | 1.5
2017-07-10 | 10:45 | 1.7156 | 0 | 0 | 1.5 | 25 | 78.5744
2017-07-10 | 10:50 | 1.7249 | 0 |  | 1.5
2017-07-10 | 10:55 | 1.7109 | 0 |  | 1.5
2017-07-10 | 11:00 | 1.7397 | 0 | 0 | 1.5 | 25 | 79.5894
2017-07-10 | 11:05 | 1.7078 | 0 |  | 1.5
2017-07-10 | 11:10 | 1.7171 | 0 |  | 1.5
2017-07-10 | 11:15 | 1.7327 | 0 | 0 | 1.5 | 25 | 80.3326
2017-07-10 | 11:20 | 1.7592 | 0 |  | 1.5
2017-07-10 | 11:25 | 1.7553 | 0 |  | 1.5
2017-07-10 | 11:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 80.9843
2017-07-10 | 11:35 | 1.7491 | 0 |  | 1.5
2017-07-10 | 11:40 | 1.7039 | 0 |  | 1.5
2017-07-10 | 11:45 | 1.7382 | 0 | 0 | 1.5 | 25 | 81.1553
2017-07-10 | 11:50 | 1.7132 | 0 |  | 1.5
2017-07-10 | 11:55 | 1.7171 | 0 |  | 1.5
2017-07-10 | 12:00 | 1.6968 | 0 | 0 | 1.5 | 25 | 82.1476
2017-07-10 | 12:05 | 1.6758 | 0 |  | 1.5
2017-07-10 | 12:10 | 1.675 | 0 |  | 1.5
2017-07-10 | 12:15 | 1.7312 | 0 | 0 | 1.5 | 25 | 83.673
2017-07-10 | 12:20 | 1.7304 | 0 |  | 1.5
2017-07-10 | 12:25 | 1.7288 | 0 |  | 1.5
2017-07-10 | 12:30 | 1.7273 | 0 | 0 | 1.5 | 25 | 84.1011
2017-07-10 | 12:35 | 1.7405 | 0 |  | 1.5
2017-07-10 | 12:40 | 1.753 | 0 |  | 1.5
2017-07-10 | 12:45 | 1.7686 | 0 | 0 | 1.5 | 25 | 84.106
2017-07-10 | 12:50 | 1.7928 | 0 |  | 1.5
2017-07-10 | 12:55 | 1.7319 | 0 |  | 1.5
2017-07-10 | 13:00 | 1.7374 | 0 | 0 | 1.5 | 25 | 84.1876
2017-07-10 | 13:05 | 1.6867 | 0 |  | 1.5
2017-07-10 | 13:10 | 1.6961 | 0 |  | 1.5
2017-07-10 | 13:15 | 1.6898 | 0 | 0 | 1.5 | 25 | 85.685
2017-07-10 | 13:20 | 1.6797 | 0 |  | 1.5
2017-07-10 | 13:25 | 1.7101 | 0 |  | 1.5
2017-07-10 | 13:30 | 1.6961 | 0 | 0 | 1.5 | 25 | 87.1818
2017-07-10 | 13:35 | 1.7101 | 0 |  | 1.5
2017-07-10 | 13:40 | 1.7358 | 0 |  | 1.5
2017-07-10 | 13:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 88.1145
2017-07-10 | 13:50 | 1.8107 | 0 |  | 1.5
2017-07-10 | 13:55 | 1.8661 | 0 |  | 1.5
2017-07-10 | 14:00 | 1.8006 | 0 | 0 | 1.5 | 25 | 86.1827
2017-07-10 | 14:05 | 1.7881 | 0 |  | 1.5
2017-07-10 | 14:10 | 1.7772 | 0 |  | 1.5
2017-07-10 | 14:15 | 1.7803 | 0 | 0 | 1.5 | 25 | 84.6806
2017-07-10 | 14:20 | 1.6898 | 0 |  | 1.5
2017-07-10 | 14:25 | 1.7592 | 0 |  | 1.5
2017-07-10 | 14:30 | 1.7569 | 0 | 0 | 1.5 | 25 | 85.0827
2017-07-10 | 14:35 | 1.7787 | 0 |  | 1.5
2017-07-10 | 14:40 | 1.7748 | 0 |  | 1.5
2017-07-10 | 14:45 | 1.746 | 0 | 0 | 1.5 | 25 | 84.5257
2017-07-10 | 14:50 | 1.7577 | 0 |  | 1.5
2017-07-10 | 14:55 | 1.7616 | 0 |  | 1.5
2017-07-10 | 15:00 | 1.7694 | 0 | 0 | 1.5 | 25 | 84.0516
2017-07-10 | 15:05 | 1.7553 | 0 |  | 1.5
2017-07-10 | 15:10 | 1.8146 | 0 |  | 1.5
2017-07-10 | 15:15 | 1.7873 | 0 | 0 | 1.5 | 25 | 83.0875
2017-07-10 | 15:20 | 1.7358 | 0 |  | 1.5
2017-07-10 | 15:25 | 1.7959 | 0 |  | 1.5
2017-07-10 | 15:30 | 1.7655 | 0.047304 | 0 | 1.5 | 25.1955 | 82.4715
2017-07-10 | 15:35 | 1.7655 | 0 |  | 1.5
2017-07-10 | 15:40 | 1.7702 | 0 |  | 1.5
2017-07-10 | 15:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 82.22
2017-07-10 | 15:50 | 1.7358 | 0 |  | 1.5
2017-07-10 | 15:55 | 1.7748 | 0 |  | 1.5
2017-07-10 | 16:00 | 1.7421 | 0 | 0 | 1.5 | 25 | 81.6717
2017-07-10 | 16:05 | 1.7639 | 0 |  | 1.5
2017-07-10 | 16:10 | 1.767 | 0 |  | 1.5
2017-07-10 | 16:15 | 1.7826 | 0 | 0 | 1.5 | 25 | 81.3358
2017-07-10 | 16:20 | 1.7663 | 0 |  | 1.5
2017-07-10 | 16:25 | 1.7608 | 0 |  | 1.5
2017-07-10 | 16:30 | 1.7327 | 0 | 0 | 1.5 | 25 | 80.8832
2017-07-10 | 16:35 | 1.7429 | 0 |  | 1.5
2017-07-10 | 16:40 | 1.7897 | 0 |  | 1.5
2017-07-10 | 16:45 | 1.7873 | 0 | 0 | 1.5 | 25 | 80.135
2017-07-10 | 16:50 | 1.7764 | 0 |  | 1.5
2017-07-10 | 16:55 | 1.7475 | 0 |  | 1.5
2017-07-10 | 17:00 | 1.746 | 0 | 0 | 1.5 | 25 | 79.6393
2017-07-10 | 17:05 | 1.7421 | 0 |  | 1.5
2017-07-10 | 17:10 | 1.7499 | 0 |  | 1.5
2017-07-10 | 17:15 | 1.7577 | 0 | 0 | 1.5 | 25 | 79.8195
2017-07-10 | 17:20 | 1.7327 | 0 |  | 1.5
2017-07-10 | 17:25 | 1.7312 | 0 |  | 1.5
2017-07-10 | 17:30 | 1.753 | 0 | 0 | 1.5 | 25 | 79.7806
2017-07-10 | 17:35 | 1.7538 | 0 |  | 1.5
2017-07-10 | 17:40 | 1.7764 | 0 |  | 1.5
2017-07-10 | 17:45 | 1.7795 | 0 | 0 | 1.5 | 25 | 79.4217
2017-07-10 | 17:50 | 1.7608 | 0 |  | 1.5
2017-07-10 | 17:55 | 1.7585 | 0 |  | 1.5
2017-07-10 | 18:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 78.9976
2017-07-10 | 18:05 | 1.7616 | 0 |  | 1.5
2017-07-10 | 18:10 | 1.739 | 0 |  | 1.5
2017-07-10 | 18:15 | 1.7522 | 0 | 0 | 1.5 | 25 | 78.6794
2017-07-10 | 18:20 | 1.7881 | 0 |  | 1.5
2017-07-10 | 18:25 | 1.7553 | 0 |  | 1.5
2017-07-10 | 18:30 | 1.7538 | 0 | 0 | 1.5 | 25 | 78.3408
2017-07-10 | 18:35 | 1.7733 | 0 |  | 1.5
2017-07-10 | 18:40 | 1.767 | 0 |  | 1.5
2017-07-10 | 18:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 77.9363
2017-07-10 | 18:50 | 1.767 | 0 |  | 1.5
2017-07-10 | 18:55 | 1.7624 | 0 |  | 1.5
2017-07-10 | 19:00 | 1.739 | 0 | 0 | 1.5 | 25 | 77.6199
2017-07-10 | 19:05 | 1.721 | 0 |  | 1.5
2017-07-10 | 19:10 | 1.7538 | 0 |  | 1.5
2017-07-10 | 19:15 | 1.7366 | 0 | 0 | 1.5 | 25 | 77.4808
2017-07-10 | 19:20 | 1.7709 | 0 |  | 1.5
2017-07-10 | 19:25 | 1.7475 | 0 |  | 1.5
2017-07-10 | 19:30 | 1.7647 | 0 | 0 | 1.5 | 25 | 77.0309
2017-07-10 | 19:35 | 1.7873 | 0.11117 |  | 1.5
2017-07-10 | 19:40 | 1.7553 | 0 |  | 1.5
2017-07-10 | 19:45 | 1.7725 | 0 | 0 | 1.5 | 25 | 76.5767
2017-07-10 | 19:50 | 1.76 | 0 |  | 1.5
2017-07-10 | 19:55 | 1.7546 | 0 |  | 1.5
2017-07-10 | 20:00 | 1.753 | 0 | 0 | 1.5 | 25 | 76.3356
2017-07-10 | 20:05 | 1.767 | 0 |  | 1.5
2017-07-10 | 20:10 | 1.7873 | 0 |  | 1.5
2017-07-10 | 20:15 | 1.7709 | 0 | 0 | 1.5 | 25 | 76.1377
2017-07-10 | 20:20 | 1.7499 | 0 |  | 1.5
2017-07-10 | 20:25 | 1.7405 | 0 |  | 1.5
2017-07-10 | 20:30 | 1.7569 | 0 | 0 | 1.5 | 25 | 76.0017
2017-07-10 | 20:35 | 1.7296 | 0 |  | 1.5
2017-07-10 | 20:40 | 1.7405 | 0 |  | 1.5
2017-07-10 | 20:45 | 1.7483 | 0.48018 | 0 | 1.5 | 28.7654 | 75.7721
2017-07-10 | 20:50 | 1.7468 | 1.2872 |  | 1.5
2017-07-10 | 20:55 | 1.728 | 1.2119 |  | 1.5
2017-07-10 | 21:00 | 1.7803 | 0.46393 | 0 | 1.5 | 29.432 | 75.751
2017-07-10 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-10 | 21:10 | -0.1034 | 0 |  | 1.5
2017-07-10 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-10 | 21:25 | -0.10652 | 0 |  | 1.5
2017-07-10 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-10 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-10 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-10 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 22:20 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:25 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:40 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-10 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-10 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-10 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-10 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 23:20 | -0.10964 | 0 |  | 1.5
2017-07-10 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-10 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 23:35 | -0.10652 | 0 |  | 1.5
2017-07-10 | 23:40 | -0.10652 | 0 |  | 1.5
2017-07-10 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-10 | 23:50 | -0.10652 | 0 |  | 1.5
2017-07-10 | 23:55 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 0:05 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:10 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 0:20 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:25 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 0:35 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:40 | -0.10574 | 0 |  | 1.5
2017-07-11 | 0:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 0:50 | -0.10652 | 0 |  | 1.5
2017-07-11 | 0:55 | -0.10652 | 0 |  | 1.5
2017-07-11 | 1:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 1:05 | -0.10652 | 0 |  | 1.5
2017-07-11 | 1:10 | -0.10652 | 0 |  | 1.5
2017-07-11 | 1:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 1:20 | -0.10964 | 0 |  | 1.5
2017-07-11 | 1:25 | -0.10964 | 0 |  | 1.5
2017-07-11 | 1:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 1:35 | -0.10964 | 0 |  | 1.5
2017-07-11 | 1:40 | -0.10964 | 0 |  | 1.5
2017-07-11 | 1:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 1:50 | -0.10964 | 0 |  | 1.5
2017-07-11 | 1:55 | -0.10964 | 0 |  | 1.5
2017-07-11 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 2:05 | -0.10964 | 0 |  | 1.5
2017-07-11 | 2:10 | -0.10964 | 0 |  | 1.5
2017-07-11 | 2:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 2:20 | -0.10964 | 0 |  | 1.5
2017-07-11 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-11 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-11 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-11 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 2:50 | -0.10964 | 0 |  | 1.5
2017-07-11 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-11 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-11 | 3:10 | -0.10964 | 0 |  | 1.5
2017-07-11 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-11 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-11 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-11 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-11 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-11 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-11 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-11 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-11 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-11 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-11 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-11 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-11 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-11 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-11 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 5:05 | 2.7311 | 5.6435 |  | 10
2017-07-11 | 5:10 | 2.3045 | 9.7382 |  | 10
2017-07-11 | 5:15 | 2.1968 | 8.3817 | 1 | 10 | 86.3966 | 83.3581
2017-07-11 | 5:20 | 2.0034 | 7.5413 |  | 10
2017-07-11 | 5:25 | 1.9425 | 6.8353 |  | 10
2017-07-11 | 5:30 | 1.9035 | 6.447 | 1 | 9.0431 | 67.1155 | 77.0972
2017-07-11 | 5:35 | 1.7748 | 5.8574 |  | 8.2117
2017-07-11 | 5:40 | 1.8365 | 5.8164 |  | 9.7243
2017-07-11 | 5:45 | 1.8162 | 5.9795 | 1 | 10 | 62.4802 | 75.5088
2017-07-11 | 5:50 | 1.8076 | 5.7663 |  | 10
2017-07-11 | 5:55 | 1.7834 | 5.8288 |  | 8.616
2017-07-11 | 6:00 | 1.7195 | 5.4532 | 1 | 7.6082 | 57.4645 | 74.7238
2017-07-11 | 6:05 | 1.7702 | 5.5351 |  | 9.871
2017-07-11 | 6:10 | 1.7312 | 5.9582 |  | 7.3065
2017-07-11 | 6:15 | 1.7787 | 5.5794 | 1 | 9.6236 | 58.444 | 74.5982
2017-07-11 | 6:20 | 1.7904 | 5.7881 |  | 10
2017-07-11 | 6:25 | 1.7764 | 5.7766 |  | 10
2017-07-11 | 6:30 | 1.7631 | 5.7609 | 1 | 10 | 60.1732 | 74.0212
2017-07-11 | 6:35 | 1.7475 | 5.6576 |  | 10
2017-07-11 | 6:40 | 1.7725 | 5.3057 |  | 10
2017-07-11 | 6:45 | 1.7444 | 5.5997 | 1 | 10 | 58.6135 | 73.7498
2017-07-11 | 6:50 | 1.7413 | 5.2818 |  | 10
2017-07-11 | 6:55 | 1.7795 | 5.0563 |  | 10
2017-07-11 | 7:00 | 1.76 | 4.7288 | 1 | 10 | 50.5396 | 73.4128
2017-07-11 | 7:05 | 1.7616 | 4.9112 |  | 10
2017-07-11 | 7:10 | 1.7413 | 5.1189 |  | 10
2017-07-11 | 7:15 | 1.746 | 4.9062 | 1 | 10 | 52.2936 | 73.2322
2017-07-11 | 7:20 | 1.7709 | 4.474 |  | 10
2017-07-11 | 7:25 | 1.721 | 4.1234 |  | 10
2017-07-11 | 7:30 | 1.7819 | 3.9344 | 1 | 10 | 42.1914 | 72.6636
2017-07-11 | 7:35 | 1.7639 | 3.8911 |  | 10
2017-07-11 | 7:40 | 1.7522 | 3.8678 |  | 10
2017-07-11 | 7:45 | 1.7553 | 4.2475 | 1 | 10 | 45.6306 | 72.4347
2017-07-11 | 7:50 | 1.7577 | 3.7413 |  | 10
2017-07-11 | 7:55 | 1.7616 | 3.4447 |  | 10
2017-07-11 | 8:00 | 1.753 | 2.9994 | 1 | 10 | 33.2709 | 72.0039
2017-07-11 | 8:05 | 1.7007 | 3.1533 |  | 10
2017-07-11 | 8:10 | 1.7343 | 3.2191 |  | 10
2017-07-11 | 8:15 | 1.7577 | 3.1974 | 1 | 10 | 35.3439 | 72.4326
2017-07-11 | 8:20 | 1.7226 | 3.3515 |  | 10
2017-07-11 | 8:25 | 1.7709 | 3.1147 |  | 10
2017-07-11 | 8:30 | 1.746 | 3.1345 | 1 | 10 | 35.1147 | 72.6705
2017-07-11 | 8:35 | 1.7577 | 3.7775 |  | 10
2017-07-11 | 8:40 | 1.728 | 4.4772 |  | 10
2017-07-11 | 8:45 | 1.7405 | 4.2911 | 1 | 10 | 45.7 | 72.7922
2017-07-11 | 8:50 | 1.7421 | 3.7361 |  | 10
2017-07-11 | 8:55 | 1.7608 | 3.5291 |  | 10
2017-07-11 | 9:00 | 1.7475 | 4.2889 | 1 | 10 | 45.3194 | 72.7846
2017-07-11 | 9:05 | 1.7444 | 4.5058 |  | 10
2017-07-11 | 9:10 | 1.7265 | 4.7171 |  | 10
2017-07-11 | 9:15 | 1.7101 | 5.5091 | 1 | 10 | 56.4 | 72.995
2017-07-11 | 9:20 | 1.746 | 5.5695 |  | 10
2017-07-11 | 9:25 | 1.7202 | 5.6548 |  | 10
2017-07-11 | 9:30 | 1.7218 | 5.7186 | 1 | 10 | 59.4385 | 73.2162
2017-07-11 | 9:35 | 1.7241 | 5.4563 |  | 10
2017-07-11 | 9:40 | 1.7678 | 5.1273 |  | 10
2017-07-11 | 9:45 | 1.7241 | 5.5183 | 1 | 10 | 57.4113 | 73.3595
2017-07-11 | 9:50 | 1.7585 | 5.1069 |  | 10
2017-07-11 | 9:55 | 1.714 | 4.7274 |  | 10
2017-07-11 | 10:00 | 1.7249 | 4.5929 | 1 | 10 | 49.1007 | 73.8887
2017-07-11 | 10:05 | 1.7358 | 5.0299 |  | 10
2017-07-11 | 10:10 | 1.7639 | 4.8249 |  | 10
2017-07-11 | 10:15 | 1.7358 | 4.822 | 1 | 10 | 50.3636 | 74.0801
2017-07-11 | 10:20 | 1.7709 | 4.563 |  | 10
2017-07-11 | 10:25 | 1.746 | 5.1036 |  | 10
2017-07-11 | 10:30 | 1.7429 | 4.9326 | 1 | 10 | 52.712 | 74.2549
2017-07-11 | 10:35 | 1.7366 | 4.6956 |  | 10
2017-07-11 | 10:40 | 1.7343 | 4.5012 |  | 10
2017-07-11 | 10:45 | 1.7039 | 4.8069 | 1 | 10 | 49.9283 | 74.6885
2017-07-11 | 10:50 | 1.7374 | 4.5998 |  | 10
2017-07-11 | 10:55 | 1.739 | 4.7109 |  | 10
2017-07-11 | 11:00 | 1.6961 | 4.2492 | 1 | 10 | 45.9189 | 75.2882
2017-07-11 | 11:05 | 1.7078 | 4.2944 |  | 10
2017-07-11 | 11:10 | 1.7491 | 5.1279 |  | 10
2017-07-11 | 11:15 | 1.5174 | 4.0955 | 0 | 1.5 | 44.8038 | 77.0418
2017-07-11 | 11:20 | 1.6797 | 2.7164 |  | 1.5
2017-07-11 | 11:25 | 1.7031 | 1.7073 |  | 1.5
2017-07-11 | 11:30 | 1.7093 | 0.86948 | 0 | 1.5 | 25 | 78.7281
2017-07-11 | 11:35 | 1.7351 | 0.036849 |  | 1.5
2017-07-11 | 11:40 | 1.8131 | 0 |  | 1.5
2017-07-11 | 11:45 | 1.7655 | 0 | 0 | 1.5 | 25 | 78.7878
2017-07-11 | 11:50 | 1.7312 | 0 |  | 1.5
2017-07-11 | 11:55 | 1.7694 | 0 |  | 1.5
2017-07-11 | 12:00 | 1.753 | 0 | 0 | 1.5 | 25 | 78.5671
2017-07-11 | 12:05 | 1.746 | 0 |  | 1.5
2017-07-11 | 12:10 | 1.7366 | 0 |  | 1.5
2017-07-11 | 12:15 | 1.7483 | 0 | 0 | 1.5 | 25 | 78.549
2017-07-11 | 12:20 | 1.7631 | 0 |  | 1.5
2017-07-11 | 12:25 | 1.7421 | 0 |  | 1.5
2017-07-11 | 12:30 | 1.7273 | 0 | 0 | 1.5 | 25 | 78.8665
2017-07-11 | 12:35 | 1.6602 | 0 |  | 1.5
2017-07-11 | 12:40 | 1.7007 | 0 |  | 1.5
2017-07-11 | 12:45 | 1.7249 | 0 | 0 | 1.5 | 25 | 80.3381
2017-07-11 | 12:50 | 1.6883 | 0 |  | 1.5
2017-07-11 | 12:55 | 1.6516 | 0 |  | 1.5
2017-07-11 | 13:00 | 1.7156 | 0 | 0 | 1.5 | 25 | 82.0556
2017-07-11 | 13:05 | 1.6383 | 0 |  | 1.5
2017-07-11 | 13:10 | 1.6524 | 0 |  | 1.5
2017-07-11 | 13:15 | 1.6539 | 0 | 0 | 1.5 | 25 | 84.7874
2017-07-11 | 13:20 | 1.7218 | 0 |  | 1.5
2017-07-11 | 13:25 | 1.7335 | 0 |  | 1.5
2017-07-11 | 13:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 85.6962
2017-07-11 | 13:35 | 1.7421 | 0 |  | 1.5
2017-07-11 | 13:40 | 1.7304 | 0 |  | 1.5
2017-07-11 | 13:45 | 1.6992 | 0 | 0 | 1.5 | 25 | 86.3962
2017-07-11 | 13:50 | 1.7109 | 0 |  | 1.5
2017-07-11 | 13:55 | 1.6968 | 0 |  | 1.5
2017-07-11 | 14:00 | 1.7078 | 0 | 0 | 1.5 | 25 | 87.5965
2017-07-11 | 14:05 | 1.7577 | 0 |  | 1.5
2017-07-11 | 14:10 | 1.7382 | 0 |  | 1.5
2017-07-11 | 14:15 | 1.7553 | 0 | 0 | 1.5 | 25 | 87.866
2017-07-11 | 14:20 | 1.7678 | 0 |  | 1.5
2017-07-11 | 14:25 | 1.7756 | 0 |  | 1.5
2017-07-11 | 14:30 | 1.7943 | 0 | 0 | 1.5 | 25 | 87.2
2017-07-11 | 14:35 | 1.7585 | 0 |  | 1.5
2017-07-11 | 14:40 | 1.8193 | 0 |  | 1.5
2017-07-11 | 14:45 | 1.7764 | 0 | 0 | 1.5 | 25 | 86.2734
2017-07-11 | 14:50 | 1.7561 | 0 |  | 1.5
2017-07-11 | 14:55 | 1.7865 | 0 |  | 1.5
2017-07-11 | 15:00 | 1.7959 | 0 | 0 | 1.5 | 25 | 85.9524
2017-07-11 | 15:05 | 1.7702 | 0 |  | 1.5
2017-07-11 | 15:10 | 1.7624 | 0 |  | 1.5
2017-07-11 | 15:15 | 1.7702 | 0 | 0 | 1.5 | 25 | 85.2886
2017-07-11 | 15:20 | 1.7514 | 0 |  | 1.5
2017-07-11 | 15:25 | 1.7639 | 0 |  | 1.5
2017-07-11 | 15:30 | 1.7382 | 0 | 0 | 1.5 | 25 | 85.3132
2017-07-11 | 15:35 | 1.7499 | 0 |  | 1.5
2017-07-11 | 15:40 | 1.7421 | 0 |  | 1.5
2017-07-11 | 15:45 | 1.7335 | 0 | 0 | 1.5 | 25 | 85.3526
2017-07-11 | 15:50 | 1.7499 | 0 |  | 1.5
2017-07-11 | 15:55 | 1.7951 | 0 |  | 1.5
2017-07-11 | 16:00 | 1.7943 | 0 | 0 | 1.5 | 25 | 84.7544
2017-07-11 | 16:05 | 1.778 | 0 |  | 1.5
2017-07-11 | 16:10 | 1.7819 | 0 |  | 1.5
2017-07-11 | 16:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 83.7838
2017-07-11 | 16:20 | 1.7717 | 0 |  | 1.5
2017-07-11 | 16:25 | 1.7748 | 0 |  | 1.5
2017-07-11 | 16:30 | 1.7725 | 0 | 0 | 1.5 | 25 | 83.2824
2017-07-11 | 16:35 | 1.7842 | 0 |  | 1.5
2017-07-11 | 16:40 | 1.7904 | 0 |  | 1.5
2017-07-11 | 16:45 | 1.7889 | 0 | 0 | 1.5 | 25 | 82.2861
2017-07-11 | 16:50 | 1.7491 | 0 |  | 1.5
2017-07-11 | 16:55 | 1.7702 | 0 |  | 1.5
2017-07-11 | 17:00 | 1.785 | 0 | 0 | 1.5 | 25 | 81.5885
2017-07-11 | 17:05 | 1.7748 | 0 |  | 1.5
2017-07-11 | 17:10 | 1.7702 | 0 |  | 1.5
2017-07-11 | 17:15 | 1.7936 | 0 | 0 | 1.5 | 25 | 80.9054
2017-07-11 | 17:20 | 1.7928 | 0 |  | 1.5
2017-07-11 | 17:25 | 1.7608 | 0 |  | 1.5
2017-07-11 | 17:30 | 1.8053 | 0 | 0 | 1.5 | 25 | 79.9611
2017-07-11 | 17:35 | 1.8006 | 0 |  | 1.5
2017-07-11 | 17:40 | 1.7858 | 0 |  | 1.5
2017-07-11 | 17:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 79.0329
2017-07-11 | 17:50 | 1.7561 | 0 |  | 1.5
2017-07-11 | 17:55 | 1.7826 | 0 |  | 1.5
2017-07-11 | 18:00 | 1.7475 | 0 | 0 | 1.5 | 25 | 78.4166
2017-07-11 | 18:05 | 1.7819 | 0 |  | 1.5
2017-07-11 | 18:10 | 1.7631 | 0 |  | 1.5
2017-07-11 | 18:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 77.8948
2017-07-11 | 18:20 | 1.7335 | 0 |  | 1.5
2017-07-11 | 18:25 | 1.7514 | 0 |  | 1.5
2017-07-11 | 18:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 78.0115
2017-07-11 | 18:35 | 1.767 | 0 |  | 1.5
2017-07-11 | 18:40 | 1.76 | 0 |  | 1.5
2017-07-11 | 18:45 | 1.7468 | 0 | 0 | 1.5 | 25 | 77.7638
2017-07-11 | 18:50 | 1.7491 | 0 |  | 1.5
2017-07-11 | 18:55 | 1.7436 | 0 |  | 1.5
2017-07-11 | 19:00 | 1.7694 | 0 | 0 | 1.5 | 25 | 77.8199
2017-07-11 | 19:05 | 1.7234 | 0 |  | 1.5
2017-07-11 | 19:10 | 1.7421 | 0 |  | 1.5
2017-07-11 | 19:15 | 1.7468 | 0 | 0 | 1.5 | 25 | 78.0966
2017-07-11 | 19:20 | 1.7475 | 0 |  | 1.5
2017-07-11 | 19:25 | 1.7444 | 0 |  | 1.5
2017-07-11 | 19:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 78.065
2017-07-11 | 19:35 | 1.728 | 0 |  | 1.5
2017-07-11 | 19:40 | 1.7413 | 0 |  | 1.5
2017-07-11 | 19:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 78.6139
2017-07-11 | 19:50 | 1.7351 | 0 |  | 1.5
2017-07-11 | 19:55 | 1.7023 | 0 |  | 1.5
2017-07-11 | 20:00 | 1.7678 | 0 | 0 | 1.5 | 25 | 78.7018
2017-07-11 | 20:05 | 1.7577 | 0 |  | 1.5
2017-07-11 | 20:10 | 1.7475 | 0 |  | 1.5
2017-07-11 | 20:15 | 1.7592 | 0 | 0 | 1.5 | 25 | 78.2276
2017-07-11 | 20:20 | 1.7639 | 0 |  | 1.5
2017-07-11 | 20:25 | 1.7507 | 0 |  | 1.5
2017-07-11 | 20:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 78.0072
2017-07-11 | 20:35 | 1.7639 | 0 |  | 1.5
2017-07-11 | 20:40 | 1.7382 | 0 |  | 1.5
2017-07-11 | 20:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 77.6865
2017-07-11 | 20:50 | 1.7733 | 0 |  | 1.5
2017-07-11 | 20:55 | 1.746 | 0 |  | 1.5
2017-07-11 | 21:00 | 1.7538 | 0 | 0 | 1.5 | 25 | 77.3613
2017-07-11 | 21:05 | -0.1034 | 0 |  | 1.5
2017-07-11 | 21:10 | -0.10496 | 0 |  | 1.5
2017-07-11 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-11 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-11 | 21:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-11 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-11 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-11 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-11 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-11 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-11 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-11 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-11 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 22:35 | -0.1073 | 0 |  | 1.5
2017-07-11 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-11 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-11 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-11 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-11 | 23:10 | -0.10652 | 0 |  | 1.5
2017-07-11 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-11 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-11 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 23:35 | -0.10574 | 0 |  | 1.5
2017-07-11 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-11 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-11 | 23:50 | -0.10652 | 0 |  | 1.5
2017-07-11 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:10 | -0.10652 | 0 |  | 1.5
2017-07-12 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 0:20 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:25 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:40 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 0:50 | -0.10574 | 0 |  | 1.5
2017-07-12 | 0:55 | -0.10574 | 0 |  | 1.5
2017-07-12 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-12 | 1:10 | -0.10574 | 0 |  | 1.5
2017-07-12 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 1:20 | -0.10964 | 0 |  | 1.5
2017-07-12 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-12 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 1:35 | -0.10964 | 0 |  | 1.5
2017-07-12 | 1:40 | -0.10964 | 0 |  | 1.5
2017-07-12 | 1:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 1:50 | -0.10964 | 0 |  | 1.5
2017-07-12 | 1:55 | -0.10964 | 0 |  | 1.5
2017-07-12 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 2:05 | -0.11276 | 0 |  | 1.5
2017-07-12 | 2:10 | -0.10886 | 0 |  | 1.5
2017-07-12 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 2:20 | -0.10886 | 0 |  | 1.5
2017-07-12 | 2:25 | -0.10964 | 0 |  | 1.5
2017-07-12 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 2:35 | -0.10886 | 0 |  | 1.5
2017-07-12 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-12 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 2:50 | -0.10964 | 0 |  | 1.5
2017-07-12 | 2:55 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:10 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 3:20 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:25 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-12 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:10 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-12 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-12 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 5:05 | 2.4605 | 5.6114 |  | 10
2017-07-12 | 5:10 | 2.1836 | 9.8279 |  | 10
2017-07-12 | 5:15 | 2.0829 | 9.5795 | 1 | 10 | 97.8133 | 87.3447
2017-07-12 | 5:20 | 2.0393 | 8.6654 |  | 10
2017-07-12 | 5:25 | 1.9706 | 8.0554 |  | 10
2017-07-12 | 5:30 | 1.9051 | 7.8281 | 1 | 10 | 80.612 | 80.7728
2017-07-12 | 5:35 | 1.8708 | 7.2848 |  | 10
2017-07-12 | 5:40 | 1.8404 | 6.8761 |  | 10
2017-07-12 | 5:45 | 1.8154 | 6.6697 | 1 | 10 | 69.3882 | 78.1344
2017-07-12 | 5:50 | 1.8201 | 6.4469 |  | 10
2017-07-12 | 5:55 | 1.7694 | 6.2897 |  | 10
2017-07-12 | 6:00 | 1.7819 | 6.0408 | 1 | 10 | 63.0225 | 76.7769
2017-07-12 | 6:05 | 1.7429 | 6.6406 |  | 10
2017-07-12 | 6:10 | 1.7522 | 6.8796 |  | 10
2017-07-12 | 6:15 | 1.7678 | 7.0415 | 1 | 10 | 72.5937 | 76.4741
2017-07-12 | 6:20 | 1.7678 | 7.2774 |  | 10
2017-07-12 | 6:25 | 1.7702 | 6.9891 |  | 10
2017-07-12 | 6:30 | 1.7748 | 6.8886 | 1 | 10 | 71.3903 | 76.3873
2017-07-12 | 6:35 | 1.7647 | 6.7333 |  | 10
2017-07-12 | 6:40 | 1.7733 | 6.6944 |  | 10
2017-07-12 | 6:45 | 1.7772 | 6.6099 | 1 | 10 | 68.7833 | 76.1457
2017-07-12 | 6:50 | 1.7546 | 6.1687 |  | 10
2017-07-12 | 6:55 | 1.7686 | 6.2343 |  | 10
2017-07-12 | 7:00 | 1.7764 | 5.8094 | 1 | 10 | 61.1426 | 75.3659
2017-07-12 | 7:05 | 1.7733 | 6.0899 |  | 10
2017-07-12 | 7:10 | 1.7686 | 5.9133 |  | 10
2017-07-12 | 7:15 | 1.7514 | 5.869 | 1 | 10 | 61.3 | 75.097
2017-07-12 | 7:20 | 1.7491 | 5.5767 |  | 10
2017-07-12 | 7:25 | 1.7522 | 5.4235 |  | 10
2017-07-12 | 7:30 | 1.7655 | 5.4808 | 1 | 10 | 57.6094 | 74.8079
2017-07-12 | 7:35 | 1.753 | 5.0903 |  | 10
2017-07-12 | 7:40 | 1.7585 | 4.8989 |  | 10
2017-07-12 | 7:45 | 1.7608 | 4.9412 | 1 | 10 | 52.8222 | 74.3159
2017-07-12 | 7:50 | 1.7733 | 5.0706 |  | 10
2017-07-12 | 7:55 | 1.7553 | 5.1656 |  | 10
2017-07-12 | 8:00 | 1.7444 | 4.8304 | 1 | 10 | 51.9792 | 74.0202
2017-07-12 | 8:05 | 1.7577 | 4.9031 |  | 10
2017-07-12 | 8:10 | 1.7132 | 5.5993 |  | 10
2017-07-12 | 8:15 | 1.7686 | 5.9935 | 1 | 10 | 62.0349 | 74.2707
2017-07-12 | 8:20 | 1.7429 | 5.8962 |  | 10
2017-07-12 | 8:25 | 1.7764 | 5.5903 |  | 10
2017-07-12 | 8:30 | 1.7319 | 4.9077 | 1 | 10 | 52.2562 | 74.1963
2017-07-12 | 8:35 | 1.7436 | 5.0229 |  | 10
2017-07-12 | 8:40 | 1.7148 | 5.5531 |  | 10
2017-07-12 | 8:45 | 1.7304 | 5.2155 | 1 | 10 | 55.5042 | 74.2516
2017-07-12 | 8:50 | 1.7507 | 5.4862 |  | 10
2017-07-12 | 8:55 | 1.7351 | 5.5469 |  | 10
2017-07-12 | 9:00 | 1.7483 | 5.6799 | 1 | 10 | 59.5149 | 74.436
2017-07-12 | 9:05 | 1.7382 | 5.3818 |  | 10
2017-07-12 | 9:10 | 1.7241 | 5.6542 |  | 10
2017-07-12 | 9:15 | 1.7538 | 5.505 | 1 | 10 | 58.612 | 74.5672
2017-07-12 | 9:20 | 1.7273 | 5.5082 |  | 10
2017-07-12 | 9:25 | 1.7694 | 5.5964 |  | 10
2017-07-12 | 9:30 | 1.7522 | 5.4585 | 1 | 10 | 57.8 | 74.7877
2017-07-12 | 9:35 | 1.7499 | 4.9483 |  | 10
2017-07-12 | 9:40 | 1.7561 | 5.2536 |  | 10
2017-07-12 | 9:45 | 1.7569 | 4.9206 | 1 | 10 | 52.5044 | 74.9392
2017-07-12 | 9:50 | 1.7592 | 4.5486 |  | 10
2017-07-12 | 9:55 | 1.7358 | 4.4775 |  | 10
2017-07-12 | 10:00 | 1.5362 | 3.1991 | 1 | 10 | 36.5975 | 76.7811
2017-07-12 | 10:05 | 1.7007 | 3.6891 |  | 10
2017-07-12 | 10:10 | 1.5603 | 3.6301 |  | 1.5
2017-07-12 | 10:15 | 1.6539 | 0 | 0 | 1.5 | 25 | 78.3602
2017-07-12 | 10:20 | 1.6539 | 0 |  | 1.5
2017-07-12 | 10:25 | 1.5681 | 0 |  | 1.5
2017-07-12 | 10:30 | 1.6656 | 0 | 0 | 1.5 | 25 | 81.9543
2017-07-12 | 10:35 | 1.7109 | 0 |  | 1.5
2017-07-12 | 10:40 | 1.7288 | 0 |  | 1.5
2017-07-12 | 10:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 82.7153
2017-07-12 | 10:50 | 1.7405 | 0 |  | 1.5
2017-07-12 | 10:55 | 1.7413 | 0 |  | 1.5
2017-07-12 | 11:00 | 1.7624 | 0 | 0 | 1.5 | 25 | 82.9813
2017-07-12 | 11:05 | 1.7436 | 0 |  | 1.5
2017-07-12 | 11:10 | 1.7335 | 0 |  | 1.5
2017-07-12 | 11:15 | 1.7312 | 0 | 0 | 1.5 | 25 | 83.3195
2017-07-12 | 11:20 | 1.7499 | 0 |  | 1.5
2017-07-12 | 11:25 | 1.7702 | 0 |  | 1.5
2017-07-12 | 11:30 | 1.7226 | 0 | 0 | 1.5 | 25 | 83.6977
2017-07-12 | 11:35 | 1.7358 | 0 |  | 1.5
2017-07-12 | 11:40 | 1.7085 | 0 |  | 1.5
2017-07-12 | 11:45 | 1.7031 | 0 | 0 | 1.5 | 25 | 84.6215
2017-07-12 | 11:50 | 1.6883 | 0 |  | 1.5
2017-07-12 | 11:55 | 1.7163 | 0 |  | 1.5
2017-07-12 | 12:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 85.656
2017-07-12 | 12:05 | 1.7007 | 0 |  | 1.5
2017-07-12 | 12:10 | 1.7163 | 0 |  | 1.5
2017-07-12 | 12:15 | 1.739 | 0 | 0 | 1.5 | 25 | 86.2917
2017-07-12 | 12:20 | 1.7171 | 0 |  | 1.5
2017-07-12 | 12:25 | 1.7007 | 0 |  | 1.5
2017-07-12 | 12:30 | 1.7241 | 0 | 0 | 1.5 | 25 | 87.2674
2017-07-12 | 12:35 | 1.7787 | 0 |  | 1.5
2017-07-12 | 12:40 | 1.7078 | 0 |  | 1.5
2017-07-12 | 12:45 | 1.7507 | 0 | 0 | 1.5 | 25 | 87.3842
2017-07-12 | 12:50 | 1.778 | 0 |  | 1.5
2017-07-12 | 12:55 | 1.7195 | 0 |  | 1.5
2017-07-12 | 13:00 | 1.7499 | 0 | 0 | 1.5 | 25 | 87.3757
2017-07-12 | 13:05 | 1.7397 | 0 |  | 1.5
2017-07-12 | 13:10 | 1.7499 | 0 |  | 1.5
2017-07-12 | 13:15 | 1.7335 | 0 | 0 | 1.5 | 25 | 87.26
2017-07-12 | 13:20 | 1.739 | 0 |  | 1.5
2017-07-12 | 13:25 | 1.7616 | 0 |  | 1.5
2017-07-12 | 13:30 | 1.7475 | 0 | 0 | 1.5 | 25 | 87.7721
2017-07-12 | 13:35 | 1.7538 | 0 |  | 1.5
2017-07-12 | 13:40 | 1.7507 | 0 |  | 1.5
2017-07-12 | 13:45 | 1.8154 | 0 | 0 | 1.5 | 25 | 87.5328
2017-07-12 | 13:50 | 1.8053 | 0 |  | 1.5
2017-07-12 | 13:55 | 1.7967 | 0 |  | 1.5
2017-07-12 | 14:00 | 1.7686 | 0 | 0 | 1.5 | 25 | 86.2686
2017-07-12 | 14:05 | 1.7631 | 0 |  | 1.5
2017-07-12 | 14:10 | 1.7624 | 0 |  | 1.5
2017-07-12 | 14:15 | 1.7335 | 0 | 0 | 1.5 | 25 | 85.9545
2017-07-12 | 14:20 | 1.7468 | 0 |  | 1.5
2017-07-12 | 14:25 | 1.7491 | 0 |  | 1.5
2017-07-12 | 14:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 85.9098
2017-07-12 | 14:35 | 1.6719 | 0 |  | 1.5
2017-07-12 | 14:40 | 1.6922 | 0 |  | 1.5
2017-07-12 | 14:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 87.2183
2017-07-12 | 14:50 | 1.7335 | 0 |  | 1.5
2017-07-12 | 14:55 | 1.7156 | 0 |  | 1.5
2017-07-12 | 15:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 87.6232
2017-07-12 | 15:05 | 1.7585 | 0 |  | 1.5
2017-07-12 | 15:10 | 1.7171 | 0 |  | 1.5
2017-07-12 | 15:15 | 1.7234 | 0 | 0 | 1.5 | 25 | 87.9563
2017-07-12 | 15:20 | 1.7429 | 0 |  | 1.5
2017-07-12 | 15:25 | 1.7748 | 0 |  | 1.5
2017-07-12 | 15:30 | 1.7538 | 0 | 0 | 1.5 | 25 | 87.9144
2017-07-12 | 15:35 | 1.7842 | 0 |  | 1.5
2017-07-12 | 15:40 | 1.7967 | 0 |  | 1.5
2017-07-12 | 15:45 | 1.7826 | 0 | 0 | 1.5 | 25 | 87.1865
2017-07-12 | 15:50 | 1.7772 | 0 |  | 1.5
2017-07-12 | 15:55 | 1.7764 | 0 |  | 1.5
2017-07-12 | 16:00 | 1.7717 | 0 | 0 | 1.5 | 25 | 86.495
2017-07-12 | 16:05 | 1.7397 | 0 |  | 1.5
2017-07-12 | 16:10 | 1.76 | 0 |  | 1.5
2017-07-12 | 16:15 | 1.7475 | 0 | 0 | 1.5 | 25 | 86.2468
2017-07-12 | 16:20 | 1.7475 | 0 |  | 1.5
2017-07-12 | 16:25 | 1.7616 | 0 |  | 1.5
2017-07-12 | 16:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 86.0104
2017-07-12 | 16:35 | 1.7928 | 0 |  | 1.5
2017-07-12 | 16:40 | 1.8068 | 0 |  | 1.5
2017-07-12 | 16:45 | 1.8076 | 0 | 0 | 1.5 | 25 | 84.7617
2017-07-12 | 16:50 | 1.7975 | 0 |  | 1.5
2017-07-12 | 16:55 | 1.7897 | 0 |  | 1.5
2017-07-12 | 17:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 83.7909
2017-07-12 | 17:05 | 1.7694 | 0 |  | 1.5
2017-07-12 | 17:10 | 1.7975 | 0 |  | 1.5
2017-07-12 | 17:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 83.2105
2017-07-12 | 17:20 | 1.7631 | 0 |  | 1.5
2017-07-12 | 17:25 | 1.778 | 0 |  | 1.5
2017-07-12 | 17:30 | 1.7936 | 0 | 0 | 1.5 | 25 | 82.5067
2017-07-12 | 17:35 | 1.8076 | 0 |  | 1.5
2017-07-12 | 17:40 | 1.7842 | 0 |  | 1.5
2017-07-12 | 17:45 | 1.7889 | 0 | 0 | 1.5 | 25 | 81.365
2017-07-12 | 17:50 | 1.7912 | 0 |  | 1.5
2017-07-12 | 17:55 | 1.792 | 0 |  | 1.5
2017-07-12 | 18:00 | 1.7756 | 0 | 0 | 1.5 | 25 | 80.4724
2017-07-12 | 18:05 | 1.7327 | 0 |  | 1.5
2017-07-12 | 18:10 | 1.7897 | 0 |  | 1.5
2017-07-12 | 18:15 | 1.7694 | 0 | 0 | 1.5 | 25 | 79.7925
2017-07-12 | 18:20 | 1.7865 | 0 |  | 1.5
2017-07-12 | 18:25 | 1.767 | 0 |  | 1.5
2017-07-12 | 18:30 | 1.7741 | 0 | 0 | 1.5 | 25 | 79.2927
2017-07-12 | 18:35 | 1.7795 | 0 |  | 1.5
2017-07-12 | 18:40 | 1.7756 | 0 |  | 1.5
2017-07-12 | 18:45 | 1.7725 | 0 | 0 | 1.5 | 25 | 78.7288
2017-07-12 | 18:50 | 1.7585 | 0 |  | 1.5
2017-07-12 | 18:55 | 1.7733 | 0 |  | 1.5
2017-07-12 | 19:00 | 1.7678 | 0 | 0 | 1.5 | 25 | 78.2478
2017-07-12 | 19:05 | 1.7249 | 0 |  | 1.5
2017-07-12 | 19:10 | 1.7514 | 0 |  | 1.5
2017-07-12 | 19:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 78.2614
2017-07-12 | 19:20 | 1.7171 | 0 |  | 1.5
2017-07-12 | 19:25 | 1.7202 | 0 |  | 1.5
2017-07-12 | 19:30 | 1.7218 | 0 | 0 | 1.5 | 25 | 78.6917
2017-07-12 | 19:35 | 1.7148 | 0 |  | 1.5
2017-07-12 | 19:40 | 1.6992 | 0 |  | 1.5
2017-07-12 | 19:45 | 1.7179 | 0 | 0 | 1.5 | 25 | 79.9608
2017-07-12 | 19:50 | 1.7343 | 0 |  | 1.5
2017-07-12 | 19:55 | 1.7218 | 0 |  | 1.5
2017-07-12 | 20:00 | 1.7296 | 0 | 0 | 1.5 | 25 | 80.5396
2017-07-12 | 20:05 | 1.7514 | 0 |  | 1.5
2017-07-12 | 20:10 | 1.7577 | 0 |  | 1.5
2017-07-12 | 20:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 80.5234
2017-07-12 | 20:20 | 1.7772 | 0 |  | 1.5
2017-07-12 | 20:25 | 1.767 | 0 |  | 1.5
2017-07-12 | 20:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 80.2987
2017-07-12 | 20:35 | 1.7663 | 0 |  | 1.5
2017-07-12 | 20:40 | 1.7865 | 0 |  | 1.5
2017-07-12 | 20:45 | 1.7772 | 0 | 0 | 1.5 | 25 | 79.604
2017-07-12 | 20:50 | 1.7834 | 0 |  | 1.5
2017-07-12 | 20:55 | 1.7834 | 0 |  | 1.5
2017-07-12 | 21:00 | 1.8029 | 0 | 0 | 1.5 | 25 | 78.6873
2017-07-12 | 21:05 | -0.10574 | 0 |  | 1.5
2017-07-12 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-12 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 21:20 | -0.10652 | 0 |  | 1.5
2017-07-12 | 21:25 | -0.10652 | 0 |  | 1.5
2017-07-12 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-12 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-12 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-12 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-12 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-12 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-12 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-12 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-12 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-12 | 22:40 | -0.10652 | 0 |  | 1.5
2017-07-12 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-12 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-12 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-12 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-12 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-12 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-12 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 23:35 | -0.10574 | 0 |  | 1.5
2017-07-12 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-12 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-12 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-12 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:10 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 0:20 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:25 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:40 | -0.10574 | 0 |  | 1.5
2017-07-13 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 0:50 | -0.10418 | 0 |  | 1.5
2017-07-13 | 0:55 | -0.10496 | 0 |  | 1.5
2017-07-13 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 1:05 | -0.10574 | 0 |  | 1.5
2017-07-13 | 1:10 | -0.10574 | 0 |  | 1.5
2017-07-13 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 1:20 | -0.10964 | 0 |  | 1.5
2017-07-13 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-13 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 1:35 | -0.10886 | 0 |  | 1.5
2017-07-13 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-13 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 1:50 | -0.10964 | 0 |  | 1.5
2017-07-13 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-13 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-13 | 2:10 | -0.1112 | 0 |  | 1.5
2017-07-13 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-13 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-13 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-13 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-13 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-13 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-13 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-13 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-13 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-13 | 3:25 | -0.1112 | 0 |  | 1.5
2017-07-13 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-13 | 3:40 | -0.1112 | 0 |  | 1.5
2017-07-13 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 3:50 | -0.1112 | 0 |  | 1.5
2017-07-13 | 3:55 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 4:05 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:10 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:25 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 4:35 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:40 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 4:50 | -0.1112 | 0 |  | 1.5
2017-07-13 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-13 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 5:05 | 2.4347 | 5.9604 |  | 10
2017-07-13 | 5:10 | 2.143 | 10 |  | 10
2017-07-13 | 5:15 | 2.1149 | 9.8969 | 1 | 10 | 99.182 | 88.2927
2017-07-13 | 5:20 | 2.0346 | 9.7165 |  | 10
2017-07-13 | 5:25 | 2.0026 | 8.9928 |  | 10
2017-07-13 | 5:30 | 1.9067 | 8.3913 | 1 | 10 | 84.8535 | 81.3666
2017-07-13 | 5:35 | 1.8653 | 7.8103 |  | 10
2017-07-13 | 5:40 | 1.8458 | 7.4717 |  | 10
2017-07-13 | 5:45 | 1.8107 | 7.0177 | 1 | 10 | 71.3537 | 78.344
2017-07-13 | 5:50 | 1.8162 | 6.8046 |  | 10
2017-07-13 | 5:55 | 1.7834 | 6.6623 |  | 10
2017-07-13 | 6:00 | 1.7741 | 6.4395 | 1 | 10 | 65.6035 | 76.9246
2017-07-13 | 6:05 | 1.7959 | 6.3147 |  | 10
2017-07-13 | 6:10 | 1.7717 | 6.296 |  | 10
2017-07-13 | 6:15 | 1.778 | 6.5317 | 1 | 10 | 66.2296 | 76.0882
2017-07-13 | 6:20 | 1.7592 | 6.2797 |  | 10
2017-07-13 | 6:25 | 1.7686 | 5.9404 |  | 10
2017-07-13 | 6:30 | 1.7803 | 6.2368 | 1 | 10 | 63.1327 | 75.506
2017-07-13 | 6:35 | 1.7561 | 6.2788 |  | 10
2017-07-13 | 6:40 | 1.767 | 6.3011 |  | 10
2017-07-13 | 6:45 | 1.7975 | 6.3091 | 1 | 10 | 64.2292 | 75.1054
2017-07-13 | 6:50 | 1.7468 | 5.9772 |  | 10
2017-07-13 | 6:55 | 1.7834 | 5.8892 |  | 10
2017-07-13 | 7:00 | 1.7795 | 5.3839 | 1 | 10 | 55.7922 | 74.5799
2017-07-13 | 7:05 | 1.7631 | 5.3392 |  | 10
2017-07-13 | 7:10 | 1.7663 | 5.5677 |  | 10
2017-07-13 | 7:15 | 1.7639 | 5.8962 | 1 | 10 | 59.795 | 74.1746
2017-07-13 | 7:20 | 1.7764 | 5.5843 |  | 10
2017-07-13 | 7:25 | 1.7553 | 5.2946 |  | 10
2017-07-13 | 7:30 | 1.7624 | 5.0513 | 1 | 10 | 51.9883 | 73.9086
2017-07-13 | 7:35 | 1.7608 | 4.408 |  | 10
2017-07-13 | 7:40 | 1.7608 | 4.3235 |  | 10
2017-07-13 | 7:45 | 1.778 | 4.2649 | 1 | 10 | 44.9316 | 73.5871
2017-07-13 | 7:50 | 1.7702 | 3.7836 |  | 10
2017-07-13 | 7:55 | 1.7686 | 3.9666 |  | 10
2017-07-13 | 8:00 | 1.7452 | 3.5113 | 1 | 10 | 37.1556 | 73.4613
2017-07-13 | 8:05 | 1.7709 | 3.5235 |  | 10
2017-07-13 | 8:10 | 1.7483 | 4.0348 |  | 10
2017-07-13 | 8:15 | 1.7351 | 4.1981 | 1 | 10 | 43.8943 | 73.47
2017-07-13 | 8:20 | 1.778 | 4.7006 |  | 10
2017-07-13 | 8:25 | 1.785 | 4.5422 |  | 10
2017-07-13 | 8:30 | 1.7647 | 4.2837 | 1 | 10 | 44.5081 | 73.2864
2017-07-13 | 8:35 | 1.7608 | 4.2477 |  | 10
2017-07-13 | 8:40 | 1.746 | 4.5088 |  | 10
2017-07-13 | 8:45 | 1.7397 | 4.6729 | 1 | 10 | 48.0011 | 73.3744
2017-07-13 | 8:50 | 1.7538 | 4.1589 |  | 10
2017-07-13 | 8:55 | 1.6922 | 3.8433 |  | 10
2017-07-13 | 9:00 | 1.714 | 4.2096 | 1 | 10 | 42.951 | 74.3266
2017-07-13 | 9:05 | 1.7499 | 4.2631 |  | 10
2017-07-13 | 9:10 | 1.7483 | 4.5864 |  | 10
2017-07-13 | 9:15 | 1.7772 | 4.5966 | 1 | 10 | 47.7321 | 74.1022
2017-07-13 | 9:20 | 1.7483 | 4.6526 |  | 10
2017-07-13 | 9:25 | 1.7101 | 4.5984 |  | 10
2017-07-13 | 9:30 | 1.6976 | 5.1359 | 1 | 10 | 52.8432 | 74.9133
2017-07-13 | 9:35 | 1.7319 | 4.8639 |  | 10
2017-07-13 | 9:40 | 1.6906 | 5.0043 |  | 10
2017-07-13 | 9:45 | 1.7546 | 5.0334 | 1 | 10 | 52.2976 | 75.3158
2017-07-13 | 9:50 | 1.7234 | 4.7082 |  | 10
2017-07-13 | 9:55 | 1.7171 | 4.3091 |  | 10
2017-07-13 | 10:00 | 1.7093 | 4.123 | 1 | 10 | 43.1814 | 75.8308
2017-07-13 | 10:05 | 1.7202 | 4.3575 |  | 10
2017-07-13 | 10:10 | 1.6493 | 2.9567 |  | 1.5
2017-07-13 | 10:15 | 1.6859 | 1.7893 | 0 | 1.5 | 25.1037 | 78.2184
2017-07-13 | 10:20 | 1.6867 | 0.66255 |  | 1.5
2017-07-13 | 10:25 | 1.6446 | 0 |  | 1.5
2017-07-13 | 10:30 | 1.6968 | 0 | 0 | 1.5 | 25 | 80.3
2017-07-13 | 10:35 | 1.7 | 0 |  | 1.5
2017-07-13 | 10:40 | 1.6602 | 0 |  | 1.5
2017-07-13 | 10:45 | 1.6703 | 0 | 0 | 1.5 | 25 | 82.0493
2017-07-13 | 10:50 | 1.7226 | 0 |  | 1.5
2017-07-13 | 10:55 | 1.7429 | 0 |  | 1.5
2017-07-13 | 11:00 | 1.76 | 0 | 0 | 1.5 | 25 | 82.7493
2017-07-13 | 11:05 | 1.7507 | 0 |  | 1.5
2017-07-13 | 11:10 | 1.7561 | 0 |  | 1.5
2017-07-13 | 11:15 | 1.831 | 0 | 0 | 1.5 | 25 | 82.2776
2017-07-13 | 11:20 | 1.7842 | 0 |  | 1.5
2017-07-13 | 11:25 | 1.7717 | 0 |  | 1.5
2017-07-13 | 11:30 | 1.7421 | 0 | 0 | 1.5 | 25 | 81.4397
2017-07-13 | 11:35 | 1.7405 | 0 |  | 1.5
2017-07-13 | 11:40 | 1.7163 | 0 |  | 1.5
2017-07-13 | 11:45 | 1.7195 | 0 | 0 | 1.5 | 25 | 81.8552
2017-07-13 | 11:50 | 1.7327 | 0 |  | 1.5
2017-07-13 | 11:55 | 1.7374 | 0 |  | 1.5
2017-07-13 | 12:00 | 1.7546 | 0 | 0 | 1.5 | 25 | 82.3407
2017-07-13 | 12:05 | 1.7639 | 0 |  | 1.5
2017-07-13 | 12:10 | 1.7491 | 0 |  | 1.5
2017-07-13 | 12:15 | 1.7468 | 0 | 0 | 1.5 | 25 | 82.2176
2017-07-13 | 12:20 | 1.6688 | 0 |  | 1.5
2017-07-13 | 12:25 | 1.7039 | 0 |  | 1.5
2017-07-13 | 12:30 | 1.7179 | 0 | 0 | 1.5 | 25 | 83.4239
2017-07-13 | 12:35 | 1.7039 | 0 |  | 1.5
2017-07-13 | 12:40 | 1.7538 | 0 |  | 1.5
2017-07-13 | 12:45 | 1.7608 | 0 | 0 | 1.5 | 25 | 83.9091
2017-07-13 | 12:50 | 1.7538 | 0 |  | 1.5
2017-07-13 | 12:55 | 1.7195 | 0 |  | 1.5
2017-07-13 | 13:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 83.6852
2017-07-13 | 13:05 | 1.7413 | 0 |  | 1.5
2017-07-13 | 13:10 | 1.7553 | 0 |  | 1.5
2017-07-13 | 13:15 | 1.7546 | 0 | 0 | 1.5 | 25 | 83.9323
2017-07-13 | 13:20 | 1.7234 | 0 |  | 1.5
2017-07-13 | 13:25 | 1.7436 | 0 |  | 1.5
2017-07-13 | 13:30 | 1.7733 | 0 | 0 | 1.5 | 25 | 84.0255
2017-07-13 | 13:35 | 1.7343 | 0 |  | 1.5
2017-07-13 | 13:40 | 1.7327 | 0 |  | 1.5
2017-07-13 | 13:45 | 1.7546 | 0 | 0 | 1.5 | 25 | 84.1934
2017-07-13 | 13:50 | 1.7538 | 0 |  | 1.5
2017-07-13 | 13:55 | 1.7195 | 0 |  | 1.5
2017-07-13 | 14:00 | 1.7647 | 0 | 0 | 1.5 | 25 | 84.0647
2017-07-13 | 14:05 | 1.7702 | 0 |  | 1.5
2017-07-13 | 14:10 | 1.728 | 0 |  | 1.5
2017-07-13 | 14:15 | 1.6571 | 0 | 0 | 1.5 | 25 | 84.4495
2017-07-13 | 14:20 | 1.65 | 0 |  | 1.5
2017-07-13 | 14:25 | 1.6516 | 0 |  | 1.5
2017-07-13 | 14:30 | 1.7015 | 0 | 0 | 1.5 | 25 | 86.6732
2017-07-13 | 14:35 | 1.7132 | 0 |  | 1.5
2017-07-13 | 14:40 | 1.7335 | 0 |  | 1.5
2017-07-13 | 14:45 | 1.7132 | 0 | 0 | 1.5 | 25 | 87.2271
2017-07-13 | 14:50 | 1.7522 | 0 |  | 1.5
2017-07-13 | 14:55 | 1.7429 | 0 |  | 1.5
2017-07-13 | 15:00 | 1.7803 | 0 | 0 | 1.5 | 25 | 87.3465
2017-07-13 | 15:05 | 1.7764 | 0 |  | 1.5
2017-07-13 | 15:10 | 1.7826 | 0 |  | 1.5
2017-07-13 | 15:15 | 1.7811 | 0 | 0 | 1.5 | 25 | 86.9432
2017-07-13 | 15:20 | 1.8037 | 0 |  | 1.5
2017-07-13 | 15:25 | 1.8029 | 0 |  | 1.5
2017-07-13 | 15:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 86.4709
2017-07-13 | 15:35 | 1.7312 | 0 |  | 1.5
2017-07-13 | 15:40 | 1.7405 | 0 |  | 1.5
2017-07-13 | 15:45 | 1.7709 | 0 | 0 | 1.5 | 25 | 86.5219
2017-07-13 | 15:50 | 1.7273 | 0 |  | 1.5
2017-07-13 | 15:55 | 1.7842 | 0 |  | 1.5
2017-07-13 | 16:00 | 1.7709 | 0 | 0 | 1.5 | 25 | 86.292
2017-07-13 | 16:05 | 1.7491 | 0 |  | 1.5
2017-07-13 | 16:10 | 1.8021 | 0 |  | 1.5
2017-07-13 | 16:15 | 1.8053 | 0 | 0 | 1.5 | 25 | 84.9236
2017-07-13 | 16:20 | 1.7967 | 0 |  | 1.5
2017-07-13 | 16:25 | 1.8162 | 0 |  | 1.5
2017-07-13 | 16:30 | 1.7811 | 0 | 0 | 1.5 | 25 | 83.8014
2017-07-13 | 16:35 | 1.7811 | 0 |  | 1.5
2017-07-13 | 16:40 | 1.7553 | 0 |  | 1.5
2017-07-13 | 16:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 83.2483
2017-07-13 | 16:50 | 1.7499 | 0 |  | 1.5
2017-07-13 | 16:55 | 1.7171 | 0 |  | 1.5
2017-07-13 | 17:00 | 1.7374 | 0 | 0 | 1.5 | 25 | 83.1666
2017-07-13 | 17:05 | 1.7366 | 0 |  | 1.5
2017-07-13 | 17:10 | 1.785 | 0 |  | 1.5
2017-07-13 | 17:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 82.9975
2017-07-13 | 17:20 | 1.806 | 0 |  | 1.5
2017-07-13 | 17:25 | 1.7975 | 0 |  | 1.5
2017-07-13 | 17:30 | 1.7975 | 0 | 0 | 1.5 | 25 | 82.1962
2017-07-13 | 17:35 | 1.7928 | 0 |  | 1.5
2017-07-13 | 17:40 | 1.7787 | 0 |  | 1.5
2017-07-13 | 17:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 81.2562
2017-07-13 | 17:50 | 1.7858 | 0 |  | 1.5
2017-07-13 | 17:55 | 1.8014 | 0 |  | 1.5
2017-07-13 | 18:00 | 1.7694 | 0 | 0 | 1.5 | 25 | 80.318
2017-07-13 | 18:05 | 1.7647 | 0 |  | 1.5
2017-07-13 | 18:10 | 1.7553 | 0 |  | 1.5
2017-07-13 | 18:15 | 1.7631 | 0 | 0 | 1.5 | 25 | 79.8091
2017-07-13 | 18:20 | 1.7881 | 0 |  | 1.5
2017-07-13 | 18:25 | 1.7639 | 0 |  | 1.5
2017-07-13 | 18:30 | 1.7772 | 0 | 0 | 1.5 | 25 | 79.3151
2017-07-13 | 18:35 | 1.8006 | 0 |  | 1.5
2017-07-13 | 18:40 | 1.7741 | 0 |  | 1.5
2017-07-13 | 18:45 | 1.7647 | 0 | 0 | 1.5 | 25 | 79.0917
2017-07-13 | 18:50 | 1.7413 | 0 |  | 1.5
2017-07-13 | 18:55 | 1.7452 | 0 |  | 1.5
2017-07-13 | 19:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 79.482
2017-07-13 | 19:05 | 1.7444 | 0 |  | 1.5
2017-07-13 | 19:10 | 1.7405 | 0 |  | 1.5
2017-07-13 | 19:15 | 1.7444 | 0 | 0 | 1.5 | 25 | 79.9593
2017-07-13 | 19:20 | 1.7585 | 0 |  | 1.5
2017-07-13 | 19:25 | 1.7124 | 0 |  | 1.5
2017-07-13 | 19:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 80.2682
2017-07-13 | 19:35 | 1.721 | 0 |  | 1.5
2017-07-13 | 19:40 | 1.7507 | 0 |  | 1.5
2017-07-13 | 19:45 | 1.7553 | 0 | 0 | 1.5 | 25 | 80.4168
2017-07-13 | 19:50 | 1.7608 | 0 |  | 1.5
2017-07-13 | 19:55 | 1.7725 | 0 |  | 1.5
2017-07-13 | 20:00 | 1.7842 | 0 | 0 | 1.5 | 25 | 80.3968
2017-07-13 | 20:05 | 1.7756 | 0 |  | 1.5
2017-07-13 | 20:10 | 1.7725 | 0 |  | 1.5
2017-07-13 | 20:15 | 1.7624 | 0 | 0 | 1.5 | 25 | 80.3984
2017-07-13 | 20:20 | 1.7647 | 0 |  | 1.5
2017-07-13 | 20:25 | 1.7624 | 0 |  | 1.5
2017-07-13 | 20:30 | 1.7858 | 0 | 0 | 1.5 | 25 | 80.1108
2017-07-13 | 20:35 | 1.7764 | 0 |  | 1.5
2017-07-13 | 20:40 | 1.7538 | 0 |  | 1.5
2017-07-13 | 20:45 | 1.7795 | 0 | 0 | 1.5 | 25 | 79.6109
2017-07-13 | 20:50 | 1.7569 | 0 |  | 1.5
2017-07-13 | 20:55 | 1.7624 | 0 |  | 1.5
2017-07-13 | 21:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 79.2944
2017-07-13 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-13 | 21:10 | -0.1073 | 0 |  | 1.5
2017-07-13 | 21:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-13 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-13 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-13 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-13 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-13 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-13 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 22:05 | -0.1073 | 0 |  | 1.5
2017-07-13 | 22:10 | -0.1073 | 0 |  | 1.5
2017-07-13 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-13 | 22:25 | -0.10652 | 0 |  | 1.5
2017-07-13 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 22:35 | -0.1073 | 0 |  | 1.5
2017-07-13 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-13 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-13 | 22:55 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 23:05 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:10 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 23:20 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:25 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 23:35 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:40 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-13 | 23:50 | -0.1073 | 0 |  | 1.5
2017-07-13 | 23:55 | -0.1073 | 0 |  | 1.5
2017-07-14 | 0:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 0:05 | -0.10652 | 0 |  | 1.5
2017-07-14 | 0:10 | -0.10652 | 0 |  | 1.5
2017-07-14 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 0:20 | -0.10886 | 0 |  | 1.5
2017-07-14 | 0:25 | -0.10652 | 0 |  | 1.5
2017-07-14 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-14 | 0:40 | -0.1073 | 0 |  | 1.5
2017-07-14 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 0:50 | -0.1073 | 0 |  | 1.5
2017-07-14 | 0:55 | -0.1073 | 0 |  | 1.5
2017-07-14 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 1:05 | -0.1073 | 0 |  | 1.5
2017-07-14 | 1:10 | -0.1073 | 0 |  | 1.5
2017-07-14 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 1:20 | -0.11042 | 0 |  | 1.5
2017-07-14 | 1:25 | -0.10964 | 0 |  | 1.5
2017-07-14 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 1:35 | -0.11042 | 0 |  | 1.5
2017-07-14 | 1:40 | -0.11042 | 0 |  | 1.5
2017-07-14 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-14 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-14 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 3:35 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-14 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 4:20 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-14 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-14 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-14 | 5:00 | -0.11042 | 0 | 1 | 0 | 0 | 25.375
2017-07-14 | 5:05 | 2.5361 | 5.5015 |  | 10
2017-07-14 | 5:10 | 2.1929 | 9.8339 |  | 10
2017-07-14 | 5:15 | 2.0525 | 9.3076 | 1 | 10 | 95.2288 | 86.8866
2017-07-14 | 5:20 | 2.0034 | 8.5177 |  | 10
2017-07-14 | 5:25 | 1.9558 | 8.099 |  | 10
2017-07-14 | 5:30 | 1.8833 | 7.5144 | 1 | 10 | 77.6792 | 81.3273
2017-07-14 | 5:35 | 1.8497 | 7.1518 |  | 10
2017-07-14 | 5:40 | 1.8107 | 6.8825 |  | 10
2017-07-14 | 5:45 | 1.7967 | 6.4417 | 1 | 10 | 66.9914 | 79.0414
2017-07-14 | 5:50 | 1.8123 | 6.4129 |  | 10
2017-07-14 | 5:55 | 1.785 | 6.1892 |  | 10
2017-07-14 | 6:00 | 1.7811 | 6.0771 | 1 | 10 | 63.6038 | 77.9759
2017-07-14 | 6:05 | 1.7663 | 6.2481 |  | 10
2017-07-14 | 6:10 | 1.7475 | 6.3488 |  | 10
2017-07-14 | 6:15 | 1.7452 | 6.575 | 1 | 10 | 68.1407 | 77.7667
2017-07-14 | 6:20 | 1.7413 | 6.3253 |  | 10
2017-07-14 | 6:25 | 1.7585 | 6.2622 |  | 10
2017-07-14 | 6:30 | 1.778 | 6.2392 | 1 | 10 | 65.0343 | 77.4729
2017-07-14 | 6:35 | 1.7702 | 6.0575 |  | 10
2017-07-14 | 6:40 | 1.7491 | 6.442 |  | 10
2017-07-14 | 6:45 | 1.7335 | 6.2968 | 1 | 10 | 65.8059 | 77.3515
2017-07-14 | 6:50 | 1.778 | 6.4048 |  | 10
2017-07-14 | 6:55 | 1.8014 | 6.4213 |  | 10
2017-07-14 | 7:00 | 1.7608 | 6.3624 | 1 | 10 | 66.1048 | 76.7112
2017-07-14 | 7:05 | 1.7655 | 6.0692 |  | 10
2017-07-14 | 7:10 | 1.7538 | 5.8982 |  | 10
2017-07-14 | 7:15 | 1.7936 | 5.5405 | 1 | 10 | 58.5 | 76.3143
2017-07-14 | 7:20 | 1.7717 | 5.3317 |  | 10
2017-07-14 | 7:25 | 1.7647 | 5.0491 |  | 10
2017-07-14 | 7:30 | 1.7725 | 4.7986 | 1 | 10 | 50.7443 | 75.9585
2017-07-14 | 7:35 | 1.7709 | 4.6586 |  | 10
2017-07-14 | 7:40 | 1.7507 | 4.6678 |  | 10
2017-07-14 | 7:45 | 1.7865 | 4.4792 | 1 | 10 | 47.9112 | 75.6877
2017-07-14 | 7:50 | 1.7499 | 4.7707 |  | 10
2017-07-14 | 7:55 | 1.7429 | 4.5876 |  | 10
2017-07-14 | 8:00 | 1.7561 | 4.7181 | 1 | 10 | 50.481 | 75.5578
2017-07-14 | 8:05 | 1.7421 | 5.213 |  | 10
2017-07-14 | 8:10 | 1.7702 | 5.0622 |  | 10
2017-07-14 | 8:15 | 1.7429 | 4.8365 | 1 | 10 | 51.9448 | 75.7246
2017-07-14 | 8:20 | 1.746 | 4.5708 |  | 10
2017-07-14 | 8:25 | 1.728 | 4.6009 |  | 10
2017-07-14 | 8:30 | 1.7148 | 4.5049 | 1 | 10 | 48.1645 | 75.8101
2017-07-14 | 8:35 | 1.714 | 4.8753 |  | 10
2017-07-14 | 8:40 | 1.7585 | 4.8809 |  | 10
2017-07-14 | 8:45 | 1.7187 | 4.7032 | 1 | 10 | 50.5303 | 76.0521
2017-07-14 | 8:50 | 1.7702 | 4.4945 |  | 10
2017-07-14 | 8:55 | 1.7421 | 4.0954 |  | 10
2017-07-14 | 9:00 | 1.7366 | 4.0689 | 1 | 10 | 43.613 | 76.1026
2017-07-14 | 9:05 | 1.7241 | 5.0913 |  | 10
2017-07-14 | 9:10 | 1.7265 | 4.9562 |  | 10
2017-07-14 | 9:15 | 1.7312 | 4.9413 | 1 | 10 | 52.3327 | 76.3312
2017-07-14 | 9:20 | 1.707 | 4.9274 |  | 10
2017-07-14 | 9:25 | 1.7241 | 5.2533 |  | 10
2017-07-14 | 9:30 | 1.7101 | 5.3538 | 1 | 10 | 56.3952 | 76.9267
2017-07-14 | 9:35 | 1.7304 | 5.1313 |  | 10
2017-07-14 | 9:40 | 1.76 | 4.7377 |  | 10
2017-07-14 | 9:45 | 1.7358 | 4.6572 | 1 | 10 | 50.0676 | 77.1517
2017-07-14 | 9:50 | 1.7382 | 4.2038 |  | 10
2017-07-14 | 9:55 | 1.739 | 4.0959 |  | 10
2017-07-14 | 10:00 | 1.5869 | 2.7873 | 0 | 1.5 | 33.175 | 78.0713
2017-07-14 | 10:05 | 1.6329 | 0 |  | 1.5
2017-07-14 | 10:10 | 1.6461 | 0 |  | 1.5
2017-07-14 | 10:15 | 1.7078 | 0 | 0 | 1.5 | 25 | 80.8294
2017-07-14 | 10:20 | 1.728 | 0 |  | 1.5
2017-07-14 | 10:25 | 1.7093 | 0 |  | 1.5
2017-07-14 | 10:30 | 1.7 | 0 | 0 | 1.5 | 25 | 81.9283
2017-07-14 | 10:35 | 1.7062 | 0 |  | 1.5
2017-07-14 | 10:40 | 1.7577 | 0 |  | 1.5
2017-07-14 | 10:45 | 1.7218 | 0 | 0 | 1.5 | 25 | 82.4013
2017-07-14 | 10:50 | 1.7132 | 0 |  | 1.5
2017-07-14 | 10:55 | 1.7327 | 0 |  | 1.5
2017-07-14 | 11:00 | 1.7429 | 0 | 0 | 1.5 | 25 | 82.8597
2017-07-14 | 11:05 | 1.7351 | 0 |  | 1.5
2017-07-14 | 11:10 | 1.707 | 0 |  | 1.5
2017-07-14 | 11:15 | 1.7358 | 0 | 0 | 1.5 | 25 | 83.3857
2017-07-14 | 11:20 | 1.7195 | 0 |  | 1.5
2017-07-14 | 11:25 | 1.728 | 0 |  | 1.5
2017-07-14 | 11:30 | 1.7585 | 0 | 0 | 1.5 | 25 | 83.8519
2017-07-14 | 11:35 | 1.7522 | 0 |  | 1.5
2017-07-14 | 11:40 | 1.6953 | 0 |  | 1.5
2017-07-14 | 11:45 | 1.707 | 0 | 0 | 1.5 | 25 | 84.323
2017-07-14 | 11:50 | 1.7156 | 0 |  | 1.5
2017-07-14 | 11:55 | 1.6859 | 0 |  | 1.5
2017-07-14 | 12:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 85.5135
2017-07-14 | 12:05 | 1.7124 | 0 |  | 1.5
2017-07-14 | 12:10 | 1.7046 | 0 |  | 1.5
2017-07-14 | 12:15 | 1.7023 | 0 | 0 | 1.5 | 25 | 86.5108
2017-07-14 | 12:20 | 1.7319 | 0 |  | 1.5
2017-07-14 | 12:25 | 1.7265 | 0 |  | 1.5
2017-07-14 | 12:30 | 1.7405 | 0 | 0 | 1.5 | 25 | 87.18
2017-07-14 | 12:35 | 1.7273 | 0 |  | 1.5
2017-07-14 | 12:40 | 1.728 | 0 |  | 1.5
2017-07-14 | 12:45 | 1.7288 | 0 | 0 | 1.5 | 25 | 87.4006
2017-07-14 | 12:50 | 1.76 | 0 |  | 1.5
2017-07-14 | 12:55 | 1.7444 | 0 |  | 1.5
2017-07-14 | 13:00 | 1.7265 | 0 | 0 | 1.5 | 25 | 87.736
2017-07-14 | 13:05 | 1.739 | 0 |  | 1.5
2017-07-14 | 13:10 | 1.7709 | 0 |  | 1.5
2017-07-14 | 13:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 87.8572
2017-07-14 | 13:20 | 1.7249 | 0 |  | 1.5
2017-07-14 | 13:25 | 1.7163 | 0 |  | 1.5
2017-07-14 | 13:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 88.2465
2017-07-14 | 13:35 | 1.7234 | 0 |  | 1.5
2017-07-14 | 13:40 | 1.7483 | 0 |  | 1.5
2017-07-14 | 13:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 88.4546
2017-07-14 | 13:50 | 1.7436 | 0 |  | 1.5
2017-07-14 | 13:55 | 1.7507 | 0 |  | 1.5
2017-07-14 | 14:00 | 1.7062 | 0 | 0 | 1.5 | 25 | 88.7449
2017-07-14 | 14:05 | 1.7054 | 0 |  | 1.5
2017-07-14 | 14:10 | 1.6524 | 0 |  | 1.5
2017-07-14 | 14:15 | 1.6368 | 0 | 0 | 1.5 | 25 | 90.4802
2017-07-14 | 14:20 | 1.6664 | 0 |  | 1.5
2017-07-14 | 14:25 | 1.6859 | 0 |  | 1.5
2017-07-14 | 14:30 | 1.675 | 0 | 0 | 1.5 | 25 | 92.257
2017-07-14 | 14:35 | 1.7343 | 0 |  | 1.5
2017-07-14 | 14:40 | 1.6945 | 0 |  | 1.5
2017-07-14 | 14:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 92.8469
2017-07-14 | 14:50 | 1.7647 | 0 |  | 1.5
2017-07-14 | 14:55 | 1.7608 | 0 |  | 1.5
2017-07-14 | 15:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 92.5823
2017-07-14 | 15:05 | 1.739 | 0 |  | 1.5
2017-07-14 | 15:10 | 1.7304 | 0 |  | 1.5
2017-07-14 | 15:15 | 1.7553 | 0 | 0 | 1.5 | 25 | 92.9655
2017-07-14 | 15:20 | 1.7569 | 0 |  | 1.5
2017-07-14 | 15:25 | 1.7358 | 0 |  | 1.5
2017-07-14 | 15:30 | 1.7725 | 0 | 0 | 1.5 | 25 | 92.5751
2017-07-14 | 15:35 | 1.7881 | 0 |  | 1.5
2017-07-14 | 15:40 | 1.7663 | 0 |  | 1.5
2017-07-14 | 15:45 | 1.7873 | 0 | 0 | 1.5 | 25 | 91.4304
2017-07-14 | 15:50 | 1.8201 | 0 |  | 1.5
2017-07-14 | 15:55 | 1.7772 | 0 |  | 1.5
2017-07-14 | 16:00 | 1.7975 | 0 | 0 | 1.5 | 25 | 90.1791
2017-07-14 | 16:05 | 1.7975 | 0 |  | 1.5
2017-07-14 | 16:10 | 1.7826 | 0 |  | 1.5
2017-07-14 | 16:15 | 1.8068 | 0 | 0 | 1.5 | 25 | 89.1945
2017-07-14 | 16:20 | 1.7514 | 0 |  | 1.5
2017-07-14 | 16:25 | 1.7631 | 0 |  | 1.5
2017-07-14 | 16:30 | 1.7717 | 0 | 0 | 1.5 | 25 | 88.7517
2017-07-14 | 16:35 | 1.7834 | 0 |  | 1.5
2017-07-14 | 16:40 | 1.7468 | 0 |  | 1.5
2017-07-14 | 16:45 | 1.7842 | 0 | 0 | 1.5 | 25 | 88.3932
2017-07-14 | 16:50 | 1.7639 | 0 |  | 1.5
2017-07-14 | 16:55 | 1.739 | 0 |  | 1.5
2017-07-14 | 17:00 | 1.7585 | 0 | 0 | 1.5 | 25 | 88.1736
2017-07-14 | 17:05 | 1.7288 | 0 |  | 1.5
2017-07-14 | 17:10 | 1.7553 | 0 |  | 1.5
2017-07-14 | 17:15 | 1.7733 | 0 | 0 | 1.5 | 25 | 87.7781
2017-07-14 | 17:20 | 1.7655 | 0 |  | 1.5
2017-07-14 | 17:25 | 1.7546 | 0 |  | 1.5
2017-07-14 | 17:30 | 1.76 | 0 | 0 | 1.5 | 25 | 87.3175
2017-07-14 | 17:35 | 1.7717 | 0 |  | 1.5
2017-07-14 | 17:40 | 1.8068 | 0 |  | 1.5
2017-07-14 | 17:45 | 1.7873 | 0 | 0 | 1.5 | 25 | 86.5927
2017-07-14 | 17:50 | 1.7507 | 0 |  | 1.5
2017-07-14 | 17:55 | 1.7764 | 0 |  | 1.5
2017-07-14 | 18:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 85.882
2017-07-14 | 18:05 | 1.7826 | 0 |  | 1.5
2017-07-14 | 18:10 | 1.778 | 0 |  | 1.5
2017-07-14 | 18:15 | 1.7694 | 0 | 0 | 1.5 | 25 | 85.4357
2017-07-14 | 18:20 | 1.7569 | 0 |  | 1.5
2017-07-14 | 18:25 | 1.7452 | 0 |  | 1.5
2017-07-14 | 18:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 85.168
2017-07-14 | 18:35 | 1.767 | 0 |  | 1.5
2017-07-14 | 18:40 | 1.7725 | 0 |  | 1.5
2017-07-14 | 18:45 | 1.778 | 0 | 0 | 1.5 | 25 | 84.7993
2017-07-14 | 18:50 | 1.7842 | 0 |  | 1.5
2017-07-14 | 18:55 | 1.7741 | 0 |  | 1.5
2017-07-14 | 19:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 84.2741
2017-07-14 | 19:05 | 1.778 | 0 |  | 1.5
2017-07-14 | 19:10 | 1.7772 | 0 |  | 1.5
2017-07-14 | 19:15 | 1.7475 | 0 | 0 | 1.5 | 25 | 83.7151
2017-07-14 | 19:20 | 1.7811 | 0 |  | 1.5
2017-07-14 | 19:25 | 1.7647 | 0 |  | 1.5
2017-07-14 | 19:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 83.2261
2017-07-14 | 19:35 | 1.7951 | 0 |  | 1.5
2017-07-14 | 19:40 | 1.7694 | 0 |  | 1.5
2017-07-14 | 19:45 | 1.8014 | 0 | 0 | 1.5 | 25 | 82.7502
2017-07-14 | 19:50 | 1.7928 | 0 |  | 1.5
2017-07-14 | 19:55 | 1.7475 | 0 |  | 1.5
2017-07-14 | 20:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 82.3449
2017-07-14 | 20:05 | 1.7702 | 0 |  | 1.5
2017-07-14 | 20:10 | 1.7514 | 0 |  | 1.5
2017-07-14 | 20:15 | 1.7998 | 0 | 0 | 1.5 | 25 | 81.7282
2017-07-14 | 20:20 | 1.7764 | 0 |  | 1.5
2017-07-14 | 20:25 | 1.778 | 0 |  | 1.5
2017-07-14 | 20:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 81.1603
2017-07-14 | 20:35 | 1.7912 | 0 |  | 1.5
2017-07-14 | 20:40 | 1.7514 | 0 |  | 1.5
2017-07-14 | 20:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 80.7486
2017-07-14 | 20:50 | 1.7647 | 0 |  | 1.5
2017-07-14 | 20:55 | 1.7663 | 0 |  | 1.5
2017-07-14 | 21:00 | 1.7733 | 0 | 0 | 1.5 | 25 | 0
2017-07-14 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-14 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-14 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-14 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-14 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 21:35 | -0.10496 | 0 |  | 1.5
2017-07-14 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-14 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-14 | 21:55 | -0.10574 | 0 |  | 1.5
2017-07-14 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 22:05 | -0.10496 | 0 |  | 1.5
2017-07-14 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-14 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 22:20 | -0.10652 | 0 |  | 1.5
2017-07-14 | 22:25 | -0.10652 | 0 |  | 1.5
2017-07-14 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-14 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-14 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-14 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-14 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-14 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-14 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 23:20 | -0.10574 | 0 |  | 1.5
2017-07-14 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-14 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 23:35 | -0.10574 | 0 |  | 1.5
2017-07-14 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-14 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-14 | 23:50 | -0.10418 | 0 |  | 1.5
2017-07-14 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-15 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-15 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-15 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-15 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-15 | 0:15 | -0.10496 | 0 |  | 1.5 |  | 0
2017-07-15 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-15 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-15 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-15 | 0:30 | -0.10496 | 0 |  | 1.5 |  | 0
2017-07-15 | 0:35 | -0.10496 | 0 |  | 1.5
2017-07-15 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-15 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-15 | 0:45 | -0.10496 | 0 |  | 1.5 |  | 0
2017-07-15 | 0:50 | -0.10496 | 0 |  | 1.5
2017-07-15 | 0:55 | -0.10496 | 0 |  | 1.5
2017-07-15 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-15 | 1:00 | -0.10496 | 0 |  | 1.5 |  | 0
2017-07-15 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-15 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-15 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-15 | 1:15 | -0.10496 | 0 |  | 1.5 |  | 0
2017-07-15 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-15 | 1:25 | -0.10808 | 0 |  | 1.5
2017-07-15 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-15 | 1:30 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-15 | 1:35 | -0.10886 | 0 |  | 1.5
2017-07-15 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-15 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-15 | 1:45 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-15 | 1:50 | -0.10886 | 0 |  | 1.5
2017-07-15 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-15 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-15 | 2:00 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-15 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-15 | 2:10 | -0.10886 | 0 |  | 1.5
2017-07-15 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-15 | 2:15 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-15 | 2:20 | -0.10886 | 0 |  | 1.5
2017-07-15 | 2:25 | -0.10886 | 0 |  | 1.5
2017-07-15 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-15 | 2:30 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-15 | 2:35 | -0.10964 | 0 |  | 1.5
2017-07-15 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-15 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-15 | 2:45 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-15 | 2:50 | -0.10964 | 0 |  | 1.5
2017-07-15 | 2:55 | -0.10964 | 0 |  | 1.5
2017-07-15 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-15 | 3:00 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-15 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-15 | 3:10 | -0.10964 | 0 |  | 1.5
2017-07-15 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 3:15 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 3:20 | -0.10964 | 0 |  | 1.5
2017-07-15 | 3:25 | -0.10964 | 0 |  | 1.5
2017-07-15 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 3:30 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-15 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-15 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 3:45 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-15 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 4:00 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-15 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 4:15 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 4:20 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 4:30 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-15 | 4:45 | -0.11042 | 0 |  | 1.5 |  | 0
2017-07-15 | 4:50 | -0.11042 | 0 |  | 1.5
2017-07-15 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-15 | 5:00 | -0.11042 | 0 | 1 | 0 | 0
2017-07-15 | 5:00 | -0.11042 | 0 |  | 0 |  | 25.375
2017-07-15 | 5:05 | 2.3388 | 6.3064 |  | 10
2017-07-15 | 5:10 | 2.1461 | 9.9956 |  | 10
2017-07-15 | 5:15 | 2.0502 | 10 | 1 | 10 | 100
2017-07-15 | 5:15 | 2.0502 | 10 |  | 10 |  | 89.0663
2017-07-15 | 5:20 | 1.9847 | 9.811 |  | 10
2017-07-15 | 5:25 | 1.9464 | 9.3003 |  | 10
2017-07-15 | 5:30 | 1.9113 | 9.0743 | 1 | 10 | 91.2621
2017-07-15 | 5:30 | 1.9113 | 9.0743 |  | 10 |  | 83.2518
2017-07-15 | 5:35 | 1.8638 | 8.3598 |  | 10
2017-07-15 | 5:40 | 1.8435 | 7.8967 |  | 10
2017-07-15 | 5:45 | 1.8263 | 7.5149 | 1 | 10 | 76.2243
2017-07-15 | 5:45 | 1.8263 | 7.5149 |  | 10 |  | 80.4774
2017-07-15 | 5:50 | 1.8092 | 7.2544 |  | 10
2017-07-15 | 5:55 | 1.7741 | 7.2098 |  | 10
2017-07-15 | 6:00 | 1.8021 | 6.922 | 1 | 10 | 70.2639
2017-07-15 | 6:00 | 1.8021 | 6.922 |  | 10 |  | 79.0384
2017-07-15 | 6:05 | 1.7928 | 7.3916 |  | 10
2017-07-15 | 6:10 | 1.7624 | 7.3769 |  | 10
2017-07-15 | 6:15 | 1.7624 | 7.4087 | 1 | 10 | 74.7687
2017-07-15 | 6:15 | 1.7624 | 7.4087 |  | 10 |  | 78.5655
2017-07-15 | 6:20 | 1.7741 | 7.4404 |  | 10
2017-07-15 | 6:25 | 1.7725 | 7.0606 |  | 10
2017-07-15 | 6:30 | 1.8146 | 6.9489 | 1 | 10 | 70.4725
2017-07-15 | 6:30 | 1.8146 | 6.9489 |  | 10 |  | 77.8823
2017-07-15 | 6:35 | 1.7569 | 6.6115 |  | 10
2017-07-15 | 6:40 | 1.8053 | 6.6363 |  | 10
2017-07-15 | 6:45 | 1.7912 | 6.5129 | 1 | 10 | 66.3443
2017-07-15 | 6:45 | 1.7912 | 6.5129 |  | 10 |  | 76.9183
2017-07-15 | 6:50 | 1.7553 | 6.2577 |  | 10
2017-07-15 | 6:55 | 1.792 | 6.384 |  | 10
2017-07-15 | 7:00 | 1.7725 | 6.0311 | 1 | 10 | 61.752
2017-07-15 | 7:00 | 1.7725 | 6.0311 |  | 10 |  | 76.4001
2017-07-15 | 7:05 | 1.7694 | 6.267 |  | 10
2017-07-15 | 7:10 | 1.7897 | 6.4394 |  | 10
2017-07-15 | 7:15 | 1.7569 | 6.3926 | 1 | 10 | 64.8523
2017-07-15 | 7:15 | 1.7569 | 6.3926 |  | 10 |  | 75.8787
2017-07-15 | 7:20 | 1.7803 | 6.4831 |  | 10
2017-07-15 | 7:25 | 1.753 | 6.3526 |  | 10
2017-07-15 | 7:30 | 1.7553 | 6.4107 | 1 | 10 | 65.1488
2017-07-15 | 7:30 | 1.7553 | 6.4107 |  | 10 |  | 75.6178
2017-07-15 | 7:35 | 1.76 | 6.2005 |  | 10
2017-07-15 | 7:40 | 1.7546 | 6.231 |  | 10
2017-07-15 | 7:45 | 1.7546 | 6.1953 | 1 | 10 | 63.1649
2017-07-15 | 7:45 | 1.7546 | 6.1953 |  | 10 |  | 75.5189
2017-07-15 | 7:50 | 1.7647 | 6.0227 |  | 10
2017-07-15 | 7:55 | 1.7444 | 6.1409 |  | 10
2017-07-15 | 8:00 | 1.7296 | 5.9928 | 1 | 10 | 61.105
2017-07-15 | 8:00 | 1.7296 | 5.9928 |  | 10 |  | 75.4319
2017-07-15 | 8:05 | 1.7499 | 6.1942 |  | 10
2017-07-15 | 8:10 | 1.7366 | 6.2541 |  | 10
2017-07-15 | 8:15 | 1.7343 | 6.1669 | 1 | 10 | 62.661
2017-07-15 | 8:15 | 1.7343 | 6.1669 |  | 10 |  | 75.5609
2017-07-15 | 8:20 | 1.746 | 6.3902 |  | 10
2017-07-15 | 8:25 | 1.7624 | 6.1679 |  | 10
2017-07-15 | 8:30 | 1.7397 | 6.3186 | 1 | 10 | 64.0479
2017-07-15 | 8:30 | 1.7397 | 6.3186 |  | 10 |  | 75.5969
2017-07-15 | 8:35 | 1.7514 | 6.3402 |  | 10
2017-07-15 | 8:40 | 1.7483 | 6.3346 |  | 10
2017-07-15 | 8:45 | 1.767 | 6.3133 | 1 | 10 | 64.0739
2017-07-15 | 8:45 | 1.767 | 6.3133 |  | 10 |  | 75.6074
2017-07-15 | 8:50 | 1.7475 | 6.3871 |  | 10
2017-07-15 | 8:55 | 1.7483 | 6.4449 |  | 10
2017-07-15 | 9:00 | 1.76 | 6.245 | 1 | 10 | 63.5422
2017-07-15 | 9:00 | 1.76 | 6.245 |  | 10 |  | 75.7994
2017-07-15 | 9:05 | 1.7382 | 6.4946 |  | 10
2017-07-15 | 9:10 | 1.7382 | 6.6735 |  | 10
2017-07-15 | 9:15 | 1.7546 | 6.7635 | 1 | 10 | 68.3173
2017-07-15 | 9:15 | 1.7546 | 6.7635 |  | 10 |  | 76.0102
2017-07-15 | 9:20 | 1.7335 | 7.0217 |  | 10
2017-07-15 | 9:25 | 1.7421 | 7.0557 |  | 10
2017-07-15 | 9:30 | 1.5533 | 4.9766 | 0 | 1.5 | 52.2468
2017-07-15 | 9:30 | 1.5533 | 4.9766 |  | 1.5 |  | 78.8698
2017-07-15 | 9:35 | 1.7288 | 3.6288 |  | 1.5
2017-07-15 | 9:40 | 1.7748 | 0.50065 |  | 1.5
2017-07-15 | 9:45 | 1.8045 | 0 | 0 | 1.5 | 25
2017-07-15 | 9:45 | 1.8045 | 0 |  | 1.5 |  | 79.0168
2017-07-15 | 9:50 | 1.7904 | 0 |  | 1.5
2017-07-15 | 9:55 | 1.7694 | 0 |  | 1.5
2017-07-15 | 10:00 | 1.7522 | 0 | 0 | 1.5 | 25
2017-07-15 | 10:00 | 1.7522 | 0 |  | 1.5 |  | 78.8696
2017-07-15 | 10:05 | 1.753 | 0 |  | 1.5
2017-07-15 | 10:10 | 1.7397 | 0 |  | 1.5
2017-07-15 | 10:15 | 1.7444 | 0 | 0 | 1.5 | 25
2017-07-15 | 10:15 | 1.7444 | 0 |  | 1.5 |  | 79.0335
2017-07-15 | 10:20 | 1.7475 | 0 |  | 1.5
2017-07-15 | 10:25 | 1.7171 | 0 |  | 1.5
2017-07-15 | 10:30 | 1.7561 | 0 | 0 | 1.5 | 25
2017-07-15 | 10:30 | 1.7561 | 0 |  | 1.5 |  | 79.1908
2017-07-15 | 10:35 | 1.7117 | 0 |  | 1.5
2017-07-15 | 10:40 | 1.7483 | 0 |  | 1.5
2017-07-15 | 10:45 | 1.7514 | 0 | 0 | 1.5 | 25
2017-07-15 | 10:45 | 1.7514 | 0 |  | 1.5 |  | 79.395
2017-07-15 | 10:50 | 1.7351 | 0 |  | 1.5
2017-07-15 | 10:55 | 1.7241 | 0 |  | 1.5
2017-07-15 | 11:00 | 1.7663 | 0 | 0 | 1.5 | 25
2017-07-15 | 11:00 | 1.7663 | 0 |  | 1.5 |  | 79.6059
2017-07-15 | 11:05 | 1.7241 | 0 |  | 1.5
2017-07-15 | 11:10 | 1.7218 | 0 |  | 1.5
2017-07-15 | 11:15 | 1.7413 | 0 | 0 | 1.5 | 25
2017-07-15 | 11:15 | 1.7413 | 0 |  | 1.5 |  | 80.2453
2017-07-15 | 11:20 | 1.7249 | 0 |  | 1.5
2017-07-15 | 11:25 | 1.7538 | 0 |  | 1.5
2017-07-15 | 11:30 | 1.7382 | 0 | 0 | 1.5 | 25
2017-07-15 | 11:30 | 1.7382 | 0 |  | 1.5 |  | 80.4976
2017-07-15 | 11:35 | 1.7483 | 0 |  | 1.5
2017-07-15 | 11:40 | 1.7429 | 0 |  | 1.5
2017-07-15 | 11:45 | 1.721 | 0 | 0 | 1.5 | 25
2017-07-15 | 11:45 | 1.721 | 0 |  | 1.5 |  | 80.9754
2017-07-15 | 11:50 | 1.739 | 0 |  | 1.5
2017-07-15 | 11:55 | 1.7397 | 0 |  | 1.5
2017-07-15 | 12:00 | 1.7397 | 0 | 0 | 1.5 | 25
2017-07-15 | 12:00 | 1.7397 | 0 |  | 1.5 |  | 81.4176
2017-07-15 | 12:05 | 1.7522 | 0 |  | 1.5
2017-07-15 | 12:10 | 1.7374 | 0 |  | 1.5
2017-07-15 | 12:15 | 1.7171 | 0 | 0 | 1.5 | 25
2017-07-15 | 12:15 | 1.7171 | 0 |  | 1.5 |  | 81.9348
2017-07-15 | 12:20 | 1.7257 | 0 |  | 1.5
2017-07-15 | 12:25 | 1.7265 | 0 |  | 1.5
2017-07-15 | 12:30 | 1.7234 | 0 | 0 | 1.5 | 25
2017-07-15 | 12:30 | 1.7234 | 0 |  | 1.5 |  | 82.5717
2017-07-15 | 12:35 | 1.7421 | 0 |  | 1.5
2017-07-15 | 12:40 | 1.7163 | 0 |  | 1.5
2017-07-15 | 12:45 | 1.721 | 0 | 0 | 1.5 | 25
2017-07-15 | 12:45 | 1.721 | 0 |  | 1.5 |  | 83.2356
2017-07-15 | 12:50 | 1.7296 | 0 |  | 1.5
2017-07-15 | 12:55 | 1.7288 | 0 |  | 1.5
2017-07-15 | 13:00 | 1.7273 | 0 | 0 | 1.5 | 25
2017-07-15 | 13:00 | 1.7273 | 0 |  | 1.5 |  | 83.8692
2017-07-15 | 13:05 | 1.7124 | 0 |  | 1.5
2017-07-15 | 13:10 | 1.7351 | 0 |  | 1.5
2017-07-15 | 13:15 | 1.7413 | 0 | 0 | 1.5 | 25
2017-07-15 | 13:15 | 1.7413 | 0 |  | 1.5 |  | 84.5653
2017-07-15 | 13:20 | 1.7319 | 0 |  | 1.5
2017-07-15 | 13:25 | 1.7335 | 0 |  | 1.5
2017-07-15 | 13:30 | 1.7241 | 0 | 0 | 1.5 | 25
2017-07-15 | 13:30 | 1.7241 | 0 |  | 1.5 |  | 85.3527
2017-07-15 | 13:35 | 1.7312 | 0 |  | 1.5
2017-07-15 | 13:40 | 1.7148 | 0 |  | 1.5
2017-07-15 | 13:45 | 1.7366 | 0 | 0 | 1.5 | 25
2017-07-15 | 13:45 | 1.7366 | 0 |  | 1.5 |  | 85.9443
2017-07-15 | 13:50 | 1.7452 | 0 |  | 1.5
2017-07-15 | 13:55 | 1.7195 | 0 |  | 1.5
2017-07-15 | 14:00 | 1.7312 | 0 | 0 | 1.5 | 25
2017-07-15 | 14:00 | 1.7312 | 0 |  | 1.5 |  | 86.4711
2017-07-15 | 14:05 | 1.7117 | 0 |  | 1.5
2017-07-15 | 14:10 | 1.7569 | 0 |  | 1.5
2017-07-15 | 14:15 | 1.7046 | 0 | 0 | 1.5 | 25
2017-07-15 | 14:15 | 1.7046 | 0 |  | 1.5 |  | 87.0579
2017-07-15 | 14:20 | 1.7234 | 0 |  | 1.5
2017-07-15 | 14:25 | 1.7218 | 0 |  | 1.5
2017-07-15 | 14:30 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-15 | 14:30 | 1.7585 | 0 |  | 1.5 |  | 87.5627
2017-07-15 | 14:35 | 1.7553 | 0 |  | 1.5
2017-07-15 | 14:40 | 1.746 | 0 |  | 1.5
2017-07-15 | 14:45 | 1.7475 | 0 | 0 | 1.5 | 25
2017-07-15 | 14:45 | 1.7475 | 0 |  | 1.5 |  | 87.7113
2017-07-15 | 14:50 | 1.7413 | 0 |  | 1.5
2017-07-15 | 14:55 | 1.7811 | 0 |  | 1.5
2017-07-15 | 15:00 | 1.7982 | 0 | 0 | 1.5 | 25
2017-07-15 | 15:00 | 1.7982 | 0 |  | 1.5 |  | 87.2914
2017-07-15 | 15:05 | 1.7546 | 0 |  | 1.5
2017-07-15 | 15:10 | 1.7826 | 0 |  | 1.5
2017-07-15 | 15:15 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-15 | 15:15 | 1.7709 | 0 |  | 1.5 |  | 86.3208
2017-07-15 | 15:20 | 1.7967 | 0 |  | 1.5
2017-07-15 | 15:25 | 1.8029 | 0 |  | 1.5
2017-07-15 | 15:30 | 1.8014 | 0 | 0 | 1.5 | 25
2017-07-15 | 15:30 | 1.8014 | 0 |  | 1.5 |  | 85.0776
2017-07-15 | 15:35 | 1.7592 | 0 |  | 1.5
2017-07-15 | 15:40 | 1.7912 | 0 |  | 1.5
2017-07-15 | 15:45 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-15 | 15:45 | 1.7709 | 0 |  | 1.5 |  | 84.2926
2017-07-15 | 15:50 | 1.7889 | 0 |  | 1.5
2017-07-15 | 15:55 | 1.7998 | 0 |  | 1.5
2017-07-15 | 16:00 | 1.7928 | 0 | 0 | 1.5 | 25
2017-07-15 | 16:00 | 1.7928 | 0 |  | 1.5 |  | 83.7438
2017-07-15 | 16:05 | 1.7795 | 0 |  | 1.5
2017-07-15 | 16:10 | 1.7592 | 0 |  | 1.5
2017-07-15 | 16:15 | 1.7468 | 0 | 0 | 1.5 | 25
2017-07-15 | 16:15 | 1.7468 | 0 |  | 1.5 |  | 83.3732
2017-07-15 | 16:20 | 1.785 | 0 |  | 1.5
2017-07-15 | 16:25 | 1.7748 | 0 |  | 1.5
2017-07-15 | 16:30 | 1.785 | 0 | 0 | 1.5 | 25
2017-07-15 | 16:30 | 1.785 | 0 |  | 1.5 |  | 82.8374
2017-07-15 | 16:35 | 1.7514 | 0 |  | 1.5
2017-07-15 | 16:40 | 1.7655 | 0 |  | 1.5
2017-07-15 | 16:45 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-15 | 16:45 | 1.7639 | 0 |  | 1.5 |  | 82.5126
2017-07-15 | 16:50 | 1.7725 | 0 |  | 1.5
2017-07-15 | 16:55 | 1.7904 | 0 |  | 1.5
2017-07-15 | 17:00 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-15 | 17:00 | 1.7639 | 0 |  | 1.5 |  | 81.9831
2017-07-15 | 17:05 | 1.7538 | 0 |  | 1.5
2017-07-15 | 17:10 | 1.7561 | 0 |  | 1.5
2017-07-15 | 17:15 | 1.767 | 0 | 0 | 1.5 | 25
2017-07-15 | 17:15 | 1.767 | 0 |  | 1.5 |  | 81.5731
2017-07-15 | 17:20 | 1.767 | 0 |  | 1.5
2017-07-15 | 17:25 | 1.792 | 0 |  | 1.5
2017-07-15 | 17:30 | 1.7655 | 0 | 0 | 1.5 | 25
2017-07-15 | 17:30 | 1.7655 | 0 |  | 1.5 |  | 81.0614
2017-07-15 | 17:35 | 1.7577 | 0 |  | 1.5
2017-07-15 | 17:40 | 1.7585 | 0 |  | 1.5
2017-07-15 | 17:45 | 1.753 | 0 | 0 | 1.5 | 25
2017-07-15 | 17:45 | 1.753 | 0 |  | 1.5 |  | 80.621
2017-07-15 | 17:50 | 1.7491 | 0 |  | 1.5
2017-07-15 | 17:55 | 1.785 | 0 |  | 1.5
2017-07-15 | 18:00 | 1.7748 | 0 | 0 | 1.5 | 25
2017-07-15 | 18:00 | 1.7748 | 0 |  | 1.5 |  | 80.0141
2017-07-15 | 18:05 | 1.76 | 0 |  | 1.5
2017-07-15 | 18:10 | 1.7912 | 0 |  | 1.5
2017-07-15 | 18:15 | 1.7764 | 0 | 0 | 1.5 | 25
2017-07-15 | 18:15 | 1.7764 | 0 |  | 1.5 |  | 79.5615
2017-07-15 | 18:20 | 1.7709 | 0 |  | 1.5
2017-07-15 | 18:25 | 1.7624 | 0 |  | 1.5
2017-07-15 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-15 | 18:30 | 1.7585 | 0 |  | 1.5 |  | 79.3186
2017-07-15 | 18:35 | 1.7397 | 0 |  | 1.5
2017-07-15 | 18:40 | 1.7709 | 0 |  | 1.5
2017-07-15 | 18:45 | 1.7678 | 0 | 0 | 1.5 | 25.0005
2017-07-15 | 18:45 | 1.7678 | 0 |  | 1.5 |  | 79.5253
2017-07-15 | 18:50 | 1.7694 | 0 |  | 1.5
2017-07-15 | 18:55 | 1.7397 | 0 |  | 1.5
2017-07-15 | 19:00 | 1.7569 | 0 | 0 | 1.5 | 25
2017-07-15 | 19:00 | 1.7569 | 0 |  | 1.5 |  | 79.4819
2017-07-15 | 19:05 | 1.7522 | 0 |  | 1.5
2017-07-15 | 19:10 | 1.7483 | 0 |  | 1.5
2017-07-15 | 19:15 | 1.7655 | 0 | 0 | 1.5 | 25
2017-07-15 | 19:15 | 1.7655 | 0 |  | 1.5 |  | 79.4172
2017-07-15 | 19:20 | 1.7452 | 0 |  | 1.5
2017-07-15 | 19:25 | 1.7351 | 0 |  | 1.5
2017-07-15 | 19:30 | 1.7343 | 0 | 0 | 1.5 | 25
2017-07-15 | 19:30 | 1.7343 | 0 |  | 1.5 |  | 79.6292
2017-07-15 | 19:35 | 1.7608 | 0 |  | 1.5
2017-07-15 | 19:40 | 1.7374 | 0 |  | 1.5
2017-07-15 | 19:45 | 1.7553 | 0 | 0 | 1.5 | 25
2017-07-15 | 19:45 | 1.7553 | 0 |  | 1.5 |  | 79.7745
2017-07-15 | 19:50 | 1.767 | 0 |  | 1.5
2017-07-15 | 19:55 | 1.7491 | 0 |  | 1.5
2017-07-15 | 20:00 | 1.7429 | 0 | 0 | 1.5 | 25
2017-07-15 | 20:00 | 1.7429 | 0 |  | 1.5 |  | 79.6768
2017-07-15 | 20:05 | 1.7608 | 0 |  | 1.5
2017-07-15 | 20:10 | 1.7569 | 0 |  | 1.5
2017-07-15 | 20:15 | 1.7499 | 0 | 0 | 1.5 | 25
2017-07-15 | 20:15 | 1.7499 | 0 |  | 1.5 |  | 79.513
2017-07-15 | 20:20 | 1.7592 | 0 |  | 1.5
2017-07-15 | 20:25 | 1.7436 | 0 |  | 1.5
2017-07-15 | 20:30 | 1.7928 | 0 | 0 | 1.5 | 25
2017-07-15 | 20:30 | 1.7928 | 0 |  | 1.5 |  | 79.2173
2017-07-15 | 20:35 | 1.7592 | 0 |  | 1.5
2017-07-15 | 20:40 | 1.7522 | 0 |  | 1.5
2017-07-15 | 20:45 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-15 | 20:45 | 1.7585 | 0 |  | 1.5 |  | 78.9335
2017-07-15 | 20:50 | 1.7577 | 0 |  | 1.5
2017-07-15 | 20:55 | 1.7748 | 0 |  | 1.5
2017-07-15 | 21:00 | 1.7608 | 0 | 0 | 1.5 | 25
2017-07-15 | 21:00 | 1.7608 | 0 |  | 1.5 |  | 0
2017-07-15 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-15 | 21:10 | -0.10496 | 0 |  | 1.5
2017-07-15 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-15 | 21:15 | -0.10496 | 0 |  | 1.5 |  | 0
2017-07-15 | 21:20 | -0.10496 | 0 |  | 1.5
2017-07-15 | 21:25 | -0.10418 | 0 |  | 1.5
2017-07-15 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-15 | 21:30 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-15 | 21:35 | -0.10964 | 0 |  | 1.5
2017-07-15 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-15 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-15 | 21:45 | -0.10652 | 0 |  | 1.5 |  | 0
2017-07-15 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-15 | 21:55 | -0.1073 | 0 |  | 1.5
2017-07-15 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-15 | 22:00 | -0.1073 | 0 |  | 1.5 |  | 0
2017-07-15 | 22:05 | -0.10808 | 0 |  | 1.5
2017-07-15 | 22:10 | -0.10808 | 0 |  | 1.5
2017-07-15 | 22:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-15 | 22:15 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-15 | 22:20 | -0.10886 | 0 |  | 1.5
2017-07-15 | 22:25 | -0.10886 | 0 |  | 1.5
2017-07-15 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-15 | 22:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-15 | 22:35 | -0.10808 | 0 |  | 1.5
2017-07-15 | 22:40 | -0.10886 | 0 |  | 1.5
2017-07-15 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-15 | 22:45 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-15 | 22:50 | -0.10808 | 0 |  | 1.5
2017-07-15 | 22:55 | -0.10808 | 0 |  | 1.5
2017-07-15 | 23:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-15 | 23:00 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-15 | 23:05 | -0.1073 | 0 |  | 1.5
2017-07-15 | 23:10 | -0.10808 | 0 |  | 1.5
2017-07-15 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-15 | 23:15 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-15 | 23:20 | -0.10886 | 0 |  | 1.5
2017-07-15 | 23:25 | -0.10808 | 0 |  | 1.5
2017-07-15 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-15 | 23:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-07-15 | 23:35 | -0.10808 | 0 |  | 1.5
2017-07-15 | 23:40 | -0.10808 | 0 |  | 1.5
2017-07-15 | 23:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-15 | 23:45 | -0.10886 | 0 |  | 1.5 |  | 0
2017-07-15 | 23:50 | -0.10808 | 0 |  | 1.5
2017-07-15 | 23:55 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-16 | 0:00 | -0.10964 | 0 |  | 1.5 |  | 0
2017-07-16 | 0:05 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:10 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 0:20 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:25 | -0.10808 | 0 |  | 1.5
2017-07-16 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 0:35 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:40 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 0:50 | -0.10886 | 0 |  | 1.5
2017-07-16 | 0:55 | -0.10886 | 0 |  | 1.5
2017-07-16 | 1:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 1:05 | -0.10808 | 0 |  | 1.5
2017-07-16 | 1:10 | -0.10886 | 0 |  | 1.5
2017-07-16 | 1:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 1:20 | -0.1112 | 0 |  | 1.5
2017-07-16 | 1:25 | -0.1112 | 0 |  | 1.5
2017-07-16 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 1:35 | -0.1112 | 0 |  | 1.5
2017-07-16 | 1:40 | -0.1112 | 0 |  | 1.5
2017-07-16 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 1:50 | -0.1112 | 0 |  | 1.5
2017-07-16 | 1:55 | -0.1112 | 0 |  | 1.5
2017-07-16 | 2:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 2:05 | -0.1112 | 0 |  | 1.5
2017-07-16 | 2:10 | -0.1112 | 0 |  | 1.5
2017-07-16 | 2:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 2:20 | -0.11198 | 0 |  | 1.5
2017-07-16 | 2:25 | -0.1112 | 0 |  | 1.5
2017-07-16 | 2:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 2:35 | -0.11198 | 0 |  | 1.5
2017-07-16 | 2:40 | -0.11198 | 0 |  | 1.5
2017-07-16 | 2:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-16 | 2:55 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 3:05 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:10 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 3:20 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:25 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:40 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 3:50 | -0.1112 | 0 |  | 1.5
2017-07-16 | 3:55 | -0.11198 | 0 |  | 1.5
2017-07-16 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 4:05 | -0.1112 | 0 |  | 1.5
2017-07-16 | 4:10 | -0.11198 | 0 |  | 1.5
2017-07-16 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-16 | 4:25 | -0.1112 | 0 |  | 1.5
2017-07-16 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 4:35 | -0.1112 | 0 |  | 1.5
2017-07-16 | 4:40 | -0.11198 | 0 |  | 1.5
2017-07-16 | 4:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 4:50 | -0.1112 | 0 |  | 1.5
2017-07-16 | 4:55 | -0.1112 | 0 |  | 1.5
2017-07-16 | 5:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 5:05 | 2.4987 | 5.7506 |  | 10
2017-07-16 | 5:10 | 2.2046 | 9.6611 |  | 10
2017-07-16 | 5:15 | 2.104 | 9.352 | 1 | 10 | 96.0194 | 86.7885
2017-07-16 | 5:20 | 1.9893 | 9.0589 |  | 10
2017-07-16 | 5:25 | 1.9301 | 8.2105 |  | 10
2017-07-16 | 5:30 | 1.884 | 8.0026 | 1 | 10 | 82.9174 | 81.0811
2017-07-16 | 5:35 | 1.8786 | 7.2625 |  | 10
2017-07-16 | 5:40 | 1.8482 | 6.7513 |  | 10
2017-07-16 | 5:45 | 1.8287 | 6.4684 | 1 | 10 | 68.0858 | 78.3721
2017-07-16 | 5:50 | 1.8146 | 6.0624 |  | 10
2017-07-16 | 5:55 | 1.8068 | 6.0396 |  | 10
2017-07-16 | 6:00 | 1.7624 | 5.9099 | 1 | 10 | 62.5404 | 77.0283
2017-07-16 | 6:05 | 1.7631 | 6.2112 |  | 10
2017-07-16 | 6:10 | 1.746 | 6.4973 |  | 10
2017-07-16 | 6:15 | 1.76 | 6.5057 | 1 | 10 | 68.0764 | 76.6387
2017-07-16 | 6:20 | 1.7444 | 6.7651 |  | 10
2017-07-16 | 6:25 | 1.7429 | 6.5485 |  | 10
2017-07-16 | 6:30 | 1.7436 | 6.7551 | 1 | 10 | 70.4099 | 76.774
2017-07-16 | 6:35 | 1.7865 | 6.54 |  | 10
2017-07-16 | 6:40 | 1.7811 | 6.4135 |  | 10
2017-07-16 | 6:45 | 1.7873 | 6.3967 | 1 | 10 | 67.258 | 76.2431
2017-07-16 | 6:50 | 1.7678 | 6.1795 |  | 10
2017-07-16 | 6:55 | 1.7694 | 6.3395 |  | 10
2017-07-16 | 7:00 | 1.7592 | 6.1078 | 1 | 10 | 64.489 | 75.7625
2017-07-16 | 7:05 | 1.7475 | 6.1118 |  | 10
2017-07-16 | 7:10 | 1.7725 | 6.0762 |  | 10
2017-07-16 | 7:15 | 1.7522 | 6.0703 | 1 | 10 | 63.7282 | 75.4544
2017-07-16 | 7:20 | 1.7631 | 6.0758 |  | 10
2017-07-16 | 7:25 | 1.7655 | 5.781 |  | 10
2017-07-16 | 7:30 | 1.7335 | 5.8134 | 1 | 10 | 61.3467 | 75.2839
2017-07-16 | 7:35 | 1.7491 | 5.702 |  | 10
2017-07-16 | 7:40 | 1.767 | 5.6702 |  | 10
2017-07-16 | 7:45 | 1.767 | 5.8559 | 1 | 10 | 61.8617 | 75.1997
2017-07-16 | 7:50 | 1.7756 | 5.6006 |  | 10
2017-07-16 | 7:55 | 1.7663 | 5.7496 |  | 10
2017-07-16 | 8:00 | 1.7647 | 5.6647 | 1 | 10 | 60.0923 | 75.0655
2017-07-16 | 8:05 | 1.7678 | 5.6209 |  | 10
2017-07-16 | 8:10 | 1.7546 | 5.6983 |  | 10
2017-07-16 | 8:15 | 1.7249 | 5.6298 | 1 | 10 | 59.5475 | 75.0355
2017-07-16 | 8:20 | 1.76 | 5.9078 |  | 10
2017-07-16 | 8:25 | 1.76 | 5.5788 |  | 10
2017-07-16 | 8:30 | 1.7569 | 5.7071 | 1 | 10 | 60.2387 | 75.0512
2017-07-16 | 8:35 | 1.7577 | 5.616 |  | 10
2017-07-16 | 8:40 | 1.739 | 5.4852 |  | 10
2017-07-16 | 8:45 | 1.7195 | 5.793 | 1 | 10 | 61.1863 | 75.1751
2017-07-16 | 8:50 | 1.7452 | 5.7663 |  | 10
2017-07-16 | 8:55 | 1.7421 | 6.103 |  | 10
2017-07-16 | 9:00 | 1.7514 | 6.0154 | 1 | 10 | 63.5259 | 75.2423
2017-07-16 | 9:05 | 1.7694 | 5.9143 |  | 10
2017-07-16 | 9:10 | 1.7546 | 5.8373 |  | 10
2017-07-16 | 9:15 | 1.7444 | 5.8647 | 1 | 10 | 61.8784 | 75.3038
2017-07-16 | 9:20 | 1.7405 | 6.2817 |  | 10
2017-07-16 | 9:25 | 1.7499 | 6.1237 |  | 10
2017-07-16 | 9:30 | 1.7514 | 6.591 | 1 | 10 | 68.7344 | 75.4319
2017-07-16 | 9:35 | 1.7218 | 6.5333 |  | 10
2017-07-16 | 9:40 | 1.5018 | 5.2417 |  | 1.5
2017-07-16 | 9:45 | 1.6594 | 4.1187 | 0 | 1.5 | 45.2573 | 78.567
2017-07-16 | 9:50 | 1.7382 | 2.9187 |  | 1.5
2017-07-16 | 9:55 | 1.7553 | 0.28964 |  | 1.5
2017-07-16 | 10:00 | 1.7475 | 0 | 0 | 1.5 | 25 | 79.0355
2017-07-16 | 10:05 | 1.7124 | 0 |  | 1.5
2017-07-16 | 10:10 | 1.7358 | 0 |  | 1.5
2017-07-16 | 10:15 | 1.7709 | 0 | 0 | 1.5 | 25 | 79.3829
2017-07-16 | 10:20 | 1.7592 | 0 |  | 1.5
2017-07-16 | 10:25 | 1.753 | 0 |  | 1.5
2017-07-16 | 10:30 | 1.7429 | 0 | 0 | 1.5 | 25 | 79.2798
2017-07-16 | 10:35 | 1.7577 | 0 |  | 1.5
2017-07-16 | 10:40 | 1.746 | 0 |  | 1.5
2017-07-16 | 10:45 | 1.7444 | 0 | 0 | 1.5 | 25 | 79.0477
2017-07-16 | 10:50 | 1.7382 | 0 |  | 1.5
2017-07-16 | 10:55 | 1.7655 | 0 |  | 1.5
2017-07-16 | 11:00 | 1.7234 | 0 | 0 | 1.5 | 25 | 79.0323
2017-07-16 | 11:05 | 1.76 | 0 |  | 1.5
2017-07-16 | 11:10 | 1.7514 | 0 |  | 1.5
2017-07-16 | 11:15 | 1.746 | 0 | 0 | 1.5 | 25 | 78.9071
2017-07-16 | 11:20 | 1.7647 | 0 |  | 1.5
2017-07-16 | 11:25 | 1.7421 | 0 |  | 1.5
2017-07-16 | 11:30 | 1.7304 | 0 | 0 | 1.5 | 25 | 78.8108
2017-07-16 | 11:35 | 1.7803 | 0 |  | 1.5
2017-07-16 | 11:40 | 1.7397 | 0 |  | 1.5
2017-07-16 | 11:45 | 1.7148 | 0 | 0 | 1.5 | 25 | 78.9519
2017-07-16 | 11:50 | 1.728 | 0 |  | 1.5
2017-07-16 | 11:55 | 1.7499 | 0 |  | 1.5
2017-07-16 | 12:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.2228
2017-07-16 | 12:05 | 1.7249 | 0 |  | 1.5
2017-07-16 | 12:10 | 1.7499 | 0 |  | 1.5
2017-07-16 | 12:15 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.2935
2017-07-16 | 12:20 | 1.728 | 0 |  | 1.5
2017-07-16 | 12:25 | 1.7592 | 0 |  | 1.5
2017-07-16 | 12:30 | 1.7265 | 0 | 0 | 1.5 | 25 | 79.7277
2017-07-16 | 12:35 | 1.7351 | 0 |  | 1.5
2017-07-16 | 12:40 | 1.7499 | 0 |  | 1.5
2017-07-16 | 12:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 79.856
2017-07-16 | 12:50 | 1.7546 | 0 |  | 1.5
2017-07-16 | 12:55 | 1.7507 | 0 |  | 1.5
2017-07-16 | 13:00 | 1.7343 | 0 | 0 | 1.5 | 25 | 79.778
2017-07-16 | 13:05 | 1.7514 | 0 |  | 1.5
2017-07-16 | 13:10 | 1.7078 | 0 |  | 1.5
2017-07-16 | 13:15 | 1.7327 | 0 | 0 | 1.5 | 25 | 80.2475
2017-07-16 | 13:20 | 1.7241 | 0 |  | 1.5
2017-07-16 | 13:25 | 1.7655 | 0 |  | 1.5
2017-07-16 | 13:30 | 1.753 | 0 | 0 | 1.5 | 25 | 80.34
2017-07-16 | 13:35 | 1.7592 | 0 |  | 1.5
2017-07-16 | 13:40 | 1.7624 | 0 |  | 1.5
2017-07-16 | 13:45 | 1.753 | 0 | 0 | 1.5 | 25 | 80.1716
2017-07-16 | 13:50 | 1.7429 | 0 |  | 1.5
2017-07-16 | 13:55 | 1.7335 | 0 |  | 1.5
2017-07-16 | 14:00 | 1.7569 | 0 | 0 | 1.5 | 25 | 80.2392
2017-07-16 | 14:05 | 1.753 | 0 |  | 1.5
2017-07-16 | 14:10 | 1.7234 | 0 |  | 1.5
2017-07-16 | 14:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 80.169
2017-07-16 | 14:20 | 1.728 | 0 |  | 1.5
2017-07-16 | 14:25 | 1.739 | 0 |  | 1.5
2017-07-16 | 14:30 | 1.7265 | 0 | 0 | 1.5 | 25 | 80.5003
2017-07-16 | 14:35 | 1.76 | 0 |  | 1.5
2017-07-16 | 14:40 | 1.7296 | 0 |  | 1.5
2017-07-16 | 14:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 80.8339
2017-07-16 | 14:50 | 1.7561 | 0 |  | 1.5
2017-07-16 | 14:55 | 1.7397 | 0 |  | 1.5
2017-07-16 | 15:00 | 1.7288 | 0 | 0 | 1.5 | 25 | 81.0827
2017-07-16 | 15:05 | 1.7468 | 0 |  | 1.5
2017-07-16 | 15:10 | 1.7257 | 0 |  | 1.5
2017-07-16 | 15:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 81.2987
2017-07-16 | 15:20 | 1.7312 | 0 |  | 1.5
2017-07-16 | 15:25 | 1.7444 | 0 |  | 1.5
2017-07-16 | 15:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 81.4746
2017-07-16 | 15:35 | 1.7616 | 0 |  | 1.5
2017-07-16 | 15:40 | 1.753 | 0 |  | 1.5
2017-07-16 | 15:45 | 1.7569 | 0 | 0 | 1.5 | 25 | 81.4385
2017-07-16 | 15:50 | 1.7421 | 0 |  | 1.5
2017-07-16 | 15:55 | 1.7444 | 0 |  | 1.5
2017-07-16 | 16:00 | 1.7514 | 0 | 0 | 1.5 | 25 | 81.3057
2017-07-16 | 16:05 | 1.7483 | 0 |  | 1.5
2017-07-16 | 16:10 | 1.7561 | 0 |  | 1.5
2017-07-16 | 16:15 | 1.753 | 0 | 0 | 1.5 | 25 | 81.2365
2017-07-16 | 16:20 | 1.7468 | 0 |  | 1.5
2017-07-16 | 16:25 | 1.7444 | 0 |  | 1.5
2017-07-16 | 16:30 | 1.7702 | 0 | 0 | 1.5 | 25 | 81.0478
2017-07-16 | 16:35 | 1.7577 | 0 |  | 1.5
2017-07-16 | 16:40 | 1.8053 | 0 |  | 1.5
2017-07-16 | 16:45 | 1.7265 | 0 | 0 | 1.5 | 25 | 81.1206
2017-07-16 | 16:50 | 1.7546 | 0 |  | 1.5
2017-07-16 | 16:55 | 1.7678 | 0 |  | 1.5
2017-07-16 | 17:00 | 1.7117 | 0 | 0 | 1.5 | 25 | 81.2203
2017-07-16 | 17:05 | 1.7397 | 0 |  | 1.5
2017-07-16 | 17:10 | 1.7756 | 0 |  | 1.5
2017-07-16 | 17:15 | 1.7694 | 0 | 0 | 1.5 | 25 | 80.8034
2017-07-16 | 17:20 | 1.7733 | 0 |  | 1.5
2017-07-16 | 17:25 | 1.753 | 0 |  | 1.5
2017-07-16 | 17:30 | 1.7702 | 0 | 0 | 1.5 | 25 | 80.2575
2017-07-16 | 17:35 | 1.7592 | 0 |  | 1.5
2017-07-16 | 17:40 | 1.7975 | 0 |  | 1.5
2017-07-16 | 17:45 | 1.76 | 0 | 0 | 1.5 | 25 | 79.9126
2017-07-16 | 17:50 | 1.7772 | 0 |  | 1.5
2017-07-16 | 17:55 | 1.7546 | 0 |  | 1.5
2017-07-16 | 18:00 | 1.746 | 0 | 0 | 1.5 | 25 | 79.4435
2017-07-16 | 18:05 | 1.7733 | 0 |  | 1.5
2017-07-16 | 18:10 | 1.7694 | 0 |  | 1.5
2017-07-16 | 18:15 | 1.753 | 0 | 0 | 1.5 | 25 | 79.0495
2017-07-16 | 18:20 | 1.7514 | 0 |  | 1.5
2017-07-16 | 18:25 | 1.7507 | 0 |  | 1.5
2017-07-16 | 18:30 | 1.7655 | 0 | 0 | 1.5 | 25 | 78.8866
2017-07-16 | 18:35 | 1.7569 | 0 |  | 1.5
2017-07-16 | 18:40 | 1.7429 | 0 |  | 1.5
2017-07-16 | 18:45 | 1.7429 | 0 | 0 | 1.5 | 25 | 78.7226
2017-07-16 | 18:50 | 1.7335 | 0 |  | 1.5
2017-07-16 | 18:55 | 1.7397 | 0 |  | 1.5
2017-07-16 | 19:00 | 1.7436 | 0 | 0 | 1.5 | 25 | 78.4792
2017-07-16 | 19:05 | 1.7608 | 0 |  | 1.5
2017-07-16 | 19:10 | 1.7468 | 0 |  | 1.5
2017-07-16 | 19:15 | 1.7358 | 0 | 0 | 1.5 | 25 | 78.3552
2017-07-16 | 19:20 | 1.7514 | 0 |  | 1.5
2017-07-16 | 19:25 | 1.7382 | 0 |  | 1.5
2017-07-16 | 19:30 | 1.7819 | 0 | 0 | 1.5 | 25 | 78.1433
2017-07-16 | 19:35 | 1.7366 | 0 |  | 1.5
2017-07-16 | 19:40 | 1.7499 | 0 |  | 1.5
2017-07-16 | 19:45 | 1.7382 | 0 | 0 | 1.5 | 25 | 78.074
2017-07-16 | 19:50 | 1.753 | 0 |  | 1.5
2017-07-16 | 19:55 | 1.7257 | 0 |  | 1.5
2017-07-16 | 20:00 | 1.739 | 0 | 0 | 1.5 | 25 | 78.097
2017-07-16 | 20:05 | 1.7421 | 0 |  | 1.5
2017-07-16 | 20:10 | 1.7429 | 0 |  | 1.5
2017-07-16 | 20:15 | 1.7429 | 0 | 0 | 1.5 | 25 | 77.9448
2017-07-16 | 20:20 | 1.7631 | 0 |  | 1.5
2017-07-16 | 20:25 | 1.767 | 0 |  | 1.5
2017-07-16 | 20:30 | 1.7561 | 0 | 0 | 1.5 | 25 | 77.7537
2017-07-16 | 20:35 | 1.7678 | 0 |  | 1.5
2017-07-16 | 20:40 | 1.7452 | 0 |  | 1.5
2017-07-16 | 20:45 | 1.7538 | 0 | 0 | 1.5 | 25 | 77.5998
2017-07-16 | 20:50 | 1.7553 | 0 |  | 1.5
2017-07-16 | 20:55 | 1.739 | 0 |  | 1.5
2017-07-16 | 21:00 | 1.7803 | 0 | 0 | 1.5 | 25 | 77.7505
2017-07-16 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-16 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-16 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-16 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-16 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-16 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-16 | 21:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-16 | 21:55 | -0.1073 | 0 |  | 1.5
2017-07-16 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 22:05 | -0.1073 | 0 |  | 1.5
2017-07-16 | 22:10 | -0.10808 | 0 |  | 1.5
2017-07-16 | 22:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 22:20 | -0.10808 | 0 |  | 1.5
2017-07-16 | 22:25 | -0.10808 | 0 |  | 1.5
2017-07-16 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 22:35 | -0.10808 | 0 |  | 1.5
2017-07-16 | 22:40 | -0.10808 | 0 |  | 1.5
2017-07-16 | 22:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 22:50 | -0.10808 | 0 |  | 1.5
2017-07-16 | 22:55 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 23:05 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:10 | -0.10886 | 0 |  | 1.5
2017-07-16 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 23:20 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:25 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 23:35 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:40 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-16 | 23:50 | -0.10808 | 0 |  | 1.5
2017-07-16 | 23:55 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 0:05 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:10 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 0:20 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:25 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 0:35 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:40 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 0:50 | -0.10808 | 0 |  | 1.5
2017-07-17 | 0:55 | -0.10808 | 0 |  | 1.5
2017-07-17 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 1:05 | -0.1073 | 0 |  | 1.5
2017-07-17 | 1:10 | -0.10808 | 0 |  | 1.5
2017-07-17 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 1:20 | -0.1112 | 0 |  | 1.5
2017-07-17 | 1:25 | -0.1112 | 0 |  | 1.5
2017-07-17 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 1:35 | -0.1112 | 0 |  | 1.5
2017-07-17 | 1:40 | -0.1112 | 0 |  | 1.5
2017-07-17 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-17 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-17 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-17 | 2:10 | -0.1112 | 0 |  | 1.5
2017-07-17 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-17 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-17 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 2:35 | -0.11042 | 0 |  | 1.5
2017-07-17 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-17 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-17 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-17 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-17 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-17 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-17 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-17 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-17 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-17 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-17 | 4:40 | -0.1112 | 0 |  | 1.5
2017-07-17 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 4:50 | -0.11042 | 0 |  | 1.5
2017-07-17 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-17 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 5:05 | 2.7826 | 4.7836 |  | 10
2017-07-17 | 5:10 | 2.4449 | 9.5505 |  | 10
2017-07-17 | 5:15 | 1.9589 | 8.0053 | 1 | 7.7172 | 83.9993 | 84.1202
2017-07-17 | 5:20 | 2.0034 | 6.6246 |  | 8.1259
2017-07-17 | 5:25 | 1.9605 | 5.756 |  | 8.6633
2017-07-17 | 5:30 | 1.909 | 5.5905 | 1 | 9.3174 | 58.9361 | 78.5176
2017-07-17 | 5:35 | 1.8443 | 5.4085 |  | 8.4282
2017-07-17 | 5:40 | 1.8053 | 5.0959 |  | 8.5686
2017-07-17 | 5:45 | 1.8271 | 5.0186 | 1 | 10 | 53.643 | 76.2862
2017-07-17 | 5:50 | 1.7865 | 4.8261 |  | 9.6417
2017-07-17 | 5:55 | 1.7624 | 4.9036 |  | 10
2017-07-17 | 6:00 | 1.7499 | 4.7687 | 1 | 10 | 51.1467 | 75.3897
2017-07-17 | 6:05 | 1.7616 | 5.0913 |  | 9.9956
2017-07-17 | 6:10 | 1.7608 | 5.3807 |  | 10
2017-07-17 | 6:15 | 1.7694 | 5.245 | 1 | 10 | 55.5865 | 75.1103
2017-07-17 | 6:20 | 1.7686 | 5.5743 |  | 10
2017-07-17 | 6:25 | 1.7639 | 5.3784 |  | 10
2017-07-17 | 6:30 | 1.767 | 5.3578 | 1 | 10 | 56.7035 | 74.9955
2017-07-17 | 6:35 | 1.7436 | 5.4589 |  | 10
2017-07-17 | 6:40 | 1.7436 | 5.1562 |  | 10
2017-07-17 | 6:45 | 1.7397 | 5.3079 | 1 | 10 | 56.2703 | 75.0174
2017-07-17 | 6:50 | 1.7452 | 4.7418 |  | 10
2017-07-17 | 6:55 | 1.76 | 4.9501 |  | 10
2017-07-17 | 7:00 | 1.7132 | 4.8428 | 1 | 10 | 51.6365 | 74.9546
2017-07-17 | 7:05 | 1.7062 | 4.4699 |  | 10
2017-07-17 | 7:10 | 1.7577 | 4.6997 |  | 10
2017-07-17 | 7:15 | 1.7452 | 4.4807 | 1 | 10 | 47.9161 | 74.7655
2017-07-17 | 7:20 | 1.7561 | 4.4058 |  | 10
2017-07-17 | 7:25 | 1.7741 | 4.1152 |  | 10
2017-07-17 | 7:30 | 1.7787 | 4.0396 | 1 | 10 | 44.3071 | 74.3627
2017-07-17 | 7:35 | 1.7468 | 4.0601 |  | 10
2017-07-17 | 7:40 | 1.753 | 3.9837 |  | 10
2017-07-17 | 7:45 | 1.7374 | 3.98 | 1 | 10 | 42.8585 | 74.2989
2017-07-17 | 7:50 | 1.7764 | 3.7417 |  | 10
2017-07-17 | 7:55 | 1.7351 | 3.4053 |  | 10
2017-07-17 | 8:00 | 1.7452 | 3.0398 | 1 | 10 | 34.1942 | 74.2813
2017-07-17 | 8:05 | 1.7257 | 2.9568 |  | 10
2017-07-17 | 8:10 | 1.7257 | 3.3442 |  | 10
2017-07-17 | 8:15 | 1.7163 | 4.0906 | 1 | 10 | 43.4197 | 74.5486
2017-07-17 | 8:20 | 1.7273 | 4.5958 |  | 10
2017-07-17 | 8:25 | 1.7514 | 4.8006 |  | 10
2017-07-17 | 8:30 | 1.739 | 5.1696 | 1 | 10 | 54.302 | 74.9526
2017-07-17 | 8:35 | 1.7327 | 5.255 |  | 10
2017-07-17 | 8:40 | 1.7546 | 5.4795 |  | 10
2017-07-17 | 8:45 | 1.7577 | 5.8014 | 1 | 10 | 61.3043 | 75.1884
2017-07-17 | 8:50 | 1.714 | 6.0199 |  | 10
2017-07-17 | 8:55 | 1.7327 | 5.7305 |  | 10
2017-07-17 | 9:00 | 1.7686 | 5.2647 | 1 | 10 | 56.4 | 75.4204
2017-07-17 | 9:05 | 1.7483 | 5.1593 |  | 10
2017-07-17 | 9:10 | 1.7132 | 5.9862 |  | 10
2017-07-17 | 9:15 | 1.7163 | 6.028 | 1 | 10 | 63.3 | 75.9933
2017-07-17 | 9:20 | 1.7608 | 5.618 |  | 10
2017-07-17 | 9:25 | 1.7241 | 5.8707 |  | 10
2017-07-17 | 9:30 | 1.7733 | 5.5133 | 1 | 10 | 58.2864 | 76.118
2017-07-17 | 9:35 | 1.7397 | 5.2722 |  | 10
2017-07-17 | 9:40 | 1.7351 | 5.2449 |  | 10
2017-07-17 | 9:45 | 1.6625 | 6.0456 | 1 | 10 | 63.6666 | 76.4863
2017-07-17 | 9:50 | 1.7046 | 5.9487 |  | 10
2017-07-17 | 9:55 | 1.7382 | 5.3339 |  | 10
2017-07-17 | 10:00 | 1.7444 | 5.0145 | 1 | 10 | 52.9932 | 77.2294
2017-07-17 | 10:05 | 1.5003 | 3.7761 |  | 1.5
2017-07-17 | 10:10 | 1.6477 | 3.0932 |  | 1.5
2017-07-17 | 10:15 | 1.6984 | 2.3981 | 0 | 1.5 | 28.1755 | 80.5051
2017-07-17 | 10:20 | 1.7249 | 1.7877 |  | 1.5
2017-07-17 | 10:25 | 1.7085 | 0 |  | 1.5
2017-07-17 | 10:30 | 1.6945 | 0 | 0 | 1.5 | 25 | 81.6738
2017-07-17 | 10:35 | 1.7093 | 0 |  | 1.5
2017-07-17 | 10:40 | 1.7226 | 0 |  | 1.5
2017-07-17 | 10:45 | 1.7296 | 0 | 0 | 1.5 | 25 | 82.3389
2017-07-17 | 10:50 | 1.7491 | 0 |  | 1.5
2017-07-17 | 10:55 | 1.7366 | 0 |  | 1.5
2017-07-17 | 11:00 | 1.7382 | 0 | 0 | 1.5 | 25 | 82.7603
2017-07-17 | 11:05 | 1.7117 | 0 |  | 1.5
2017-07-17 | 11:10 | 1.7312 | 0 |  | 1.5
2017-07-17 | 11:15 | 1.7343 | 0 | 0 | 1.5 | 25 | 83.258
2017-07-17 | 11:20 | 1.7195 | 0 |  | 1.5
2017-07-17 | 11:25 | 1.689 | 0 |  | 1.5
2017-07-17 | 11:30 | 1.7078 | 0 | 0 | 1.5 | 25 | 84.3281
2017-07-17 | 11:35 | 1.7109 | 0 |  | 1.5
2017-07-17 | 11:40 | 1.6992 | 0 |  | 1.5
2017-07-17 | 11:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 85.2331
2017-07-17 | 11:50 | 1.7218 | 0 |  | 1.5
2017-07-17 | 11:55 | 1.7631 | 0 |  | 1.5
2017-07-17 | 12:00 | 1.7085 | 0 | 0 | 1.5 | 25 | 85.6796
2017-07-17 | 12:05 | 1.7499 | 0 |  | 1.5
2017-07-17 | 12:10 | 1.7031 | 0 |  | 1.5
2017-07-17 | 12:15 | 1.7117 | 0 | 0 | 1.5 | 25 | 86.5489
2017-07-17 | 12:20 | 1.7156 | 0 |  | 1.5
2017-07-17 | 12:25 | 1.7156 | 0 |  | 1.5
2017-07-17 | 12:30 | 1.7756 | 0 | 0 | 1.5 | 25 | 86.8307
2017-07-17 | 12:35 | 1.7452 | 0 |  | 1.5
2017-07-17 | 12:40 | 1.7179 | 0 |  | 1.5
2017-07-17 | 12:45 | 1.728 | 0 | 0 | 1.5 | 25 | 86.9177
2017-07-17 | 12:50 | 1.7156 | 0 |  | 1.5
2017-07-17 | 12:55 | 1.661 | 0.019657 |  | 1.5
2017-07-17 | 13:00 | 1.7093 | 0 | 0 | 1.5 | 25 | 87.9487
2017-07-17 | 13:05 | 1.6992 | 0 |  | 1.5
2017-07-17 | 13:10 | 1.7187 | 0 |  | 1.5
2017-07-17 | 13:15 | 1.7312 | 0 | 0 | 1.5 | 25 | 88.9348
2017-07-17 | 13:20 | 1.7382 | 0 |  | 1.5
2017-07-17 | 13:25 | 1.7468 | 0 |  | 1.5
2017-07-17 | 13:30 | 1.7709 | 0 | 0 | 1.5 | 25 | 89.1425
2017-07-17 | 13:35 | 1.7553 | 0 |  | 1.5
2017-07-17 | 13:40 | 1.7639 | 0 |  | 1.5
2017-07-17 | 13:45 | 1.7639 | 0 | 0 | 1.5 | 25 | 88.9221
2017-07-17 | 13:50 | 1.7514 | 0 |  | 1.5
2017-07-17 | 13:55 | 1.7538 | 0 |  | 1.5
2017-07-17 | 14:00 | 1.7351 | 0 | 0 | 1.5 | 25 | 88.7251
2017-07-17 | 14:05 | 1.76 | 0 |  | 1.5
2017-07-17 | 14:10 | 1.7546 | 0 |  | 1.5
2017-07-17 | 14:15 | 1.7546 | 0 | 0 | 1.5 | 25 | 88.6632
2017-07-17 | 14:20 | 1.7436 | 0 |  | 1.5
2017-07-17 | 14:25 | 1.753 | 0 |  | 1.5
2017-07-17 | 14:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 88.5289
2017-07-17 | 14:35 | 1.7616 | 0 |  | 1.5
2017-07-17 | 14:40 | 1.7468 | 0 |  | 1.5
2017-07-17 | 14:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 88.6281
2017-07-17 | 14:50 | 1.7382 | 0 |  | 1.5
2017-07-17 | 14:55 | 1.7163 | 0 |  | 1.5
2017-07-17 | 15:00 | 1.7343 | 0 | 0 | 1.5 | 25 | 89.1397
2017-07-17 | 15:05 | 1.7148 | 0 |  | 1.5
2017-07-17 | 15:10 | 1.714 | 0 |  | 1.5
2017-07-17 | 15:15 | 1.6812 | 0 | 0 | 1.5 | 25 | 89.7902
2017-07-17 | 15:20 | 1.7132 | 0 |  | 1.5
2017-07-17 | 15:25 | 1.7608 | 0 |  | 1.5
2017-07-17 | 15:30 | 1.7764 | 0 | 0 | 1.5 | 25 | 89.9371
2017-07-17 | 15:35 | 1.7709 | 0 |  | 1.5
2017-07-17 | 15:40 | 1.7819 | 0 |  | 1.5
2017-07-17 | 15:45 | 1.7928 | 0 | 0 | 1.5 | 25 | 89.2591
2017-07-17 | 15:50 | 1.799 | 0 |  | 1.5
2017-07-17 | 15:55 | 1.7819 | 0 |  | 1.5
2017-07-17 | 16:00 | 1.7904 | 0 | 0 | 1.5 | 25 | 88.1962
2017-07-17 | 16:05 | 1.7733 | 0 |  | 1.5
2017-07-17 | 16:10 | 1.7858 | 0 |  | 1.5
2017-07-17 | 16:15 | 1.7811 | 0 | 0 | 1.5 | 25 | 87.4822
2017-07-17 | 16:20 | 1.7624 | 0 |  | 1.5
2017-07-17 | 16:25 | 1.7655 | 0 |  | 1.5
2017-07-17 | 16:30 | 1.7561 | 0 | 0 | 1.5 | 25 | 86.6539
2017-07-17 | 16:35 | 1.7577 | 0 |  | 1.5
2017-07-17 | 16:40 | 1.7678 | 0 |  | 1.5
2017-07-17 | 16:45 | 1.7748 | 0 | 0 | 1.5 | 25 | 86.0192
2017-07-17 | 16:50 | 1.7811 | 0 |  | 1.5
2017-07-17 | 16:55 | 1.7452 | 0 |  | 1.5
2017-07-17 | 17:00 | 1.76 | 0 | 0 | 1.5 | 25 | 85.5613
2017-07-17 | 17:05 | 1.76 | 0 |  | 1.5
2017-07-17 | 17:10 | 1.7795 | 0 |  | 1.5
2017-07-17 | 17:15 | 1.8107 | 0 | 0 | 1.5 | 25 | 84.9301
2017-07-17 | 17:20 | 1.7865 | 0 |  | 1.5
2017-07-17 | 17:25 | 1.7803 | 0 |  | 1.5
2017-07-17 | 17:30 | 1.7858 | 0 | 0 | 1.5 | 25 | 83.8959
2017-07-17 | 17:35 | 1.7709 | 0 |  | 1.5
2017-07-17 | 17:40 | 1.7943 | 0 |  | 1.5
2017-07-17 | 17:45 | 1.785 | 0 | 0 | 1.5 | 25 | 82.9977
2017-07-17 | 17:50 | 1.7639 | 0 |  | 1.5
2017-07-17 | 17:55 | 1.7647 | 0 |  | 1.5
2017-07-17 | 18:00 | 1.7717 | 0 | 0 | 1.5 | 25 | 82.3869
2017-07-17 | 18:05 | 1.7819 | 0 |  | 1.5
2017-07-17 | 18:10 | 1.7748 | 0 |  | 1.5
2017-07-17 | 18:15 | 1.7631 | 0 | 0 | 1.5 | 25 | 81.6918
2017-07-17 | 18:20 | 1.7725 | 0 |  | 1.5
2017-07-17 | 18:25 | 1.7725 | 0 |  | 1.5
2017-07-17 | 18:30 | 1.7616 | 0 | 0 | 1.5 | 25 | 81.201
2017-07-17 | 18:35 | 1.7561 | 0 |  | 1.5
2017-07-17 | 18:40 | 1.7483 | 0 |  | 1.5
2017-07-17 | 18:45 | 1.7717 | 0 | 0 | 1.5 | 25 | 80.8314
2017-07-17 | 18:50 | 1.7592 | 0 |  | 1.5
2017-07-17 | 18:55 | 1.7647 | 0 |  | 1.5
2017-07-17 | 19:00 | 1.7655 | 0 | 0 | 1.5 | 25 | 80.6157
2017-07-17 | 19:05 | 1.7327 | 0 |  | 1.5
2017-07-17 | 19:10 | 1.7078 | 0 |  | 1.5
2017-07-17 | 19:15 | 1.767 | 0 | 0 | 1.5 | 25 | 80.7277
2017-07-17 | 19:20 | 1.7702 | 0 |  | 1.5
2017-07-17 | 19:25 | 1.7585 | 0 |  | 1.5
2017-07-17 | 19:30 | 1.7327 | 0 | 0 | 1.5 | 25 | 80.6687
2017-07-17 | 19:35 | 1.7288 | 0 |  | 1.5
2017-07-17 | 19:40 | 1.7374 | 0 |  | 1.5
2017-07-17 | 19:45 | 1.689 | 0 | 0 | 1.5 | 25 | 81.0684
2017-07-17 | 19:50 | 1.7296 | 0 |  | 1.5
2017-07-17 | 19:55 | 1.7491 | 0 |  | 1.5
2017-07-17 | 20:00 | 1.714 | 0 | 0 | 1.5 | 25 | 81.3009
2017-07-17 | 20:05 | 1.7179 | 0 |  | 1.5
2017-07-17 | 20:10 | 1.7195 | 0 |  | 1.5
2017-07-17 | 20:15 | 1.7569 | 0 | 0 | 1.5 | 25 | 81.3068
2017-07-17 | 20:20 | 1.7257 | 0 |  | 1.5
2017-07-17 | 20:25 | 1.7382 | 0 |  | 1.5
2017-07-17 | 20:30 | 1.7234 | 0 | 0 | 1.5 | 25 | 81.3628
2017-07-17 | 20:35 | 1.7507 | 0 |  | 1.5
2017-07-17 | 20:40 | 1.7499 | 0 |  | 1.5
2017-07-17 | 20:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 81.3167
2017-07-17 | 20:50 | 1.7429 | 0 |  | 1.5
2017-07-17 | 20:55 | 1.7351 | 0 |  | 1.5
2017-07-17 | 21:00 | 1.7374 | 0 | 0 | 1.5 | 25 | 81.2511
2017-07-17 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-17 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-17 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-17 | 21:25 | -0.1073 | 0 |  | 1.5
2017-07-17 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 21:35 | -0.1073 | 0 |  | 1.5
2017-07-17 | 21:40 | -0.1073 | 0 |  | 1.5
2017-07-17 | 21:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 21:50 | -0.10808 | 0 |  | 1.5
2017-07-17 | 21:55 | -0.10808 | 0 |  | 1.5
2017-07-17 | 22:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 22:05 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:10 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 22:20 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:25 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 22:35 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:40 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 22:50 | -0.10886 | 0 |  | 1.5
2017-07-17 | 22:55 | -0.10886 | 0 |  | 1.5
2017-07-17 | 23:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 23:05 | -0.10886 | 0 |  | 1.5
2017-07-17 | 23:10 | -0.10886 | 0 |  | 1.5
2017-07-17 | 23:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 23:20 | -0.10886 | 0 |  | 1.5
2017-07-17 | 23:25 | -0.10808 | 0 |  | 1.5
2017-07-17 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 23:35 | -0.10808 | 0 |  | 1.5
2017-07-17 | 23:40 | -0.10808 | 0 |  | 1.5
2017-07-17 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-17 | 23:50 | -0.10808 | 0 |  | 1.5
2017-07-17 | 23:55 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 0:05 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:10 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 0:20 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:25 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 0:35 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:40 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 0:50 | -0.10808 | 0 |  | 1.5
2017-07-18 | 0:55 | -0.10808 | 0 |  | 1.5
2017-07-18 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 1:05 | -0.10808 | 0 |  | 1.5
2017-07-18 | 1:10 | -0.10808 | 0 |  | 1.5
2017-07-18 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-18 | 1:25 | -0.1112 | 0 |  | 1.5
2017-07-18 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 1:35 | -0.1112 | 0 |  | 1.5
2017-07-18 | 1:40 | -0.11042 | 0 |  | 1.5
2017-07-18 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-18 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-18 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-18 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-18 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-18 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-18 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 2:35 | -0.1112 | 0 |  | 1.5
2017-07-18 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-18 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 2:50 | -0.1112 | 0 |  | 1.5
2017-07-18 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-18 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-18 | 3:10 | -0.1112 | 0 |  | 1.5
2017-07-18 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-18 | 3:25 | -0.1112 | 0 |  | 1.5
2017-07-18 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-18 | 3:40 | -0.11042 | 0 |  | 1.5
2017-07-18 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-18 | 3:55 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 4:05 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:10 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 4:20 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:25 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 4:35 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:40 | -0.11588 | 0 |  | 1.5
2017-07-18 | 4:45 | -0.11666 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 4:50 | -0.1112 | 0 |  | 1.5
2017-07-18 | 4:55 | -0.1112 | 0 |  | 1.5
2017-07-18 | 5:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 5:05 | 2.5236 | 5.5643 |  | 10
2017-07-18 | 5:10 | 2.207 | 9.7753 |  | 10
2017-07-18 | 5:15 | 2.0751 | 9.0931 | 1 | 10 | 93.2544 | 86.6981
2017-07-18 | 5:20 | 1.9901 | 8.4094 |  | 10
2017-07-18 | 5:25 | 1.923 | 7.8458 |  | 10
2017-07-18 | 5:30 | 1.87 | 7.369 | 1 | 10 | 76.2755 | 81.4839
2017-07-18 | 5:35 | 1.8333 | 6.9915 |  | 10
2017-07-18 | 5:40 | 1.8045 | 6.6565 |  | 10
2017-07-18 | 5:45 | 1.7943 | 6.362 | 1 | 10 | 66.4609 | 79.3876
2017-07-18 | 5:50 | 1.7702 | 6.1928 |  | 10
2017-07-18 | 5:55 | 1.7655 | 6.0344 |  | 10
2017-07-18 | 6:00 | 1.7928 | 6.0893 | 1 | 10 | 63.4323 | 78.5153
2017-07-18 | 6:05 | 1.7725 | 6.1888 |  | 10
2017-07-18 | 6:10 | 1.7553 | 6.4502 |  | 10
2017-07-18 | 6:15 | 1.7553 | 6.6687 | 1 | 10 | 69.1167 | 78.2756
2017-07-18 | 6:20 | 1.7585 | 6.7334 |  | 10
2017-07-18 | 6:25 | 1.7702 | 6.8344 |  | 10
2017-07-18 | 6:30 | 1.7421 | 6.8151 | 1 | 10 | 70.5791 | 78.3508
2017-07-18 | 6:35 | 1.7374 | 6.7164 |  | 10
2017-07-18 | 6:40 | 1.7717 | 6.3572 |  | 10
2017-07-18 | 6:45 | 1.7616 | 6.2365 | 1 | 10 | 65.1848 | 77.9283
2017-07-18 | 6:50 | 1.7507 | 5.8539 |  | 10
2017-07-18 | 6:55 | 1.7787 | 6.0513 |  | 10
2017-07-18 | 7:00 | 1.7491 | 5.6073 | 1 | 10 | 58.4517 | 77.4949
2017-07-18 | 7:05 | 1.7561 | 5.6419 |  | 10
2017-07-18 | 7:10 | 1.7538 | 5.6064 |  | 10
2017-07-18 | 7:15 | 1.7382 | 5.7479 | 1 | 10 | 59.9378 | 77.4431
2017-07-18 | 7:20 | 1.7397 | 5.3612 |  | 10
2017-07-18 | 7:25 | 1.7436 | 5.0181 |  | 10
2017-07-18 | 7:30 | 1.7491 | 4.6827 | 1 | 10 | 49.8482 | 77.1331
2017-07-18 | 7:35 | 1.7741 | 4.1096 |  | 10
2017-07-18 | 7:40 | 1.7553 | 3.9412 |  | 10
2017-07-18 | 7:45 | 1.746 | 4.1294 | 1 | 10 | 43.903 | 76.9516
2017-07-18 | 7:50 | 1.7265 | 3.7205 |  | 10
2017-07-18 | 7:55 | 1.7507 | 3.692 |  | 10
2017-07-18 | 8:00 | 1.7616 | 3.6396 | 1 | 10 | 39.3872 | 76.7892
2017-07-18 | 8:05 | 1.7273 | 3.8764 |  | 10
2017-07-18 | 8:10 | 1.7421 | 4.8663 |  | 10
2017-07-18 | 8:15 | 1.7343 | 4.7264 | 1 | 10 | 49.9649 | 76.9962
2017-07-18 | 8:20 | 1.6968 | 5.3673 |  | 10
2017-07-18 | 8:25 | 1.7335 | 5.9328 |  | 10
2017-07-18 | 8:30 | 1.7249 | 5.9489 | 1 | 10 | 60.9818 | 78.0229
2017-07-18 | 8:35 | 1.7366 | 5.7409 |  | 10
2017-07-18 | 8:40 | 1.7522 | 6.1408 |  | 10
2017-07-18 | 8:45 | 1.7772 | 6.0899 | 1 | 10 | 62.734 | 77.7012
2017-07-18 | 8:50 | 1.7499 | 6.2069 |  | 10
2017-07-18 | 8:55 | 1.7218 | 6.2461 |  | 10
2017-07-18 | 9:00 | 1.7382 | 6.3143 | 1 | 10 | 65.5106 | 77.8686
2017-07-18 | 9:05 | 1.7561 | 6.1075 |  | 10
2017-07-18 | 9:10 | 1.7546 | 6.0317 |  | 10
2017-07-18 | 9:15 | 1.7436 | 6.3979 | 1 | 10 | 65.5047 | 77.8884
2017-07-18 | 9:20 | 1.7616 | 6.0939 |  | 10
2017-07-18 | 9:25 | 1.7429 | 5.3048 |  | 10
2017-07-18 | 9:30 | 1.7015 | 5.7368 | 1 | 10 | 58.9629 | 77.9997
2017-07-18 | 9:35 | 1.7023 | 6.0485 |  | 1.5
2017-07-18 | 9:40 | 1.5728 | 4.2604 |  | 1.5
2017-07-18 | 9:45 | 1.6984 | 2.4089 | 0 | 1.5 | 28.2459 | 81.5552
2017-07-18 | 9:50 | 1.7647 | 0.93963 |  | 1.5
2017-07-18 | 9:55 | 1.7109 | 0 |  | 1.5
2017-07-18 | 10:00 | 1.7327 | 0 | 0 | 1.5 | 25 | 81.9789
2017-07-18 | 10:05 | 1.7413 | 0 |  | 1.5
2017-07-18 | 10:10 | 1.7265 | 0 |  | 1.5
2017-07-18 | 10:15 | 1.7046 | 0 | 0 | 1.5 | 25 | 82.7377
2017-07-18 | 10:20 | 1.6875 | 0 |  | 1.5
2017-07-18 | 10:25 | 1.7436 | 0 |  | 1.5
2017-07-18 | 10:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 83.5876
2017-07-18 | 10:35 | 1.7156 | 0 |  | 1.5
2017-07-18 | 10:40 | 1.7218 | 0 |  | 1.5
2017-07-18 | 10:45 | 1.7413 | 0 | 0 | 1.5 | 25 | 83.9664
2017-07-18 | 10:50 | 1.7475 | 0 |  | 1.5
2017-07-18 | 10:55 | 1.7538 | 0 |  | 1.5
2017-07-18 | 11:00 | 1.7288 | 0 | 0 | 1.5 | 25 | 83.9954
2017-07-18 | 11:05 | 1.7249 | 0 |  | 1.5
2017-07-18 | 11:10 | 1.7226 | 0 |  | 1.5
2017-07-18 | 11:15 | 1.7577 | 0 | 0 | 1.5 | 25 | 84.3719
2017-07-18 | 11:20 | 1.7288 | 0 |  | 1.5
2017-07-18 | 11:25 | 1.7273 | 0 |  | 1.5
2017-07-18 | 11:30 | 1.7179 | 0 | 0 | 1.5 | 25 | 85.2146
2017-07-18 | 11:35 | 1.7265 | 0 |  | 1.5
2017-07-18 | 11:40 | 1.7249 | 0 |  | 1.5
2017-07-18 | 11:45 | 1.7023 | 0 | 0 | 1.5 | 25 | 85.9478
2017-07-18 | 11:50 | 1.7062 | 0 |  | 1.5
2017-07-18 | 11:55 | 1.7109 | 0 |  | 1.5
2017-07-18 | 12:00 | 1.6883 | 0 | 0 | 1.5 | 25 | 87.105
2017-07-18 | 12:05 | 1.6992 | 0 |  | 1.5
2017-07-18 | 12:10 | 1.7327 | 0 |  | 1.5
2017-07-18 | 12:15 | 1.739 | 0 | 0 | 1.5 | 25 | 87.8384
2017-07-18 | 12:20 | 1.728 | 0 |  | 1.5
2017-07-18 | 12:25 | 1.7226 | 0 |  | 1.5
2017-07-18 | 12:30 | 1.6945 | 0 | 0 | 1.5 | 25 | 88.1983
2017-07-18 | 12:35 | 1.7507 | 0 |  | 1.5
2017-07-18 | 12:40 | 1.739 | 0 |  | 1.5
2017-07-18 | 12:45 | 1.7327 | 0 | 0 | 1.5 | 25 | 88.7506
2017-07-18 | 12:50 | 1.7429 | 0 |  | 1.5
2017-07-18 | 12:55 | 1.7366 | 0 |  | 1.5
2017-07-18 | 13:00 | 1.7889 | 0 | 0 | 1.5 | 25 | 88.7599
2017-07-18 | 13:05 | 1.7912 | 0 |  | 1.5
2017-07-18 | 13:10 | 1.7475 | 0 |  | 1.5
2017-07-18 | 13:15 | 1.7468 | 0 | 0 | 1.5 | 25 | 88.0507
2017-07-18 | 13:20 | 1.7296 | 0 |  | 1.5
2017-07-18 | 13:25 | 1.7546 | 0 |  | 1.5
2017-07-18 | 13:30 | 1.7514 | 0 | 0 | 1.5 | 25 | 87.9199
2017-07-18 | 13:35 | 1.7569 | 0 |  | 1.5
2017-07-18 | 13:40 | 1.7561 | 0 |  | 1.5
2017-07-18 | 13:45 | 1.7475 | 0 | 0 | 1.5 | 25 | 87.834
2017-07-18 | 13:50 | 1.7787 | 0 |  | 1.5
2017-07-18 | 13:55 | 1.7631 | 0 |  | 1.5
2017-07-18 | 14:00 | 1.7241 | 0 | 0 | 1.5 | 25 | 87.7855
2017-07-18 | 14:05 | 1.7436 | 0 |  | 1.5
2017-07-18 | 14:10 | 1.7257 | 0 |  | 1.5
2017-07-18 | 14:15 | 1.7312 | 0 | 0 | 1.5 | 25 | 88.2549
2017-07-18 | 14:20 | 1.6867 | 0 |  | 1.5
2017-07-18 | 14:25 | 1.7132 | 0 |  | 1.5
2017-07-18 | 14:30 | 1.7335 | 0 | 0 | 1.5 | 25 | 89.0267
2017-07-18 | 14:35 | 1.7366 | 0 |  | 1.5
2017-07-18 | 14:40 | 1.7241 | 0 |  | 1.5
2017-07-18 | 14:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 89.5535
2017-07-18 | 14:50 | 1.7327 | 0 |  | 1.5
2017-07-18 | 14:55 | 1.7569 | 0 |  | 1.5
2017-07-18 | 15:00 | 1.7826 | 0 | 0 | 1.5 | 25 | 89.8121
2017-07-18 | 15:05 | 1.7538 | 0 |  | 1.5
2017-07-18 | 15:10 | 1.7655 | 0 |  | 1.5
2017-07-18 | 15:15 | 1.739 | 0 | 0 | 1.5 | 25 | 89.7744
2017-07-18 | 15:20 | 1.7655 | 0 |  | 1.5
2017-07-18 | 15:25 | 1.7296 | 0 |  | 1.5
2017-07-18 | 15:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 90.1873
2017-07-18 | 15:35 | 1.7444 | 0 |  | 1.5
2017-07-18 | 15:40 | 1.7647 | 0 |  | 1.5
2017-07-18 | 15:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 90.3211
2017-07-18 | 15:50 | 1.7514 | 0 |  | 1.5
2017-07-18 | 15:55 | 1.7335 | 0 |  | 1.5
2017-07-18 | 16:00 | 1.7312 | 0 | 0 | 1.5 | 25 | 90.667
2017-07-18 | 16:05 | 1.7514 | 0 |  | 1.5
2017-07-18 | 16:10 | 1.7304 | 0 |  | 1.5
2017-07-18 | 16:15 | 1.7756 | 0 | 0 | 1.5 | 25 | 90.5736
2017-07-18 | 16:20 | 1.8006 | 0 |  | 1.5
2017-07-18 | 16:25 | 1.7897 | 0 |  | 1.5
2017-07-18 | 16:30 | 1.7881 | 0 | 0 | 1.5 | 25 | 89.5853
2017-07-18 | 16:35 | 1.7655 | 0 |  | 1.5
2017-07-18 | 16:40 | 1.7748 | 0 |  | 1.5
2017-07-18 | 16:45 | 1.7694 | 0 | 0 | 1.5 | 25 | 88.7
2017-07-18 | 16:50 | 1.7514 | 0 |  | 1.5
2017-07-18 | 16:55 | 1.7553 | 0 |  | 1.5
2017-07-18 | 17:00 | 1.7787 | 0 | 0 | 1.5 | 25 | 88.3175
2017-07-18 | 17:05 | 1.7647 | 0 |  | 1.5
2017-07-18 | 17:10 | 1.7639 | 0 |  | 1.5
2017-07-18 | 17:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 88.0736
2017-07-18 | 17:20 | 1.7795 | 0 |  | 1.5
2017-07-18 | 17:25 | 1.7772 | 0 |  | 1.5
2017-07-18 | 17:30 | 1.746 | 0 | 0 | 1.5 | 25 | 87.5315
2017-07-18 | 17:35 | 1.7951 | 0 |  | 1.5
2017-07-18 | 17:40 | 1.7616 | 0 |  | 1.5
2017-07-18 | 17:45 | 1.7639 | 0 | 0 | 1.5 | 25 | 86.8685
2017-07-18 | 17:50 | 1.7795 | 0 |  | 1.5
2017-07-18 | 17:55 | 1.7631 | 0 |  | 1.5
2017-07-18 | 18:00 | 1.7819 | 0 | 0 | 1.5 | 25 | 86.2367
2017-07-18 | 18:05 | 1.7733 | 0 |  | 1.5
2017-07-18 | 18:10 | 1.76 | 0 |  | 1.5
2017-07-18 | 18:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 85.642
2017-07-18 | 18:20 | 1.7772 | 0 |  | 1.5
2017-07-18 | 18:25 | 1.7811 | 0 |  | 1.5
2017-07-18 | 18:30 | 1.7709 | 0 | 0 | 1.5 | 25 | 85.1713
2017-07-18 | 18:35 | 1.753 | 0 |  | 1.5
2017-07-18 | 18:40 | 1.7592 | 0 |  | 1.5
2017-07-18 | 18:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 84.9256
2017-07-18 | 18:50 | 1.746 | 0 |  | 1.5
2017-07-18 | 18:55 | 1.7585 | 0 |  | 1.5
2017-07-18 | 19:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 84.8534
2017-07-18 | 19:05 | 1.7561 | 0 |  | 1.5
2017-07-18 | 19:10 | 1.7436 | 0 |  | 1.5
2017-07-18 | 19:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 84.5548
2017-07-18 | 19:20 | 1.721 | 0 |  | 1.5
2017-07-18 | 19:25 | 1.7811 | 0 |  | 1.5
2017-07-18 | 19:30 | 1.7265 | 0 | 0 | 1.5 | 25 | 84.4378
2017-07-18 | 19:35 | 1.753 | 0 |  | 1.5
2017-07-18 | 19:40 | 1.7507 | 0 |  | 1.5
2017-07-18 | 19:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 84.3324
2017-07-18 | 19:50 | 1.7351 | 0 |  | 1.5
2017-07-18 | 19:55 | 1.7709 | 0 |  | 1.5
2017-07-18 | 20:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 84.1195
2017-07-18 | 20:05 | 1.7795 | 0 |  | 1.5
2017-07-18 | 20:10 | 1.7795 | 0 |  | 1.5
2017-07-18 | 20:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 83.7798
2017-07-18 | 20:20 | 1.7585 | 0 |  | 1.5
2017-07-18 | 20:25 | 1.7959 | 0 |  | 1.5
2017-07-18 | 20:30 | 1.7803 | 0 | 0 | 1.5 | 25 | 83.2629
2017-07-18 | 20:35 | 1.7569 | 0 |  | 1.5
2017-07-18 | 20:40 | 1.7468 | 0 |  | 1.5
2017-07-18 | 20:45 | 1.7413 | 0 | 0 | 1.5 | 25 | 82.9543
2017-07-18 | 20:50 | 1.753 | 0 |  | 1.5
2017-07-18 | 20:55 | 1.7553 | 0 |  | 1.5
2017-07-18 | 21:00 | 1.7577 | 0 | 0 | 1.5 | 25 | 82.4566
2017-07-18 | 21:05 | -0.1034 | 0 |  | 1.5
2017-07-18 | 21:10 | -0.10418 | 0 |  | 1.5
2017-07-18 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 21:20 | -0.10496 | 0 |  | 1.5
2017-07-18 | 21:25 | -0.10496 | 0 |  | 1.5
2017-07-18 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 21:35 | -0.10496 | 0 |  | 1.5
2017-07-18 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-18 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 21:50 | -0.10496 | 0 |  | 1.5
2017-07-18 | 21:55 | -0.10574 | 0 |  | 1.5
2017-07-18 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-18 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-18 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 22:20 | -0.10652 | 0 |  | 1.5
2017-07-18 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-18 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-18 | 22:40 | -0.10652 | 0 |  | 1.5
2017-07-18 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-18 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-18 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-18 | 23:10 | -0.10652 | 0 |  | 1.5
2017-07-18 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-18 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-18 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 23:35 | -0.10652 | 0 |  | 1.5
2017-07-18 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-18 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-18 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-18 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-19 | 0:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-19 | 0:05 | -0.10964 | 0 |  | 1.5
2017-07-19 | 0:10 | -0.10574 | 0 |  | 1.5
2017-07-19 | 0:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-19 | 0:15 | [5 empty] | 0
2017-07-19 | 0:20 | -0.10652 | 0 |  | 1.5
2017-07-19 | 0:25 | -0.10574 | 0 |  | 1.5
2017-07-19 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 0:30 |  |  |  | 1.5 |  | 0
2017-07-19 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-19 | 0:40 | -0.10574 | 0 |  | 1.5
2017-07-19 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 0:45 | [5 empty] | 0
2017-07-19 | 0:50 | -0.10652 | 0 |  | 1.5
2017-07-19 | 0:55 | -0.10574 | 0 |  | 1.5
2017-07-19 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 1:00 |  |  |  | 1.5 |  | 0
2017-07-19 | 1:05 | -0.10574 | 0 |  | 1.5
2017-07-19 | 1:10 | -0.10652 | 0 |  | 1.5
2017-07-19 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 1:15 | [5 empty] | 0
2017-07-19 | 1:20 | -0.10964 | 0 |  | 1.5
2017-07-19 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-19 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 1:30 | [5 empty] | 0
2017-07-19 | 1:35 | -0.10964 | 0 |  | 1.5
2017-07-19 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-19 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 1:45 | [5 empty] | 0
2017-07-19 | 1:50 | -0.10886 | 0 |  | 1.5
2017-07-19 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-19 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 2:00 |  |  |  | 1.5 |  | 0
2017-07-19 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-19 | 2:10 | -0.10964 | 0 |  | 1.5
2017-07-19 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 2:15 | [5 empty] | 0
2017-07-19 | 2:20 | -0.10964 | 0 |  | 1.5
2017-07-19 | 2:25 | -0.10886 | 0 |  | 1.5
2017-07-19 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 2:30 |  |  |  | 1.5 |  | 0
2017-07-19 | 2:35 | -0.10964 | 0 |  | 1.5
2017-07-19 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-19 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-19 | 2:45 | [5 empty] | 0
2017-07-19 | 2:50 | -0.10964 | 0 |  | 1.5
2017-07-19 | 2:55 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-19 | 3:00 |  |  |  | 1.5 |  | 0
2017-07-19 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:10 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-19 | 3:15 | [5 empty] | 0
2017-07-19 | 3:20 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:25 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-19 | 3:30 |  |  |  | 1.5 |  | 0
2017-07-19 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-19 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 3:45 | [5 empty] | 0
2017-07-19 | 3:50 | -0.10886 | 0 |  | 1.5
2017-07-19 | 3:55 | -0.10886 | 0 |  | 1.5
2017-07-19 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 4:00 | [5 empty] | 0
2017-07-19 | 4:05 | -0.10886 | 0 |  | 1.5
2017-07-19 | 4:10 | -0.10886 | 0 |  | 1.5
2017-07-19 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 4:15 | [5 empty] | 0
2017-07-19 | 4:20 | -0.10886 | 0 |  | 1.5
2017-07-19 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-19 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-19 | 4:30 |  |  |  | 1.5 |  | 0
2017-07-19 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-19 | 4:40 | -0.10886 | 0 |  | 1.5
2017-07-19 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-19 | 4:45 | [5 empty] | 0
2017-07-19 | 4:50 | -0.10886 | 0 |  | 1.5
2017-07-19 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-19 | 5:00 | -0.10886 | 0 | 1 | 0 | 0
2017-07-19 | 5:00 |  |  |  | 0 |  | 25
2017-07-19 | 5:05 | 2.4558 | 5.7742 |  | 10
2017-07-19 | 5:10 | 2.1898 | 9.8542 |  | 10
2017-07-19 | 5:15 | 2.0447 | 9.6757 | 1 | 10 | 98.205
2017-07-19 | 5:15 | [5 empty] | 87.7525
2017-07-19 | 5:20 | 1.962 | 9.0652 |  | 10
2017-07-19 | 5:25 | 1.8895 | 8.7259 |  | 10
2017-07-19 | 5:30 | 1.884 | 8.1413 | 1 | 10 | 83.2109
2017-07-19 | 5:30 |  |  |  | 10 |  | 82.899
2017-07-19 | 5:35 | 1.8638 | 7.8396 |  | 9.9763
2017-07-19 | 5:40 | 1.8185 | 7.4925 |  | 9.0609
2017-07-19 | 5:45 | 1.8099 | 7.191 | 1 | 10 | 73.6636
2017-07-19 | 5:45 | [5 empty] | 80.6115
2017-07-19 | 5:50 | 1.8255 | 7.0723 |  | 10
2017-07-19 | 5:55 | 1.778 | 6.6617 |  | 10
2017-07-19 | 6:00 | 1.7826 | 6.639 | 1 | 10 | 68.2906
2017-07-19 | 6:00 |  |  |  | 10 |  | 79.5527
2017-07-19 | 6:05 | 1.7452 | 6.6369 |  | 10
2017-07-19 | 6:10 | 1.7733 | 6.9018 |  | 10
2017-07-19 | 6:15 | 1.7429 | 7.5854 | 1 | 10 | 76.8065
2017-07-19 | 6:15 | [5 empty] | 79.353
2017-07-19 | 6:20 | 1.6937 | 8.8139 |  | 10
2017-07-19 | 6:25 | 1.6508 | 9.8047 |  | 10
2017-07-19 | 6:30 | 1.6625 | 9.785 | 1 | 10 | 98.4834
2017-07-19 | 6:30 | [5 empty] | 81.0096
2017-07-19 | 6:35 | 1.682 | 10 |  | 10
2017-07-19 | 6:40 | 1.7327 | 9.9377 |  | 10
2017-07-19 | 6:45 | 1.739 | 9.3551 | 1 | 10 | 94.0638
2017-07-19 | 6:45 | [5 empty] | 81.6544
2017-07-19 | 6:50 | 1.7943 | 8.8949 |  | 10
2017-07-19 | 6:55 | 1.8084 | 7.767 |  | 10
2017-07-19 | 7:00 | 1.792 | 6.9276 | 1 | 10 | 70.7982
2017-07-19 | 7:00 |  |  |  | 10 |  | 80.5789
2017-07-19 | 7:05 | 1.8497 | 6.5866 |  | 10
2017-07-19 | 7:10 | 1.7873 | 6.4879 |  | 10
2017-07-19 | 7:15 | 1.7811 | 6.5605 | 1 | 10 | 66.536
2017-07-19 | 7:15 |  |  |  | 10 |  | 79.0481
2017-07-19 | 7:20 | 1.7686 | 6.1615 |  | 10
2017-07-19 | 7:25 | 1.7717 | 6.1801 |  | 10
2017-07-19 | 7:30 | 1.7546 | 6.2406 | 1 | 10 | 63.1944
2017-07-19 | 7:30 | [5 empty] | 78.5814
2017-07-19 | 7:35 | 1.76 | 6.1118 |  | 10
2017-07-19 | 7:40 | 1.7686 | 6.2331 |  | 10
2017-07-19 | 7:45 | 1.8021 | 5.9991 | 1 | 10 | 60.8302
2017-07-19 | 7:45 | [5 empty] | 77.9403
2017-07-19 | 7:50 | 0.0916 | 4.9726 |  | 10
2017-07-19 | 7:55 | 1.9815 | 5.8707 |  | 10
2017-07-19 | 8:00 | 1.9238 | 6.5532 |  | 10
2017-07-19 | 8:00 |  |  | 1 | 10 | 0
2017-07-19 | 8:00 | 1.9691 | 6.5268 |  | 10 |  | 79.5835
2017-07-19 | 8:05 | 1.8778 | 6.8673 |  | 10
2017-07-19 | 8:10 | 1.7928 | 8.0367 |  | 10
2017-07-19 | 8:15 | 1.6828 | 9.2743 | 1 | 10 | 93.7281
2017-07-19 | 8:15 | [5 empty] | 77.3632
2017-07-19 | 8:20 | 1.7327 | 7.2349 |  | 10
2017-07-19 | 8:25 | 1.7741 | 5.9889 |  | 10
2017-07-19 | 8:30 | 1.7561 | 5.5929 | 1 | 10 | 57.3293
2017-07-19 | 8:30 | [5 empty] | 77.3038
2017-07-19 | 8:35 | 1.7967 | 4.8983 |  | 10
2017-07-19 | 8:40 | 1.7709 | 4.6432 |  | 10
2017-07-19 | 8:45 | -0.1034 | 3.4259 | 1 | 10 | 49.7838
2017-07-19 | 8:45 | [5 empty] | 78.8
2017-07-19 | 8:50 | -0.10574 | 1.0799 |  | 10
2017-07-19 | 8:55 | -0.10574 | 0 |  | 10
2017-07-19 | 9:00 | 2.6492 | 0 | 1 | 10 | 0
2017-07-19 | 9:00 | 2.6492 | 0 |  | 10 |  | 96.0521
2017-07-19 | 9:05 | 2.4846 | 0 |  | 10
2017-07-19 | 9:10 | 2.1641 | 5.6715 |  | 10
2017-07-19 | 9:15 | 2.0057 | 8.6521 | 1 | 10 | 0
2017-07-19 | 9:15 | [5 empty] | 81.0553
2017-07-19 | 9:20 | 1.7312 | 8.9364 |  | 10
2017-07-19 | 9:25 | 1.7889 | 7.4941 |  | 10
2017-07-19 | 9:30 | 1.8302 | 6.4772 | 1 | 10 | 70.1038
2017-07-19 | 9:30 |  |  |  | 10 |  | 79.395
2017-07-19 | 9:35 | 1.7639 | 5.9304 |  | 10
2017-07-19 | 9:40 | 1.7865 | 5.3572 |  | 10
2017-07-19 | 9:45 | 1.7975 | 5.2147 | 1 | 10 | 57.3606
2017-07-19 | 9:45 | [5 empty] | 78.3134
2017-07-19 | 9:50 | 1.7811 | 4.4352 |  | 10
2017-07-19 | 9:55 | 1.7764 | 4.1158 |  | 10
2017-07-19 | 10:00 | 1.7257 | 4.2709 | 1 | 10 | 47.5409
2017-07-19 | 10:00 |  |  |  | 10 |  | 77.7771
2017-07-19 | 10:05 | 1.7468 | 4.1518 |  | 10
2017-07-19 | 10:10 | 1.4808 | 3.3101 |  | 1.5
2017-07-19 | 10:15 | 1.6781 | 2.6501 | 0 | 1.5 | 32.1383
2017-07-19 | 10:15 | [5 empty] | 80.3014
2017-07-19 | 10:20 | 1.6937 | 0.007917 |  | 1.5
2017-07-19 | 10:25 | 1.7054 | 0 |  | 1.5
2017-07-19 | 10:30 | 1.7374 | 0 | 0 | 1.5 | 25
2017-07-19 | 10:30 |  |  |  | 1.5 |  | 81.7876
2017-07-19 | 10:35 | 1.7436 | 0 |  | 1.5
2017-07-19 | 10:40 | 1.7483 | 0 |  | 1.5
2017-07-19 | 10:45 | 1.7226 | 0 | 0 | 1.5 | 25
2017-07-19 | 10:45 | [5 empty] | 82.0472
2017-07-19 | 10:50 | 1.7319 | 0 |  | 1.5
2017-07-19 | 10:55 | 1.7265 | 0 |  | 1.5
2017-07-19 | 11:00 | 1.76 | 0 | 0 | 1.5 | 25
2017-07-19 | 11:00 |  |  |  | 1.5 |  | 82.2596
2017-07-19 | 11:05 | 1.7514 | 0 |  | 1.5
2017-07-19 | 11:10 | 1.7312 | 0 |  | 1.5
2017-07-19 | 11:15 | 1.7241 | 0 | 0 | 1.5 | 25
2017-07-19 | 11:15 | [5 empty] | 82.81
2017-07-19 | 11:20 | 1.7054 | 0 |  | 1.5
2017-07-19 | 11:25 | 1.7358 | 0 |  | 1.5
2017-07-19 | 11:30 | 1.7288 | 0 | 0 | 1.5 | 25
2017-07-19 | 11:30 | [5 empty] | 83.5179
2017-07-19 | 11:35 | 1.7366 | 0 |  | 1.5
2017-07-19 | 11:40 | 1.7483 | 0 |  | 1.5
2017-07-19 | 11:45 | 1.7031 | 0 | 0 | 1.5 | 25
2017-07-19 | 11:45 | [5 empty] | 84.1431
2017-07-19 | 11:50 | 1.7522 | 0 |  | 1.5
2017-07-19 | 11:55 | 1.7265 | 0 |  | 1.5
2017-07-19 | 12:00 | 1.7421 | 0 | 0 | 1.5 | 25
2017-07-19 | 12:00 | [5 empty] | 84.6687
2017-07-19 | 12:05 | 1.7413 | 0 |  | 1.5
2017-07-19 | 12:10 | 1.7468 | 0 |  | 1.5
2017-07-19 | 12:15 | 1.6992 | 0 | 0 | 1.5 | 25
2017-07-19 | 12:15 | [5 empty] | 85.3511
2017-07-19 | 12:20 | 1.7319 | 0 |  | 1.5
2017-07-19 | 12:25 | 1.7655 | 0 |  | 1.5
2017-07-19 | 12:30 | 1.7257 | 0 | 0 | 1.5 | 25
2017-07-19 | 12:30 |  |  |  | 1.5 |  | 85.7855
2017-07-19 | 12:35 | 1.7046 | 0 |  | 1.5
2017-07-19 | 12:40 | 1.7257 | 0 |  | 1.5
2017-07-19 | 12:45 | 1.7226 | 0 | 0 | 1.5 | 25
2017-07-19 | 12:45 | [5 empty] | 86.4631
2017-07-19 | 12:50 | 1.7093 | 0 |  | 1.5
2017-07-19 | 12:55 | 1.7249 | 0 |  | 1.5
2017-07-19 | 13:00 | 1.6656 | 0 | 0 | 1.5 | 25
2017-07-19 | 13:00 |  |  |  | 1.5 |  | 87.6333
2017-07-19 | 13:05 | 1.7288 | 0 |  | 1.5
2017-07-19 | 13:10 | 1.7249 | 0 |  | 1.5
2017-07-19 | 13:15 | 1.7124 | 0 | 0 | 1.5 | 25
2017-07-19 | 13:15 | [5 empty] | 88.5695
2017-07-19 | 13:20 | 1.746 | 0 |  | 1.5
2017-07-19 | 13:25 | 1.7873 | 0 |  | 1.5
2017-07-19 | 13:30 | 1.778 | 0 | 0 | 1.5 | 25
2017-07-19 | 13:30 | [5 empty] | 88.0743
2017-07-19 | 13:35 | 1.7702 | 0 |  | 1.5
2017-07-19 | 13:40 | 1.7819 | 0 |  | 1.5
2017-07-19 | 13:45 | 1.7452 | 0 | 0 | 1.5 | 25
2017-07-19 | 13:45 | [5 empty] | 87.5059
2017-07-19 | 13:50 | 1.7187 | 0 |  | 1.5
2017-07-19 | 13:55 | 1.7663 | 0 |  | 1.5
2017-07-19 | 14:00 | 1.767 | 0 | 0 | 1.5 | 25
2017-07-19 | 14:00 |  |  |  | 1.5 |  | 87.384
2017-07-19 | 14:05 | 1.7296 | 0 |  | 1.5
2017-07-19 | 14:10 | 1.7522 | 0 |  | 1.5
2017-07-19 | 14:15 | 1.7265 | 0 | 0 | 1.5 | 25
2017-07-19 | 14:15 |  |  |  | 1.5 |  | 87.9227
2017-07-19 | 14:20 | 1.7054 | 0 |  | 1.5
2017-07-19 | 14:25 | 1.7296 | 0 |  | 1.5
2017-07-19 | 14:30 | 1.714 | 0 | 0 | 1.5 | 25
2017-07-19 | 14:30 | [5 empty] | 88.7884
2017-07-19 | 14:35 | 1.7452 | 0 |  | 1.5
2017-07-19 | 14:40 | 1.7148 | 0 |  | 1.5
2017-07-19 | 14:45 | 1.7475 | 0 | 0 | 1.5 | 25
2017-07-19 | 14:45 | [5 empty] | 89.1638
2017-07-19 | 14:50 | 1.7655 | 0 |  | 1.5
2017-07-19 | 14:55 | 1.7959 | 0 |  | 1.5
2017-07-19 | 15:00 | 1.7998 | 0 | 0 | 1.5 | 25
2017-07-19 | 15:00 | [5 empty] | 88.5886
2017-07-19 | 15:05 | 1.7553 | 0 |  | 1.5
2017-07-19 | 15:10 | 1.7639 | 0 |  | 1.5
2017-07-19 | 15:15 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-19 | 15:15 |  |  |  | 1.5 |  | 88.1716
2017-07-19 | 15:20 | 1.767 | 0 |  | 1.5
2017-07-19 | 15:25 | 1.7897 | 0 |  | 1.5
2017-07-19 | 15:30 | 1.7756 | 0 | 0 | 1.5 | 25
2017-07-19 | 15:30 |  |  |  | 1.5 |  | 87.4398
2017-07-19 | 15:35 | 1.7881 | 0 |  | 1.5
2017-07-19 | 15:40 | 1.8006 | 0 |  | 1.5
2017-07-19 | 15:45 | 1.785 | 0 | 0 | 1.5 | 25
2017-07-19 | 15:45 | [5 empty] | 86.1159
2017-07-19 | 15:50 | 1.7928 | 0 |  | 1.5
2017-07-19 | 15:55 | 1.8146 | 0 |  | 1.5
2017-07-19 | 16:00 | 1.8021 | 0 | 0 | 1.5 | 25
2017-07-19 | 16:00 |  |  |  | 1.5 |  | 84.8582
2017-07-19 | 16:05 | 1.7873 | 0 |  | 1.5
2017-07-19 | 16:10 | 1.7499 | 0 |  | 1.5
2017-07-19 | 16:15 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-19 | 16:15 | [5 empty] | 84.3091
2017-07-19 | 16:20 | 1.7569 | 0 |  | 1.5
2017-07-19 | 16:25 | 1.7624 | 0 |  | 1.5
2017-07-19 | 16:30 | 1.7616 | 0 | 0 | 1.5 | 25
2017-07-19 | 16:30 |  |  |  | 1.5 |  | 84.3798
2017-07-19 | 16:35 | 1.7717 | 0 |  | 1.5
2017-07-19 | 16:40 | 1.7483 | 0 |  | 1.5
2017-07-19 | 16:45 | 1.767 | 0 | 0 | 1.5 | 25
2017-07-19 | 16:45 | [5 empty] | 83.9708
2017-07-19 | 16:50 | 1.7702 | 0 |  | 1.5
2017-07-19 | 16:55 | 1.7694 | 0 |  | 1.5
2017-07-19 | 17:00 | 1.7577 | 0 | 0 | 1.5 | 25
2017-07-19 | 17:00 | [5 empty] | 83.5334
2017-07-19 | 17:05 | 1.7218 | 0 |  | 1.5
2017-07-19 | 17:10 | 1.7717 | 0 |  | 1.5
2017-07-19 | 17:15 | 1.7655 | 0 | 0 | 1.5 | 25
2017-07-19 | 17:15 |  |  |  | 1.5 |  | 83.2689
2017-07-19 | 17:20 | 1.767 | 0 |  | 1.5
2017-07-19 | 17:25 | 1.7312 | 0 |  | 1.5
2017-07-19 | 17:30 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-19 | 17:30 | [5 empty] | 83.2359
2017-07-19 | 17:35 | 1.7842 | 0 |  | 1.5
2017-07-19 | 17:40 | 1.7826 | 0 |  | 1.5
2017-07-19 | 17:45 | 1.7569 | 0 | 0 | 1.5 | 25
2017-07-19 | 17:45 | [5 empty] | 82.7298
2017-07-19 | 17:50 | 1.7943 | 0 |  | 1.5
2017-07-19 | 17:55 | 1.7803 | 0 |  | 1.5
2017-07-19 | 18:00 | 1.7561 | 0 | 0 | 1.5 | 25
2017-07-19 | 18:00 |  |  |  | 1.5 |  | 82.0364
2017-07-19 | 18:05 | 1.7585 | 0 |  | 1.5
2017-07-19 | 18:10 | 1.7538 | 0 |  | 1.5
2017-07-19 | 18:15 | 1.7429 | 0 | 0 | 1.5 | 25
2017-07-19 | 18:15 | [5 empty] | 82.0264
2017-07-19 | 18:20 | 1.7678 | 0 |  | 1.5
2017-07-19 | 18:25 | 1.7522 | 0 |  | 1.5
2017-07-19 | 18:30 | 1.7616 | 0 | 0 | 1.5 | 25
2017-07-19 | 18:30 |  |  |  | 1.5 |  | 81.8785
2017-07-19 | 18:35 | 1.7553 | 0 |  | 1.5
2017-07-19 | 18:40 | 1.753 | 0 |  | 1.5
2017-07-19 | 18:45 | 1.7319 | 0 | 0 | 1.5 | 25
2017-07-19 | 18:45 | [5 empty] | 81.749
2017-07-19 | 18:50 | 1.7468 | 0 |  | 1.5
2017-07-19 | 18:55 | 1.7624 | 0 |  | 1.5
2017-07-19 | 19:00 | 1.7366 | 0 | 0 | 1.5 | 25
2017-07-19 | 19:00 |  |  |  | 1.5 |  | 81.345
2017-07-19 | 19:05 | 1.7468 | 0 |  | 1.5
2017-07-19 | 19:10 | 1.7538 | 0 |  | 1.5
2017-07-19 | 19:15 | 1.7546 | 0 | 0 | 1.5 | 25
2017-07-19 | 19:15 | [5 empty] | 81.2002
2017-07-19 | 19:20 | 1.7678 | 0 |  | 1.5
2017-07-19 | 19:25 | 1.7624 | 0 |  | 1.5
2017-07-19 | 19:30 | 1.7748 | 0 | 0 | 1.5 | 25
2017-07-19 | 19:30 |  |  |  | 1.5 |  | 80.8738
2017-07-19 | 19:35 | 1.7475 | 0 |  | 1.5
2017-07-19 | 19:40 | 1.753 | 0 |  | 1.5
2017-07-19 | 19:45 | 1.7733 | 0 | 0 | 1.5 | 25
2017-07-19 | 19:45 | [5 empty] | 80.7286
2017-07-19 | 19:50 | 1.7764 | 0 |  | 1.5
2017-07-19 | 19:55 | 1.7546 | 0 |  | 1.5
2017-07-19 | 20:00 | 1.7795 | 0 | 0 | 1.5 | 25
2017-07-19 | 20:00 |  |  |  | 1.5 |  | 80.3738
2017-07-19 | 20:05 | 1.76 | 0 |  | 1.5
2017-07-19 | 20:10 | 1.746 | 0 |  | 1.5
2017-07-19 | 20:15 | 1.7561 | 0 | 0 | 1.5 | 25
2017-07-19 | 20:15 | [5 empty] | 80.2975
2017-07-19 | 20:20 | 1.7546 | 0 |  | 1.5
2017-07-19 | 20:25 | 1.7234 | 0 |  | 1.5
2017-07-19 | 20:30 | 1.7608 | 0 | 0 | 1.5 | 25
2017-07-19 | 20:30 |  |  |  | 1.5 |  | 80.4703
2017-07-19 | 20:35 | 1.7413 | 0 |  | 1.5
2017-07-19 | 20:40 | 1.7475 | 0 |  | 1.5
2017-07-19 | 20:45 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-19 | 20:45 | [5 empty] | 80.51
2017-07-19 | 20:50 | 1.7639 | 0 |  | 1.5
2017-07-19 | 20:55 | 1.7694 | 0 |  | 1.5
2017-07-19 | 21:00 | 1.767 | 0 | 0 | 1.5 | 25
2017-07-19 | 21:00 | [5 empty] | 0
2017-07-19 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-19 | 21:10 | -0.10418 | 0 |  | 1.5
2017-07-19 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-19 | 21:15 |  |  |  | 1.5 |  | 0
2017-07-19 | 21:20 | -0.10496 | 0 |  | 1.5
2017-07-19 | 21:25 | -0.10496 | 0 |  | 1.5
2017-07-19 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 21:30 |  |  |  | 1.5 |  | 0
2017-07-19 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-19 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-19 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 21:45 | [5 empty] | 0
2017-07-19 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-19 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-19 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-19 | 22:00 | [5 empty] | 0
2017-07-19 | 22:05 | -0.10964 | 0 |  | 1.5
2017-07-19 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-19 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-19 | 22:15 | [5 empty] | 0
2017-07-19 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-19 | 22:25 | -0.10652 | 0 |  | 1.5
2017-07-19 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 22:30 | [5 empty] | 0
2017-07-19 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-19 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-19 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-19 | 22:45 | [5 empty] | 0
2017-07-19 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-19 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-19 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-19 | 23:00 |  |  |  | 1.5 |  | 0
2017-07-19 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-19 | 23:10 | -0.10496 | 0 |  | 1.5
2017-07-19 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-19 | 23:15 | [5 empty] | 0
2017-07-19 | 23:20 | -0.10496 | 0 |  | 1.5
2017-07-19 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-19 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-19 | 23:30 |  |  |  | 1.5 |  | 0
2017-07-19 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-19 | 23:40 | -0.10496 | 0 |  | 1.5
2017-07-19 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-19 | 23:45 | [5 empty] | 0
2017-07-19 | 23:50 | -0.10496 | 0 |  | 1.5
2017-07-19 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-20 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-20 | 0:00 | [5 empty] | 0
2017-07-20 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-20 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-20 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-20 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-20 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-20 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-20 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 0:50 | -0.10418 | 0 |  | 1.5
2017-07-20 | 0:55 | -0.10574 | 0 |  | 1.5
2017-07-20 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 1:05 | -0.10574 | 0 |  | 1.5
2017-07-20 | 1:10 | -0.10574 | 0 |  | 1.5
2017-07-20 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-20 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-20 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 1:35 | -0.10886 | 0 |  | 1.5
2017-07-20 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-20 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 1:50 | -0.10886 | 0 |  | 1.5
2017-07-20 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:10 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 2:20 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:25 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 2:35 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:40 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 2:50 | -0.10886 | 0 |  | 1.5
2017-07-20 | 2:55 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 3:05 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:10 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 3:20 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:25 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 3:35 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:40 | -0.10886 | 0 |  | 1.5
2017-07-20 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-20 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-20 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 4:05 | -0.10886 | 0 |  | 1.5
2017-07-20 | 4:10 | -0.10886 | 0 |  | 1.5
2017-07-20 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-20 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-20 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-20 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-20 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-20 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-20 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 5:05 | 2.3528 | 5.769 |  | 10
2017-07-20 | 5:10 | 2.1282 | 9.9983 |  | 10
2017-07-20 | 5:15 | 2.0611 | 9.9622 | 1 | 10 | 99.7776 | 88.6354
2017-07-20 | 5:20 | 1.9519 | 9.9427 |  | 10
2017-07-20 | 5:25 | 1.9152 | 9.4262 |  | 10
2017-07-20 | 5:30 | 1.8856 | 8.7499 | 1 | 10 | 88.2573 | 83.5021
2017-07-20 | 5:35 | 1.8825 | 8.2931 |  | 10
2017-07-20 | 5:40 | 1.8489 | 7.6132 |  | 10
2017-07-20 | 5:45 | 1.8567 | 7.2977 | 1 | 10 | 74.0969 | 80.4984
2017-07-20 | 5:50 | 1.8333 | 6.9813 |  | 10
2017-07-20 | 5:55 | 1.8115 | 6.7238 |  | 10
2017-07-20 | 6:00 | 1.7694 | 6.5321 | 1 | 10 | 66.5006 | 78.6448
2017-07-20 | 6:05 | 1.8029 | 6.3336 |  | 10
2017-07-20 | 6:10 | 1.7569 | 6.7521 |  | 10
2017-07-20 | 6:15 | 1.7772 | 6.6773 | 1 | 10 | 67.971 | 77.8741
2017-07-20 | 6:20 | 1.7967 | 6.2591 |  | 10
2017-07-20 | 6:25 | 1.7631 | 6.3098 |  | 10
2017-07-20 | 6:30 | 1.7912 | 6.2551 | 1 | 10 | 63.5851 | 77.3759
2017-07-20 | 6:35 | 1.7631 | 6.2557 |  | 10
2017-07-20 | 6:40 | 1.7631 | 6.1489 |  | 10
2017-07-20 | 6:45 | 1.7702 | 6.2295 | 1 | 10 | 63.2026 | 77.1932
2017-07-20 | 6:50 | 1.7873 | 6.2206 |  | 10
2017-07-20 | 6:55 | 1.7257 | 5.9398 |  | 10
2017-07-20 | 7:00 | 1.785 | 5.99 | 1 | 10 | 60.7747 | 76.8396
2017-07-20 | 7:05 | 1.7826 | 5.7743 |  | 10
2017-07-20 | 7:10 | 1.7358 | 6.142 |  | 10
2017-07-20 | 7:15 | 1.7468 | 6.4502 | 1 | 10 | 65.7768 | 76.599
2017-07-20 | 7:20 | 1.7569 | 6.5145 |  | 10
2017-07-20 | 7:25 | 1.7585 | 6.2394 |  | 10
2017-07-20 | 7:30 | 1.7647 | 5.5595 | 1 | 10 | 57.2514 | 76.5243
2017-07-20 | 7:35 | 1.7741 | 5.7088 |  | 10
2017-07-20 | 7:40 | 1.7429 | 5.5531 |  | 10
2017-07-20 | 7:45 | 1.7351 | 5.1286 | 1 | 10 | 52.8104 | 76.4239
2017-07-20 | 7:50 | 1.7514 | 4.8337 |  | 10
2017-07-20 | 7:55 | 1.7273 | 4.4822 |  | 10
2017-07-20 | 8:00 | 1.7351 | 4.5084 | 1 | 10 | 47.0898 | 76.6309
2017-07-20 | 8:05 | 1.7296 | 4.6152 |  | 10
2017-07-20 | 8:10 | 1.7249 | 4.7998 |  | 10
2017-07-20 | 8:15 | 1.7273 | 4.7115 | 1 | 10 | 49.3426 | 76.9458
2017-07-20 | 8:20 | 1.7257 | 4.7886 |  | 10
2017-07-20 | 8:25 | 1.7413 | 4.6723 |  | 10
2017-07-20 | 8:30 | 1.7748 | 4.417 | 1 | 10 | 46.2348 | 76.9105
2017-07-20 | 8:35 | 1.7577 | 5.0214 |  | 10
2017-07-20 | 8:40 | 1.7187 | 5.7407 |  | 10
2017-07-20 | 8:45 | 1.7429 | 5.7513 | 1 | 10 | 57.6242 | 77.1337
2017-07-20 | 8:50 | 1.739 | 5.4598 |  | 10
2017-07-20 | 8:55 | 1.7475 | 4.9697 |  | 10
2017-07-20 | 9:00 | 1.7343 | 4.8112 | 1 | 10 | 49.5431 | 76.9856
2017-07-20 | 9:05 | 1.7514 | 5.0038 |  | 10
2017-07-20 | 9:10 | 1.7265 | 5.6574 |  | 10
2017-07-20 | 9:15 | 1.7249 | 6.1279 | 1 | 10 | 62.443 | 77.376
2017-07-20 | 9:20 | 1.7265 | 5.4654 |  | 10
2017-07-20 | 9:25 | 1.7257 | 5.6462 |  | 10
2017-07-20 | 9:30 | 1.7241 | 5.4848 | 1 | 10 | 56.737 | 77.748
2017-07-20 | 9:35 | 1.7491 | 5.9166 |  | 10
2017-07-20 | 9:40 | 1.7148 | 5.8645 |  | 10
2017-07-20 | 9:45 | 1.533 | 4.5129 | 0 | 1.5 | 48.2309 | 79.2723
2017-07-20 | 9:50 | 1.6898 | 1.4315 |  | 1.5
2017-07-20 | 9:55 | 1.6859 | 0 |  | 1.5
2017-07-20 | 10:00 | 1.6929 | 0 | 0 | 1.5 | 25 | 81.2667
2017-07-20 | 10:05 | 1.6992 | 0 |  | 1.5
2017-07-20 | 10:10 | 1.7327 | 0 |  | 1.5
2017-07-20 | 10:15 | 1.7249 | 0 | 0 | 1.5 | 25 | 81.7729
2017-07-20 | 10:20 | 1.7647 | 0 |  | 1.5
2017-07-20 | 10:25 | 1.7179 | 0 |  | 1.5
2017-07-20 | 10:30 | 1.6805 | 0 | 0 | 1.5 | 25 | 82.6826
2017-07-20 | 10:35 | 1.668 | 0 |  | 1.5
2017-07-20 | 10:40 | 1.7319 | 0 |  | 1.5
2017-07-20 | 10:45 | 1.7093 | 0 | 0 | 1.5 | 25 | 84.0202
2017-07-20 | 10:50 | 1.7553 | 0 |  | 1.5
2017-07-20 | 10:55 | 1.7733 | 0 |  | 1.5
2017-07-20 | 11:00 | 1.9223 | 0.58238 | 1 | 10 | 29.8833 | 82.2368
2017-07-20 | 11:05 | 1.6992 | 2.3656 |  | 1.5
2017-07-20 | 11:10 | 1.7062 | 0.64085 |  | 1.5
2017-07-20 | 11:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 82.5984
2017-07-20 | 11:20 | 1.7046 | 0 |  | 1.5
2017-07-20 | 11:25 | 1.7585 | 0 |  | 1.5
2017-07-20 | 11:30 | 1.7382 | 0 | 0 | 1.5 | 25 | 82.8122
2017-07-20 | 11:35 | 1.7624 | 0 |  | 1.5
2017-07-20 | 11:40 | 1.7148 | 0 |  | 1.5
2017-07-20 | 11:45 | 1.7483 | 0 | 0 | 1.5 | 25 | 82.9255
2017-07-20 | 11:50 | 1.7452 | 0 |  | 1.5
2017-07-20 | 11:55 | 1.7538 | 0 |  | 1.5
2017-07-20 | 12:00 | 1.7491 | 0 | 0 | 1.5 | 25 | 83.0505
2017-07-20 | 12:05 | 1.76 | 0 |  | 1.5
2017-07-20 | 12:10 | 1.7429 | 0 |  | 1.5
2017-07-20 | 12:15 | 1.7787 | 0 | 0 | 1.5 | 25 | 83.1075
2017-07-20 | 12:20 | 1.7756 | 0 |  | 1.5
2017-07-20 | 12:25 | 1.7686 | 0 |  | 1.5
2017-07-20 | 12:30 | 1.7912 | 0 | 0 | 1.5 | 25 | 82.5258
2017-07-20 | 12:35 | 1.7382 | 0 |  | 1.5
2017-07-20 | 12:40 | 1.7592 | 0 |  | 1.5
2017-07-20 | 12:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 82.4555
2017-07-20 | 12:50 | 1.7499 | 0 |  | 1.5
2017-07-20 | 12:55 | 1.753 | 0 |  | 1.5
2017-07-20 | 13:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 82.7352
2017-07-20 | 13:05 | 1.7436 | 0 |  | 1.5
2017-07-20 | 13:10 | 1.6937 | 0 |  | 1.5
2017-07-20 | 13:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 83.0595
2017-07-20 | 13:20 | 1.7553 | 0 |  | 1.5
2017-07-20 | 13:25 | 1.7218 | 0 |  | 1.5
2017-07-20 | 13:30 | 1.7218 | 0 | 0 | 1.5 | 25 | 83.2725
2017-07-20 | 13:35 | 1.746 | 0 |  | 1.5
2017-07-20 | 13:40 | 1.739 | 0 |  | 1.5
2017-07-20 | 13:45 | 1.7202 | 0 | 0 | 1.5 | 25 | 83.8309
2017-07-20 | 13:50 | 1.7538 | 0 |  | 1.5
2017-07-20 | 13:55 | 1.7624 | 0 |  | 1.5
2017-07-20 | 14:00 | 1.7569 | 0 | 0 | 1.5 | 25 | 83.7812
2017-07-20 | 14:05 | 1.7382 | 0 |  | 1.5
2017-07-20 | 14:10 | 1.714 | 0 |  | 1.5
2017-07-20 | 14:15 | 1.7483 | 0 | 0 | 1.5 | 25 | 84.2687
2017-07-20 | 14:20 | 1.7319 | 0 |  | 1.5
2017-07-20 | 14:25 | 1.739 | 0 |  | 1.5
2017-07-20 | 14:30 | 1.7109 | 0 | 0 | 1.5 | 25 | 84.8514
2017-07-20 | 14:35 | 1.7335 | 0 |  | 1.5
2017-07-20 | 14:40 | 1.7624 | 0 |  | 1.5
2017-07-20 | 14:45 | 1.7514 | 0 | 0 | 1.5 | 25 | 84.9654
2017-07-20 | 14:50 | 1.7663 | 0 |  | 1.5
2017-07-20 | 14:55 | 1.7421 | 0 |  | 1.5
2017-07-20 | 15:00 | 1.7351 | 0 | 0 | 1.5 | 25 | 84.9579
2017-07-20 | 15:05 | 1.7195 | 0 |  | 1.5
2017-07-20 | 15:10 | 1.7358 | 0 |  | 1.5
2017-07-20 | 15:15 | 1.7382 | 0 | 0 | 1.5 | 25 | 85.1595
2017-07-20 | 15:20 | 1.7538 | 0 |  | 1.5
2017-07-20 | 15:25 | 1.7405 | 0 |  | 1.5
2017-07-20 | 15:30 | 1.7429 | 0 | 0 | 1.5 | 25 | 85.4537
2017-07-20 | 15:35 | 1.7156 | 0 |  | 1.5
2017-07-20 | 15:40 | 1.707 | 0 |  | 1.5
2017-07-20 | 15:45 | 1.7007 | 0 | 0 | 1.5 | 25 | 86.112
2017-07-20 | 15:50 | 1.7452 | 0 |  | 1.5
2017-07-20 | 15:55 | 1.7585 | 0 |  | 1.5
2017-07-20 | 16:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 86.5712
2017-07-20 | 16:05 | 1.7842 | 0 |  | 1.5
2017-07-20 | 16:10 | 1.7351 | 0 |  | 1.5
2017-07-20 | 16:15 | 1.7499 | 0 | 0 | 1.5 | 25 | 86.5809
2017-07-20 | 16:20 | 1.7787 | 0 |  | 1.5
2017-07-20 | 16:25 | 1.7249 | 0 |  | 1.5
2017-07-20 | 16:30 | 1.7709 | 0 | 0 | 1.5 | 25 | 86.0713
2017-07-20 | 16:35 | 1.7592 | 0 |  | 1.5
2017-07-20 | 16:40 | 1.7725 | 0 |  | 1.5
2017-07-20 | 16:45 | 1.7694 | 0 | 0 | 1.5 | 25 | 85.5003
2017-07-20 | 16:50 | 1.7678 | 0 |  | 1.5
2017-07-20 | 16:55 | 1.7772 | 0 |  | 1.5
2017-07-20 | 17:00 | 1.7811 | 0 | 0 | 1.5 | 25 | 84.7536
2017-07-20 | 17:05 | 1.7694 | 0 |  | 1.5
2017-07-20 | 17:10 | 1.7655 | 0 |  | 1.5
2017-07-20 | 17:15 | 1.7834 | 0 | 0 | 1.5 | 25 | 84.3272
2017-07-20 | 17:20 | 1.8014 | 0 |  | 1.5
2017-07-20 | 17:25 | 1.7741 | 0 |  | 1.5
2017-07-20 | 17:30 | 1.7912 | 0 | 0 | 1.5 | 25 | 83.5358
2017-07-20 | 17:35 | 1.7834 | 0 |  | 1.5
2017-07-20 | 17:40 | 1.799 | 0 |  | 1.5
2017-07-20 | 17:45 | 1.8006 | 0 | 0 | 1.5 | 25 | 82.4568
2017-07-20 | 17:50 | 1.7538 | 0 |  | 1.5
2017-07-20 | 17:55 | 1.7561 | 0 |  | 1.5
2017-07-20 | 18:00 | 1.7709 | 0 | 0 | 1.5 | 25 | 81.8572
2017-07-20 | 18:05 | 1.7592 | 0 |  | 1.5
2017-07-20 | 18:10 | 1.7569 | 0 |  | 1.5
2017-07-20 | 18:15 | 1.746 | 0 | 0 | 1.5 | 25 | 81.5504
2017-07-20 | 18:20 | 1.7741 | 0 |  | 1.5
2017-07-20 | 18:25 | 1.7639 | 0 |  | 1.5
2017-07-20 | 18:30 | 1.7904 | 0 | 0 | 1.5 | 25 | 81.0277
2017-07-20 | 18:35 | 1.8053 | 0 |  | 1.5
2017-07-20 | 18:40 | 1.7647 | 0 |  | 1.5
2017-07-20 | 18:45 | 1.7163 | 0 | 0 | 1.5 | 25 | 80.6051
2017-07-20 | 18:50 | 1.7694 | 0 |  | 1.5
2017-07-20 | 18:55 | 1.76 | 0 |  | 1.5
2017-07-20 | 19:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 80.5946
2017-07-20 | 19:05 | 1.7826 | 0 |  | 1.5
2017-07-20 | 19:10 | 1.7561 | 0 |  | 1.5
2017-07-20 | 19:15 | 1.7561 | 0 | 0 | 1.5 | 25 | 80.1983
2017-07-20 | 19:20 | 1.7546 | 0 |  | 1.5
2017-07-20 | 19:25 | 1.739 | 0 |  | 1.5
2017-07-20 | 19:30 | 1.739 | 0 | 0 | 1.5 | 25 | 80.1692
2017-07-20 | 19:35 | 1.753 | 0 |  | 1.5
2017-07-20 | 19:40 | 1.7647 | 0 |  | 1.5
2017-07-20 | 19:45 | 1.7748 | 0 | 0 | 1.5 | 25 | 80.0579
2017-07-20 | 19:50 | 1.7694 | 0 |  | 1.5
2017-07-20 | 19:55 | 1.7616 | 0 |  | 1.5
2017-07-20 | 20:00 | 1.7382 | 0 | 0 | 1.5 | 25 | 79.9712
2017-07-20 | 20:05 | 1.7561 | 0 |  | 1.5
2017-07-20 | 20:10 | 1.7343 | 0 |  | 1.5
2017-07-20 | 20:15 | 1.7592 | 0 | 0 | 1.5 | 25 | 79.8387
2017-07-20 | 20:20 | 1.7663 | 0 |  | 1.5
2017-07-20 | 20:25 | 1.7624 | 0 |  | 1.5
2017-07-20 | 20:30 | 1.7483 | 0 | 0 | 1.5 | 25 | 79.7178
2017-07-20 | 20:35 | 1.7561 | 0 |  | 1.5
2017-07-20 | 20:40 | 1.7647 | 0 |  | 1.5
2017-07-20 | 20:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 79.645
2017-07-20 | 20:50 | 1.7522 | 0 |  | 1.5
2017-07-20 | 20:55 | 1.7475 | 0 |  | 1.5
2017-07-20 | 21:00 | 1.753 | 0 | 0 | 1.5 | 25 | 79.5199
2017-07-20 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-20 | 21:10 | -0.10418 | 0 |  | 1.5
2017-07-20 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 21:20 | -0.1073 | 0 |  | 1.5
2017-07-20 | 21:25 | -0.10808 | 0 |  | 1.5
2017-07-20 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-20 | 21:40 | -0.10808 | 0 |  | 1.5
2017-07-20 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-20 | 21:55 | -0.10964 | 0 |  | 1.5
2017-07-20 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-20 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-20 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-20 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-20 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-20 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-20 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-20 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-20 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 23:05 | -0.10808 | 0 |  | 1.5
2017-07-20 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-20 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-20 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-20 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 23:35 | -0.10652 | 0 |  | 1.5
2017-07-20 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-20 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-20 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-20 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:10 | -0.10964 | 0 |  | 1.5
2017-07-21 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 0:20 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:25 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:40 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 0:50 | -0.10574 | 0 |  | 1.5
2017-07-21 | 0:55 | -0.10574 | 0 |  | 1.5
2017-07-21 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 1:05 | -0.10574 | 0 |  | 1.5
2017-07-21 | 1:10 | -0.10574 | 0 |  | 1.5
2017-07-21 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 1:20 | -0.10964 | 0 |  | 1.5
2017-07-21 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-21 | 1:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 1:35 | -0.10886 | 0 |  | 1.5
2017-07-21 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-21 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 1:50 | -0.1112 | 0 |  | 1.5
2017-07-21 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-21 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 2:05 | -0.10964 | 0 |  | 1.5
2017-07-21 | 2:10 | -0.10964 | 0 |  | 1.5
2017-07-21 | 2:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 2:20 | -0.10886 | 0 |  | 1.5
2017-07-21 | 2:25 | -0.10964 | 0 |  | 1.5
2017-07-21 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 2:35 | -0.10964 | 0 |  | 1.5
2017-07-21 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-21 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 2:50 | -0.10964 | 0 |  | 1.5
2017-07-21 | 2:55 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:10 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 3:20 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:25 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-21 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:10 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-21 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-21 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 5:05 | 2.5213 | 5.6577 |  | 10
2017-07-21 | 5:10 | 2.2093 | 9.7188 |  | 10
2017-07-21 | 5:15 | 2.0517 | 9.3496 | 1 | 10 | 95.2526 | 87.1975
2017-07-21 | 5:20 | 1.9706 | 8.8728 |  | 10
2017-07-21 | 5:25 | 1.9223 | 8.1794 |  | 10
2017-07-21 | 5:30 | 1.8762 | 7.8678 | 1 | 10 | 80.8847 | 81.8502
2017-07-21 | 5:35 | 1.8497 | 7.3569 |  | 10
2017-07-21 | 5:40 | 1.8248 | 7.1497 |  | 10
2017-07-21 | 5:45 | 1.8154 | 6.7373 | 1 | 10 | 69.9381 | 79.5143
2017-07-21 | 5:50 | 1.8099 | 6.5191 |  | 10
2017-07-21 | 5:55 | 1.7967 | 6.4321 |  | 10
2017-07-21 | 6:00 | 1.8006 | 6.0905 | 1 | 10 | 63.5165 | 78.2013
2017-07-21 | 6:05 | 1.7288 | 6.303 |  | 10
2017-07-21 | 6:10 | 1.7826 | 6.4311 |  | 10
2017-07-21 | 6:15 | 1.7624 | 6.4745 | 1 | 10 | 66.9546 | 77.7935
2017-07-21 | 6:20 | 1.7507 | 6.5301 |  | 10
2017-07-21 | 6:25 | 1.778 | 6.4599 |  | 10
2017-07-21 | 6:30 | 1.7717 | 6.2744 | 1 | 10 | 65.3682 | 77.5619
2017-07-21 | 6:35 | 1.7694 | 6.163 |  | 10
2017-07-21 | 6:40 | 1.7343 | 6.2167 |  | 10
2017-07-21 | 6:45 | 1.7631 | 6.4099 | 1 | 10 | 66.3016 | 77.4312
2017-07-21 | 6:50 | 1.7834 | 6.4929 |  | 10
2017-07-21 | 6:55 | 1.7452 | 6.8026 |  | 10
2017-07-21 | 7:00 | 1.7608 | 6.5463 | 1 | 10 | 67.88 | 77.1971
2017-07-21 | 7:05 | 1.7218 | 6.4529 |  | 10
2017-07-21 | 7:10 | 1.7795 | 6.1406 |  | 10
2017-07-21 | 7:15 | 1.7538 | 6.061 | 1 | 10 | 62.8982 | 77.1753
2017-07-21 | 7:20 | 1.7647 | 6.165 |  | 10
2017-07-21 | 7:25 | 1.7577 | 5.8491 |  | 10
2017-07-21 | 7:30 | 1.7842 | 5.648 | 1 | 10 | 59.4808 | 76.8117
2017-07-21 | 7:35 | 1.7616 | 5.4179 |  | 10
2017-07-21 | 7:40 | 1.7475 | 5.2216 |  | 10
2017-07-21 | 7:45 | 1.7561 | 4.9942 | 1 | 10 | 53.1384 | 76.6543
2017-07-21 | 7:50 | 1.7335 | 4.5309 |  | 10
2017-07-21 | 7:55 | 1.7733 | 4.2201 |  | 10
2017-07-21 | 8:00 | 1.7733 | 4.1 | 1 | 10 | 44.2857 | 76.364
2017-07-21 | 8:05 | 1.767 | 3.9546 |  | 10
2017-07-21 | 8:10 | 1.7429 | 3.782 |  | 10
2017-07-21 | 8:15 | 1.7374 | 3.8233 | 1 | 10 | 40.5819 | 76.3246
2017-07-21 | 8:20 | 1.7374 | 5.0649 |  | 10
2017-07-21 | 8:25 | 1.7444 | 5.1655 |  | 10
2017-07-21 | 8:30 | 1.7241 | 4.9183 | 1 | 10 | 51.8645 | 76.719
2017-07-21 | 8:35 | 1.8006 | 4.9471 |  | 10
2017-07-21 | 8:40 | 1.7468 | 5.2711 |  | 10
2017-07-21 | 8:45 | 1.7585 | 5.4293 | 1 | 10 | 56.9 | 76.6963
2017-07-21 | 8:50 | 1.7468 | 5.9443 |  | 10
2017-07-21 | 8:55 | 1.7421 | 5.8101 |  | 10
2017-07-21 | 9:00 | 1.7327 | 5.7085 | 1 | 10 | 60.0878 | 76.8947
2017-07-21 | 9:05 | 1.7436 | 5.7202 |  | 10
2017-07-21 | 9:10 | 1.76 | 5.3285 |  | 10
2017-07-21 | 9:15 | 1.7873 | 5.7642 | 1 | 10 | 59.4141 | 76.9074
2017-07-21 | 9:20 | 1.7491 | 6.4751 |  | 10
2017-07-21 | 9:25 | 1.7046 | 6.6485 |  | 10
2017-07-21 | 9:30 | 1.7062 | 6.7136 | 1 | 10 | 68.8257 | 77.7235
2017-07-21 | 9:35 | 1.7507 | 6.3376 |  | 10
2017-07-21 | 9:40 | 1.7663 | 5.7591 |  | 10
2017-07-21 | 9:45 | 1.7202 | 5.8598 | 1 | 10 | 61.1114 | 78.1696
2017-07-21 | 9:50 | 1.7312 | 5.6438 |  | 10
2017-07-21 | 9:55 | 1.767 | 5.324 |  | 10
2017-07-21 | 10:00 | 1.6243 | 3.5659 | 0 | 1.5 | 39.6445 | 79.41
2017-07-21 | 10:05 | 1.7187 | 1.9439 |  | 1.5
2017-07-21 | 10:10 | 1.7241 | 0 |  | 1.5
2017-07-21 | 10:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 80.2371
2017-07-21 | 10:20 | 1.7491 | 0 |  | 1.5
2017-07-21 | 10:25 | 1.7569 | 0 |  | 1.5
2017-07-21 | 10:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 80.445
2017-07-21 | 10:35 | 1.739 | 0 |  | 1.5
2017-07-21 | 10:40 | 1.7179 | 0 |  | 1.5
2017-07-21 | 10:45 | 1.767 | 0 | 0 | 1.5 | 25 | 80.4995
2017-07-21 | 10:50 | 1.7312 | 0 |  | 1.5
2017-07-21 | 10:55 | 1.7163 | 0 |  | 1.5
2017-07-21 | 11:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 81.0299
2017-07-21 | 11:05 | 1.7257 | 0 |  | 1.5
2017-07-21 | 11:10 | 1.7397 | 0 |  | 1.5
2017-07-21 | 11:15 | 1.7327 | 0 | 0 | 1.5 | 25 | 81.4033
2017-07-21 | 11:20 | 1.7374 | 0 |  | 1.5
2017-07-21 | 11:25 | 1.7187 | 0 |  | 1.5
2017-07-21 | 11:30 | 1.707 | 0 | 0 | 1.5 | 25 | 82.1078
2017-07-21 | 11:35 | 1.7218 | 0 |  | 1.5
2017-07-21 | 11:40 | 1.7179 | 0 |  | 1.5
2017-07-21 | 11:45 | 1.7023 | 0 | 0 | 1.5 | 25 | 83.1646
2017-07-21 | 11:50 | 1.7265 | 0 |  | 1.5
2017-07-21 | 11:55 | 1.7218 | 0 |  | 1.5
2017-07-21 | 12:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 83.814
2017-07-21 | 12:05 | 1.7499 | 0 |  | 1.5
2017-07-21 | 12:10 | 1.7234 | 0 |  | 1.5
2017-07-21 | 12:15 | 1.6961 | 0 | 0 | 1.5 | 25 | 84.81
2017-07-21 | 12:20 | 1.7163 | 0 |  | 1.5
2017-07-21 | 12:25 | 1.7039 | 0 |  | 1.5
2017-07-21 | 12:30 | 1.6968 | 0 | 0 | 1.5 | 25 | 86.1267
2017-07-21 | 12:35 | 1.7257 | 0 |  | 1.5
2017-07-21 | 12:40 | 1.7429 | 0 |  | 1.5
2017-07-21 | 12:45 | 1.7327 | 0 | 0 | 1.5 | 25 | 86.5705
2017-07-21 | 12:50 | 1.7343 | 0 |  | 1.5
2017-07-21 | 12:55 | 1.7585 | 0 |  | 1.5
2017-07-21 | 13:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 86.6708
2017-07-21 | 13:05 | 1.7546 | 0 |  | 1.5
2017-07-21 | 13:10 | 1.753 | 0 |  | 1.5
2017-07-21 | 13:15 | 1.778 | 0 | 0 | 1.5 | 25 | 86.6924
2017-07-21 | 13:20 | 1.7452 | 0 |  | 1.5
2017-07-21 | 13:25 | 1.7327 | 0 |  | 1.5
2017-07-21 | 13:30 | 1.7577 | 0 | 0 | 1.5 | 25 | 86.6493
2017-07-21 | 13:35 | 1.7421 | 0 |  | 1.5
2017-07-21 | 13:40 | 1.7202 | 0 |  | 1.5
2017-07-21 | 13:45 | 1.7023 | 0 | 0 | 1.5 | 25 | 87.3833
2017-07-21 | 13:50 | 1.7234 | 0 |  | 1.5
2017-07-21 | 13:55 | 1.7616 | 0 |  | 1.5
2017-07-21 | 14:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 87.8369
2017-07-21 | 14:05 | 1.7507 | 0 |  | 1.5
2017-07-21 | 14:10 | 1.7592 | 0 |  | 1.5
2017-07-21 | 14:15 | 1.7678 | 0 | 0 | 1.5 | 25 | 87.5889
2017-07-21 | 14:20 | 1.739 | 0 |  | 1.5
2017-07-21 | 14:25 | 1.7491 | 0 |  | 1.5
2017-07-21 | 14:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 87.6768
2017-07-21 | 14:35 | 1.7483 | 0 |  | 1.5
2017-07-21 | 14:40 | 1.76 | 0 |  | 1.5
2017-07-21 | 14:45 | 1.767 | 0 | 0 | 1.5 | 25 | 87.605
2017-07-21 | 14:50 | 1.7748 | 0 |  | 1.5
2017-07-21 | 14:55 | 1.7561 | 0 |  | 1.5
2017-07-21 | 15:00 | 1.76 | 0 | 0 | 1.5 | 25 | 87.4117
2017-07-21 | 15:05 | 1.7514 | 0 |  | 1.5
2017-07-21 | 15:10 | 1.7163 | 0 |  | 1.5
2017-07-21 | 15:15 | 1.7234 | 0 | 0 | 1.5 | 25 | 87.6254
2017-07-21 | 15:20 | 1.7405 | 0 |  | 1.5
2017-07-21 | 15:25 | 1.7787 | 0 |  | 1.5
2017-07-21 | 15:30 | 1.7639 | 0 | 0 | 1.5 | 25 | 87.5434
2017-07-21 | 15:35 | 1.7795 | 0 |  | 1.5
2017-07-21 | 15:40 | 1.7803 | 0 |  | 1.5
2017-07-21 | 15:45 | 1.7928 | 0 | 0 | 1.5 | 25 | 86.8274
2017-07-21 | 15:50 | 1.7733 | 0 |  | 1.5
2017-07-21 | 15:55 | 1.7553 | 0 |  | 1.5
2017-07-21 | 16:00 | 1.7624 | 0 | 0 | 1.5 | 25 | 86.2468
2017-07-21 | 16:05 | 1.7834 | 0 |  | 1.5
2017-07-21 | 16:10 | 1.7842 | 0 |  | 1.5
2017-07-21 | 16:15 | 1.7709 | 0 | 0 | 1.5 | 25 | 85.6731
2017-07-21 | 16:20 | 1.7647 | 0 |  | 1.5
2017-07-21 | 16:25 | 1.753 | 0 |  | 1.5
2017-07-21 | 16:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 85.3789
2017-07-21 | 16:35 | 1.7702 | 0 |  | 1.5
2017-07-21 | 16:40 | 1.7296 | 0 |  | 1.5
2017-07-21 | 16:45 | 1.76 | 0 | 0 | 1.5 | 25 | 85.7074
2017-07-21 | 16:50 | 1.8053 | 0 |  | 1.5
2017-07-21 | 16:55 | 1.7756 | 0 |  | 1.5
2017-07-21 | 17:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 85.0124
2017-07-21 | 17:05 | 1.7452 | 0 |  | 1.5
2017-07-21 | 17:10 | 1.7865 | 0 |  | 1.5
2017-07-21 | 17:15 | 1.7405 | 0 | 0 | 1.5 | 25 | 84.4867
2017-07-21 | 17:20 | 1.7764 | 0 |  | 1.5
2017-07-21 | 17:25 | 1.8053 | 0 |  | 1.5
2017-07-21 | 17:30 | 1.7764 | 0 | 0 | 1.5 | 25 | 83.9752
2017-07-21 | 17:35 | 1.7873 | 0 |  | 1.5
2017-07-21 | 17:40 | 1.7725 | 0 |  | 1.5
2017-07-21 | 17:45 | 1.746 | 0 | 0 | 1.5 | 25 | 83.2769
2017-07-21 | 17:50 | 1.7865 | 0 |  | 1.5
2017-07-21 | 17:55 | 1.7889 | 0 |  | 1.5
2017-07-21 | 18:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 82.8107
2017-07-21 | 18:05 | 1.7733 | 0 |  | 1.5
2017-07-21 | 18:10 | 1.7811 | 0 |  | 1.5
2017-07-21 | 18:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 82.3932
2017-07-21 | 18:20 | 1.7709 | 0 |  | 1.5
2017-07-21 | 18:25 | 1.7608 | 0 |  | 1.5
2017-07-21 | 18:30 | 1.7819 | 0 | 0 | 1.5 | 25 | 81.9528
2017-07-21 | 18:35 | 1.7741 | 0 |  | 1.5
2017-07-21 | 18:40 | 1.7811 | 0 |  | 1.5
2017-07-21 | 18:45 | 1.753 | 0 | 0 | 1.5 | 25 | 81.4343
2017-07-21 | 18:50 | 1.7694 | 0 |  | 1.5
2017-07-21 | 18:55 | 1.7686 | 0 |  | 1.5
2017-07-21 | 19:00 | 1.753 | 0 | 0 | 1.5 | 25 | 81.1238
2017-07-21 | 19:05 | 1.7694 | 0 |  | 1.5
2017-07-21 | 19:10 | 1.7475 | 0 |  | 1.5
2017-07-21 | 19:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 80.819
2017-07-21 | 19:20 | 1.7647 | 0 |  | 1.5
2017-07-21 | 19:25 | 1.7507 | 0 |  | 1.5
2017-07-21 | 19:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 80.6767
2017-07-21 | 19:35 | 1.753 | 0 |  | 1.5
2017-07-21 | 19:40 | 1.7741 | 0 |  | 1.5
2017-07-21 | 19:45 | 1.7374 | 0 | 0 | 1.5 | 25 | 80.541
2017-07-21 | 19:50 | 1.7358 | 0 |  | 1.5
2017-07-21 | 19:55 | 1.753 | 0 |  | 1.5
2017-07-21 | 20:00 | 1.7553 | 0 | 0 | 1.5 | 25 | 80.3178
2017-07-21 | 20:05 | 1.7592 | 0 |  | 1.5
2017-07-21 | 20:10 | 1.767 | 0 |  | 1.5
2017-07-21 | 20:15 | 1.7444 | 0 | 0 | 1.5 | 25 | 80.1353
2017-07-21 | 20:20 | 1.7304 | 0 |  | 1.5
2017-07-21 | 20:25 | 1.7483 | 0 |  | 1.5
2017-07-21 | 20:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 79.968
2017-07-21 | 20:35 | 1.7639 | 0 |  | 1.5
2017-07-21 | 20:40 | 1.7709 | 0 |  | 1.5
2017-07-21 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 25 | 79.8384
2017-07-21 | 20:50 | 1.7624 | 0 |  | 1.5
2017-07-21 | 20:55 | 1.7468 | 0 |  | 1.5
2017-07-21 | 21:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.7003
2017-07-21 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-21 | 21:10 | -0.10496 | 0 |  | 1.5
2017-07-21 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 21:20 | -0.10652 | 0 |  | 1.5
2017-07-21 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-21 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-21 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-21 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-21 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-21 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 22:05 | -0.10886 | 0 |  | 1.5
2017-07-21 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-21 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-21 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-21 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-21 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-21 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-21 | 22:55 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 23:20 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 23:35 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-21 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-21 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 0:35 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 0:50 | -0.10496 | 0 |  | 1.5
2017-07-22 | 0:55 | -0.1034 | 0 |  | 1.5
2017-07-22 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-22 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-22 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-22 | 1:25 | -0.10808 | 0 |  | 1.5
2017-07-22 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 1:35 | -0.10808 | 0 |  | 1.5
2017-07-22 | 1:40 | -0.10808 | 0 |  | 1.5
2017-07-22 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 1:50 | -0.10808 | 0 |  | 1.5
2017-07-22 | 1:55 | -0.10808 | 0 |  | 1.5
2017-07-22 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-22 | 2:10 | -0.10808 | 0 |  | 1.5
2017-07-22 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 2:20 | -0.10808 | 0 |  | 1.5
2017-07-22 | 2:25 | -0.10808 | 0 |  | 1.5
2017-07-22 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 2:35 | -0.10808 | 0 |  | 1.5
2017-07-22 | 2:40 | -0.10808 | 0 |  | 1.5
2017-07-22 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 2:50 | -0.10886 | 0 |  | 1.5
2017-07-22 | 2:55 | -0.10808 | 0 |  | 1.5
2017-07-22 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 3:05 | -0.10808 | 0 |  | 1.5
2017-07-22 | 3:10 | -0.10886 | 0 |  | 1.5
2017-07-22 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 3:20 | -0.10964 | 0 |  | 1.5
2017-07-22 | 3:25 | -0.10964 | 0 |  | 1.5
2017-07-22 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 3:35 | -0.10886 | 0 |  | 1.5
2017-07-22 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-22 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-22 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:10 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:40 | -0.11588 | 0 |  | 1.5
2017-07-22 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-22 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-22 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 5:05 | 2.2912 | 6.0328 |  | 10
2017-07-22 | 5:10 | 2.1071 | 10 |  | 10
2017-07-22 | 5:15 | 2.033 | 10 | 1 | 10 | 100 | 90.1365
2017-07-22 | 5:20 | 1.9815 | 10 |  | 10
2017-07-22 | 5:25 | 1.9254 | 9.8677 |  | 10
2017-07-22 | 5:30 | 1.8716 | 9.2731 | 1 | 10 | 93.428 | 85.1818
2017-07-22 | 5:35 | 1.8755 | 8.7613 |  | 10
2017-07-22 | 5:40 | 1.8294 | 8.3714 |  | 10
2017-07-22 | 5:45 | 1.8287 | 7.6753 | 1 | 10 | 77.8242 | 82.4793
2017-07-22 | 5:50 | 1.8131 | 7.3886 |  | 10
2017-07-22 | 5:55 | 1.8333 | 7.1236 |  | 10
2017-07-22 | 6:00 | 1.8131 | 6.8594 | 1 | 10 | 69.6204 | 80.1738
2017-07-22 | 6:05 | 1.7936 | 6.9797 |  | 10
2017-07-22 | 6:10 | 1.7655 | 6.7392 |  | 10
2017-07-22 | 6:15 | 1.7678 | 7.005 | 1 | 10 | 70.7761 | 79.0976
2017-07-22 | 6:20 | 1.7897 | 6.8326 |  | 10
2017-07-22 | 6:25 | 1.7717 | 6.6277 |  | 10
2017-07-22 | 6:30 | 1.7663 | 6.5362 | 1 | 10 | 66.4892 | 78.5084
2017-07-22 | 6:35 | 1.7819 | 6.4354 |  | 10
2017-07-22 | 6:40 | 1.7686 | 6.5609 |  | 10
2017-07-22 | 6:45 | 1.7499 | 6.1828 | 1 | 10 | 63.1938 | 78.2374
2017-07-22 | 6:50 | 1.7694 | 6.1638 |  | 10
2017-07-22 | 6:55 | 1.6937 | 6.1784 |  | 1.5
2017-07-22 | 7:00 | 1.7054 | 1.9324 | 0 | 1.5 | 25 | 79.3578
2017-07-22 | 7:05 | 1.8326 | 2.8191 |  | 10
2017-07-22 | 7:10 | 1.824 | 4.292 |  | 10
2017-07-22 | 7:15 | 1.7748 | 5.2514 | 1 | 10 | 66.4274 | 77.6499
2017-07-22 | 7:20 | 1.7975 | 5.5229 |  | 10
2017-07-22 | 7:25 | 1.7569 | 5.6855 |  | 10
2017-07-22 | 7:30 | 1.7608 | 5.9846 | 1 | 10 | 73.8932 | 77.1724
2017-07-22 | 7:35 | 1.7483 | 5.8985 |  | 10
2017-07-22 | 7:40 | 1.7507 | 5.9996 |  | 10
2017-07-22 | 7:45 | 1.7608 | 5.6681 | 1 | 10 | 71.1877 | 77.204
2017-07-22 | 7:50 | 1.7382 | 5.7553 |  | 10
2017-07-22 | 7:55 | 1.7148 | 5.959 |  | 10
2017-07-22 | 8:00 | 1.7452 | 5.8772 | 1 | 10 | 72.8024 | 77.4178
2017-07-22 | 8:05 | 1.7288 | 6.1096 |  | 10
2017-07-22 | 8:10 | 1.7967 | 3.2356 |  | 10
2017-07-22 | 8:15 | 1.7951 | 1.239 | 1 | 10 | 28.7 | 76.9744
2017-07-22 | 8:20 | 1.5954 | 0 |  | 1.5
2017-07-22 | 8:25 | 1.6656 | 0 |  | 1.5
2017-07-22 | 8:30 | 1.6758 | 0 | 0 | 1.5 | 25 | 78.7232
2017-07-22 | 8:35 | 1.6906 | 0 |  | 1.5
2017-07-22 | 8:40 | 1.7039 | 0 |  | 1.5
2017-07-22 | 8:45 | 1.7452 | 0 | 0 | 1.5 | 25 | 79.8009
2017-07-22 | 8:50 | 1.7733 | 0 |  | 1.5
2017-07-22 | 8:55 | 1.739 | 0 |  | 1.5
2017-07-22 | 9:00 | 1.746 | 0 | 0 | 1.5 | 25 | 79.988
2017-07-22 | 9:05 | 1.7265 | 0 |  | 1.5
2017-07-22 | 9:10 | 1.7429 | 0 |  | 1.5
2017-07-22 | 9:15 | 1.7366 | 0 | 0 | 1.5 | 25 | 79.9916
2017-07-22 | 9:20 | 1.7202 | 0 |  | 1.5
2017-07-22 | 9:25 | 1.7507 | 0 |  | 1.5
2017-07-22 | 9:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 80.1799
2017-07-22 | 9:35 | 1.7241 | 0 |  | 1.5
2017-07-22 | 9:40 | 1.7702 | 0 |  | 1.5
2017-07-22 | 9:45 | 1.7678 | 0 | 0 | 1.5 | 25 | 80.1636
2017-07-22 | 9:50 | 1.7405 | 0 |  | 1.5
2017-07-22 | 9:55 | 1.746 | 0 |  | 1.5
2017-07-22 | 10:00 | 1.7397 | 0 | 0 | 1.5 | 25 | 80.3456
2017-07-22 | 10:05 | 1.7624 | 0 |  | 1.5
2017-07-22 | 10:10 | 1.7249 | 0 |  | 1.5
2017-07-22 | 10:15 | 1.7358 | 0 | 0 | 1.5 | 25 | 80.5956
2017-07-22 | 10:20 | 1.746 | 0 |  | 1.5
2017-07-22 | 10:25 | 1.7093 | 0 |  | 1.5
2017-07-22 | 10:30 | 1.7327 | 0 | 0 | 1.5 | 25 | 81.0017
2017-07-22 | 10:35 | 1.7452 | 0 |  | 1.5
2017-07-22 | 10:40 | 1.7507 | 0 |  | 1.5
2017-07-22 | 10:45 | 1.7608 | 0 | 0 | 1.5 | 25 | 81.2578
2017-07-22 | 10:50 | 1.753 | 0 |  | 1.5
2017-07-22 | 10:55 | 1.7608 | 0 |  | 1.5
2017-07-22 | 11:00 | 1.7241 | 0 | 0 | 1.5 | 25 | 81.5946
2017-07-22 | 11:05 | 1.7296 | 0 |  | 1.5
2017-07-22 | 11:10 | 1.7319 | 0 |  | 1.5
2017-07-22 | 11:15 | 1.721 | 0 | 0 | 1.5 | 25 | 82.2335
2017-07-22 | 11:20 | 1.7202 | 0 |  | 1.5
2017-07-22 | 11:25 | 1.7351 | 0 |  | 1.5
2017-07-22 | 11:30 | 1.7273 | 0 | 0 | 1.5 | 25 | 82.9176
2017-07-22 | 11:35 | 1.6914 | 0 |  | 1.5
2017-07-22 | 11:40 | 1.7109 | 0 |  | 1.5
2017-07-22 | 11:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 83.7042
2017-07-22 | 11:50 | 1.7405 | 0 |  | 1.5
2017-07-22 | 11:55 | 1.7842 | 0 |  | 1.5
2017-07-22 | 12:00 | 1.7499 | 0 | 0 | 1.5 | 25 | 83.612
2017-07-22 | 12:05 | 1.7694 | 0 |  | 1.5
2017-07-22 | 12:10 | 1.7397 | 0 |  | 1.5
2017-07-22 | 12:15 | 1.7397 | 0 | 0 | 1.5 | 25 | 83.8093
2017-07-22 | 12:20 | 1.7257 | 0 |  | 1.5
2017-07-22 | 12:25 | 1.7288 | 0 |  | 1.5
2017-07-22 | 12:30 | 1.7054 | 0 | 0 | 1.5 | 25 | 84.3784
2017-07-22 | 12:35 | 1.7226 | 0 |  | 1.5
2017-07-22 | 12:40 | 1.7546 | 0 |  | 1.5
2017-07-22 | 12:45 | 1.7015 | 0 | 0 | 1.5 | 25 | 85.1602
2017-07-22 | 12:50 | 1.6976 | 0 |  | 1.5
2017-07-22 | 12:55 | 1.7374 | 0 |  | 1.5
2017-07-22 | 13:00 | 1.7179 | 0 | 0 | 1.5 | 25 | 85.9109
2017-07-22 | 13:05 | 1.7366 | 0 |  | 1.5
2017-07-22 | 13:10 | 1.7265 | 0 |  | 1.5
2017-07-22 | 13:15 | 1.7312 | 0 | 0 | 1.5 | 25 | 86.5951
2017-07-22 | 13:20 | 1.7319 | 0 |  | 1.5
2017-07-22 | 13:25 | 1.7405 | 0 |  | 1.5
2017-07-22 | 13:30 | 1.7101 | 0 | 0 | 1.5 | 25 | 87.4005
2017-07-22 | 13:35 | 1.7241 | 0 |  | 1.5
2017-07-22 | 13:40 | 1.7312 | 0 |  | 1.5
2017-07-22 | 13:45 | 1.7241 | 0 | 0 | 1.5 | 25 | 88.2269
2017-07-22 | 13:50 | 1.7148 | 0 |  | 1.5
2017-07-22 | 13:55 | 1.7046 | 0 |  | 1.5
2017-07-22 | 14:00 | 1.7163 | 0 | 0 | 1.5 | 25 | 88.8707
2017-07-22 | 14:05 | 1.7234 | 0 |  | 1.5
2017-07-22 | 14:10 | 1.7257 | 0 |  | 1.5
2017-07-22 | 14:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 89.2983
2017-07-22 | 14:20 | 1.7202 | 0 |  | 1.5
2017-07-22 | 14:25 | 1.7265 | 0 |  | 1.5
2017-07-22 | 14:30 | 1.7483 | 0 | 0 | 1.5 | 25 | 89.6766
2017-07-22 | 14:35 | 1.7405 | 0 |  | 1.5
2017-07-22 | 14:40 | 1.7273 | 0 |  | 1.5
2017-07-22 | 14:45 | 1.7616 | 0 | 0 | 1.5 | 25 | 90.1643
2017-07-22 | 14:50 | 1.7483 | 0 |  | 1.5
2017-07-22 | 14:55 | 1.7319 | 0 |  | 1.5
2017-07-22 | 15:00 | 1.767 | 0 | 0 | 1.5 | 25 | 90.4637
2017-07-22 | 15:05 | 1.746 | 0 |  | 1.5
2017-07-22 | 15:10 | 1.7351 | 0 |  | 1.5
2017-07-22 | 15:15 | 1.7514 | 0 | 0 | 1.5 | 25 | 90.4418
2017-07-22 | 15:20 | 1.7764 | 0 |  | 1.5
2017-07-22 | 15:25 | 1.7522 | 0 |  | 1.5
2017-07-22 | 15:30 | 1.7616 | 0 | 0 | 1.5 | 25 | 90.2517
2017-07-22 | 15:35 | 1.7764 | 0 |  | 1.5
2017-07-22 | 15:40 | 1.7546 | 0 |  | 1.5
2017-07-22 | 15:45 | 1.7764 | 0 | 0 | 1.5 | 25 | 89.7887
2017-07-22 | 15:50 | 1.7514 | 0 |  | 1.5
2017-07-22 | 15:55 | 1.7624 | 0 |  | 1.5
2017-07-22 | 16:00 | 1.7733 | 0.010001 | 0 | 1.5 | 25 | 89.2776
2017-07-22 | 16:05 | 1.7764 | 0 |  | 1.5
2017-07-22 | 16:10 | 1.7616 | 0 |  | 1.5
2017-07-22 | 16:15 | 1.7382 | 0 | 0 | 1.5 | 25 | 88.9118
2017-07-22 | 16:20 | 1.7725 | 0 |  | 1.5
2017-07-22 | 16:25 | 1.7717 | 0 |  | 1.5
2017-07-22 | 16:30 | 1.8014 | 0 | 0 | 1.5 | 25 | 88.3677
2017-07-22 | 16:35 | 1.7382 | 0 |  | 1.5
2017-07-22 | 16:40 | 1.7429 | 0 |  | 1.5
2017-07-22 | 16:45 | 1.753 | 0 | 0 | 1.5 | 25 | 88.1645
2017-07-22 | 16:50 | 1.746 | 0 |  | 1.5
2017-07-22 | 16:55 | 1.7546 | 0 |  | 1.5
2017-07-22 | 17:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 88.0203
2017-07-22 | 17:05 | 1.7725 | 0 |  | 1.5
2017-07-22 | 17:10 | 1.7678 | 0 |  | 1.5
2017-07-22 | 17:15 | 1.7826 | 0 | 0 | 1.5 | 25 | 87.7438
2017-07-22 | 17:20 | 1.7569 | 0 |  | 1.5
2017-07-22 | 17:25 | 1.7912 | 0 |  | 1.5
2017-07-22 | 17:30 | 1.792 | 0 | 0 | 1.5 | 25 | 87.0501
2017-07-22 | 17:35 | 1.7741 | 0 |  | 1.5
2017-07-22 | 17:40 | 1.7491 | 0 |  | 1.5
2017-07-22 | 17:45 | 1.778 | 0 | 0 | 1.5 | 25 | 86.395
2017-07-22 | 17:50 | 1.7842 | 0 |  | 1.5
2017-07-22 | 17:55 | 1.7842 | 0 |  | 1.5
2017-07-22 | 18:00 | 1.8068 | 0 | 0 | 1.5 | 25 | 85.5609
2017-07-22 | 18:05 | 1.8021 | 0 |  | 1.5
2017-07-22 | 18:10 | 1.7702 | 0 |  | 1.5
2017-07-22 | 18:15 | 1.7834 | 0 | 0 | 1.5 | 25 | 84.8264
2017-07-22 | 18:20 | 1.7756 | 0 |  | 1.5
2017-07-22 | 18:25 | 1.7881 | 0 |  | 1.5
2017-07-22 | 18:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 84.1895
2017-07-22 | 18:35 | 1.7647 | 0 |  | 1.5
2017-07-22 | 18:40 | 1.7616 | 0 |  | 1.5
2017-07-22 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 83.7058
2017-07-22 | 18:50 | 1.7826 | 0 |  | 1.5
2017-07-22 | 18:55 | 1.7889 | 0 |  | 1.5
2017-07-22 | 19:00 | 1.7811 | 0 | 0 | 1.5 | 25 | 83.0145
2017-07-22 | 19:05 | 1.7881 | 0 |  | 1.5
2017-07-22 | 19:10 | 1.7538 | 0 |  | 1.5
2017-07-22 | 19:15 | 1.7109 | 0 | 0 | 1.5 | 25 | 82.8647
2017-07-22 | 19:20 | 1.7663 | 0 |  | 1.5
2017-07-22 | 19:25 | 1.7639 | 0 |  | 1.5
2017-07-22 | 19:30 | 1.7686 | 0 | 0 | 1.5 | 25 | 82.7768
2017-07-22 | 19:35 | 1.7436 | 0 |  | 1.5
2017-07-22 | 19:40 | 1.7319 | 0 |  | 1.5
2017-07-22 | 19:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 82.8268
2017-07-22 | 19:50 | 1.7491 | 0 |  | 1.5
2017-07-22 | 19:55 | 1.7538 | 0 |  | 1.5
2017-07-22 | 20:00 | 1.7733 | 0 | 0 | 1.5 | 25 | 82.5633
2017-07-22 | 20:05 | 1.7787 | 0 |  | 1.5
2017-07-22 | 20:10 | 1.7748 | 0 |  | 1.5
2017-07-22 | 20:15 | 1.7811 | 0 | 0 | 1.5 | 25 | 82.141
2017-07-22 | 20:20 | 1.7421 | 0 |  | 1.5
2017-07-22 | 20:25 | 1.7998 | 0 |  | 1.5
2017-07-22 | 20:30 | 1.7881 | 0 | 0 | 1.5 | 25 | 81.6959
2017-07-22 | 20:35 | 1.7647 | 0 |  | 1.5
2017-07-22 | 20:40 | 1.7304 | 0 |  | 1.5
2017-07-22 | 20:45 | 1.7733 | 0 | 0 | 1.5 | 25 | 81.4021
2017-07-22 | 20:50 | 1.7429 | 0 |  | 1.5
2017-07-22 | 20:55 | 1.7772 | 0 |  | 1.5
2017-07-22 | 21:00 | 1.7444 | 0 | 0 | 1.5 | 25 | 81.1557
2017-07-22 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-22 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-22 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-22 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-22 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-22 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-22 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-22 | 21:55 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-22 | 22:55 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 23:05 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:10 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 23:20 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:25 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:40 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-22 | 23:50 | -0.10496 | 0 |  | 1.5
2017-07-22 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-23 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-23 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-23 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 0:20 | -0.10418 | 0 |  | 1.5
2017-07-23 | 0:25 | -0.10418 | 0 |  | 1.5
2017-07-23 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 0:35 | -0.1034 | 0 |  | 1.5
2017-07-23 | 0:40 | -0.1034 | 0 |  | 1.5
2017-07-23 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 0:50 | -0.1034 | 0 |  | 1.5
2017-07-23 | 0:55 | -0.1034 | 0 |  | 1.5
2017-07-23 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 1:05 | -0.1034 | 0 |  | 1.5
2017-07-23 | 1:10 | -0.1034 | 0 |  | 1.5
2017-07-23 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 1:20 | -0.10652 | 0 |  | 1.5
2017-07-23 | 1:25 | -0.10652 | 0 |  | 1.5
2017-07-23 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 1:35 | -0.10652 | 0 |  | 1.5
2017-07-23 | 1:40 | -0.10652 | 0 |  | 1.5
2017-07-23 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 1:50 | -0.10652 | 0 |  | 1.5
2017-07-23 | 1:55 | -0.10652 | 0 |  | 1.5
2017-07-23 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 2:05 | -0.10652 | 0 |  | 1.5
2017-07-23 | 2:10 | -0.10652 | 0 |  | 1.5
2017-07-23 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 2:20 | -0.1073 | 0 |  | 1.5
2017-07-23 | 2:25 | -0.1073 | 0 |  | 1.5
2017-07-23 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 2:35 | -0.1073 | 0 |  | 1.5
2017-07-23 | 2:40 | -0.1073 | 0 |  | 1.5
2017-07-23 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 2:50 | -0.1073 | 0 |  | 1.5
2017-07-23 | 2:55 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 3:05 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:10 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 3:20 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:25 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 3:35 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:40 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 3:50 | -0.1073 | 0 |  | 1.5
2017-07-23 | 3:55 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 4:05 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:10 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 4:20 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:25 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 4:35 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:40 | -0.10808 | 0 |  | 1.5
2017-07-23 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 4:50 | -0.1073 | 0 |  | 1.5
2017-07-23 | 4:55 | -0.10808 | 0 |  | 1.5
2017-07-23 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 5:05 | 2.0517 | 5.8038 |  | 10
2017-07-23 | 5:10 | 1.9191 | 10 |  | 10
2017-07-23 | 5:15 | 1.9012 | 10 | 1 | 10 | 100 | 93.9
2017-07-23 | 5:20 | 1.8677 | 10 |  | 10
2017-07-23 | 5:25 | 1.8591 | 10 |  | 10
2017-07-23 | 5:30 | 1.9301 | 10 | 1 | 10 | 100 | 90.2984
2017-07-23 | 5:35 | 1.9503 | 9.9843 |  | 10
2017-07-23 | 5:40 | 1.8996 | 9.716 |  | 10
2017-07-23 | 5:45 | 1.8536 | 9.3883 | 1 | 10 | 94.3028 | 85.7104
2017-07-23 | 5:50 | 1.8357 | 9.1066 |  | 10
2017-07-23 | 5:55 | 1.8544 | 8.7441 |  | 10
2017-07-23 | 6:00 | 1.8365 | 8.3025 | 1 | 10 | 83.8839 | 83.1933
2017-07-23 | 6:05 | 1.8185 | 7.9959 |  | 10
2017-07-23 | 6:10 | 1.8279 | 7.9301 |  | 10
2017-07-23 | 6:15 | 1.8021 | 7.6846 | 1 | 10 | 77.6689 | 81.2412
2017-07-23 | 6:20 | 1.8014 | 7.8288 |  | 10
2017-07-23 | 6:25 | 1.7975 | 7.4824 |  | 10
2017-07-23 | 6:30 | 1.7904 | 7.4849 | 1 | 10 | 75.2838 | 79.9737
2017-07-23 | 6:35 | 1.7764 | 7.6755 |  | 10
2017-07-23 | 6:40 | 1.7819 | 7.5631 |  | 10
2017-07-23 | 6:45 | 1.7655 | 7.6539 | 1 | 10 | 77.4734 | 79.4271
2017-07-23 | 6:50 | 1.7624 | 7.0198 |  | 10
2017-07-23 | 6:55 | 1.7717 | 6.7962 |  | 10
2017-07-23 | 7:00 | 1.7764 | 6.5816 | 1 | 10 | 67.0389 | 78.8481
2017-07-23 | 7:05 | 1.7468 | 6.3431 |  | 10
2017-07-23 | 7:10 | 1.7709 | 6.6866 |  | 10
2017-07-23 | 7:15 | 1.7663 | 7.2925 | 1 | 10 | 73.7372 | 78.4403
2017-07-23 | 7:20 | 1.7709 | 6.9816 |  | 10
2017-07-23 | 7:25 | 1.7468 | 6.5388 |  | 10
2017-07-23 | 7:30 | 1.7577 | 6.4837 | 1 | 10 | 65.5948 | 78.1218
2017-07-23 | 7:35 | 1.7561 | 6.458 |  | 10
2017-07-23 | 7:40 | 1.7756 | 6.4567 |  | 10
2017-07-23 | 7:45 | 1.7694 | 6.8658 | 1 | 10 | 68.8608 | 77.931
2017-07-23 | 7:50 | 1.7741 | 6.4165 |  | 10
2017-07-23 | 7:55 | 1.7522 | 6.085 |  | 10
2017-07-23 | 8:00 | 1.7569 | 6.4667 | 1 | 10 | 65.8867 | 77.7227
2017-07-23 | 8:05 | 1.753 | 6.2413 |  | 10
2017-07-23 | 8:10 | 1.7709 | 5.8004 |  | 10
2017-07-23 | 8:15 | 1.682 | 2.0146 | 0 | 1.5 | 25 | 78.1123
2017-07-23 | 8:20 | 1.6875 | 0 |  | 1.5
2017-07-23 | 8:25 | 1.7202 | 0 |  | 1.5
2017-07-23 | 8:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 78.9902
2017-07-23 | 8:35 | 1.7624 | 0 |  | 1.5
2017-07-23 | 8:40 | 1.739 | 0 |  | 1.5
2017-07-23 | 8:45 | 1.7413 | 0 | 0 | 1.5 | 25 | 79.1428
2017-07-23 | 8:50 | 1.7514 | 0 |  | 1.5
2017-07-23 | 8:55 | 1.7553 | 0 |  | 1.5
2017-07-23 | 9:00 | 1.753 | 0 | 0 | 1.5 | 25 | 78.9602
2017-07-23 | 9:05 | 1.7834 | 0 |  | 1.5
2017-07-23 | 9:10 | 1.7553 | 0 |  | 1.5
2017-07-23 | 9:15 | 1.7429 | 0 | 0 | 1.5 | 25 | 78.9908
2017-07-23 | 9:20 | 1.7507 | 0 |  | 1.5
2017-07-23 | 9:25 | 1.7475 | 0 |  | 1.5
2017-07-23 | 9:30 | 1.746 | 0 | 0 | 1.5 | 25 | 79.0174
2017-07-23 | 9:35 | 1.7382 | 0 |  | 1.5
2017-07-23 | 9:40 | 1.7561 | 0 |  | 1.5
2017-07-23 | 9:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 79.1145
2017-07-23 | 9:50 | 1.7569 | 0 |  | 1.5
2017-07-23 | 9:55 | 1.7429 | 0 |  | 1.5
2017-07-23 | 10:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 79.3436
2017-07-23 | 10:05 | 1.7366 | 0 |  | 1.5
2017-07-23 | 10:10 | 1.7546 | 0 |  | 1.5
2017-07-23 | 10:15 | 1.7475 | 0 | 0 | 1.5 | 25 | 79.363
2017-07-23 | 10:20 | 1.7717 | 0 |  | 1.5
2017-07-23 | 10:25 | 1.7452 | 0 |  | 1.5
2017-07-23 | 10:30 | 1.7226 | 0 | 0 | 1.5 | 25 | 79.5097
2017-07-23 | 10:35 | 1.7444 | 0 |  | 1.5
2017-07-23 | 10:40 | 1.7234 | 0 |  | 1.5
2017-07-23 | 10:45 | 1.7351 | 0 | 0 | 1.5 | 25 | 79.6891
2017-07-23 | 10:50 | 1.7429 | 0 |  | 1.5
2017-07-23 | 10:55 | 1.7468 | 0 |  | 1.5
2017-07-23 | 11:00 | 1.7117 | 0 | 0 | 1.5 | 25 | 79.8591
2017-07-23 | 11:05 | 1.7202 | 0 |  | 1.5
2017-07-23 | 11:10 | 1.7171 | 0 |  | 1.5
2017-07-23 | 11:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 80.0368
2017-07-23 | 11:20 | 1.7374 | 0 |  | 1.5
2017-07-23 | 11:25 | 1.7514 | 0 |  | 1.5
2017-07-23 | 11:30 | 1.7413 | 0 | 0 | 1.5 | 25 | 80.2868
2017-07-23 | 11:35 | 1.7374 | 0 |  | 1.5
2017-07-23 | 11:40 | 1.7569 | 0 |  | 1.5
2017-07-23 | 11:45 | 1.7452 | 0 | 0 | 1.5 | 25 | 80.6406
2017-07-23 | 11:50 | 1.6929 | 0 |  | 1.5
2017-07-23 | 11:55 | 1.7148 | 0 |  | 1.5
2017-07-23 | 12:00 | 1.7304 | 0 | 0 | 1.5 | 25 | 81.2234
2017-07-23 | 12:05 | 1.7265 | 0 |  | 1.5
2017-07-23 | 12:10 | 1.7132 | 0 |  | 1.5
2017-07-23 | 12:15 | 1.7132 | 0 | 0 | 1.5 | 25 | 82.1191
2017-07-23 | 12:20 | 1.7187 | 0 |  | 1.5
2017-07-23 | 12:25 | 1.7273 | 0 |  | 1.5
2017-07-23 | 12:30 | 1.7062 | 0 | 0 | 1.5 | 25 | 82.9493
2017-07-23 | 12:35 | 1.7015 | 0 |  | 1.5
2017-07-23 | 12:40 | 1.7109 | 0 |  | 1.5
2017-07-23 | 12:45 | 1.6922 | 0 | 0 | 1.5 | 25 | 84.3175
2017-07-23 | 12:50 | 1.6929 | 0 |  | 1.5
2017-07-23 | 12:55 | 1.6953 | 0 |  | 1.5
2017-07-23 | 13:00 | 1.7374 | 0 | 0 | 1.5 | 25 | 85.4708
2017-07-23 | 13:05 | 1.7514 | 0 |  | 1.5
2017-07-23 | 13:10 | 1.7358 | 0 |  | 1.5
2017-07-23 | 13:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 85.8081
2017-07-23 | 13:20 | 1.7397 | 0 |  | 1.5
2017-07-23 | 13:25 | 1.7475 | 0 |  | 1.5
2017-07-23 | 13:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 85.9772
2017-07-23 | 13:35 | 1.7296 | 0 |  | 1.5
2017-07-23 | 13:40 | 1.7444 | 0 |  | 1.5
2017-07-23 | 13:45 | 1.7444 | 0 | 0 | 1.5 | 25 | 86.2365
2017-07-23 | 13:50 | 1.7195 | 0 |  | 1.5
2017-07-23 | 13:55 | 1.7319 | 0 |  | 1.5
2017-07-23 | 14:00 | 1.7694 | 0 | 0 | 1.5 | 25 | 86.5609
2017-07-23 | 14:05 | 1.7483 | 0 |  | 1.5
2017-07-23 | 14:10 | 1.7335 | 0 |  | 1.5
2017-07-23 | 14:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 86.7902
2017-07-23 | 14:20 | 1.7429 | 0 |  | 1.5
2017-07-23 | 14:25 | 1.7335 | 0 |  | 1.5
2017-07-23 | 14:30 | 1.7202 | 0 | 0 | 1.5 | 25 | 87.1038
2017-07-23 | 14:35 | 1.7663 | 0 |  | 1.5
2017-07-23 | 14:40 | 1.7608 | 0 |  | 1.5
2017-07-23 | 14:45 | 1.7616 | 0 | 0 | 1.5 | 25 | 87.0399
2017-07-23 | 14:50 | 1.7585 | 0 |  | 1.5
2017-07-23 | 14:55 | 1.7117 | 0 |  | 1.5
2017-07-23 | 15:00 | 1.7288 | 0 | 0 | 1.5 | 25 | 87.2169
2017-07-23 | 15:05 | 1.7335 | 0 |  | 1.5
2017-07-23 | 15:10 | 1.7429 | 0 |  | 1.5
2017-07-23 | 15:15 | 1.7686 | 0 | 0 | 1.5 | 25 | 87.2433
2017-07-23 | 15:20 | 1.7631 | 0 |  | 1.5
2017-07-23 | 15:25 | 1.7756 | 0 |  | 1.5
2017-07-23 | 15:30 | 1.7787 | 0 | 0 | 1.5 | 25 | 86.8548
2017-07-23 | 15:35 | 1.7655 | 0 |  | 1.5
2017-07-23 | 15:40 | 1.7608 | 0 |  | 1.5
2017-07-23 | 15:45 | 1.753 | 0 | 0 | 1.5 | 25 | 86.3077
2017-07-23 | 15:50 | 1.7577 | 0 |  | 1.5
2017-07-23 | 15:55 | 1.7249 | 0 |  | 1.5
2017-07-23 | 16:00 | 1.7663 | 0 | 0 | 1.5 | 25 | 86.0626
2017-07-23 | 16:05 | 1.7865 | 0 |  | 1.5
2017-07-23 | 16:10 | 1.7538 | 0 |  | 1.5
2017-07-23 | 16:15 | 1.7702 | 0 | 0 | 1.5 | 25 | 85.7098
2017-07-23 | 16:20 | 1.7686 | 0 |  | 1.5
2017-07-23 | 16:25 | 1.7624 | 0 |  | 1.5
2017-07-23 | 16:30 | 1.767 | 0 | 0 | 1.5 | 25 | 85.2209
2017-07-23 | 16:35 | 1.7647 | 0 |  | 1.5
2017-07-23 | 16:40 | 1.7787 | 0 |  | 1.5
2017-07-23 | 16:45 | 1.7733 | 0 | 0 | 1.5 | 25 | 84.6861
2017-07-23 | 16:50 | 1.7507 | 0 |  | 1.5
2017-07-23 | 16:55 | 1.7546 | 0 |  | 1.5
2017-07-23 | 17:00 | 1.7709 | 0 | 0 | 1.5 | 25 | 84.1161
2017-07-23 | 17:05 | 1.7569 | 0 |  | 1.5
2017-07-23 | 17:10 | 1.7842 | 0 |  | 1.5
2017-07-23 | 17:15 | 1.767 | 0 | 0 | 1.5 | 25 | 83.506
2017-07-23 | 17:20 | 1.8006 | 0 |  | 1.5
2017-07-23 | 17:25 | 1.7928 | 0 |  | 1.5
2017-07-23 | 17:30 | 1.7943 | 0 | 0 | 1.5 | 25 | 82.6593
2017-07-23 | 17:35 | 1.7663 | 0 |  | 1.5
2017-07-23 | 17:40 | 1.7733 | 0 |  | 1.5
2017-07-23 | 17:45 | 1.7764 | 0 | 0 | 1.5 | 25 | 82.0052
2017-07-23 | 17:50 | 1.7811 | 0 |  | 1.5
2017-07-23 | 17:55 | 1.7959 | 0 |  | 1.5
2017-07-23 | 18:00 | 1.7421 | 0 | 0 | 1.5 | 25 | 81.2888
2017-07-23 | 18:05 | 1.7475 | 0 |  | 1.5
2017-07-23 | 18:10 | 1.7631 | 0 |  | 1.5
2017-07-23 | 18:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 81.0546
2017-07-23 | 18:20 | 1.7764 | 0 |  | 1.5
2017-07-23 | 18:25 | 1.7538 | 0 |  | 1.5
2017-07-23 | 18:30 | 1.7655 | 0 | 0 | 1.5 | 25 | 80.64
2017-07-23 | 18:35 | 1.7491 | 0 |  | 1.5
2017-07-23 | 18:40 | 1.7475 | 0 |  | 1.5
2017-07-23 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 80.4531
2017-07-23 | 18:50 | 1.7639 | 0 |  | 1.5
2017-07-23 | 18:55 | 1.7507 | 0 |  | 1.5
2017-07-23 | 19:00 | 1.7444 | 0 | 0 | 1.5 | 25 | 80.3162
2017-07-23 | 19:05 | 1.7499 | 0 |  | 1.5
2017-07-23 | 19:10 | 1.7514 | 0 |  | 1.5
2017-07-23 | 19:15 | 1.739 | 0 | 0 | 1.5 | 25 | 80.1824
2017-07-23 | 19:20 | 1.7702 | 0.088268 |  | 1.5
2017-07-23 | 19:25 | 1.7569 | 0 |  | 1.5
2017-07-23 | 19:30 | 1.7663 | 0 | 0 | 1.5 | 25 | 79.9776
2017-07-23 | 19:35 | 1.7709 | 0.13615 |  | 1.5
2017-07-23 | 19:40 | 1.7327 | 0 |  | 1.5
2017-07-23 | 19:45 | 1.7452 | 0.013443 | 0 | 1.5 | 25 | 79.7059
2017-07-23 | 19:50 | 1.7452 | 0 |  | 1.5
2017-07-23 | 19:55 | 1.7475 | 0 |  | 1.5
2017-07-23 | 20:00 | 1.739 | 0 | 0 | 1.5 | 25 | 79.4762
2017-07-23 | 20:05 | 1.7639 | 0 |  | 1.5
2017-07-23 | 20:10 | 1.7483 | 0 |  | 1.5
2017-07-23 | 20:15 | 1.7655 | 0 | 0 | 1.5 | 25 | 79.2522
2017-07-23 | 20:20 | 1.7312 | 0 |  | 1.5
2017-07-23 | 20:25 | 1.7319 | 0 |  | 1.5
2017-07-23 | 20:30 | 1.7436 | 0 | 0 | 1.5 | 25 | 79.399
2017-07-23 | 20:35 | 1.7468 | 0 |  | 1.5
2017-07-23 | 20:40 | 1.7725 | 0 |  | 1.5
2017-07-23 | 20:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 79.411
2017-07-23 | 20:50 | 1.7358 | 0 |  | 1.5
2017-07-23 | 20:55 | 1.7491 | 0 |  | 1.5
2017-07-23 | 21:00 | 1.7132 | 0 | 0 | 1.5 | 25 | 79.4412
2017-07-23 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-23 | 21:10 | -0.10496 | 0 |  | 1.5
2017-07-23 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-23 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-23 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 21:35 | -0.1073 | 0 |  | 1.5
2017-07-23 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-23 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 21:50 | -0.1073 | 0 |  | 1.5
2017-07-23 | 21:55 | -0.10808 | 0 |  | 1.5
2017-07-23 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 22:05 | -0.1073 | 0 |  | 1.5
2017-07-23 | 22:10 | -0.10808 | 0 |  | 1.5
2017-07-23 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 22:20 | -0.10808 | 0 |  | 1.5
2017-07-23 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-23 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 22:35 | -0.10808 | 0 |  | 1.5
2017-07-23 | 22:40 | -0.10808 | 0 |  | 1.5
2017-07-23 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 22:50 | -0.10808 | 0 |  | 1.5
2017-07-23 | 22:55 | -0.1073 | 0 |  | 1.5
2017-07-23 | 23:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 23:05 | -0.10808 | 0 |  | 1.5
2017-07-23 | 23:10 | -0.10808 | 0 |  | 1.5
2017-07-23 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 23:20 | -0.10808 | 0 |  | 1.5
2017-07-23 | 23:25 | -0.1073 | 0 |  | 1.5
2017-07-23 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 23:35 | -0.1073 | 0 |  | 1.5
2017-07-23 | 23:40 | -0.1073 | 0 |  | 1.5
2017-07-23 | 23:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-23 | 23:50 | -0.1073 | 0 |  | 1.5
2017-07-23 | 23:55 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 0:05 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:10 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 0:20 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:25 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 0:35 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:40 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 0:50 | -0.1073 | 0 |  | 1.5
2017-07-24 | 0:55 | -0.1073 | 0 |  | 1.5
2017-07-24 | 1:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 1:05 | -0.10652 | 0 |  | 1.5
2017-07-24 | 1:10 | -0.1073 | 0 |  | 1.5
2017-07-24 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 1:20 | -0.11042 | 0 |  | 1.5
2017-07-24 | 1:25 | -0.11042 | 0 |  | 1.5
2017-07-24 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 1:35 | -0.11042 | 0 |  | 1.5
2017-07-24 | 1:40 | -0.11042 | 0 |  | 1.5
2017-07-24 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 1:50 | -0.11042 | 0 |  | 1.5
2017-07-24 | 1:55 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 2:05 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:10 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 2:20 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:25 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 2:35 | -0.1112 | 0 |  | 1.5
2017-07-24 | 2:40 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-24 | 2:55 | -0.11042 | 0 |  | 1.5
2017-07-24 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 3:05 | -0.11042 | 0 |  | 1.5
2017-07-24 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-24 | 3:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 3:20 | -0.1112 | 0 |  | 1.5
2017-07-24 | 3:25 | -0.1112 | 0 |  | 1.5
2017-07-24 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 3:35 | -0.1112 | 0 |  | 1.5
2017-07-24 | 3:40 | -0.1112 | 0 |  | 1.5
2017-07-24 | 3:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 3:50 | -0.11042 | 0 |  | 1.5
2017-07-24 | 3:55 | -0.1112 | 0 |  | 1.5
2017-07-24 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 4:05 | -0.11042 | 0 |  | 1.5
2017-07-24 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-24 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 4:20 | -0.11042 | 0 |  | 1.5
2017-07-24 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-24 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-24 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-24 | 4:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 4:50 | -0.11198 | 0 |  | 1.5
2017-07-24 | 4:55 | -0.11198 | 0 |  | 1.5
2017-07-24 | 5:00 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 5:05 | 2.625 | 5.1117 |  | 10
2017-07-24 | 5:10 | 2.3684 | 9.9376 |  | 10
2017-07-24 | 5:15 | 2.1274 | 8.6295 | 1 | 10 | 89.1504 | 85.3836
2017-07-24 | 5:20 | 1.9784 | 7.5763 |  | 10
2017-07-24 | 5:25 | 1.9363 | 7.0772 |  | 10
2017-07-24 | 5:30 | 1.8918 | 6.401 | 1 | 10 | 67.1484 | 79.8581
2017-07-24 | 5:35 | 1.8341 | 6.1921 |  | 10
2017-07-24 | 5:40 | 1.8232 | 5.9334 |  | 10
2017-07-24 | 5:45 | 1.7803 | 5.9015 | 1 | 10 | 61.8718 | 77.9073
2017-07-24 | 5:50 | 1.785 | 6.001 |  | 10
2017-07-24 | 5:55 | 1.785 | 5.5452 |  | 10
2017-07-24 | 6:00 | 1.7187 | 5.6013 | 1 | 10 | 59.0016 | 77.1504
2017-07-24 | 6:05 | 1.7608 | 5.8268 |  | 10
2017-07-24 | 6:10 | 1.721 | 5.9991 |  | 10
2017-07-24 | 6:15 | 1.7608 | 6.0315 | 1 | 10 | 63.3323 | 76.9646
2017-07-24 | 6:20 | 1.714 | 5.7692 |  | 10
2017-07-24 | 6:25 | 1.7374 | 6.1235 |  | 10
2017-07-24 | 6:30 | 1.7366 | 6.1857 | 1 | 10 | 64.6724 | 77.2242
2017-07-24 | 6:35 | 1.7499 | 6.2509 |  | 10
2017-07-24 | 6:40 | 1.7834 | 5.9013 |  | 10
2017-07-24 | 6:45 | 1.7741 | 5.5399 | 1 | 10 | 58.5416 | 76.824
2017-07-24 | 6:50 | 1.7616 | 5.2673 |  | 10
2017-07-24 | 6:55 | 1.7366 | 4.9853 |  | 10
2017-07-24 | 7:00 | 1.7514 | 4.838 | 1 | 10 | 51.6458 | 76.4468
2017-07-24 | 7:05 | 1.7639 | 4.8555 |  | 10
2017-07-24 | 7:10 | 1.7405 | 4.8809 |  | 10
2017-07-24 | 7:15 | 1.767 | 4.9298 | 1 | 10 | 52.6576 | 76.4719
2017-07-24 | 7:20 | 1.7452 | 5.0007 |  | 10
2017-07-24 | 7:25 | 1.7452 | 5.0862 |  | 10
2017-07-24 | 7:30 | 1.7561 | 4.8602 | 1 | 10 | 52.1124 | 76.4352
2017-07-24 | 7:35 | 1.7834 | 4.8242 |  | 10
2017-07-24 | 7:40 | 1.7795 | 4.7091 |  | 10
2017-07-24 | 7:45 | 1.7592 | 4.2516 | 1 | 10 | 45.8859 | 76.5403
2017-07-24 | 7:50 | 1.76 | 4.0994 |  | 10
2017-07-24 | 7:55 | 1.7397 | 3.4369 |  | 10
2017-07-24 | 8:00 | 1.7655 | 3.5395 | 1 | 10 | 38.4829 | 76.5755
2017-07-24 | 8:05 | 1.7171 | 3.0622 |  | 10
2017-07-24 | 8:10 | 1.7507 | 3.5912 |  | 10
2017-07-24 | 8:15 | 1.7468 | 4.3897 | 1 | 10 | 46.7387 | 76.6528
2017-07-24 | 8:20 | 1.7397 | 3.8463 |  | 10
2017-07-24 | 8:25 | 1.7733 | 3.9239 |  | 10
2017-07-24 | 8:30 | 1.7218 | 4.1147 | 1 | 10 | 43.8061 | 76.7663
2017-07-24 | 8:35 | 1.7327 | 4.599 |  | 10
2017-07-24 | 8:40 | 1.7382 | 5.0332 |  | 10
2017-07-24 | 8:45 | 1.767 | 5.2784 | 1 | 10 | 55.4523 | 77.0618
2017-07-24 | 8:50 | 1.7397 | 5.029 |  | 10
2017-07-24 | 8:55 | 1.7031 | 5.1356 |  | 10
2017-07-24 | 9:00 | 1.739 | 5.0355 | 1 | 10 | 53.8659 | 77.2973
2017-07-24 | 9:05 | 1.7226 | 4.4816 |  | 10
2017-07-24 | 9:10 | 1.7881 | 3.2564 |  | 10
2017-07-24 | 9:15 | 1.7171 | 1.0478 | 1 | 10 | 25 | 77.3736
2017-07-24 | 9:20 | 1.6056 | 0 |  | 1.5
2017-07-24 | 9:25 | 1.6461 | 0 |  | 1.5
2017-07-24 | 9:30 | 1.6664 | 0 | 0 | 1.5 | 25 | 80.5745
2017-07-24 | 9:35 | 1.7218 | 0 |  | 1.5
2017-07-24 | 9:40 | 1.6929 | 0 |  | 1.5
2017-07-24 | 9:45 | 1.7241 | 0 | 0 | 1.5 | 25 | 81.6704
2017-07-24 | 9:50 | 1.6992 | 0 |  | 1.5
2017-07-24 | 9:55 | 1.7639 | 0 |  | 1.5
2017-07-24 | 10:00 | 1.7327 | 0 | 0 | 1.5 | 25 | 82.4791
2017-07-24 | 10:05 | 1.7156 | 0 |  | 1.5
2017-07-24 | 10:10 | 1.7374 | 0 |  | 1.5
2017-07-24 | 10:15 | 1.7647 | 0 | 0 | 1.5 | 25 | 83.0016
2017-07-24 | 10:20 | 1.7218 | 0 |  | 1.5
2017-07-24 | 10:25 | 1.7288 | 0 |  | 1.5
2017-07-24 | 10:30 | 1.7241 | 0 | 0 | 1.5 | 25 | 83.2049
2017-07-24 | 10:35 | 1.7514 | 0 |  | 1.5
2017-07-24 | 10:40 | 1.7507 | 0 |  | 1.5
2017-07-24 | 10:45 | 1.7787 | 0 | 0 | 1.5 | 25 | 82.9459
2017-07-24 | 10:50 | 1.7678 | 0 |  | 1.5
2017-07-24 | 10:55 | 1.7514 | 0 |  | 1.5
2017-07-24 | 11:00 | 1.7413 | 0 | 0 | 1.5 | 25 | 82.9344
2017-07-24 | 11:05 | 1.728 | 0 |  | 1.5
2017-07-24 | 11:10 | 1.7343 | 0 |  | 1.5
2017-07-24 | 11:15 | 1.7085 | 0 | 0 | 1.5 | 25 | 83.7906
2017-07-24 | 11:20 | 1.7382 | 0 |  | 1.5
2017-07-24 | 11:25 | 1.7273 | 0 |  | 1.5
2017-07-24 | 11:30 | 1.7195 | 0 | 0 | 1.5 | 25 | 84.5051
2017-07-24 | 11:35 | 1.7031 | 0 |  | 1.5
2017-07-24 | 11:40 | 1.7405 | 0 |  | 1.5
2017-07-24 | 11:45 | 1.7124 | 0 | 0 | 1.5 | 25 | 85.3102
2017-07-24 | 11:50 | 1.6844 | 0 |  | 1.5
2017-07-24 | 11:55 | 1.6968 | 0 |  | 1.5
2017-07-24 | 12:00 | 1.7007 | 0 | 0 | 1.5 | 25 | 86.8195
2017-07-24 | 12:05 | 1.6867 | 0 |  | 1.5
2017-07-24 | 12:10 | 1.7109 | 0 |  | 1.5
2017-07-24 | 12:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 87.694
2017-07-24 | 12:20 | 1.7358 | 0 |  | 1.5
2017-07-24 | 12:25 | 1.7413 | 0 |  | 1.5
2017-07-24 | 12:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 87.8358
2017-07-24 | 12:35 | 1.7296 | 0 |  | 1.5
2017-07-24 | 12:40 | 1.7273 | 0 |  | 1.5
2017-07-24 | 12:45 | 1.7429 | 0 | 0 | 1.5 | 25 | 88.2017
2017-07-24 | 12:50 | 1.7507 | 0 |  | 1.5
2017-07-24 | 12:55 | 1.7553 | 0 |  | 1.5
2017-07-24 | 13:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 88.4945
2017-07-24 | 13:05 | 1.7304 | 0 |  | 1.5
2017-07-24 | 13:10 | 1.7109 | 0 |  | 1.5
2017-07-24 | 13:15 | 1.7156 | 0 | 0 | 1.5 | 25 | 89.0835
2017-07-24 | 13:20 | 1.7093 | 0 |  | 1.5
2017-07-24 | 13:25 | 1.7273 | 0 |  | 1.5
2017-07-24 | 13:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 89.7654
2017-07-24 | 13:35 | 1.7421 | 0 |  | 1.5
2017-07-24 | 13:40 | 1.7265 | 0 |  | 1.5
2017-07-24 | 13:45 | 1.7608 | 0 | 0 | 1.5 | 25 | 90.0665
2017-07-24 | 13:50 | 1.7226 | 0 |  | 1.5
2017-07-24 | 13:55 | 1.7039 | 0 |  | 1.5
2017-07-24 | 14:00 | 1.7039 | 0 | 0 | 1.5 | 25 | 91.1425
2017-07-24 | 14:05 | 1.7312 | 0 |  | 1.5
2017-07-24 | 14:10 | 1.7366 | 0 |  | 1.5
2017-07-24 | 14:15 | 1.7374 | 0 | 0 | 1.5 | 25 | 91.6152
2017-07-24 | 14:20 | 1.7257 | 0 |  | 1.5
2017-07-24 | 14:25 | 1.7234 | 0 |  | 1.5
2017-07-24 | 14:30 | 1.6836 | 0 | 0 | 1.5 | 25 | 92.571
2017-07-24 | 14:35 | 1.6812 | 0 |  | 1.5
2017-07-24 | 14:40 | 1.7319 | 0 |  | 1.5
2017-07-24 | 14:45 | 1.7468 | 0 | 0 | 1.5 | 25 | 93.5583
2017-07-24 | 14:50 | 1.7507 | 0 |  | 1.5
2017-07-24 | 14:55 | 1.7702 | 0 |  | 1.5
2017-07-24 | 15:00 | 1.7912 | 0 | 0 | 1.5 | 25 | 93.337
2017-07-24 | 15:05 | 1.7608 | 0 |  | 1.5
2017-07-24 | 15:10 | 1.7647 | 0 |  | 1.5
2017-07-24 | 15:15 | 1.7561 | 0 | 0 | 1.5 | 25 | 93.037
2017-07-24 | 15:20 | 1.7405 | 0 |  | 1.5
2017-07-24 | 15:25 | 1.7756 | 0 |  | 1.5
2017-07-24 | 15:30 | 1.7561 | 0 | 0 | 1.5 | 25 | 92.8553
2017-07-24 | 15:35 | 1.7577 | 0 |  | 1.5
2017-07-24 | 15:40 | 1.7647 | 0 |  | 1.5
2017-07-24 | 15:45 | 1.7624 | 0 | 0 | 1.5 | 25 | 92.6342
2017-07-24 | 15:50 | 1.7257 | 0 |  | 1.5
2017-07-24 | 15:55 | 1.7491 | 0 |  | 1.5
2017-07-24 | 16:00 | 1.7296 | 0 | 0 | 1.5 | 25 | 92.8736
2017-07-24 | 16:05 | 1.7405 | 0 |  | 1.5
2017-07-24 | 16:10 | 1.7179 | 0 |  | 1.5
2017-07-24 | 16:15 | 1.7085 | 0 | 0 | 1.5 | 25 | 93.1416
2017-07-24 | 16:20 | 1.7265 | 0 |  | 1.5
2017-07-24 | 16:25 | 1.7491 | 0 |  | 1.5
2017-07-24 | 16:30 | 1.6984 | 0 | 0 | 1.5 | 25 | 93.718
2017-07-24 | 16:35 | 1.7413 | 0 |  | 1.5
2017-07-24 | 16:40 | 1.7577 | 0 |  | 1.5
2017-07-24 | 16:45 | 1.8099 | 0 | 0 | 1.5 | 25 | 93.3588
2017-07-24 | 16:50 | 1.8123 | 0 |  | 1.5
2017-07-24 | 16:55 | 1.8372 | 0 |  | 1.5
2017-07-24 | 17:00 | 1.7967 | 0 | 0 | 1.5 | 25 | 91.7244
2017-07-24 | 17:05 | 1.8255 | 0 |  | 1.5
2017-07-24 | 17:10 | 1.817 | 0 |  | 1.5
2017-07-24 | 17:15 | 1.8372 | 0 | 0 | 1.5 | 25 | 89.7623
2017-07-24 | 17:20 | 1.8333 | 0 |  | 1.5
2017-07-24 | 17:25 | 1.7772 | 0 |  | 1.5
2017-07-24 | 17:30 | 1.7928 | 0 | 0 | 1.5 | 25 | 88.362
2017-07-24 | 17:35 | 1.8193 | 0 |  | 1.5
2017-07-24 | 17:40 | 1.7967 | 0 |  | 1.5
2017-07-24 | 17:45 | 1.7873 | 0 | 0 | 1.5 | 25 | 87.2061
2017-07-24 | 17:50 | 1.7826 | 0 |  | 1.5
2017-07-24 | 17:55 | 1.7842 | 0 |  | 1.5
2017-07-24 | 18:00 | 1.8154 | 0 | 0 | 1.5 | 25 | 85.8487
2017-07-24 | 18:05 | 1.8115 | 0 |  | 1.5
2017-07-24 | 18:10 | 1.8123 | 0 |  | 1.5
2017-07-24 | 18:15 | 1.806 | 0 | 0 | 1.5 | 25 | 84.4037
2017-07-24 | 18:20 | 1.7553 | 0 |  | 1.5
2017-07-24 | 18:25 | 1.7982 | 0 |  | 1.5
2017-07-24 | 18:30 | 1.767 | 0 | 0 | 1.5 | 25 | 83.4326
2017-07-24 | 18:35 | 1.7951 | 0 |  | 1.5
2017-07-24 | 18:40 | 1.7218 | 0 |  | 1.5
2017-07-24 | 18:45 | 1.7639 | 0 | 0 | 1.5 | 25 | 82.9073
2017-07-24 | 18:50 | 1.76 | 0 |  | 1.5
2017-07-24 | 18:55 | 1.7616 | 0 |  | 1.5
2017-07-24 | 19:00 | 1.7873 | 0 | 0 | 1.5 | 25 | 82.4669
2017-07-24 | 19:05 | 1.7374 | 0 |  | 1.5
2017-07-24 | 19:10 | 1.7429 | 0 |  | 1.5
2017-07-24 | 19:15 | 1.7936 | 0 | 0 | 1.5 | 25 | 81.8711
2017-07-24 | 19:20 | 1.7561 | 0 |  | 1.5
2017-07-24 | 19:25 | 1.767 | 0 |  | 1.5
2017-07-24 | 19:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 81.5153
2017-07-24 | 19:35 | 1.7444 | 0 |  | 1.5
2017-07-24 | 19:40 | 1.7288 | 0 |  | 1.5
2017-07-24 | 19:45 | 1.7585 | 0 | 0 | 1.5 | 25 | 81.4545
2017-07-24 | 19:50 | 1.7296 | 0 |  | 1.5
2017-07-24 | 19:55 | 1.7522 | 0 |  | 1.5
2017-07-24 | 20:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 81.4808
2017-07-24 | 20:05 | 1.7717 | 0 |  | 1.5
2017-07-24 | 20:10 | 1.7631 | 0 |  | 1.5
2017-07-24 | 20:15 | 1.7585 | 0 | 0 | 1.5 | 25 | 81.2623
2017-07-24 | 20:20 | 1.7577 | 0 |  | 1.5
2017-07-24 | 20:25 | 1.7702 | 0 |  | 1.5
2017-07-24 | 20:30 | 1.7741 | 0 | 0 | 1.5 | 25 | 80.8608
2017-07-24 | 20:35 | 1.7795 | 0 |  | 1.5
2017-07-24 | 20:40 | 1.7553 | 0 |  | 1.5
2017-07-24 | 20:45 | 1.7538 | 0 | 0 | 1.5 | 25 | 80.548
2017-07-24 | 20:50 | 1.7577 | 0 |  | 1.5
2017-07-24 | 20:55 | 1.7616 | 0 |  | 1.5
2017-07-24 | 21:00 | 1.7639 | 0 | 0 | 1.5 | 25 | 80.2571
2017-07-24 | 21:05 | -0.1034 | 0 |  | 1.5
2017-07-24 | 21:10 | -0.10418 | 0 |  | 1.5
2017-07-24 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 21:20 | -0.10496 | 0 |  | 1.5
2017-07-24 | 21:25 | -0.10496 | 0 |  | 1.5
2017-07-24 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-24 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-24 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-24 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-24 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-24 | 22:55 | -0.10574 | 0 |  | 1.5
2017-07-24 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-24 | 23:10 | -0.10496 | 0 |  | 1.5
2017-07-24 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 23:20 | -0.10496 | 0 |  | 1.5
2017-07-24 | 23:25 | -0.10496 | 0 |  | 1.5
2017-07-24 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-24 | 23:40 | -0.10496 | 0 |  | 1.5
2017-07-24 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-24 | 23:50 | -0.10496 | 0 |  | 1.5
2017-07-24 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 0:35 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 0:50 | -0.10496 | 0 |  | 1.5
2017-07-25 | 0:55 | -0.10496 | 0 |  | 1.5
2017-07-25 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-25 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-25 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-25 | 1:25 | -0.10808 | 0 |  | 1.5
2017-07-25 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 1:35 | -0.10808 | 0 |  | 1.5
2017-07-25 | 1:40 | -0.10808 | 0 |  | 1.5
2017-07-25 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 1:50 | -0.10808 | 0 |  | 1.5
2017-07-25 | 1:55 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 2:05 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:10 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 2:20 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:25 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 2:35 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:40 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 2:50 | -0.10808 | 0 |  | 1.5
2017-07-25 | 2:55 | -0.10808 | 0 |  | 1.5
2017-07-25 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 3:05 | -0.10886 | 0 |  | 1.5
2017-07-25 | 3:10 | -0.10886 | 0 |  | 1.5
2017-07-25 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 3:20 | -0.10886 | 0 |  | 1.5
2017-07-25 | 3:25 | -0.10886 | 0 |  | 1.5
2017-07-25 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-25 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-25 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-25 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:10 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-25 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-25 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 5:05 | 2.235 | 5.9892 |  | 10
2017-07-25 | 5:10 | 2.1227 | 9.9998 |  | 10
2017-07-25 | 5:15 | 2.0252 | 10 | 1 | 10 | 100 | 90.1545
2017-07-25 | 5:20 | 1.9964 | 10 |  | 10
2017-07-25 | 5:25 | 1.9316 | 9.6647 |  | 10
2017-07-25 | 5:30 | 1.8848 | 9.2055 | 1 | 10 | 92.534 | 84.9003
2017-07-25 | 5:35 | 1.9028 | 8.7933 |  | 10
2017-07-25 | 5:40 | 1.8583 | 8.3256 |  | 10
2017-07-25 | 5:45 | 1.8606 | 8.3056 | 1 | 10 | 83.5721 | 81.8258
2017-07-25 | 5:50 | 1.8287 | 7.81 |  | 10
2017-07-25 | 5:55 | 1.7951 | 7.5788 |  | 10
2017-07-25 | 6:00 | 1.8123 | 7.3186 | 1 | 10 | 74.2507 | 80.0041
2017-07-25 | 6:05 | 1.7897 | 7.2939 |  | 10
2017-07-25 | 6:10 | 1.7756 | 7.6133 |  | 10
2017-07-25 | 6:15 | 1.7608 | 7.2741 | 1 | 10 | 73.6038 | 79.1176
2017-07-25 | 6:20 | 1.7577 | 7.3264 |  | 10
2017-07-25 | 6:25 | 1.7663 | 7.2581 |  | 10
2017-07-25 | 6:30 | 1.7811 | 7.2533 | 1 | 10 | 73.2819 | 78.8107
2017-07-25 | 6:35 | 1.7522 | 6.9605 |  | 10
2017-07-25 | 6:40 | 1.7647 | 6.8015 |  | 10
2017-07-25 | 6:45 | 1.7507 | 6.9449 | 1 | 10 | 70.6905 | 78.5145
2017-07-25 | 6:50 | 1.7787 | 6.2153 |  | 10
2017-07-25 | 6:55 | 1.7522 | 6.3899 |  | 10
2017-07-25 | 7:00 | 1.7335 | 6.6474 | 1 | 10 | 67.2584 | 78.0173
2017-07-25 | 7:05 | 1.7452 | 6.5479 |  | 10
2017-07-25 | 7:10 | 1.76 | 6.7367 |  | 10
2017-07-25 | 7:15 | 1.7538 | 6.7673 | 1 | 10 | 68.4306 | 77.9925
2017-07-25 | 7:20 | 1.7694 | 7.1299 |  | 10
2017-07-25 | 7:25 | 1.7553 | 6.0282 |  | 10
2017-07-25 | 7:30 | 1.7865 | 5.8524 | 1 | 10 | 59.4248 | 77.9449
2017-07-25 | 7:35 | 1.7444 | 6.2086 |  | 10
2017-07-25 | 7:40 | 1.7756 | 5.6487 |  | 10
2017-07-25 | 7:45 | 1.7413 | 6.0634 | 1 | 10 | 61.2432 | 77.804
2017-07-25 | 7:50 | 1.7382 | 5.949 |  | 10
2017-07-25 | 7:55 | 1.7624 | 5.9419 |  | 10
2017-07-25 | 8:00 | 1.76 | 5.7778 | 1 | 10 | 59.4163 | 77.8741
2017-07-25 | 8:05 | 1.746 | 5.5179 |  | 10
2017-07-25 | 8:10 | 1.7062 | 6.1295 |  | 10
2017-07-25 | 8:15 | 1.7335 | 6.1972 | 1 | 10 | 63.476 | 78.0937
2017-07-25 | 8:20 | 1.7483 | 5.9882 |  | 10
2017-07-25 | 8:25 | 1.7429 | 5.619 |  | 10
2017-07-25 | 8:30 | 1.7468 | 5.3786 | 1 | 10 | 55.3381 | 78.1422
2017-07-25 | 8:35 | 1.7319 | 5.3064 |  | 10
2017-07-25 | 8:40 | 1.7468 | 5.3099 |  | 10
2017-07-25 | 8:45 | 1.792 | 4.1188 | 1 | 10 | 44.3893 | 78.0911
2017-07-25 | 8:50 | 1.5923 | 1.384 |  | 1.5
2017-07-25 | 8:55 | 1.6422 | 0 |  | 1.5
2017-07-25 | 9:00 | 1.6968 | 0 | 0 | 1.5 | 25 | 80.6682
2017-07-25 | 9:05 | 1.6937 | 0 |  | 1.5
2017-07-25 | 9:10 | 1.7085 | 0 |  | 1.5
2017-07-25 | 9:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 81.7517
2017-07-25 | 9:20 | 1.7522 | 0 |  | 1.5
2017-07-25 | 9:25 | 1.7585 | 0 |  | 1.5
2017-07-25 | 9:30 | 1.7358 | 0 | 0 | 1.5 | 25 | 81.9245
2017-07-25 | 9:35 | 1.7452 | 0 |  | 1.5
2017-07-25 | 9:40 | 1.7218 | 0 |  | 1.5
2017-07-25 | 9:45 | 1.7265 | 0 | 0 | 1.5 | 25 | 82.0811
2017-07-25 | 9:50 | 1.7078 | 0 |  | 1.5
2017-07-25 | 9:55 | 1.7421 | 0 |  | 1.5
2017-07-25 | 10:00 | 1.7023 | 0 | 0 | 1.5 | 25 | 82.6753
2017-07-25 | 10:05 | 1.7522 | 0 |  | 1.5
2017-07-25 | 10:10 | 1.7585 | 0 |  | 1.5
2017-07-25 | 10:15 | 1.7514 | 0 | 0 | 1.5 | 25 | 82.7957
2017-07-25 | 10:20 | 1.7421 | 0 |  | 1.5
2017-07-25 | 10:25 | 1.7741 | 0 |  | 1.5
2017-07-25 | 10:30 | 1.7538 | 0 | 0 | 1.5 | 25 | 82.6945
2017-07-25 | 10:35 | 1.7366 | 0 |  | 1.5
2017-07-25 | 10:40 | 1.6922 | 0 |  | 1.5
2017-07-25 | 10:45 | 1.7124 | 0 | 0 | 1.5 | 25 | 83.3587
2017-07-25 | 10:50 | 1.7171 | 0 |  | 1.5
2017-07-25 | 10:55 | 1.7046 | 0 |  | 1.5
2017-07-25 | 11:00 | 1.7132 | 0 | 0 | 1.5 | 25 | 84.3061
2017-07-25 | 11:05 | 1.7124 | 0 |  | 1.5
2017-07-25 | 11:10 | 1.7015 | 0 |  | 1.5
2017-07-25 | 11:15 | 1.767 | 0 | 0 | 1.5 | 25 | 85.2511
2017-07-25 | 11:20 | 1.7312 | 0 |  | 1.5
2017-07-25 | 11:25 | 1.7756 | 0 |  | 1.5
2017-07-25 | 11:30 | 1.7195 | 0 | 0 | 1.5 | 25 | 85.6726
2017-07-25 | 11:35 | 1.7421 | 0 |  | 1.5
2017-07-25 | 11:40 | 1.7436 | 0 |  | 1.5
2017-07-25 | 11:45 | 1.7413 | 0 | 0 | 1.5 | 25 | 85.7508
2017-07-25 | 11:50 | 1.7117 | 0 |  | 1.5
2017-07-25 | 11:55 | 1.7397 | 0 |  | 1.5
2017-07-25 | 12:00 | 1.7195 | 0 | 0 | 1.5 | 25 | 85.9439
2017-07-25 | 12:05 | 1.7327 | 0 |  | 1.5
2017-07-25 | 12:10 | 1.7483 | 0 |  | 1.5
2017-07-25 | 12:15 | 1.7358 | 0 | 0 | 1.5 | 25 | 86.3714
2017-07-25 | 12:20 | 1.7039 | 0 |  | 1.5
2017-07-25 | 12:25 | 1.7202 | 0 |  | 1.5
2017-07-25 | 12:30 | 1.7296 | 0 | 0 | 1.5 | 25 | 86.945
2017-07-25 | 12:35 | 1.7273 | 0 |  | 1.5
2017-07-25 | 12:40 | 1.7078 | 0 |  | 1.5
2017-07-25 | 12:45 | 1.7023 | 0 | 0 | 1.5 | 25 | 87.7024
2017-07-25 | 12:50 | 1.7171 | 0 |  | 1.5
2017-07-25 | 12:55 | 1.8396 | 0 |  | 1.5
2017-07-25 | 13:00 | 1.7943 | 0 | 0 | 1.5 | 25 | 86.7682
2017-07-25 | 13:05 | 1.785 | 0 |  | 1.5
2017-07-25 | 13:10 | 1.7444 | 0 |  | 1.5
2017-07-25 | 13:15 | 1.7382 | 0 | 0 | 1.5 | 25 | 86.4423
2017-07-25 | 13:20 | 1.7436 | 0 |  | 1.5
2017-07-25 | 13:25 | 1.7514 | 0 |  | 1.5
2017-07-25 | 13:30 | 1.7366 | 0 | 0 | 1.5 | 25 | 86.6496
2017-07-25 | 13:35 | 1.7452 | 0 |  | 1.5
2017-07-25 | 13:40 | 1.7421 | 0 |  | 1.5
2017-07-25 | 13:45 | 1.7514 | 0 | 0 | 1.5 | 25 | 87.0764
2017-07-25 | 13:50 | 1.7327 | 0 |  | 1.5
2017-07-25 | 13:55 | 1.7351 | 0 |  | 1.5
2017-07-25 | 14:00 | 1.6898 | 0 | 0 | 1.5 | 25 | 87.8679
2017-07-25 | 14:05 | 1.6344 | 0 |  | 1.5
2017-07-25 | 14:10 | 1.6446 | 0 |  | 1.5
2017-07-25 | 14:15 | 1.6532 | 0 | 0 | 1.5 | 25 | 90.4563
2017-07-25 | 14:20 | 1.6984 | 0 |  | 1.5
2017-07-25 | 14:25 | 1.7101 | 0 |  | 1.5
2017-07-25 | 14:30 | 1.7093 | 0 | 0 | 1.5 | 25 | 91.7417
2017-07-25 | 14:35 | 1.7046 | 0 |  | 1.5
2017-07-25 | 14:40 | 1.7054 | 0 |  | 1.5
2017-07-25 | 14:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 92.5875
2017-07-25 | 14:50 | 1.7319 | 0 |  | 1.5
2017-07-25 | 14:55 | 1.7327 | 0 |  | 1.5
2017-07-25 | 15:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 92.7254
2017-07-25 | 15:05 | 1.7312 | 0 |  | 1.5
2017-07-25 | 15:10 | 1.7483 | 0 |  | 1.5
2017-07-25 | 15:15 | 1.7577 | 0 | 0 | 1.5 | 25 | 92.5278
2017-07-25 | 15:20 | 1.7663 | 0 |  | 1.5
2017-07-25 | 15:25 | 1.7608 | 0 |  | 1.5
2017-07-25 | 15:30 | 1.7062 | 0 | 0 | 1.5 | 25 | 92.7198
2017-07-25 | 15:35 | 1.7663 | 0 |  | 1.5
2017-07-25 | 15:40 | 1.7179 | 0 |  | 1.5
2017-07-25 | 15:45 | 1.7787 | 0 | 0 | 1.5 | 25 | 92.6654
2017-07-25 | 15:50 | 1.7819 | 0 |  | 1.5
2017-07-25 | 15:55 | 1.7608 | 0 |  | 1.5
2017-07-25 | 16:00 | 1.7717 | 0 | 0 | 1.5 | 25 | 92.0342
2017-07-25 | 16:05 | 1.7405 | 0 |  | 1.5
2017-07-25 | 16:10 | 1.7725 | 0 |  | 1.5
2017-07-25 | 16:15 | 1.806 | 0 | 0 | 1.5 | 25 | 91.477
2017-07-25 | 16:20 | 1.7982 | 0 |  | 1.5
2017-07-25 | 16:25 | 1.8107 | 0 |  | 1.5
2017-07-25 | 16:30 | 1.8146 | 0 | 0 | 1.5 | 25 | 89.9775
2017-07-25 | 16:35 | 1.8248 | 0 |  | 1.5
2017-07-25 | 16:40 | 1.8521 | 0 |  | 1.5
2017-07-25 | 16:45 | 1.7975 | 0 | 0 | 1.5 | 25 | 88.0812
2017-07-25 | 16:50 | 1.7772 | 0 |  | 1.5
2017-07-25 | 16:55 | 1.7959 | 0 |  | 1.5
2017-07-25 | 17:00 | 1.7904 | 0 | 0 | 1.5 | 25 | 86.9551
2017-07-25 | 17:05 | 1.7686 | 0 |  | 1.5
2017-07-25 | 17:10 | 1.7725 | 0 |  | 1.5
2017-07-25 | 17:15 | 1.7826 | 0 | 0 | 1.5 | 25 | 86.0441
2017-07-25 | 17:20 | 1.785 | 0 |  | 1.5
2017-07-25 | 17:25 | 1.7842 | 0 |  | 1.5
2017-07-25 | 17:30 | 1.7764 | 0 | 0 | 1.5 | 25 | 85.2439
2017-07-25 | 17:35 | 1.7686 | 0 |  | 1.5
2017-07-25 | 17:40 | 1.7865 | 0 |  | 1.5
2017-07-25 | 17:45 | 1.7741 | 0 | 0 | 1.5 | 25 | 84.6369
2017-07-25 | 17:50 | 1.7865 | 0 |  | 1.5
2017-07-25 | 17:55 | 1.7756 | 0 |  | 1.5
2017-07-25 | 18:00 | 1.7694 | 0 | 0 | 1.5 | 25 | 83.7543
2017-07-25 | 18:05 | 1.778 | 0 |  | 1.5
2017-07-25 | 18:10 | 1.7663 | 0 |  | 1.5
2017-07-25 | 18:15 | 1.8021 | 0 | 0 | 1.5 | 25 | 82.8035
2017-07-25 | 18:20 | 1.8154 | 0 |  | 1.5
2017-07-25 | 18:25 | 1.7858 | 0 |  | 1.5
2017-07-25 | 18:30 | 1.7686 | 0 | 0 | 1.5 | 25 | 81.9274
2017-07-25 | 18:35 | 1.7382 | 0 |  | 1.5
2017-07-25 | 18:40 | 1.7507 | 0 |  | 1.5
2017-07-25 | 18:45 | 1.753 | 0 | 0 | 1.5 | 25 | 81.4968
2017-07-25 | 18:50 | 1.7819 | 0 |  | 1.5
2017-07-25 | 18:55 | 1.7858 | 0 |  | 1.5
2017-07-25 | 19:00 | 1.7444 | 0 | 0 | 1.5 | 25 | 81.2362
2017-07-25 | 19:05 | 1.7468 | 0 |  | 1.5
2017-07-25 | 19:10 | 1.7561 | 0 |  | 1.5
2017-07-25 | 19:15 | 1.7787 | 0 | 0 | 1.5 | 25 | 80.9942
2017-07-25 | 19:20 | 1.7709 | 0 |  | 1.5
2017-07-25 | 19:25 | 1.7397 | 0 |  | 1.5
2017-07-25 | 19:30 | 1.7468 | 0 | 0 | 1.5 | 25 | 80.6585
2017-07-25 | 19:35 | 1.6929 | 0 |  | 1.5
2017-07-25 | 19:40 | 1.7358 | 0 |  | 1.5
2017-07-25 | 19:45 | 1.7273 | 0 | 0 | 1.5 | 25 | 81.2331
2017-07-25 | 19:50 | 1.7366 | 0 |  | 1.5
2017-07-25 | 19:55 | 1.7413 | 0 |  | 1.5
2017-07-25 | 20:00 | 1.7358 | 0 | 0 | 1.5 | 25 | 81.7026
2017-07-25 | 20:05 | 1.7522 | 0 |  | 1.5
2017-07-25 | 20:10 | 1.7663 | 0 |  | 1.5
2017-07-25 | 20:15 | 1.76 | 0 | 0 | 1.5 | 25 | 81.7792
2017-07-25 | 20:20 | 1.7514 | 0 |  | 1.5
2017-07-25 | 20:25 | 1.7756 | 0 |  | 1.5
2017-07-25 | 20:30 | 1.7577 | 0 | 0 | 1.5 | 25 | 81.3459
2017-07-25 | 20:35 | 1.7616 | 0 |  | 1.5
2017-07-25 | 20:40 | 1.76 | 0 |  | 1.5
2017-07-25 | 20:45 | 1.7436 | 0 | 0 | 1.5 | 25 | 81.051
2017-07-25 | 20:50 | 1.7655 | 0 |  | 1.5
2017-07-25 | 20:55 | 1.7351 | 0 |  | 1.5
2017-07-25 | 21:00 | 1.7514 | 0 | 0 | 1.5 | 25 | 80.7646
2017-07-25 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-25 | 21:10 | -0.10496 | 0 |  | 1.5
2017-07-25 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-25 | 21:25 | -0.10496 | 0 |  | 1.5
2017-07-25 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 21:35 | -0.10496 | 0 |  | 1.5
2017-07-25 | 21:40 | -0.10496 | 0 |  | 1.5
2017-07-25 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-25 | 21:55 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:40 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-25 | 22:55 | -0.10574 | 0 |  | 1.5
2017-07-25 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-25 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-25 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 23:20 | -0.10574 | 0 |  | 1.5
2017-07-25 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-25 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-25 | 23:40 | -0.10496 | 0 |  | 1.5
2017-07-25 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-25 | 23:50 | -0.10496 | 0 |  | 1.5
2017-07-25 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-26 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-26 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-26 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-26 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-26 | 0:15 | [5 empty] | 0
2017-07-26 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-26 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-26 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0
2017-07-26 | 0:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 0:35 | -0.10418 | 0 |  | 1.5
2017-07-26 | 0:40 | -0.10418 | 0 |  | 1.5
2017-07-26 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0
2017-07-26 | 0:45 |  |  |  | 1.5 |  | 0
2017-07-26 | 0:50 | -0.10418 | 0 |  | 1.5
2017-07-26 | 0:55 | -0.1034 | 0 |  | 1.5
2017-07-26 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0
2017-07-26 | 1:00 |  |  |  | 1.5 |  | 0
2017-07-26 | 1:05 | -0.1034 | 0 |  | 1.5
2017-07-26 | 1:10 | -0.10418 | 0 |  | 1.5
2017-07-26 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0
2017-07-26 | 1:15 | [5 empty] | 0
2017-07-26 | 1:20 | -0.10652 | 0 |  | 1.5
2017-07-26 | 1:25 | -0.10652 | 0 |  | 1.5
2017-07-26 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-26 | 1:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 1:35 | -0.10652 | 0 |  | 1.5
2017-07-26 | 1:40 | -0.10652 | 0 |  | 1.5
2017-07-26 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 1:45 |  |  |  | 1.5 |  | 0
2017-07-26 | 1:50 | -0.1073 | 0 |  | 1.5
2017-07-26 | 1:55 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 2:00 |  |  |  | 1.5 |  | 0
2017-07-26 | 2:05 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:10 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 2:15 |  |  |  | 1.5 |  | 0
2017-07-26 | 2:20 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:25 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 2:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 2:35 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:40 | -0.10808 | 0 |  | 1.5
2017-07-26 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 2:45 | [5 empty] | 0
2017-07-26 | 2:50 | -0.1073 | 0 |  | 1.5
2017-07-26 | 2:55 | -0.1073 | 0 |  | 1.5
2017-07-26 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 3:00 |  |  |  | 1.5 |  | 0
2017-07-26 | 3:05 | -0.10808 | 0 |  | 1.5
2017-07-26 | 3:10 | -0.1073 | 0 |  | 1.5
2017-07-26 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 3:15 |  |  |  | 1.5 |  | 0
2017-07-26 | 3:20 | -0.10808 | 0 |  | 1.5
2017-07-26 | 3:25 | -0.1073 | 0 |  | 1.5
2017-07-26 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-26 | 3:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 3:35 | -0.10808 | 0 |  | 1.5
2017-07-26 | 3:40 | -0.10808 | 0 |  | 1.5
2017-07-26 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-26 | 3:45 |  |  |  | 1.5 |  | 0
2017-07-26 | 3:50 | -0.10808 | 0 |  | 1.5
2017-07-26 | 3:55 | -0.10808 | 0 |  | 1.5
2017-07-26 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-26 | 4:00 |  |  |  | 1.5 |  | 0
2017-07-26 | 4:05 | -0.10808 | 0 |  | 1.5
2017-07-26 | 4:10 | -0.10808 | 0 |  | 1.5
2017-07-26 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-07-26 | 4:15 |  |  |  | 1.5 |  | 0
2017-07-26 | 4:20 | -0.10886 | 0 |  | 1.5
2017-07-26 | 4:25 | -0.10886 | 0 |  | 1.5
2017-07-26 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-26 | 4:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 4:35 | -0.10886 | 0 |  | 1.5
2017-07-26 | 4:40 | -0.10886 | 0 |  | 1.5
2017-07-26 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-07-26 | 4:45 | [5 empty] | 0
2017-07-26 | 4:50 | -0.10886 | 0 |  | 1.5
2017-07-26 | 4:55 | -0.10886 | 0 |  | 1.5
2017-07-26 | 5:00 | -0.10886 | 0 | 1 | 0 | 0
2017-07-26 | 5:00 |  |  |  | 0 |  | 25
2017-07-26 | 5:05 | 2.2187 | 6.0461 |  | 10
2017-07-26 | 5:10 | 2.0252 | 10 |  | 10
2017-07-26 | 5:15 | 1.9706 | 10 | 1 | 10 | 100
2017-07-26 | 5:15 |  |  |  | 10 |  | 91.5215
2017-07-26 | 5:20 | 1.9932 | 10 |  | 10
2017-07-26 | 5:25 | 1.9589 | 10 |  | 10
2017-07-26 | 5:30 | 1.8716 | 9.8292 | 1 | 10 | 98.6187
2017-07-26 | 5:30 |  |  |  | 10 |  | 86.2619
2017-07-26 | 5:35 | 1.9012 | 9.1415 |  | 10
2017-07-26 | 5:40 | 1.9074 | 8.53 |  | 10
2017-07-26 | 5:45 | 1.8505 | 8.0508 | 1 | 10 | 81.6926
2017-07-26 | 5:45 |  |  |  | 10 |  | 82.8356
2017-07-26 | 5:50 | 1.8544 | 7.7984 |  | 10
2017-07-26 | 5:55 | 1.831 | 7.4209 |  | 10
2017-07-26 | 6:00 | 1.8006 | 7.1838 | 1 | 10 | 72.8066
2017-07-26 | 6:00 |  |  |  | 10 |  | 80.567
2017-07-26 | 6:05 | 1.7858 | 7.6108 |  | 10
2017-07-26 | 6:10 | 1.7865 | 7.9756 |  | 10
2017-07-26 | 6:15 | 1.7709 | 7.7179 | 1 | 10 | 77.9925
2017-07-26 | 6:15 | [5 empty] | 79.726
2017-07-26 | 6:20 | 1.7655 | 7.7467 |  | 10
2017-07-26 | 6:25 | 1.7538 | 7.747 |  | 10
2017-07-26 | 6:30 | 1.7912 | 7.399 | 1 | 10 | 74.9726
2017-07-26 | 6:30 |  |  |  | 10 |  | 79.0313
2017-07-26 | 6:35 | 1.7943 | 7.5531 |  | 10
2017-07-26 | 6:40 | 1.7608 | 7.5577 |  | 10
2017-07-26 | 6:45 | 1.7663 | 7.1059 | 1 | 10 | 72.497
2017-07-26 | 6:45 | [5 empty] | 78.567
2017-07-26 | 6:50 | 1.7951 | 6.8213 |  | 10
2017-07-26 | 6:55 | 1.767 | 7.0646 |  | 10
2017-07-26 | 7:00 | 1.7678 | 6.8132 | 1 | 10 | 69.1962
2017-07-26 | 7:00 |  |  |  | 10 |  | 78.0107
2017-07-26 | 7:05 | 1.7897 | 6.1495 |  | 10
2017-07-26 | 7:10 | 1.7514 | 6.9087 |  | 10
2017-07-26 | 7:15 | 1.7507 | 7.0363 | 1 | 10 | 71.1537
2017-07-26 | 7:15 |  |  |  | 10 |  | 77.615
2017-07-26 | 7:20 | 1.7335 | 7.2554 |  | 10
2017-07-26 | 7:25 | 1.7319 | 7.4451 |  | 10
2017-07-26 | 7:30 | 1.7335 | 7.1703 | 1 | 10 | 72.6165
2017-07-26 | 7:30 |  |  |  | 10 |  | 77.822
2017-07-26 | 7:35 | 1.7764 | 6.7958 |  | 10
2017-07-26 | 7:40 | 1.7873 | 6.071 |  | 10
2017-07-26 | 7:45 | 1.8092 | 5.9572 | 1 | 10 | 61.0638
2017-07-26 | 7:45 |  |  |  | 10 |  | 77.4268
2017-07-26 | 7:50 | 1.746 | 5.4763 |  | 10
2017-07-26 | 7:55 | 1.7452 | 4.7976 |  | 10
2017-07-26 | 8:00 | 1.7647 | 4.84 | 1 | 10 | 49.3079
2017-07-26 | 8:00 |  |  |  | 10 |  | 77.0583
2017-07-26 | 8:05 | 1.7624 | 4.3254 |  | 10
2017-07-26 | 8:10 | 1.7514 | 4.9039 |  | 10
2017-07-26 | 8:15 | 1.7304 | 5.689 | 1 | 10 | 58.193
2017-07-26 | 8:15 | [5 empty] | 76.9725
2017-07-26 | 8:20 | 1.7031 | 5.852 |  | 10
2017-07-26 | 8:25 | 1.7304 | 5.6509 |  | 10
2017-07-26 | 8:30 | 1.7468 | 5.1412 | 1 | 10 | 53.2274
2017-07-26 | 8:30 |  |  |  | 10 |  | 77.2806
2017-07-26 | 8:35 | 1.7327 | 5.272 |  | 10
2017-07-26 | 8:40 | 1.7624 | 5.439 |  | 10
2017-07-26 | 8:45 | 1.7327 | 6.029 | 1 | 10 | 60.9156
2017-07-26 | 8:45 |  |  |  | 10 |  | 77.4832
2017-07-26 | 8:50 | 1.739 | 5.2851 |  | 10
2017-07-26 | 8:55 | 1.7585 | 5.2044 |  | 10
2017-07-26 | 9:00 | 1.7265 | 5.4989 | 1 | 10 | 56.1608
2017-07-26 | 9:00 |  |  |  | 10 |  | 77.7347
2017-07-26 | 9:05 | 1.7156 | 6.2571 |  | 10
2017-07-26 | 9:10 | 1.7132 | 6.7018 |  | 10
2017-07-26 | 9:15 | 1.7078 | 6.9955 | 1 | 10 | 70.5719
2017-07-26 | 9:15 |  |  |  | 10 |  | 78.4434
2017-07-26 | 9:20 | 1.7109 | 7.1765 |  | 10
2017-07-26 | 9:25 | 1.728 | 7.132 |  | 10
2017-07-26 | 9:30 | 1.7538 | 7.311 | 1 | 10 | 73.4996
2017-07-26 | 9:30 |  |  |  | 10 |  | 78.9318
2017-07-26 | 9:35 | 1.7202 | 7.6698 |  | 10
2017-07-26 | 9:40 | 1.7444 | 7.4243 |  | 10
2017-07-26 | 9:45 | 1.8068 | 5.6153 | 1 | 10 | 58.8352
2017-07-26 | 9:45 |  |  |  | 10 |  | 79.2019
2017-07-26 | 9:50 | 1.785 | 4.4881 |  | 10
2017-07-26 | 9:55 | 1.6758 | 2.2386 |  | 1.5
2017-07-26 | 10:00 | 1.6508 | 0 | 0 | 1.5 | 25
2017-07-26 | 10:00 |  |  |  | 1.5 |  | 80.9507
2017-07-26 | 10:05 | 1.6703 | 0 |  | 1.5
2017-07-26 | 10:10 | 1.6992 | 0 |  | 1.5
2017-07-26 | 10:15 | 1.7101 | 0 | 0 | 1.5 | 25
2017-07-26 | 10:15 |  |  |  | 1.5 |  | 82.6762
2017-07-26 | 10:20 | 1.7366 | 0 |  | 1.5
2017-07-26 | 10:25 | 1.7546 | 0 |  | 1.5
2017-07-26 | 10:30 | 1.7257 | 0 | 0 | 1.5 | 25
2017-07-26 | 10:30 |  |  |  | 1.5 |  | 83.1983
2017-07-26 | 10:35 | 1.7421 | 0 |  | 1.5
2017-07-26 | 10:40 | 1.7078 | 0 |  | 1.5
2017-07-26 | 10:45 | 1.7491 | 0 | 0 | 1.5 | 25
2017-07-26 | 10:45 |  |  |  | 1.5 |  | 83.446
2017-07-26 | 10:50 | 1.7382 | 0 |  | 1.5
2017-07-26 | 10:55 | 1.7343 | 0 |  | 1.5
2017-07-26 | 11:00 | 1.7163 | 0 | 0 | 1.5 | 25
2017-07-26 | 11:00 |  |  |  | 1.5 |  | 83.9541
2017-07-26 | 11:05 | 1.714 | 0 |  | 1.5
2017-07-26 | 11:10 | 1.6914 | 0 |  | 1.5
2017-07-26 | 11:15 | 1.7335 | 0 | 0 | 1.5 | 25
2017-07-26 | 11:15 | 1.7335 | 0 |  | 1.5 |  | 84.8218
2017-07-26 | 11:20 | 1.7678 | 0 |  | 1.5
2017-07-26 | 11:25 | 1.7319 | 0 |  | 1.5
2017-07-26 | 11:30 | 1.7109 | 0 | 0 | 1.5 | 25
2017-07-26 | 11:30 |  |  |  | 1.5 |  | 85.2623
2017-07-26 | 11:35 | 1.7374 | 0 |  | 1.5
2017-07-26 | 11:40 | 1.7663 | 0 |  | 1.5
2017-07-26 | 11:45 | 1.7561 | 0 | 0 | 1.5 | 25
2017-07-26 | 11:45 |  |  |  | 1.5 |  | 85.8257
2017-07-26 | 11:50 | 1.7647 | 0 |  | 1.5
2017-07-26 | 11:55 | 1.7585 | 0 |  | 1.5
2017-07-26 | 12:00 | 1.7811 | 0 | 0 | 1.5 | 25
2017-07-26 | 12:00 |  |  |  | 1.5 |  | 85.6553
2017-07-26 | 12:05 | 1.7725 | 0 |  | 1.5
2017-07-26 | 12:10 | 1.7226 | 0 |  | 1.5
2017-07-26 | 12:15 | 1.7452 | 0 | 0 | 1.5 | 25
2017-07-26 | 12:15 |  |  |  | 1.5 |  | 85.7982
2017-07-26 | 12:20 | 1.707 | 0 |  | 1.5
2017-07-26 | 12:25 | 1.7343 | 0 |  | 1.5
2017-07-26 | 12:30 | 1.7054 | 0 | 0 | 1.5 | 25
2017-07-26 | 12:30 |  |  |  | 1.5 |  | 86.3179
2017-07-26 | 12:35 | 1.7312 | 0 |  | 1.5
2017-07-26 | 12:40 | 1.6992 | 0 |  | 1.5
2017-07-26 | 12:45 | 1.7195 | 0 | 0 | 1.5 | 25
2017-07-26 | 12:45 |  |  |  | 1.5 |  | 86.8098
2017-07-26 | 12:50 | 1.7296 | 0 |  | 1.5
2017-07-26 | 12:55 | 1.7218 | 0 |  | 1.5
2017-07-26 | 13:00 | 1.7031 | 0 | 0 | 1.5 | 25
2017-07-26 | 13:00 |  |  |  | 1.5 |  | 87.6304
2017-07-26 | 13:05 | 1.7304 | 0 |  | 1.5
2017-07-26 | 13:10 | 1.7054 | 0 |  | 1.5
2017-07-26 | 13:15 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-26 | 13:15 | [5 empty] | 88.2918
2017-07-26 | 13:20 | 1.7397 | 0 |  | 1.5
2017-07-26 | 13:25 | 1.7179 | 0 |  | 1.5
2017-07-26 | 13:30 | 1.7156 | 0 | 0 | 1.5 | 25
2017-07-26 | 13:30 |  |  |  | 1.5 |  | 88.665
2017-07-26 | 13:35 | 1.7397 | 0 |  | 1.5
2017-07-26 | 13:40 | 1.7148 | 0 |  | 1.5
2017-07-26 | 13:45 | 1.6906 | 0 | 0 | 1.5 | 25
2017-07-26 | 13:45 |  |  |  | 1.5 |  | 89.5573
2017-07-26 | 13:50 | 1.76 | 0 |  | 1.5
2017-07-26 | 13:55 | 1.7405 | 0 |  | 1.5
2017-07-26 | 14:00 | 1.7624 | 0 | 0 | 1.5 | 25
2017-07-26 | 14:00 |  |  |  | 1.5 |  | 89.6895
2017-07-26 | 14:05 | 1.7429 | 0 |  | 1.5
2017-07-26 | 14:10 | 1.7288 | 0 |  | 1.5
2017-07-26 | 14:15 | 1.7561 | 0 | 0 | 1.5 | 25
2017-07-26 | 14:15 |  |  |  | 1.5 |  | 89.798
2017-07-26 | 14:20 | 1.7358 | 0 |  | 1.5
2017-07-26 | 14:25 | 1.7491 | 0 |  | 1.5
2017-07-26 | 14:30 | 1.7085 | 0 | 0 | 1.5 | 25
2017-07-26 | 14:30 |  |  |  | 1.5 |  | 90.0848
2017-07-26 | 14:35 | 1.7257 | 0 |  | 1.5
2017-07-26 | 14:40 | 1.7374 | 0 |  | 1.5
2017-07-26 | 14:45 | 1.7592 | 0 | 0 | 1.5 | 25
2017-07-26 | 14:45 |  |  |  | 1.5 |  | 90.3599
2017-07-26 | 14:50 | 1.7741 | 0 |  | 1.5
2017-07-26 | 14:55 | 1.7553 | 0 |  | 1.5
2017-07-26 | 15:00 | 1.7592 | 0 | 0 | 1.5 | 25
2017-07-26 | 15:00 |  |  |  | 1.5 |  | 90.6051
2017-07-26 | 15:05 | 1.7421 | 0 |  | 1.5
2017-07-26 | 15:10 | 1.7577 | 0 |  | 1.5
2017-07-26 | 15:15 | 1.7312 | 0 | 0 | 1.5 | 25
2017-07-26 | 15:15 |  |  |  | 1.5 |  | 90.7548
2017-07-26 | 15:20 | 1.7444 | 0 |  | 1.5
2017-07-26 | 15:25 | 1.7702 | 0 |  | 1.5
2017-07-26 | 15:30 | 1.7405 | 0 | 0 | 1.5 | 25
2017-07-26 | 15:30 |  |  |  | 1.5 |  | 90.8384
2017-07-26 | 15:35 | 1.7709 | 0 |  | 1.5
2017-07-26 | 15:40 | 1.7195 | 0 |  | 1.5
2017-07-26 | 15:45 | 1.728 | 0 | 0 | 1.5 | 25
2017-07-26 | 15:45 |  |  |  | 1.5 |  | 91.1419
2017-07-26 | 15:50 | 1.7327 | 0 |  | 1.5
2017-07-26 | 15:55 | 1.7405 | 0 |  | 1.5
2017-07-26 | 16:00 | 1.7218 | 0 | 0 | 1.5 | 25
2017-07-26 | 16:00 |  |  |  | 1.5 |  | 91.3196
2017-07-26 | 16:05 | 1.7772 | 0 |  | 1.5
2017-07-26 | 16:10 | 1.7655 | 0 |  | 1.5
2017-07-26 | 16:15 | 1.7351 | 0 | 0 | 1.5 | 25
2017-07-26 | 16:15 |  |  |  | 1.5 |  | 91.2384
2017-07-26 | 16:20 | 1.7764 | 0 |  | 1.5
2017-07-26 | 16:25 | 1.7733 | 0 |  | 1.5
2017-07-26 | 16:30 | 1.7865 | 0 | 0 | 1.5 | 25
2017-07-26 | 16:30 |  |  |  | 1.5 |  | 90.7689
2017-07-26 | 16:35 | 1.7873 | 0 |  | 1.5
2017-07-26 | 16:40 | 1.7756 | 0 |  | 1.5
2017-07-26 | 16:45 | 1.7647 | 0 | 0 | 1.5 | 25
2017-07-26 | 16:45 |  |  |  | 1.5 |  | 89.82
2017-07-26 | 16:50 | 1.7655 | 0 |  | 1.5
2017-07-26 | 16:55 | 1.7756 | 0 |  | 1.5
2017-07-26 | 17:00 | 1.7904 | 0 | 0 | 1.5 | 25
2017-07-26 | 17:00 |  |  |  | 1.5 |  | 89.171
2017-07-26 | 17:05 | 1.7756 | 0 |  | 1.5
2017-07-26 | 17:10 | 1.7397 | 0 |  | 1.5
2017-07-26 | 17:15 | 1.7522 | 0 | 0 | 1.5 | 25
2017-07-26 | 17:15 | [5 empty] | 88.851
2017-07-26 | 17:20 | 1.7639 | 0 |  | 1.5
2017-07-26 | 17:25 | 1.7475 | 0 |  | 1.5
2017-07-26 | 17:30 | 1.7733 | 0 | 0 | 1.5 | 25
2017-07-26 | 17:30 |  |  |  | 1.5 |  | 88.3771
2017-07-26 | 17:35 | 1.785 | 0 |  | 1.5
2017-07-26 | 17:40 | 1.7725 | 0 |  | 1.5
2017-07-26 | 17:45 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-26 | 17:45 |  |  |  | 1.5 |  | 87.5337
2017-07-26 | 17:50 | 1.7678 | 0 |  | 1.5
2017-07-26 | 17:55 | 1.7998 | 0 |  | 1.5
2017-07-26 | 18:00 | 1.8068 | 0 | 0 | 1.5 | 25
2017-07-26 | 18:00 |  |  |  | 1.5 |  | 86.7336
2017-07-26 | 18:05 | 1.8084 | 0 |  | 1.5
2017-07-26 | 18:10 | 1.7725 | 0 |  | 1.5
2017-07-26 | 18:15 | 1.7858 | 0 | 0 | 1.5 | 25
2017-07-26 | 18:15 |  |  |  | 1.5 |  | 85.7425
2017-07-26 | 18:20 | 1.778 | 0 |  | 1.5
2017-07-26 | 18:25 | 1.7865 | 0 |  | 1.5
2017-07-26 | 18:30 | 1.7897 | 0 | 0 | 1.5 | 25
2017-07-26 | 18:30 |  |  |  | 1.5 |  | 84.8424
2017-07-26 | 18:35 | 1.7709 | 0 |  | 1.5
2017-07-26 | 18:40 | 1.7709 | 0 |  | 1.5
2017-07-26 | 18:45 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-26 | 18:45 |  |  |  | 1.5 |  | 84.2412
2017-07-26 | 18:50 | 1.7655 | 0 |  | 1.5
2017-07-26 | 18:55 | 1.7608 | 0 |  | 1.5
2017-07-26 | 19:00 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-26 | 19:00 |  |  |  | 1.5 |  | 84.0303
2017-07-26 | 19:05 | 1.7756 | 0 |  | 1.5
2017-07-26 | 19:10 | 1.7499 | 0 |  | 1.5
2017-07-26 | 19:15 | 1.7608 | 0 | 0 | 1.5 | 25
2017-07-26 | 19:15 | [5 empty] | 83.6741
2017-07-26 | 19:20 | 1.7795 | 0 |  | 1.5
2017-07-26 | 19:25 | 1.7592 | 0 |  | 1.5
2017-07-26 | 19:30 | 1.7452 | 0 | 0 | 1.5 | 25
2017-07-26 | 19:30 |  |  |  | 1.5 |  | 83.4251
2017-07-26 | 19:35 | 1.7468 | 0 |  | 1.5
2017-07-26 | 19:40 | 1.7265 | 0 |  | 1.5
2017-07-26 | 19:45 | 1.7546 | 0 | 0 | 1.5 | 25
2017-07-26 | 19:45 |  |  |  | 1.5 |  | 83.4986
2017-07-26 | 19:50 | 1.7702 | 0 |  | 1.5
2017-07-26 | 19:55 | 1.7795 | 0 |  | 1.5
2017-07-26 | 20:00 | 1.7842 | 0 | 0 | 1.5 | 25
2017-07-26 | 20:00 |  |  |  | 1.5 |  | 83.2017
2017-07-26 | 20:05 | 1.7663 | 0 |  | 1.5
2017-07-26 | 20:10 | 1.7733 | 0 |  | 1.5
2017-07-26 | 20:15 | 1.7522 | 0 | 0 | 1.5 | 25
2017-07-26 | 20:15 |  |  |  | 1.5 |  | 82.6276
2017-07-26 | 20:20 | 1.7569 | 0 |  | 1.5
2017-07-26 | 20:25 | 1.7694 | 0 |  | 1.5
2017-07-26 | 20:30 | 1.7725 | 0 | 0 | 1.5 | 25
2017-07-26 | 20:30 |  |  |  | 1.5 |  | 82.1745
2017-07-26 | 20:35 | 1.7772 | 0 |  | 1.5
2017-07-26 | 20:40 | 1.778 | 0 |  | 1.5
2017-07-26 | 20:45 | 1.7787 | 0 | 0 | 1.5 | 25
2017-07-26 | 20:45 |  |  |  | 1.5 |  | 81.3896
2017-07-26 | 20:50 | 1.8029 | 0 |  | 1.5
2017-07-26 | 20:55 | 1.7647 | 0 |  | 1.5
2017-07-26 | 21:00 | 1.7717 | 0 | 0 | 1.5 | 25
2017-07-26 | 21:00 | 1.7717 | 0 |  | 1.5 |  | 0
2017-07-26 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-26 | 21:10 | -0.10652 | 0 |  | 1.5
2017-07-26 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-26 | 21:15 |  |  |  | 1.5 |  | 0
2017-07-26 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-26 | 21:25 | -0.10496 | 0 |  | 1.5
2017-07-26 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-26 | 21:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 21:35 | -0.10496 | 0 |  | 1.5
2017-07-26 | 21:40 | -0.10496 | 0 |  | 1.5
2017-07-26 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-26 | 21:45 |  |  |  | 1.5 |  | 0
2017-07-26 | 21:50 | -0.10418 | 0 |  | 1.5
2017-07-26 | 21:55 | -0.10496 | 0 |  | 1.5
2017-07-26 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-26 | 22:00 |  |  |  | 1.5 |  | 0
2017-07-26 | 22:05 | -0.10496 | 0 |  | 1.5
2017-07-26 | 22:10 | -0.10574 | 0 |  | 1.5
2017-07-26 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-26 | 22:15 |  |  |  | 1.5 |  | 0
2017-07-26 | 22:20 | -0.10574 | 0 |  | 1.5
2017-07-26 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-26 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-26 | 22:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 22:35 | -0.10574 | 0 |  | 1.5
2017-07-26 | 22:40 | -0.10496 | 0 |  | 1.5
2017-07-26 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-26 | 22:45 |  |  |  | 1.5 |  | 0
2017-07-26 | 22:50 | -0.10574 | 0 |  | 1.5
2017-07-26 | 22:55 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-26 | 23:00 |  |  |  | 1.5 |  | 0
2017-07-26 | 23:05 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:10 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-26 | 23:15 |  |  |  | 1.5 |  | 0
2017-07-26 | 23:20 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-26 | 23:30 |  |  |  | 1.5 |  | 0
2017-07-26 | 23:35 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-26 | 23:45 |  |  |  | 1.5 |  | 0
2017-07-26 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-26 | 23:55 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-27 | 0:00 |  |  |  | 1.5 |  | 0
2017-07-27 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:10 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 0:20 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:25 | -0.10574 | 0 |  | 1.5
2017-07-27 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 0:35 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 0:50 | -0.10496 | 0 |  | 1.5
2017-07-27 | 0:55 | -0.10496 | 0 |  | 1.5
2017-07-27 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-27 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-27 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-27 | 1:25 | -0.10808 | 0 |  | 1.5
2017-07-27 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 1:35 | -0.10808 | 0 |  | 1.5
2017-07-27 | 1:40 | -0.10808 | 0 |  | 1.5
2017-07-27 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 1:50 | -0.10808 | 0 |  | 1.5
2017-07-27 | 1:55 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 2:05 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:10 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 2:20 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:25 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 2:35 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:40 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 2:50 | -0.10808 | 0 |  | 1.5
2017-07-27 | 2:55 | -0.10808 | 0 |  | 1.5
2017-07-27 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 3:05 | -0.10886 | 0 |  | 1.5
2017-07-27 | 3:10 | -0.10808 | 0 |  | 1.5
2017-07-27 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 3:20 | -0.10886 | 0 |  | 1.5
2017-07-27 | 3:25 | -0.10886 | 0 |  | 1.5
2017-07-27 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 3:35 | -0.10808 | 0 |  | 1.5
2017-07-27 | 3:40 | -0.10808 | 0 |  | 1.5
2017-07-27 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 3:50 | -0.10886 | 0 |  | 1.5
2017-07-27 | 3:55 | -0.10886 | 0 |  | 1.5
2017-07-27 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-27 | 4:10 | -0.10886 | 0 |  | 1.5
2017-07-27 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-27 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-27 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-27 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-27 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-27 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-27 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 5:05 | 2.2015 | 6.2383 |  | 10
2017-07-27 | 5:10 | 2.0697 | 10 |  | 10
2017-07-27 | 5:15 | 1.9831 | 10 | 1 | 10 | 100 | 91.3083
2017-07-27 | 5:20 | 1.9644 | 10 |  | 10
2017-07-27 | 5:25 | 1.9207 | 10 |  | 10
2017-07-27 | 5:30 | 1.877 | 9.998 | 1 | 10 | 100 | 86.5435
2017-07-27 | 5:35 | 1.8669 | 9.7333 |  | 10
2017-07-27 | 5:40 | 1.8614 | 9.3289 |  | 10
2017-07-27 | 5:45 | 1.8575 | 8.8346 | 1 | 10 | 88.9662 | 83.6245
2017-07-27 | 5:50 | 1.8263 | 8.4524 |  | 10
2017-07-27 | 5:55 | 1.8458 | 8.2013 |  | 10
2017-07-27 | 6:00 | 1.8193 | 8.0436 | 1 | 10 | 81.0269 | 81.3699
2017-07-27 | 6:05 | 1.7842 | 8.3743 |  | 10
2017-07-27 | 6:10 | 1.7787 | 8.4681 |  | 10
2017-07-27 | 6:15 | 1.7772 | 8.1481 | 1 | 10 | 82.4786 | 80.4954
2017-07-27 | 6:20 | 1.7803 | 7.9707 |  | 10
2017-07-27 | 6:25 | 1.7865 | 7.8209 |  | 10
2017-07-27 | 6:30 | 1.7694 | 7.7318 | 1 | 10 | 78.515 | 79.6336
2017-07-27 | 6:35 | 1.7795 | 7.3478 |  | 10
2017-07-27 | 6:40 | 1.7951 | 7.4142 |  | 10
2017-07-27 | 6:45 | 1.7959 | 6.9945 | 1 | 10 | 71.0576 | 78.8014
2017-07-27 | 6:50 | 1.7748 | 6.6949 |  | 10
2017-07-27 | 6:55 | 1.8006 | 6.9809 |  | 10
2017-07-27 | 7:00 | 1.7709 | 6.5156 | 1 | 10 | 66.104 | 78.0471
2017-07-27 | 7:05 | 1.7842 | 6.441 |  | 10
2017-07-27 | 7:10 | 1.7787 | 6.6024 |  | 10
2017-07-27 | 7:15 | 1.7522 | 6.6293 | 1 | 10 | 67.0298 | 77.5401
2017-07-27 | 7:20 | 1.7561 | 6.4042 |  | 10
2017-07-27 | 7:25 | 1.7429 | 5.9626 |  | 10
2017-07-27 | 7:30 | 1.76 | 6.3866 | 1 | 10 | 64.5893 | 77.4092
2017-07-27 | 7:35 | 1.7553 | 6.493 |  | 10
2017-07-27 | 7:40 | 1.7195 | 6.5562 |  | 10
2017-07-27 | 7:45 | 1.7429 | 6.6236 | 1 | 10 | 67.2054 | 77.4144
2017-07-27 | 7:50 | 1.7592 | 6.3256 |  | 10
2017-07-27 | 7:55 | 1.7499 | 6.1375 |  | 10
2017-07-27 | 8:00 | 1.7405 | 5.8255 | 1 | 10 | 59.1032 | 77.1202
2017-07-27 | 8:05 | 1.7686 | 5.368 |  | 10
2017-07-27 | 8:10 | 1.7702 | 5.2206 |  | 10
2017-07-27 | 8:15 | 1.7592 | 5.554 | 1 | 10 | 56 | 76.8114
2017-07-27 | 8:20 | 1.7741 | 5.7537 |  | 10
2017-07-27 | 8:25 | 1.7834 | 5.5074 |  | 10
2017-07-27 | 8:30 | 1.7616 | 5.4908 | 1 | 10 | 56.1743 | 76.5644
2017-07-27 | 8:35 | 1.7163 | 5.1112 |  | 10
2017-07-27 | 8:40 | 1.7452 | 5.6565 |  | 10
2017-07-27 | 8:45 | 1.7304 | 6.0637 | 1 | 10 | 61.4555 | 76.6295
2017-07-27 | 8:50 | 1.7397 | 6.3013 |  | 10
2017-07-27 | 8:55 | 1.7031 | 6.7533 |  | 10
2017-07-27 | 9:00 | 1.7101 | 6.7878 | 1 | 10 | 68.9933 | 77.0928
2017-07-27 | 9:05 | 1.7397 | 7.4714 |  | 10
2017-07-27 | 9:10 | 1.7319 | 7.516 |  | 10
2017-07-27 | 9:15 | 1.7148 | 7.1411 | 1 | 10 | 71.7507 | 77.6296
2017-07-27 | 9:20 | 1.7109 | 7.3048 |  | 10
2017-07-27 | 9:25 | 1.7475 | 7.4196 |  | 10
2017-07-27 | 9:30 | 1.7483 | 7.7691 | 1 | 10 | 78.1265 | 77.9925
2017-07-27 | 9:35 | 1.7304 | 7.589 |  | 10
2017-07-27 | 9:40 | 1.7491 | 7.6238 |  | 10
2017-07-27 | 9:45 | 1.7546 | 7.0855 | 1 | 10 | 72.1393 | 78.1114
2017-07-27 | 9:50 | 1.7522 | 6.8155 |  | 10
2017-07-27 | 9:55 | 1.7686 | 6.8833 |  | 10
2017-07-27 | 10:00 | 1.7834 | 6.5705 | 1 | 10 | 67.1193 | 78.0069
2017-07-27 | 10:05 | 1.7491 | 6.1896 |  | 10
2017-07-27 | 10:10 | 1.6961 | 6.1392 |  | 10
2017-07-27 | 10:15 | 1.7366 | 6.2795 | 1 | 10 | 63.6169 | 78.3404
2017-07-27 | 10:20 | 1.7382 | 6.3926 |  | 10
2017-07-27 | 10:25 | 1.7358 | 6.5297 |  | 10
2017-07-27 | 10:30 | 1.7179 | 6.9692 | 1 | 10 | 70.2924 | 78.8859
2017-07-27 | 10:35 | 1.7062 | 7.6257 |  | 10
2017-07-27 | 10:40 | 1.7429 | 7.4864 |  | 10
2017-07-27 | 10:45 | 1.7093 | 7.7171 | 1 | 10 | 78.0796 | 79.2611
2017-07-27 | 10:50 | 1.7335 | 7.3321 |  | 10
2017-07-27 | 10:55 | 1.7234 | 7.0191 |  | 10
2017-07-27 | 11:00 | 1.7257 | 7.4235 | 1 | 10 | 75.0612 | 79.4732
2017-07-27 | 11:05 | 1.7296 | 7.6785 |  | 10
2017-07-27 | 11:10 | 1.7273 | 8.0646 |  | 10
2017-07-27 | 11:15 | 1.721 | 8.1158 | 1 | 10 | 81.6922 | 80.2233
2017-07-27 | 11:20 | 1.7163 | 8.1208 |  | 10
2017-07-27 | 11:25 | 1.7296 | 7.9373 |  | 10
2017-07-27 | 11:30 | 1.7741 | 7.4161 | 1 | 10 | 75.5127 | 80.455
2017-07-27 | 11:35 | 1.76 | 7.521 |  | 10
2017-07-27 | 11:40 | 1.7546 | 7.5636 |  | 10
2017-07-27 | 11:45 | 1.7304 | 7.3215 | 1 | 10 | 74.6337 | 80.5839
2017-07-27 | 11:50 | 1.7452 | 6.934 |  | 10
2017-07-27 | 11:55 | 1.7265 | 7.0053 |  | 10
2017-07-27 | 12:00 | 1.7686 | 6.3691 | 1 | 10 | 65.7423 | 80.6258
2017-07-27 | 12:05 | 1.7343 | 6.9443 |  | 10
2017-07-27 | 12:10 | 1.8107 | 6.7173 |  | 10
2017-07-27 | 12:15 | 1.7631 | 6.7652 | 1 | 10 | 68.502 | 80.461
2017-07-27 | 12:20 | 1.7608 | 5.6654 |  | 10
2017-07-27 | 12:25 | 1.7834 | 3.8175 |  | 10
2017-07-27 | 12:30 | 1.7733 | 4.1833 | 1 | 10 | 43.9404 | 80.22
2017-07-27 | 12:35 | 1.7475 | 5.3025 |  | 10
2017-07-27 | 12:40 | 1.6711 | 2.734 |  | 1.5
2017-07-27 | 12:45 | 1.682 | 0 | 0 | 1.5 | 25 | 82.0342
2017-07-27 | 12:50 | 1.7007 | 0 |  | 1.5
2017-07-27 | 12:55 | 1.7054 | 0 |  | 1.5
2017-07-27 | 13:00 | 1.7413 | 0 | 0 | 1.5 | 25 | 82.9437
2017-07-27 | 13:05 | 1.7468 | 0 |  | 1.5
2017-07-27 | 13:10 | 1.7546 | 0 |  | 1.5
2017-07-27 | 13:15 | 1.7569 | 0 | 0 | 1.5 | 25 | 83.2474
2017-07-27 | 13:20 | 1.7499 | 0 |  | 1.5
2017-07-27 | 13:25 | 1.7452 | 0 |  | 1.5
2017-07-27 | 13:30 | 1.7023 | 0 | 0 | 1.5 | 25 | 83.8424
2017-07-27 | 13:35 | 1.6586 | 0 |  | 1.5
2017-07-27 | 13:40 | 1.6703 | 0 |  | 1.5
2017-07-27 | 13:45 | 1.6937 | 0 | 0 | 1.5 | 25 | 85.6935
2017-07-27 | 13:50 | 1.6625 | 0 |  | 1.5
2017-07-27 | 13:55 | 1.7195 | 0 |  | 1.5
2017-07-27 | 14:00 | 1.7585 | 0 | 0 | 1.5 | 25 | 87.1694
2017-07-27 | 14:05 | 1.753 | 0 |  | 1.5
2017-07-27 | 14:10 | 1.7273 | 0 |  | 1.5
2017-07-27 | 14:15 | 1.721 | 0 | 0 | 1.5 | 25 | 87.5598
2017-07-27 | 14:20 | 1.739 | 0 |  | 1.5
2017-07-27 | 14:25 | 1.7709 | 0 |  | 1.5
2017-07-27 | 14:30 | 1.7663 | 0 | 0 | 1.5 | 25 | 87.5855
2017-07-27 | 14:35 | 1.7366 | 0 |  | 1.5
2017-07-27 | 14:40 | 1.7491 | 0 |  | 1.5
2017-07-27 | 14:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 87.3775
2017-07-27 | 14:50 | 1.7787 | 0 |  | 1.5
2017-07-27 | 14:55 | 1.739 | 0 |  | 1.5
2017-07-27 | 15:00 | 1.7678 | 0 | 0 | 1.5 | 25 | 87.0525
2017-07-27 | 15:05 | 1.7717 | 0 |  | 1.5
2017-07-27 | 15:10 | 1.792 | 0 |  | 1.5
2017-07-27 | 15:15 | 1.7187 | 0 | 0 | 1.5 | 25 | 86.6753
2017-07-27 | 15:20 | 1.7304 | 0 |  | 1.5
2017-07-27 | 15:25 | 1.7358 | 0 |  | 1.5
2017-07-27 | 15:30 | 1.7296 | 0 | 0 | 1.5 | 25 | 86.8183
2017-07-27 | 15:35 | 1.7195 | 0 |  | 1.5
2017-07-27 | 15:40 | 1.7507 | 0 |  | 1.5
2017-07-27 | 15:45 | 1.7756 | 0 | 0 | 1.5 | 25 | 87.1438
2017-07-27 | 15:50 | 1.76 | 0 |  | 1.5
2017-07-27 | 15:55 | 1.7834 | 0 |  | 1.5
2017-07-27 | 16:00 | 1.7873 | 0 | 0 | 1.5 | 25 | 86.5875
2017-07-27 | 16:05 | 1.7702 | 0 |  | 1.5
2017-07-27 | 16:10 | 1.7585 | 0 |  | 1.5
2017-07-27 | 16:15 | 1.76 | 0 | 0 | 1.5 | 25 | 86.1585
2017-07-27 | 16:20 | 1.7491 | 0 |  | 1.5
2017-07-27 | 16:25 | 1.7819 | 0 |  | 1.5
2017-07-27 | 16:30 | 1.7585 | 0 | 0 | 1.5 | 25 | 86.3236
2017-07-27 | 16:35 | 1.7577 | 0 |  | 1.5
2017-07-27 | 16:40 | 1.7514 | 0 |  | 1.5
2017-07-27 | 16:45 | 1.7514 | 0 | 0 | 1.5 | 25 | 86.3098
2017-07-27 | 16:50 | 1.7834 | 0 |  | 1.5
2017-07-27 | 16:55 | 1.7553 | 0 |  | 1.5
2017-07-27 | 17:00 | 1.7772 | 0 | 0 | 1.5 | 25 | 85.92
2017-07-27 | 17:05 | 1.7678 | 0 |  | 1.5
2017-07-27 | 17:10 | 1.7764 | 0 |  | 1.5
2017-07-27 | 17:15 | 1.7538 | 0 | 0 | 1.5 | 25 | 85.2256
2017-07-27 | 17:20 | 1.7585 | 0 |  | 1.5
2017-07-27 | 17:25 | 1.7725 | 0 |  | 1.5
2017-07-27 | 17:30 | 1.7889 | 0 | 0 | 1.5 | 25 | 84.4972
2017-07-27 | 17:35 | 1.7936 | 0 |  | 1.5
2017-07-27 | 17:40 | 1.7819 | 0 |  | 1.5
2017-07-27 | 17:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 83.7103
2017-07-27 | 17:50 | 1.7717 | 0 |  | 1.5
2017-07-27 | 17:55 | 1.7452 | 0 |  | 1.5
2017-07-27 | 18:00 | 1.7569 | 0 | 0 | 1.5 | 25 | 82.9993
2017-07-27 | 18:05 | 1.7585 | 0 |  | 1.5
2017-07-27 | 18:10 | 1.7834 | 0 |  | 1.5
2017-07-27 | 18:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 82.6142
2017-07-27 | 18:20 | 1.7405 | 0 |  | 1.5
2017-07-27 | 18:25 | 1.7475 | 0 |  | 1.5
2017-07-27 | 18:30 | 1.7335 | 0 | 0 | 1.5 | 25 | 82.4424
2017-07-27 | 18:35 | 1.7639 | 0 |  | 1.5
2017-07-27 | 18:40 | 1.7366 | 0 |  | 1.5
2017-07-27 | 18:45 | 1.7538 | 0 | 0 | 1.5 | 25 | 82.2332
2017-07-27 | 18:50 | 1.7624 | 0 |  | 1.5
2017-07-27 | 18:55 | 1.7717 | 0 |  | 1.5
2017-07-27 | 19:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 82.0067
2017-07-27 | 19:05 | 1.7624 | 0 |  | 1.5
2017-07-27 | 19:10 | 1.739 | 0 |  | 1.5
2017-07-27 | 19:15 | 1.7811 | 0 | 0 | 1.5 | 25 | 81.622
2017-07-27 | 19:20 | 1.7904 | 0 |  | 1.5
2017-07-27 | 19:25 | 1.7842 | 0 |  | 1.5
2017-07-27 | 19:30 | 1.7538 | 0 | 0 | 1.5 | 25 | 81.1489
2017-07-27 | 19:35 | 1.7655 | 0 |  | 1.5
2017-07-27 | 19:40 | 1.7561 | 0 |  | 1.5
2017-07-27 | 19:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 80.8834
2017-07-27 | 19:50 | 1.7678 | 0 |  | 1.5
2017-07-27 | 19:55 | 1.7694 | 0 |  | 1.5
2017-07-27 | 20:00 | 1.7725 | 0 | 0 | 1.5 | 25 | 80.6589
2017-07-27 | 20:05 | 1.7741 | 0 |  | 1.5
2017-07-27 | 20:10 | 1.76 | 0 |  | 1.5
2017-07-27 | 20:15 | 1.7858 | 0 | 0 | 1.5 | 25 | 80.1089
2017-07-27 | 20:20 | 1.7608 | 0 |  | 1.5
2017-07-27 | 20:25 | 1.7624 | 0 |  | 1.5
2017-07-27 | 20:30 | 1.7413 | 0 | 0 | 1.5 | 25 | 79.8733
2017-07-27 | 20:35 | 1.7616 | 0 |  | 1.5
2017-07-27 | 20:40 | 1.7639 | 0 |  | 1.5
2017-07-27 | 20:45 | 1.7444 | 0 | 0 | 1.5 | 25 | 79.952
2017-07-27 | 20:50 | 1.7546 | 0 |  | 1.5
2017-07-27 | 20:55 | 1.7265 | 0 |  | 1.5
2017-07-27 | 21:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.9848
2017-07-27 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-27 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-27 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-27 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-27 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-27 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-27 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-27 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-27 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-27 | 22:10 | -0.1073 | 0 |  | 1.5
2017-07-27 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 22:20 | -0.1073 | 0 |  | 1.5
2017-07-27 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-27 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-27 | 22:40 | -0.1073 | 0 |  | 1.5
2017-07-27 | 22:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-27 | 22:55 | -0.1073 | 0 |  | 1.5
2017-07-27 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-27 | 23:10 | -0.1073 | 0 |  | 1.5
2017-07-27 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 23:20 | -0.1073 | 0 |  | 1.5
2017-07-27 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-27 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 23:35 | -0.10652 | 0 |  | 1.5
2017-07-27 | 23:40 | -0.10652 | 0 |  | 1.5
2017-07-27 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-27 | 23:50 | -0.10652 | 0 |  | 1.5
2017-07-27 | 23:55 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-28 | 0:05 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:10 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 0:15 | [5 empty] | 0
2017-07-28 | 0:20 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:25 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 0:30 |  |  |  | 1.5 |  | 0
2017-07-28 | 0:35 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:40 | -0.10652 | 0 |  | 1.5
2017-07-28 | 0:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 0:45 | [5 empty] | 0
2017-07-28 | 0:50 | -0.10808 | 0 |  | 1.5
2017-07-28 | 0:55 | -0.10652 | 0 |  | 1.5
2017-07-28 | 1:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 1:00 | [5 empty] | 0
2017-07-28 | 1:05 | -0.10652 | 0 |  | 1.5
2017-07-28 | 1:10 | -0.10652 | 0 |  | 1.5
2017-07-28 | 1:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 1:15 | [5 empty] | 0
2017-07-28 | 1:20 | -0.10964 | 0 |  | 1.5
2017-07-28 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-28 | 1:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 1:30 |  |  |  | 1.5 |  | 0
2017-07-28 | 1:35 | -0.10964 | 0 |  | 1.5
2017-07-28 | 1:40 | -0.10964 | 0 |  | 1.5
2017-07-28 | 1:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 1:45 | [5 empty] | 0
2017-07-28 | 1:50 | -0.10964 | 0 |  | 1.5
2017-07-28 | 1:55 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 2:00 | [5 empty] | 0
2017-07-28 | 2:05 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:10 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 2:15 | [5 empty] | 0
2017-07-28 | 2:20 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:25 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 2:30 |  |  |  | 1.5 |  | 0
2017-07-28 | 2:35 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:40 | -0.10964 | 0 |  | 1.5
2017-07-28 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 2:45 | [5 empty] | 0
2017-07-28 | 2:50 | -0.11042 | 0 |  | 1.5
2017-07-28 | 2:55 | -0.10964 | 0 |  | 1.5
2017-07-28 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 3:00 | [5 empty] | 0
2017-07-28 | 3:05 | -0.10964 | 0 |  | 1.5
2017-07-28 | 3:10 | -0.11042 | 0 |  | 1.5
2017-07-28 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0
2017-07-28 | 3:15 |  |  |  | 1.5 |  | 0
2017-07-28 | 3:20 | -0.11042 | 0 |  | 1.5
2017-07-28 | 3:25 | -0.11042 | 0 |  | 1.5
2017-07-28 | 3:30 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 3:30 |  |  |  | 1.5 |  | 0
2017-07-28 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-28 | 3:40 | -0.10964 | 0 |  | 1.5
2017-07-28 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 3:45 | [5 empty] | 0
2017-07-28 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-28 | 3:55 | -0.11042 | 0 |  | 1.5
2017-07-28 | 4:00 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 4:00 |  |  |  | 1.5 |  | 0
2017-07-28 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-28 | 4:10 | -0.11042 | 0 |  | 1.5
2017-07-28 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 4:15 | [5 empty] | 0
2017-07-28 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-28 | 4:25 | -0.11042 | 0 |  | 1.5
2017-07-28 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 4:30 |  |  |  | 1.5 |  | 0
2017-07-28 | 4:35 | -0.11042 | 0 |  | 1.5
2017-07-28 | 4:40 | -0.11042 | 0 |  | 1.5
2017-07-28 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0
2017-07-28 | 4:45 | [5 empty] | 0
2017-07-28 | 4:50 | -0.11042 | 0 |  | 1.5
2017-07-28 | 4:55 | -0.11042 | 0 |  | 1.5
2017-07-28 | 5:00 | -0.11042 | 0 | 1 | 0 | 0
2017-07-28 | 5:00 |  |  |  | 0 |  | 25
2017-07-28 | 5:05 | 2.5665 | 5.7001 |  | 10
2017-07-28 | 5:10 | 2.2584 | 9.7051 |  | 10
2017-07-28 | 5:15 | 2.097 | 9.2029 | 1 | 10 | 93.6573
2017-07-28 | 5:15 | [5 empty] | 85.9448
2017-07-28 | 5:20 | 1.9956 | 8.822 |  | 10
2017-07-28 | 5:25 | 1.9379 | 8.1557 |  | 10
2017-07-28 | 5:30 | 1.8349 | 7.7997 | 1 | 10 | 80.0254
2017-07-28 | 5:30 |  |  |  | 10 |  | 80.6355
2017-07-28 | 5:35 | 1.8653 | 7.3275 |  | 10
2017-07-28 | 5:40 | 1.7928 | 6.9388 |  | 10
2017-07-28 | 5:45 | 1.8131 | 6.8277 | 1 | 10 | 70.5941
2017-07-28 | 5:45 | [5 empty] | 78.3906
2017-07-28 | 5:50 | 1.7936 | 6.3605 |  | 10
2017-07-28 | 5:55 | 1.7881 | 6.4296 |  | 10
2017-07-28 | 6:00 | 1.7975 | 6.0326 | 1 | 10 | 62.8801
2017-07-28 | 6:00 |  |  |  | 10 |  | 77.2999
2017-07-28 | 6:05 | 1.8006 | 6.4712 |  | 10
2017-07-28 | 6:10 | 1.7787 | 6.7002 |  | 10
2017-07-28 | 6:15 | 1.7663 | 6.755 | 1 | 10 | 69.4967
2017-07-28 | 6:15 | [5 empty] | 77.001
2017-07-28 | 6:20 | 1.7226 | 7.0047 |  | 10
2017-07-28 | 6:25 | 1.7351 | 6.5038 |  | 10
2017-07-28 | 6:30 | 1.7608 | 6.7624 | 1 | 10 | 69.6277
2017-07-28 | 6:30 | [5 empty] | 76.9841
2017-07-28 | 6:35 | 1.7444 | 6.7194 |  | 10
2017-07-28 | 6:40 | 1.7624 | 6.7175 |  | 10
2017-07-28 | 6:45 | 1.7592 | 6.7079 | 1 | 10 | 69.3359
2017-07-28 | 6:45 | [5 empty] | 76.7588
2017-07-28 | 6:50 | 1.7499 | 6.2161 |  | 10
2017-07-28 | 6:55 | 1.7429 | 6.2882 |  | 10
2017-07-28 | 7:00 | 1.7436 | 6.0577 | 1 | 10 | 63.1589
2017-07-28 | 7:00 |  |  |  | 10 |  | 76.651
2017-07-28 | 7:05 | 1.7819 | 5.8982 |  | 10
2017-07-28 | 7:10 | 1.7655 | 6.0767 |  | 10
2017-07-28 | 7:15 | 1.746 | 5.9017 | 1 | 10 | 61.9733
2017-07-28 | 7:15 |  |  |  | 10 |  | 76.1245
2017-07-28 | 7:20 | 1.7592 | 5.9218 |  | 10
2017-07-28 | 7:25 | 1.7748 | 5.5947 |  | 10
2017-07-28 | 7:30 | 1.753 | 5.1412 | 1 | 10 | 54.2997
2017-07-28 | 7:30 |  |  |  | 10 |  | 75.7388
2017-07-28 | 7:35 | 1.7655 | 4.817 |  | 10
2017-07-28 | 7:40 | 1.7624 | 4.4562 |  | 10
2017-07-28 | 7:45 | 1.7234 | 4.3564 | 1 | 10 | 46.4052
2017-07-28 | 7:45 | [5 empty] | 75.432
2017-07-28 | 7:50 | 1.7741 | 4.0117 |  | 10
2017-07-28 | 7:55 | 1.7553 | 3.4012 |  | 10
2017-07-28 | 8:00 | 1.7234 | 3.269 | 1 | 10 | 35.6199
2017-07-28 | 8:00 |  |  |  | 10 |  | 75.1917
2017-07-28 | 8:05 | 1.7553 | 3.5714 |  | 10
2017-07-28 | 8:10 | 1.7413 | 4.4753 |  | 10
2017-07-28 | 8:15 | 1.7366 | 5.0748 | 1 | 10 | 52.6911
2017-07-28 | 8:15 | [5 empty] | 75.3134
2017-07-28 | 8:20 | 1.7405 | 5.0791 |  | 10
2017-07-28 | 8:25 | 1.7358 | 5.225 |  | 10
2017-07-28 | 8:30 | 1.753 | 5.1327 | 1 | 10 | 54.2908
2017-07-28 | 8:30 |  |  |  | 10 |  | 75.4803
2017-07-28 | 8:35 | 1.7514 | 5.2932 |  | 10
2017-07-28 | 8:40 | 1.739 | 5.2934 |  | 10
2017-07-28 | 8:45 | 1.7319 | 5.8155 | 1 | 10 | 60.8971
2017-07-28 | 8:45 | [5 empty] | 75.7208
2017-07-28 | 8:50 | 1.7429 | 5.5092 |  | 10
2017-07-28 | 8:55 | 1.7343 | 6.0192 |  | 10
2017-07-28 | 9:00 | 1.721 | 6.2911 | 1 | 10 | 64.8653
2017-07-28 | 9:00 | [5 empty] | 76.2124
2017-07-28 | 9:05 | 1.7218 | 6.4811 |  | 10
2017-07-28 | 9:10 | 1.7624 | 6.5906 |  | 10
2017-07-28 | 9:15 | 1.739 | 6.4934 | 1 | 10 | 67.5654
2017-07-28 | 9:15 |  |  |  | 10 |  | 76.4579
2017-07-28 | 9:20 | 1.721 | 6.9 |  | 10
2017-07-28 | 9:25 | 1.7561 | 6.6128 |  | 10
2017-07-28 | 9:30 | 1.7694 | 6.5801 | 1 | 10 | 68.0028
2017-07-28 | 9:30 |  |  |  | 10 |  | 76.6646
2017-07-28 | 9:35 | 1.7538 | 6.1575 |  | 10
2017-07-28 | 9:40 | 1.7343 | 6.8513 |  | 10
2017-07-28 | 9:45 | 1.7561 | 6.4352 | 1 | 10 | 67.4725
2017-07-28 | 9:45 | [5 empty] | 77.0623
2017-07-28 | 9:50 | 1.7265 | 6.2361 |  | 10
2017-07-28 | 9:55 | 1.7561 | 6.2326 |  | 10
2017-07-28 | 10:00 | 1.7444 | 6.2634 | 1 | 10 | 64.7576
2017-07-28 | 10:00 | [5 empty] | 77.2588
2017-07-28 | 10:05 | 1.739 | 6.1483 |  | 10
2017-07-28 | 10:10 | 1.7421 | 6.4465 |  | 10
2017-07-28 | 10:15 | 1.7218 | 6.3845 | 1 | 10 | 65.8711
2017-07-28 | 10:15 | [5 empty] | 77.7295
2017-07-28 | 10:20 | 1.6961 | 7.0423 |  | 10
2017-07-28 | 10:25 | 1.7023 | 6.4893 |  | 10
2017-07-28 | 10:30 | 1.753 | 7.1225 | 1 | 10 | 72.9628
2017-07-28 | 10:30 |  |  |  | 10 |  | 78.7141
2017-07-28 | 10:35 | 1.7491 | 6.773 |  | 10
2017-07-28 | 10:40 | 1.785 | 4.5554 |  | 10
2017-07-28 | 10:45 | 1.5798 | 4.0419 | 0 | 1.5 | 44.4468
2017-07-28 | 10:45 | [5 empty] | 80.3504
2017-07-28 | 10:50 | 1.6617 | 3.3972 |  | 1.5
2017-07-28 | 10:55 | 1.7499 | 0.85673 |  | 1.5
2017-07-28 | 11:00 | 1.7483 | 0 | 0 | 1.5 | 25
2017-07-28 | 11:00 |  |  |  | 1.5 |  | 81.757
2017-07-28 | 11:05 | 1.7171 | 0 |  | 1.5
2017-07-28 | 11:10 | 1.7124 | 0 |  | 1.5
2017-07-28 | 11:15 | 1.7343 | 0 | 0 | 1.5 | 25
2017-07-28 | 11:15 | [5 empty] | 82.3904
2017-07-28 | 11:20 | 1.7304 | 0 |  | 1.5
2017-07-28 | 11:25 | 1.6883 | 0 |  | 1.5
2017-07-28 | 11:30 | 1.6812 | 0 | 0 | 1.5 | 25
2017-07-28 | 11:30 | [5 empty] | 83.9088
2017-07-28 | 11:35 | 1.6968 | 0 |  | 1.5
2017-07-28 | 11:40 | 1.661 | 0 |  | 1.5
2017-07-28 | 11:45 | 1.721 | 0 | 0 | 1.5 | 25
2017-07-28 | 11:45 | [5 empty] | 85.3988
2017-07-28 | 11:50 | 1.6789 | 0 |  | 1.5
2017-07-28 | 11:55 | 1.7124 | 0 |  | 1.5
2017-07-28 | 12:00 | 1.6906 | 0 | 0 | 1.5 | 25
2017-07-28 | 12:00 |  |  |  | 1.5 |  | 86.4554
2017-07-28 | 12:05 | 1.7296 | 0 |  | 1.5
2017-07-28 | 12:10 | 1.7039 | 0 |  | 1.5
2017-07-28 | 12:15 | 1.7039 | 0 | 0 | 1.5 | 25
2017-07-28 | 12:15 | [5 empty] | 87.6324
2017-07-28 | 12:20 | 1.714 | 0 |  | 1.5
2017-07-28 | 12:25 | 1.7273 | 0 |  | 1.5
2017-07-28 | 12:30 | 1.739 | 0 | 0 | 1.5 | 25
2017-07-28 | 12:30 | [5 empty] | 88.5612
2017-07-28 | 12:35 | 1.7561 | 0 |  | 1.5
2017-07-28 | 12:40 | 1.7655 | 0 |  | 1.5
2017-07-28 | 12:45 | 1.7717 | 0 | 0 | 1.5 | 25
2017-07-28 | 12:45 | [5 empty] | 88.4625
2017-07-28 | 12:50 | 1.7826 | 0 |  | 1.5
2017-07-28 | 12:55 | 1.7569 | 0 |  | 1.5
2017-07-28 | 13:00 | 1.7179 | 0 | 0 | 1.5 | 25
2017-07-28 | 13:00 |  |  |  | 1.5 |  | 88.0816
2017-07-28 | 13:05 | 1.7179 | 0 |  | 1.5
2017-07-28 | 13:10 | 1.76 | 0 |  | 1.5
2017-07-28 | 13:15 | 1.7561 | 0 | 0 | 1.5 | 25
2017-07-28 | 13:15 | [5 empty] | 88.1255
2017-07-28 | 13:20 | 1.7678 | 0 |  | 1.5
2017-07-28 | 13:25 | 1.7678 | 0 |  | 1.5
2017-07-28 | 13:30 | 1.7663 | 0 | 0 | 1.5 | 25
2017-07-28 | 13:30 |  |  |  | 1.5 |  | 87.8589
2017-07-28 | 13:35 | 1.7631 | 0 |  | 1.5
2017-07-28 | 13:40 | 1.7787 | 0 |  | 1.5
2017-07-28 | 13:45 | 1.7585 | 0 | 0 | 1.5 | 25
2017-07-28 | 13:45 | [5 empty] | 87.7063
2017-07-28 | 13:50 | 1.7733 | 0 |  | 1.5
2017-07-28 | 13:55 | 1.8224 | 0 |  | 1.5
2017-07-28 | 14:00 | 1.7943 | 0 | 0 | 1.5 | 25
2017-07-28 | 14:00 | [5 empty] | 86.668
2017-07-28 | 14:05 | 1.7678 | 0 |  | 1.5
2017-07-28 | 14:10 | 1.7842 | 0 |  | 1.5
2017-07-28 | 14:15 | 1.7569 | 0 | 0 | 1.5 | 25
2017-07-28 | 14:15 | [5 empty] | 86.2065
2017-07-28 | 14:20 | 1.7366 | 0 |  | 1.5
2017-07-28 | 14:25 | 1.707 | 0 |  | 1.5
2017-07-28 | 14:30 | 1.7171 | 0 | 0 | 1.5 | 25
2017-07-28 | 14:30 | [5 empty] | 86.6617
2017-07-28 | 14:35 | 1.7397 | 0 |  | 1.5
2017-07-28 | 14:40 | 1.7764 | 0 |  | 1.5
2017-07-28 | 14:45 | 1.7795 | 0 | 0 | 1.5 | 25
2017-07-28 | 14:45 | [5 empty] | 86.5416
2017-07-28 | 14:50 | 1.7756 | 0 |  | 1.5
2017-07-28 | 14:55 | 1.7234 | 0 |  | 1.5
2017-07-28 | 15:00 | 1.7436 | 0 | 0 | 1.5 | 25
2017-07-28 | 15:00 | [5 empty] | 86.5536
2017-07-28 | 15:05 | 1.7491 | 0 |  | 1.5
2017-07-28 | 15:10 | 1.7569 | 0 |  | 1.5
2017-07-28 | 15:15 | 1.739 | 0 | 0 | 1.5 | 25
2017-07-28 | 15:15 | [5 empty] | 86.6484
2017-07-28 | 15:20 | 1.7663 | 0 |  | 1.5
2017-07-28 | 15:25 | 1.7374 | 0 |  | 1.5
2017-07-28 | 15:30 | 1.7522 | 0 | 0 | 1.5 | 25
2017-07-28 | 15:30 | [5 empty] | 86.9157
2017-07-28 | 15:35 | 1.7538 | 0 |  | 1.5
2017-07-28 | 15:40 | 1.7319 | 0 |  | 1.5
2017-07-28 | 15:45 | 1.7741 | 0 | 0 | 1.5 | 25
2017-07-28 | 15:45 | [5 empty] | 86.767
2017-07-28 | 15:50 | 1.7561 | 0 |  | 1.5
2017-07-28 | 15:55 | 1.7538 | 0 |  | 1.5
2017-07-28 | 16:00 | 1.7483 | 0 | 0 | 1.5 | 25
2017-07-28 | 16:00 | [5 empty] | 86.4979
2017-07-28 | 16:05 | 1.7608 | 0 |  | 1.5
2017-07-28 | 16:10 | 1.7655 | 0 |  | 1.5
2017-07-28 | 16:15 | 1.767 | 0 | 0 | 1.5 | 25
2017-07-28 | 16:15 | [5 empty] | 86.2219
2017-07-28 | 16:20 | 1.7772 | 0 |  | 1.5
2017-07-28 | 16:25 | 1.7538 | 0 |  | 1.5
2017-07-28 | 16:30 | 1.7686 | 0 | 0 | 1.5 | 25
2017-07-28 | 16:30 | [5 empty] | 85.7216
2017-07-28 | 16:35 | 1.76 | 0 |  | 1.5
2017-07-28 | 16:40 | 1.7764 | 0 |  | 1.5
2017-07-28 | 16:45 | 1.7733 | 0 | 0 | 1.5 | 25
2017-07-28 | 16:45 | [5 empty] | 85.1669
2017-07-28 | 16:50 | 1.7499 | 0 |  | 1.5
2017-07-28 | 16:55 | 1.7624 | 0 |  | 1.5
2017-07-28 | 17:00 | 1.7803 | 0 | 0 | 1.5 | 25
2017-07-28 | 17:00 | [5 empty] | 84.6553
2017-07-28 | 17:05 | 1.767 | 0 |  | 1.5
2017-07-28 | 17:10 | 1.7663 | 0 |  | 1.5
2017-07-28 | 17:15 | 1.7795 | 0 | 0 | 1.5 | 25
2017-07-28 | 17:15 | [5 empty] | 84.1542
2017-07-28 | 17:20 | 1.778 | 0 |  | 1.5
2017-07-28 | 17:25 | 1.7655 | 0 |  | 1.5
2017-07-28 | 17:30 | 1.7717 | 0 | 0 | 1.5 | 25
2017-07-28 | 17:30 | [5 empty] | 83.5634
2017-07-28 | 17:35 | 1.7624 | 0 |  | 1.5
2017-07-28 | 17:40 | 1.7842 | 0 |  | 1.5
2017-07-28 | 17:45 | 1.7865 | 0 | 0 | 1.5 | 25
2017-07-28 | 17:45 | [5 empty] | 83.064
2017-07-28 | 17:50 | 1.7897 | 0 |  | 1.5
2017-07-28 | 17:55 | 1.7702 | 0 |  | 1.5
2017-07-28 | 18:00 | 1.7631 | 0 | 0 | 1.5 | 25
2017-07-28 | 18:00 |  |  |  | 1.5 |  | 82.4757
2017-07-28 | 18:05 | 1.7811 | 0 |  | 1.5
2017-07-28 | 18:10 | 1.7897 | 0 |  | 1.5
2017-07-28 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 25
2017-07-28 | 18:15 |  |  |  | 1.5 |  | 81.9888
2017-07-28 | 18:20 | 1.7444 | 0 |  | 1.5
2017-07-28 | 18:25 | 1.7655 | 0 |  | 1.5
2017-07-28 | 18:30 | 1.7756 | 0 | 0 | 1.5 | 25
2017-07-28 | 18:30 |  |  |  | 1.5 |  | 81.6778
2017-07-28 | 18:35 | 1.7616 | 0 |  | 1.5
2017-07-28 | 18:40 | 1.7327 | 0 |  | 1.5
2017-07-28 | 18:45 | 1.7709 | 0 | 0 | 1.5 | 25
2017-07-28 | 18:45 | [5 empty] | 81.4357
2017-07-28 | 18:50 | 1.7904 | 0 |  | 1.5
2017-07-28 | 18:55 | 1.7725 | 0 |  | 1.5
2017-07-28 | 19:00 | 1.7717 | 0 | 0 | 1.5 | 25
2017-07-28 | 19:00 |  |  |  | 1.5 |  | 80.9099
2017-07-28 | 19:05 | 1.7616 | 0 |  | 1.5
2017-07-28 | 19:10 | 1.7717 | 0 |  | 1.5
2017-07-28 | 19:15 | 1.7569 | 0 | 0 | 1.5 | 25
2017-07-28 | 19:15 | [5 empty] | 80.4994
2017-07-28 | 19:20 | 1.7585 | 0 |  | 1.5
2017-07-28 | 19:25 | 1.76 | 0 |  | 1.5
2017-07-28 | 19:30 | 1.7608 | 0 | 0 | 1.5 | 25
2017-07-28 | 19:30 | [5 empty] | 80.1352
2017-07-28 | 19:35 | 1.7702 | 0 |  | 1.5
2017-07-28 | 19:40 | 1.7686 | 0 |  | 1.5
2017-07-28 | 19:45 | 1.739 | 0 | 0 | 1.5 | 25
2017-07-28 | 19:45 | [5 empty] | 79.7705
2017-07-28 | 19:50 | 1.767 | 0 |  | 1.5
2017-07-28 | 19:55 | 1.7382 | 0 |  | 1.5
2017-07-28 | 20:00 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-28 | 20:00 | [5 empty] | 79.6851
2017-07-28 | 20:05 | 1.7569 | 0 |  | 1.5
2017-07-28 | 20:10 | 1.7702 | 0 |  | 1.5
2017-07-28 | 20:15 | 1.7624 | 0 | 0 | 1.5 | 25
2017-07-28 | 20:15 | [5 empty] | 79.5212
2017-07-28 | 20:20 | 1.7468 | 0 |  | 1.5
2017-07-28 | 20:25 | 1.7546 | 0 |  | 1.5
2017-07-28 | 20:30 | 1.7639 | 0 | 0 | 1.5 | 25
2017-07-28 | 20:30 |  |  |  | 1.5 |  | 79.6525
2017-07-28 | 20:35 | 1.7351 | 0 |  | 1.5
2017-07-28 | 20:40 | 1.7569 | 0 |  | 1.5
2017-07-28 | 20:45 | 1.7397 | 0 | 0 | 1.5 | 25
2017-07-28 | 20:45 | [5 empty] | 79.7496
2017-07-28 | 20:50 | 1.753 | 0 |  | 1.5
2017-07-28 | 20:55 | 1.7647 | 0 |  | 1.5
2017-07-28 | 21:00 | 1.7436 | 0 | 0 | 1.5 | 25
2017-07-28 | 21:00 | [5 empty] | 0
2017-07-28 | 21:05 | -0.10496 | 0 |  | 1.5
2017-07-28 | 21:10 | -0.10574 | 0 |  | 1.5
2017-07-28 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-07-28 | 21:15 | [5 empty] | 0
2017-07-28 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-28 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-28 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-28 | 21:30 | [5 empty] | 0
2017-07-28 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-28 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-28 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 21:45 | [5 empty] | 0
2017-07-28 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-28 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 22:00 |  |  |  | 1.5 |  | 0
2017-07-28 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:10 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-28 | 22:15 | [5 empty] | 0
2017-07-28 | 22:20 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:25 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 22:30 | [5 empty] | 0
2017-07-28 | 22:35 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:40 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 22:45 | [5 empty] | 0
2017-07-28 | 22:50 | -0.10652 | 0 |  | 1.5
2017-07-28 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 23:00 |  |  |  | 1.5 |  | 0
2017-07-28 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:10 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 23:15 |  |  |  | 1.5 |  | 0
2017-07-28 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:25 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-07-28 | 23:30 |  |  |  | 1.5 |  | 0
2017-07-28 | 23:35 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:40 | -0.10652 | 0 |  | 1.5
2017-07-28 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-07-28 | 23:45 | [5 empty] | 0
2017-07-28 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-28 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-07-29 | 0:00 | [5 empty] | 0
2017-07-29 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:10 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 0:20 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:25 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:40 | -0.10652 | 0 |  | 1.5
2017-07-29 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 0:50 | -0.10574 | 0 |  | 1.5
2017-07-29 | 0:55 | -0.10574 | 0 |  | 1.5
2017-07-29 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 1:05 | -0.10574 | 0 |  | 1.5
2017-07-29 | 1:10 | -0.10574 | 0 |  | 1.5
2017-07-29 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-29 | 1:25 | -0.10886 | 0 |  | 1.5
2017-07-29 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 1:35 | -0.10886 | 0 |  | 1.5
2017-07-29 | 1:40 | -0.10886 | 0 |  | 1.5
2017-07-29 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 1:50 | -0.10886 | 0 |  | 1.5
2017-07-29 | 1:55 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 2:05 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:10 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 2:20 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:25 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 2:35 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:40 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 2:50 | -0.10886 | 0 |  | 1.5
2017-07-29 | 2:55 | -0.10886 | 0 |  | 1.5
2017-07-29 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 3:05 | -0.10886 | 0 |  | 1.5
2017-07-29 | 3:10 | -0.10886 | 0 |  | 1.5
2017-07-29 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 3:20 | -0.10886 | 0 |  | 1.5
2017-07-29 | 3:25 | -0.10886 | 0 |  | 1.5
2017-07-29 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 3:35 | -0.10964 | 0 |  | 1.5
2017-07-29 | 3:40 | -0.10886 | 0 |  | 1.5
2017-07-29 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 3:50 | -0.10964 | 0 |  | 1.5
2017-07-29 | 3:55 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 4:05 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:10 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 4:20 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:25 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 4:35 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:40 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:45 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 4:50 | -0.10964 | 0 |  | 1.5
2017-07-29 | 4:55 | -0.10964 | 0 |  | 1.5
2017-07-29 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 5:05 | 2.3505 | 6.0642 |  | 10
2017-07-29 | 5:10 | 2.1305 | 10 |  | 10
2017-07-29 | 5:15 | 2.0595 | 10 | 1 | 10 | 100 | 89.1096
2017-07-29 | 5:20 | 1.98 | 9.7194 |  | 10
2017-07-29 | 5:25 | 1.9332 | 9.2644 |  | 10
2017-07-29 | 5:30 | 1.8911 | 8.7887 | 1 | 10 | 88.4459 | 83.9969
2017-07-29 | 5:35 | 1.8638 | 8.6281 |  | 10
2017-07-29 | 5:40 | 1.8443 | 8.3169 |  | 10
2017-07-29 | 5:45 | 1.8099 | 8.0133 | 1 | 10 | 80.8696 | 81.4857
2017-07-29 | 5:50 | 1.8372 | 7.9054 |  | 10
2017-07-29 | 5:55 | 1.7897 | 7.5235 |  | 10
2017-07-29 | 6:00 | 1.7959 | 7.4452 | 1 | 10 | 75.1553 | 79.9054
2017-07-29 | 6:05 | 1.792 | 7.5148 |  | 10
2017-07-29 | 6:10 | 1.7787 | 7.4603 |  | 10
2017-07-29 | 6:15 | 1.7834 | 7.4713 | 1 | 10 | 75.6308 | 79.0718
2017-07-29 | 6:20 | 1.7624 | 7.1859 |  | 10
2017-07-29 | 6:25 | 1.7842 | 7.103 |  | 10
2017-07-29 | 6:30 | 1.7959 | 6.8282 | 1 | 10 | 69.472 | 78.2912
2017-07-29 | 6:35 | 1.7748 | 6.7509 |  | 10
2017-07-29 | 6:40 | 1.7444 | 6.7748 |  | 10
2017-07-29 | 6:45 | 1.7553 | 6.5614 | 1 | 10 | 66.6201 | 77.7834
2017-07-29 | 6:50 | 1.7483 | 6.7087 |  | 10
2017-07-29 | 6:55 | 1.7655 | 6.5193 |  | 10
2017-07-29 | 7:00 | 1.7717 | 6.5794 | 1 | 10 | 66.6679 | 77.531
2017-07-29 | 7:05 | 1.7507 | 6.4598 |  | 10
2017-07-29 | 7:10 | 1.8255 | 6.3999 |  | 10
2017-07-29 | 7:15 | 1.785 | 6.5705 | 1 | 10 | 66.6599 | 76.9423
2017-07-29 | 7:20 | 1.7546 | 6.435 |  | 10
2017-07-29 | 7:25 | 1.7741 | 6.588 |  | 10
2017-07-29 | 7:30 | 1.7553 | 6.4539 | 1 | 10 | 65.8907 | 76.5165
2017-07-29 | 7:35 | 1.7374 | 6.2116 |  | 10
2017-07-29 | 7:40 | 1.7678 | 6.1688 |  | 10
2017-07-29 | 7:45 | 1.778 | 6.063 | 1 | 10 | 61.7549 | 76.1855
2017-07-29 | 7:50 | 1.7312 | 6.2481 |  | 10
2017-07-29 | 7:55 | 1.7631 | 6.015 |  | 10
2017-07-29 | 8:00 | 1.7257 | 6.3337 | 1 | 10 | 64.0607 | 76.1814
2017-07-29 | 8:05 | 1.7608 | 6.6198 |  | 10
2017-07-29 | 8:10 | 1.7499 | 6.682 |  | 10
2017-07-29 | 8:15 | 1.7429 | 7.0414 | 1 | 10 | 71.2065 | 76.2721
2017-07-29 | 8:20 | 1.7335 | 6.9987 |  | 10
2017-07-29 | 8:25 | 1.7507 | 7.1852 |  | 10
2017-07-29 | 8:30 | 1.7288 | 7.2766 | 1 | 10 | 73.6731 | 76.4428
2017-07-29 | 8:35 | 1.746 | 7.0015 |  | 10
2017-07-29 | 8:40 | 1.7335 | 7.4908 |  | 10
2017-07-29 | 8:45 | 1.7546 | 7.2252 | 1 | 10 | 72.9567 | 76.6293
2017-07-29 | 8:50 | 1.7553 | 7.3519 |  | 10
2017-07-29 | 8:55 | 1.7499 | 7.1053 |  | 10
2017-07-29 | 9:00 | 1.7304 | 7.0987 | 1 | 10 | 72.1796 | 76.7402
2017-07-29 | 9:05 | 1.7499 | 6.8984 |  | 10
2017-07-29 | 9:10 | 1.7452 | 6.9094 |  | 10
2017-07-29 | 9:15 | 1.7304 | 7.5474 | 1 | 10 | 75.9267 | 76.8073
2017-07-29 | 9:20 | 1.7444 | 7.4076 |  | 10
2017-07-29 | 9:25 | 1.7522 | 7.3589 |  | 10
2017-07-29 | 9:30 | 1.7436 | 7.4378 | 1 | 10 | 75.1023 | 77.1453
2017-07-29 | 9:35 | 1.7351 | 7.3846 |  | 10
2017-07-29 | 9:40 | 1.7358 | 7.9261 |  | 10
2017-07-29 | 9:45 | 1.7296 | 7.606 | 1 | 10 | 76.9852 | 77.5672
2017-07-29 | 9:50 | 1.7569 | 7.5577 |  | 10
2017-07-29 | 9:55 | 1.4644 | 5.8276 |  | 1.5
2017-07-29 | 10:00 | 1.7811 | 1.8491 | 0 | 1.5 | 25 | 79.3199
2017-07-29 | 10:05 | 1.7265 | 0 |  | 1.5
2017-07-29 | 10:10 | 1.7436 | 0 |  | 1.5
2017-07-29 | 10:15 | 1.778 | 0 | 0 | 1.5 | 25 | 79.3593
2017-07-29 | 10:20 | 1.7202 | 0 |  | 1.5
2017-07-29 | 10:25 | 1.7655 | 0 |  | 1.5
2017-07-29 | 10:30 | 1.7195 | 0 | 0 | 1.5 | 25 | 79.511
2017-07-29 | 10:35 | 1.7405 | 0 |  | 1.5
2017-07-29 | 10:40 | 1.7663 | 0 |  | 1.5
2017-07-29 | 10:45 | 1.7491 | 0 | 0 | 1.5 | 25 | 79.5103
2017-07-29 | 10:50 | 1.7475 | 0 |  | 1.5
2017-07-29 | 10:55 | 1.7499 | 0 |  | 1.5
2017-07-29 | 11:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 79.4707
2017-07-29 | 11:05 | 1.7553 | 0 |  | 1.5
2017-07-29 | 11:10 | 1.7312 | 0 |  | 1.5
2017-07-29 | 11:15 | 1.7319 | 0 | 0 | 1.5 | 25 | 79.7419
2017-07-29 | 11:20 | 1.7639 | 0 |  | 1.5
2017-07-29 | 11:25 | 1.7639 | 0 |  | 1.5
2017-07-29 | 11:30 | 1.7382 | 0 | 0 | 1.5 | 25 | 79.7842
2017-07-29 | 11:35 | 1.7202 | 0 |  | 1.5
2017-07-29 | 11:40 | 1.753 | 0 |  | 1.5
2017-07-29 | 11:45 | 1.7132 | 0 | 0 | 1.5 | 25 | 80.0532
2017-07-29 | 11:50 | 1.739 | 0 |  | 1.5
2017-07-29 | 11:55 | 1.7561 | 0 |  | 1.5
2017-07-29 | 12:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 80.2997
2017-07-29 | 12:05 | 1.7491 | 0 |  | 1.5
2017-07-29 | 12:10 | 1.7405 | 0 |  | 1.5
2017-07-29 | 12:15 | 1.7366 | 0 | 0 | 1.5 | 25 | 80.5731
2017-07-29 | 12:20 | 1.7366 | 0 |  | 1.5
2017-07-29 | 12:25 | 1.7304 | 0 |  | 1.5
2017-07-29 | 12:30 | 1.7335 | 0 | 0 | 1.5 | 25 | 81.0881
2017-07-29 | 12:35 | 1.7312 | 0 |  | 1.5
2017-07-29 | 12:40 | 1.7382 | 0 |  | 1.5
2017-07-29 | 12:45 | 1.7382 | 0 | 0 | 1.5 | 25 | 81.6636
2017-07-29 | 12:50 | 1.7085 | 0 |  | 1.5
2017-07-29 | 12:55 | 1.7382 | 0 |  | 1.5
2017-07-29 | 13:00 | 1.7319 | 0 | 0 | 1.5 | 25 | 82.1072
2017-07-29 | 13:05 | 1.7374 | 0 |  | 1.5
2017-07-29 | 13:10 | 1.728 | 0 |  | 1.5
2017-07-29 | 13:15 | 1.7156 | 0 | 0 | 1.5 | 25 | 82.5645
2017-07-29 | 13:20 | 1.753 | 0 |  | 1.5
2017-07-29 | 13:25 | 1.7343 | 0 |  | 1.5
2017-07-29 | 13:30 | 1.7569 | 0 | 0 | 1.5 | 25 | 83.1121
2017-07-29 | 13:35 | 1.728 | 0 |  | 1.5
2017-07-29 | 13:40 | 1.721 | 0 |  | 1.5
2017-07-29 | 13:45 | 1.7109 | 0 | 0 | 1.5 | 25 | 83.8547
2017-07-29 | 13:50 | 1.76 | 0 |  | 1.5
2017-07-29 | 13:55 | 1.7405 | 0 |  | 1.5
2017-07-29 | 14:00 | 1.7156 | 0 | 0 | 1.5 | 25 | 84.6799
2017-07-29 | 14:05 | 1.7546 | 0 |  | 1.5
2017-07-29 | 14:10 | 1.76 | 0 |  | 1.5
2017-07-29 | 14:15 | 1.7553 | 0 | 0 | 1.5 | 25 | 84.646
2017-07-29 | 14:20 | 1.7748 | 0 |  | 1.5
2017-07-29 | 14:25 | 1.7514 | 0 |  | 1.5
2017-07-29 | 14:30 | 1.7608 | 0 | 0 | 1.5 | 25 | 84.5653
2017-07-29 | 14:35 | 1.746 | 0 |  | 1.5
2017-07-29 | 14:40 | 1.7319 | 0 |  | 1.5
2017-07-29 | 14:45 | 1.7616 | 0 | 0 | 1.5 | 25 | 84.436
2017-07-29 | 14:50 | 1.7592 | 0 |  | 1.5
2017-07-29 | 14:55 | 1.7553 | 0 |  | 1.5
2017-07-29 | 15:00 | 1.739 | 0 | 0 | 1.5 | 25 | 84.3033
2017-07-29 | 15:05 | 1.7787 | 0 |  | 1.5
2017-07-29 | 15:10 | 1.7413 | 0 |  | 1.5
2017-07-29 | 15:15 | 1.7538 | 0 | 0 | 1.5 | 25 | 84.2811
2017-07-29 | 15:20 | 1.7382 | 0 |  | 1.5
2017-07-29 | 15:25 | 1.7351 | 0 |  | 1.5
2017-07-29 | 15:30 | 1.7585 | 0 | 0 | 1.5 | 25 | 84.3281
2017-07-29 | 15:35 | 1.7585 | 0 |  | 1.5
2017-07-29 | 15:40 | 1.7499 | 0 |  | 1.5
2017-07-29 | 15:45 | 1.7694 | 0 | 0 | 1.5 | 25 | 84.1319
2017-07-29 | 15:50 | 1.7608 | 0 |  | 1.5
2017-07-29 | 15:55 | 1.7647 | 0 |  | 1.5
2017-07-29 | 16:00 | 1.7624 | 0 | 0 | 1.5 | 25 | 83.808
2017-07-29 | 16:05 | 1.7678 | 0 |  | 1.5
2017-07-29 | 16:10 | 1.7444 | 0 |  | 1.5
2017-07-29 | 16:15 | 1.7507 | 0 | 0 | 1.5 | 25 | 83.5733
2017-07-29 | 16:20 | 1.7569 | 0 |  | 1.5
2017-07-29 | 16:25 | 1.7686 | 0 |  | 1.5
2017-07-29 | 16:30 | 1.7546 | 0 | 0 | 1.5 | 25 | 83.1908
2017-07-29 | 16:35 | 1.76 | 0 |  | 1.5
2017-07-29 | 16:40 | 1.7507 | 0 |  | 1.5
2017-07-29 | 16:45 | 1.7585 | 0 | 0 | 1.5 | 25 | 82.8459
2017-07-29 | 16:50 | 1.7686 | 0 |  | 1.5
2017-07-29 | 16:55 | 1.76 | 0 |  | 1.5
2017-07-29 | 17:00 | 1.7678 | 0 | 0 | 1.5 | 25 | 82.3401
2017-07-29 | 17:05 | 1.7655 | 0 |  | 1.5
2017-07-29 | 17:10 | 1.7678 | 0 |  | 1.5
2017-07-29 | 17:15 | 1.7569 | 0 | 0 | 1.5 | 25 | 81.9181
2017-07-29 | 17:20 | 1.7553 | 0 |  | 1.5
2017-07-29 | 17:25 | 1.7577 | 0 |  | 1.5
2017-07-29 | 17:30 | 1.7631 | 0 | 0 | 1.5 | 25 | 81.4776
2017-07-29 | 17:35 | 1.7795 | 0 |  | 1.5
2017-07-29 | 17:40 | 1.7834 | 0 |  | 1.5
2017-07-29 | 17:45 | 1.7834 | 0 | 0 | 1.5 | 25 | 80.7168
2017-07-29 | 17:50 | 1.7936 | 0 |  | 1.5
2017-07-29 | 17:55 | 1.7764 | 0 |  | 1.5
2017-07-29 | 18:00 | 1.7553 | 0 | 0 | 1.5 | 25 | 80.2443
2017-07-29 | 18:05 | 1.7702 | 0 |  | 1.5
2017-07-29 | 18:10 | 1.7592 | 0 |  | 1.5
2017-07-29 | 18:15 | 1.7631 | 0 | 0 | 1.5 | 25 | 79.9873
2017-07-29 | 18:20 | 1.7748 | 0 |  | 1.5
2017-07-29 | 18:25 | 1.7553 | 0 |  | 1.5
2017-07-29 | 18:30 | 1.7756 | 0 | 0 | 1.5 | 25 | 79.6884
2017-07-29 | 18:35 | 1.7483 | 0 |  | 1.5
2017-07-29 | 18:40 | 1.7436 | 0 |  | 1.5
2017-07-29 | 18:45 | 1.7514 | 0 | 0 | 1.5 | 25 | 79.529
2017-07-29 | 18:50 | 1.7733 | 0 |  | 1.5
2017-07-29 | 18:55 | 1.7491 | 0 |  | 1.5
2017-07-29 | 19:00 | 1.7772 | 0 | 0 | 1.5 | 25 | 79.3215
2017-07-29 | 19:05 | 1.7639 | 0 |  | 1.5
2017-07-29 | 19:10 | 1.739 | 0 |  | 1.5
2017-07-29 | 19:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 79.1658
2017-07-29 | 19:20 | 1.7241 | 0 |  | 1.5
2017-07-29 | 19:25 | 1.7616 | 0 |  | 1.5
2017-07-29 | 19:30 | 1.7717 | 0 | 0 | 1.5 | 25 | 78.8983
2017-07-29 | 19:35 | 1.7803 | 0 |  | 1.5
2017-07-29 | 19:40 | 1.746 | 0 |  | 1.5
2017-07-29 | 19:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 78.7203
2017-07-29 | 19:50 | 1.7577 | 0 |  | 1.5
2017-07-29 | 19:55 | 1.7288 | 0 |  | 1.5
2017-07-29 | 20:00 | 1.7343 | 0 | 0 | 1.5 | 25 | 78.8644
2017-07-29 | 20:05 | 1.728 | 0 |  | 1.5
2017-07-29 | 20:10 | 1.7436 | 0 |  | 1.5
2017-07-29 | 20:15 | 1.7382 | 0 | 0 | 1.5 | 25 | 79.2037
2017-07-29 | 20:20 | 1.7429 | 0 |  | 1.5
2017-07-29 | 20:25 | 1.7522 | 0 |  | 1.5
2017-07-29 | 20:30 | 1.739 | 0 | 0 | 1.5 | 25 | 79.3624
2017-07-29 | 20:35 | 1.7616 | 0 |  | 1.5
2017-07-29 | 20:40 | 1.7468 | 0 |  | 1.5
2017-07-29 | 20:45 | 1.7647 | 0 | 0 | 1.5 | 25 | 79.3019
2017-07-29 | 20:50 | 1.7483 | 0 |  | 1.5
2017-07-29 | 20:55 | 1.7561 | 0 |  | 1.5
2017-07-29 | 21:00 | 1.767 | 0 | 0 | 1.5 | 25 | 79.1218
2017-07-29 | 21:05 | -0.10262 | 0 |  | 1.5
2017-07-29 | 21:10 | -0.1034 | 0 |  | 1.5
2017-07-29 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 21:20 | -0.10496 | 0 |  | 1.5
2017-07-29 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-29 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-29 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-29 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 21:50 | -0.10652 | 0 |  | 1.5
2017-07-29 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-29 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 22:05 | -0.10652 | 0 |  | 1.5
2017-07-29 | 22:10 | -0.1073 | 0 |  | 1.5
2017-07-29 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 22:20 | -0.10652 | 0 |  | 1.5
2017-07-29 | 22:25 | -0.1073 | 0 |  | 1.5
2017-07-29 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 22:35 | -0.1073 | 0 |  | 1.5
2017-07-29 | 22:40 | -0.10652 | 0 |  | 1.5
2017-07-29 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 22:50 | -0.1073 | 0 |  | 1.5
2017-07-29 | 22:55 | -0.10652 | 0 |  | 1.5
2017-07-29 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 23:05 | -0.10652 | 0 |  | 1.5
2017-07-29 | 23:10 | -0.10652 | 0 |  | 1.5
2017-07-29 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 23:20 | -0.10652 | 0 |  | 1.5
2017-07-29 | 23:25 | -0.10574 | 0 |  | 1.5
2017-07-29 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 23:35 | -0.10652 | 0 |  | 1.5
2017-07-29 | 23:40 | -0.10574 | 0 |  | 1.5
2017-07-29 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-29 | 23:50 | -0.10574 | 0 |  | 1.5
2017-07-29 | 23:55 | -0.10574 | 0 |  | 1.5
2017-07-30 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 0:05 | -0.10574 | 0 |  | 1.5
2017-07-30 | 0:10 | -0.10574 | 0 |  | 1.5
2017-07-30 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 0:20 | -0.10574 | 0 |  | 1.5
2017-07-30 | 0:25 | -0.10496 | 0 |  | 1.5
2017-07-30 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 0:35 | -0.10574 | 0 |  | 1.5
2017-07-30 | 0:40 | -0.10496 | 0 |  | 1.5
2017-07-30 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 0:50 | -0.10496 | 0 |  | 1.5
2017-07-30 | 0:55 | -0.10496 | 0 |  | 1.5
2017-07-30 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-30 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-30 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 1:20 | -0.10886 | 0 |  | 1.5
2017-07-30 | 1:25 | -0.10808 | 0 |  | 1.5
2017-07-30 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 1:35 | -0.10808 | 0 |  | 1.5
2017-07-30 | 1:40 | -0.10808 | 0 |  | 1.5
2017-07-30 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 1:50 | -0.10808 | 0 |  | 1.5
2017-07-30 | 1:55 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 2:05 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:10 | -0.1073 | 0 |  | 1.5
2017-07-30 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 2:20 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:25 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 2:35 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:40 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 2:50 | -0.10808 | 0 |  | 1.5
2017-07-30 | 2:55 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 3:05 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:10 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 3:20 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:25 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 3:35 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:40 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 3:50 | -0.10808 | 0 |  | 1.5
2017-07-30 | 3:55 | -0.10886 | 0 |  | 1.5
2017-07-30 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 4:05 | -0.10808 | 0 |  | 1.5
2017-07-30 | 4:10 | -0.10808 | 0 |  | 1.5
2017-07-30 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 4:20 | -0.10886 | 0 |  | 1.5
2017-07-30 | 4:25 | -0.10886 | 0 |  | 1.5
2017-07-30 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 4:35 | -0.10886 | 0 |  | 1.5
2017-07-30 | 4:40 | -0.10886 | 0 |  | 1.5
2017-07-30 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 4:50 | -0.10886 | 0 |  | 1.5
2017-07-30 | 4:55 | -0.10886 | 0 |  | 1.5
2017-07-30 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 5:05 | 2.3123 | 5.9837 |  | 10
2017-07-30 | 5:10 | 2.0494 | 10 |  | 10
2017-07-30 | 5:15 | 1.9901 | 9.999 | 1 | 10 | 100 | 90.8734
2017-07-30 | 5:20 | 1.9644 | 9.7586 |  | 10
2017-07-30 | 5:25 | 1.9667 | 9.0864 |  | 10
2017-07-30 | 5:30 | 1.9176 | 8.5956 | 1 | 10 | 86.6072 | 85.2147
2017-07-30 | 5:35 | 1.8739 | 8.4908 |  | 10
2017-07-30 | 5:40 | 1.8583 | 8.1321 |  | 10
2017-07-30 | 5:45 | 1.8287 | 8.0511 | 1 | 10 | 81.2297 | 82.1436
2017-07-30 | 5:50 | 1.8201 | 7.6517 |  | 10
2017-07-30 | 5:55 | 1.8294 | 7.3051 |  | 10
2017-07-30 | 6:00 | 1.8138 | 7.3428 | 1 | 10 | 74.3615 | 80.2785
2017-07-30 | 6:05 | 1.8271 | 7.2137 |  | 10
2017-07-30 | 6:10 | 1.7959 | 7.277 |  | 10
2017-07-30 | 6:15 | 1.7733 | 7.0022 | 1 | 10 | 71.159 | 79.019
2017-07-30 | 6:20 | 1.7889 | 6.9862 |  | 10
2017-07-30 | 6:25 | 1.8014 | 7.0806 |  | 10
2017-07-30 | 6:30 | 1.7842 | 6.9031 | 1 | 10 | 70.0312 | 78.2311
2017-07-30 | 6:35 | 1.7686 | 7.0744 |  | 10
2017-07-30 | 6:40 | 1.7647 | 6.6478 |  | 10
2017-07-30 | 6:45 | 1.7702 | 6.5458 | 1 | 10 | 66.5082 | 77.708
2017-07-30 | 6:50 | 1.7889 | 6.3766 |  | 10
2017-07-30 | 6:55 | 1.7553 | 6.0109 |  | 10
2017-07-30 | 7:00 | 1.7686 | 6.0836 | 1 | 10 | 62.0072 | 77.1406
2017-07-30 | 7:05 | 1.7647 | 6.0543 |  | 10
2017-07-30 | 7:10 | 1.7257 | 6.2945 |  | 10
2017-07-30 | 7:15 | 1.7436 | 6.3988 | 1 | 10 | 65.1359 | 76.9229
2017-07-30 | 7:20 | 1.7265 | 6.5353 |  | 10
2017-07-30 | 7:25 | 1.7452 | 6.6737 |  | 10
2017-07-30 | 7:30 | 1.7351 | 6.3897 | 1 | 10 | 65.0769 | 77.1138
2017-07-30 | 7:35 | 1.7514 | 6.6111 |  | 10
2017-07-30 | 7:40 | 1.7546 | 6.59 |  | 10
2017-07-30 | 7:45 | 1.7561 | 6.8909 | 1 | 10 | 69.72 | 77.2069
2017-07-30 | 7:50 | 1.7374 | 6.7254 |  | 10
2017-07-30 | 7:55 | 1.7382 | 6.6854 |  | 10
2017-07-30 | 8:00 | 1.76 | 6.7623 | 1 | 10 | 68.501 | 77.3754
2017-07-30 | 8:05 | 1.7187 | 6.8906 |  | 10
2017-07-30 | 8:10 | 1.7405 | 7.1078 |  | 10
2017-07-30 | 8:15 | 1.7483 | 7.0482 | 1 | 10 | 71.5415 | 77.7067
2017-07-30 | 8:20 | 1.7655 | 6.9808 |  | 10
2017-07-30 | 8:25 | 1.7538 | 7.0581 |  | 10
2017-07-30 | 8:30 | 1.7444 | 7.1135 | 1 | 10 | 71.9023 | 77.8436
2017-07-30 | 8:35 | 1.7382 | 7.3298 |  | 10
2017-07-30 | 8:40 | 1.7733 | 6.0945 |  | 10
2017-07-30 | 8:45 | 1.8177 | 3.3958 | 1 | 10 | 37.1959 | 77.3797
2017-07-30 | 8:50 | 1.7725 | 2.0797 |  | 10
2017-07-30 | 8:55 | 1.6477 | 0 |  | 1.5
2017-07-30 | 9:00 | 1.7046 | 0 | 0 | 1.5 | 25 | 78.6495
2017-07-30 | 9:05 | 1.7187 | 0 |  | 1.5
2017-07-30 | 9:10 | 1.7163 | 0 |  | 1.5
2017-07-30 | 9:15 | 1.7514 | 0 | 0 | 1.5 | 25 | 79.604
2017-07-30 | 9:20 | 1.7397 | 0 |  | 1.5
2017-07-30 | 9:25 | 1.739 | 0 |  | 1.5
2017-07-30 | 9:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 79.7444
2017-07-30 | 9:35 | 1.7351 | 0 |  | 1.5
2017-07-30 | 9:40 | 1.7218 | 0 |  | 1.5
2017-07-30 | 9:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 79.8312
2017-07-30 | 9:50 | 1.7296 | 0 |  | 1.5
2017-07-30 | 9:55 | 1.7553 | 0 |  | 1.5
2017-07-30 | 10:00 | 1.7093 | 0 | 0 | 1.5 | 25 | 79.8538
2017-07-30 | 10:05 | 1.7881 | 0 |  | 1.5
2017-07-30 | 10:10 | 1.7483 | 0 |  | 1.5
2017-07-30 | 10:15 | 1.7382 | 0 | 0 | 1.5 | 25 | 79.9413
2017-07-30 | 10:20 | 1.7577 | 0 |  | 1.5
2017-07-30 | 10:25 | 1.7475 | 0 |  | 1.5
2017-07-30 | 10:30 | 1.7733 | 0 | 0 | 1.5 | 25 | 79.984
2017-07-30 | 10:35 | 1.7475 | 0 |  | 1.5
2017-07-30 | 10:40 | 1.7678 | 0 |  | 1.5
2017-07-30 | 10:45 | 1.7265 | 0 | 0 | 1.5 | 25 | 80.3775
2017-07-30 | 10:50 | 1.7468 | 0 |  | 1.5
2017-07-30 | 10:55 | 1.739 | 0 |  | 1.5
2017-07-30 | 11:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 80.5204
2017-07-30 | 11:05 | 1.7343 | 0 |  | 1.5
2017-07-30 | 11:10 | 1.7358 | 0 |  | 1.5
2017-07-30 | 11:15 | 1.7452 | 0 | 0 | 1.5 | 25 | 80.8464
2017-07-30 | 11:20 | 1.7624 | 0 |  | 1.5
2017-07-30 | 11:25 | 1.7702 | 0 |  | 1.5
2017-07-30 | 11:30 | 1.7468 | 0 | 0 | 1.5 | 25 | 81.0075
2017-07-30 | 11:35 | 1.7468 | 0 |  | 1.5
2017-07-30 | 11:40 | 1.728 | 0 |  | 1.5
2017-07-30 | 11:45 | 1.7288 | 0 | 0 | 1.5 | 25 | 81.3716
2017-07-30 | 11:50 | 1.7156 | 0 |  | 1.5
2017-07-30 | 11:55 | 1.7296 | 0 |  | 1.5
2017-07-30 | 12:00 | 1.721 | 0 | 0 | 1.5 | 25 | 82.0288
2017-07-30 | 12:05 | 1.7288 | 0 |  | 1.5
2017-07-30 | 12:10 | 1.7514 | 0 |  | 1.5
2017-07-30 | 12:15 | 1.7444 | 0 | 0 | 1.5 | 25 | 82.4083
2017-07-30 | 12:20 | 1.7171 | 0 |  | 1.5
2017-07-30 | 12:25 | 1.7265 | 0 |  | 1.5
2017-07-30 | 12:30 | 1.7187 | 0 | 0 | 1.5 | 25 | 82.8115
2017-07-30 | 12:35 | 1.7374 | 0 |  | 1.5
2017-07-30 | 12:40 | 1.7374 | 0 |  | 1.5
2017-07-30 | 12:45 | 1.7499 | 0 | 0 | 1.5 | 25 | 83.3716
2017-07-30 | 12:50 | 1.728 | 0 |  | 1.5
2017-07-30 | 12:55 | 1.7592 | 0 |  | 1.5
2017-07-30 | 13:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 83.7142
2017-07-30 | 13:05 | 1.8068 | 0 |  | 1.5
2017-07-30 | 13:10 | 1.7678 | 0 |  | 1.5
2017-07-30 | 13:15 | 1.753 | 0 | 0 | 1.5 | 25 | 83.4377
2017-07-30 | 13:20 | 1.7475 | 0 |  | 1.5
2017-07-30 | 13:25 | 1.7522 | 0 |  | 1.5
2017-07-30 | 13:30 | 1.7569 | 0 | 0 | 1.5 | 25 | 83.603
2017-07-30 | 13:35 | 1.7319 | 0 |  | 1.5
2017-07-30 | 13:40 | 1.7444 | 0 |  | 1.5
2017-07-30 | 13:45 | 1.7452 | 0 | 0 | 1.5 | 25 | 84.0484
2017-07-30 | 13:50 | 1.7062 | 0 |  | 1.5
2017-07-30 | 13:55 | 1.7452 | 0 |  | 1.5
2017-07-30 | 14:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 84.291
2017-07-30 | 14:05 | 1.7226 | 0 |  | 1.5
2017-07-30 | 14:10 | 1.753 | 0 |  | 1.5
2017-07-30 | 14:15 | 1.7374 | 0 | 0 | 1.5 | 25 | 84.4373
2017-07-30 | 14:20 | 1.7351 | 0 |  | 1.5
2017-07-30 | 14:25 | 1.7631 | 0 |  | 1.5
2017-07-30 | 14:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 84.6297
2017-07-30 | 14:35 | 1.753 | 0 |  | 1.5
2017-07-30 | 14:40 | 1.746 | 0 |  | 1.5
2017-07-30 | 14:45 | 1.707 | 0 | 0 | 1.5 | 25 | 84.8364
2017-07-30 | 14:50 | 1.7358 | 0 |  | 1.5
2017-07-30 | 14:55 | 1.7413 | 0 |  | 1.5
2017-07-30 | 15:00 | 1.7421 | 0 | 0 | 1.5 | 25 | 84.9122
2017-07-30 | 15:05 | 1.7507 | 0 |  | 1.5
2017-07-30 | 15:10 | 1.76 | 0 |  | 1.5
2017-07-30 | 15:15 | 1.7483 | 0 | 0 | 1.5 | 25 | 85.1058
2017-07-30 | 15:20 | 1.753 | 0 |  | 1.5
2017-07-30 | 15:25 | 1.7351 | 0 |  | 1.5
2017-07-30 | 15:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 85.0209
2017-07-30 | 15:35 | 1.7475 | 0 |  | 1.5
2017-07-30 | 15:40 | 1.7514 | 0 |  | 1.5
2017-07-30 | 15:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 84.9483
2017-07-30 | 15:50 | 1.7436 | 0 |  | 1.5
2017-07-30 | 15:55 | 1.7491 | 0 |  | 1.5
2017-07-30 | 16:00 | 1.7553 | 0 | 0 | 1.5 | 25 | 84.8299
2017-07-30 | 16:05 | 1.7616 | 0 |  | 1.5
2017-07-30 | 16:10 | 1.7413 | 0 |  | 1.5
2017-07-30 | 16:15 | 1.7257 | 0 | 0 | 1.5 | 25 | 84.666
2017-07-30 | 16:20 | 1.7585 | 0 |  | 1.5
2017-07-30 | 16:25 | 1.7491 | 0 |  | 1.5
2017-07-30 | 16:30 | 1.7351 | 0 | 0 | 1.5 | 25 | 84.3629
2017-07-30 | 16:35 | 1.7616 | 0 |  | 1.5
2017-07-30 | 16:40 | 1.7772 | 0 |  | 1.5
2017-07-30 | 16:45 | 1.7756 | 0 | 0 | 1.5 | 25 | 83.9972
2017-07-30 | 16:50 | 1.7429 | 0 |  | 1.5
2017-07-30 | 16:55 | 1.7772 | 0 |  | 1.5
2017-07-30 | 17:00 | 1.7756 | 0 | 0 | 1.5 | 25 | 83.6618
2017-07-30 | 17:05 | 1.7959 | 0 |  | 1.5
2017-07-30 | 17:10 | 1.7741 | 0 |  | 1.5
2017-07-30 | 17:15 | 1.7764 | 0 | 0 | 1.5 | 25 | 83.1875
2017-07-30 | 17:20 | 1.7709 | 0 |  | 1.5
2017-07-30 | 17:25 | 1.7452 | 0 |  | 1.5
2017-07-30 | 17:30 | 1.7585 | 0 | 0 | 1.5 | 25 | 82.6663
2017-07-30 | 17:35 | 1.7904 | 0 |  | 1.5
2017-07-30 | 17:40 | 1.778 | 0 |  | 1.5
2017-07-30 | 17:45 | 1.7764 | 0 | 0 | 1.5 | 25 | 82.1322
2017-07-30 | 17:50 | 1.7741 | 0 |  | 1.5
2017-07-30 | 17:55 | 1.7624 | 0 |  | 1.5
2017-07-30 | 18:00 | 1.7702 | 0 | 0 | 1.5 | 25 | 81.586
2017-07-30 | 18:05 | 1.7748 | 0 |  | 1.5
2017-07-30 | 18:10 | 1.785 | 0 |  | 1.5
2017-07-30 | 18:15 | 1.7546 | 0 | 0 | 1.5 | 25 | 81.094
2017-07-30 | 18:20 | 1.7366 | 0 |  | 1.5
2017-07-30 | 18:25 | 1.7678 | 0 |  | 1.5
2017-07-30 | 18:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 80.8255
2017-07-30 | 18:35 | 1.7592 | 0 |  | 1.5
2017-07-30 | 18:40 | 1.7475 | 0 |  | 1.5
2017-07-30 | 18:45 | 1.7616 | 0 | 0 | 1.5 | 25 | 80.6464
2017-07-30 | 18:50 | 1.7569 | 0 |  | 1.5
2017-07-30 | 18:55 | 1.7585 | 0 |  | 1.5
2017-07-30 | 19:00 | 1.739 | 0 | 0 | 1.5 | 25 | 80.4581
2017-07-30 | 19:05 | 1.7655 | 0 |  | 1.5
2017-07-30 | 19:10 | 1.7522 | 0 |  | 1.5
2017-07-30 | 19:15 | 1.7585 | 0 | 0 | 1.5 | 25 | 80.3079
2017-07-30 | 19:20 | 1.7241 | 0 |  | 1.5
2017-07-30 | 19:25 | 1.7553 | 0 |  | 1.5
2017-07-30 | 19:30 | 1.767 | 0 | 0 | 1.5 | 25 | 80.2724
2017-07-30 | 19:35 | 1.767 | 0 |  | 1.5
2017-07-30 | 19:40 | 1.7655 | 0 |  | 1.5
2017-07-30 | 19:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 80.1708
2017-07-30 | 19:50 | 1.7881 | 0 |  | 1.5
2017-07-30 | 19:55 | 1.7514 | 0 |  | 1.5
2017-07-30 | 20:00 | 1.7522 | 0 | 0 | 1.5 | 25 | 80.2058
2017-07-30 | 20:05 | 1.7756 | 0 |  | 1.5
2017-07-30 | 20:10 | 1.7725 | 0 |  | 1.5
2017-07-30 | 20:15 | 1.7405 | 0 | 0 | 1.5 | 25 | 79.7697
2017-07-30 | 20:20 | 1.7624 | 0 |  | 1.5
2017-07-30 | 20:25 | 1.7655 | 0 |  | 1.5
2017-07-30 | 20:30 | 1.778 | 0 | 0 | 1.5 | 25 | 79.4084
2017-07-30 | 20:35 | 1.7491 | 0 |  | 1.5
2017-07-30 | 20:40 | 1.799 | 0 |  | 1.5
2017-07-30 | 20:45 | 1.7795 | 0 | 0 | 1.5 | 25 | 79.0051
2017-07-30 | 20:50 | 1.7358 | 0 |  | 1.5
2017-07-30 | 20:55 | 1.7702 | 0 |  | 1.5
2017-07-30 | 21:00 | 1.7764 | 0 | 0 | 1.5 | 25 | 78.6366
2017-07-30 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-30 | 21:10 | -0.1034 | 0 |  | 1.5
2017-07-30 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 21:20 | -0.10496 | 0 |  | 1.5
2017-07-30 | 21:25 | -0.10496 | 0 |  | 1.5
2017-07-30 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 21:35 | -0.10574 | 0 |  | 1.5
2017-07-30 | 21:40 | -0.10574 | 0 |  | 1.5
2017-07-30 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 21:50 | -0.10496 | 0 |  | 1.5
2017-07-30 | 21:55 | -0.10574 | 0 |  | 1.5
2017-07-30 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 22:05 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:10 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 22:20 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:25 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 22:35 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:40 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 22:50 | -0.10496 | 0 |  | 1.5
2017-07-30 | 22:55 | -0.10496 | 0 |  | 1.5
2017-07-30 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 23:05 | -0.10418 | 0 |  | 1.5
2017-07-30 | 23:10 | -0.10496 | 0 |  | 1.5
2017-07-30 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 23:20 | -0.10496 | 0 |  | 1.5
2017-07-30 | 23:25 | -0.10496 | 0 |  | 1.5
2017-07-30 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-30 | 23:40 | -0.10418 | 0 |  | 1.5
2017-07-30 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-30 | 23:50 | -0.10418 | 0 |  | 1.5
2017-07-30 | 23:55 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 0:05 | -0.10496 | 0 |  | 1.5
2017-07-31 | 0:10 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 0:20 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:25 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 0:35 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:40 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 0:50 | -0.10418 | 0 |  | 1.5
2017-07-31 | 0:55 | -0.10418 | 0 |  | 1.5
2017-07-31 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 1:05 | -0.10496 | 0 |  | 1.5
2017-07-31 | 1:10 | -0.10496 | 0 |  | 1.5
2017-07-31 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 1:20 | -0.10808 | 0 |  | 1.5
2017-07-31 | 1:25 | -0.10808 | 0 |  | 1.5
2017-07-31 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 1:35 | -0.10808 | 0 |  | 1.5
2017-07-31 | 1:40 | -0.1073 | 0 |  | 1.5
2017-07-31 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 1:50 | -0.1073 | 0 |  | 1.5
2017-07-31 | 1:55 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 2:05 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:10 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 2:20 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:25 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 2:35 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:40 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 2:50 | -0.1073 | 0 |  | 1.5
2017-07-31 | 2:55 | -0.1073 | 0 |  | 1.5
2017-07-31 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 3:05 | -0.1073 | 0 |  | 1.5
2017-07-31 | 3:10 | -0.1073 | 0 |  | 1.5
2017-07-31 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 3:20 | -0.1073 | 0 |  | 1.5
2017-07-31 | 3:25 | -0.1073 | 0 |  | 1.5
2017-07-31 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 3:35 | -0.1073 | 0 |  | 1.5
2017-07-31 | 3:40 | -0.10808 | 0 |  | 1.5
2017-07-31 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 3:50 | -0.10808 | 0 |  | 1.5
2017-07-31 | 3:55 | -0.1073 | 0 |  | 1.5
2017-07-31 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 4:05 | -0.10808 | 0 |  | 1.5
2017-07-31 | 4:10 | -0.10808 | 0 |  | 1.5
2017-07-31 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 4:20 | -0.10808 | 0 |  | 1.5
2017-07-31 | 4:25 | -0.1112 | 0 |  | 1.5
2017-07-31 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 4:35 | -0.10808 | 0 |  | 1.5
2017-07-31 | 4:40 | -0.10808 | 0 |  | 1.5
2017-07-31 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 4:50 | -0.10808 | 0 |  | 1.5
2017-07-31 | 4:55 | -0.10808 | 0 |  | 1.5
2017-07-31 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 5:05 | 2.3263 | 5.8888 |  | 10
2017-07-31 | 5:10 | 2.0276 | 10 |  | 10
2017-07-31 | 5:15 | 1.9706 | 10 | 1 | 10 | 100 | 91.1558
2017-07-31 | 5:20 | 1.9675 | 9.7738 |  | 10
2017-07-31 | 5:25 | 1.9714 | 9.3942 |  | 10
2017-07-31 | 5:30 | 1.8911 | 9.1851 | 1 | 10 | 92.3598 | 85.4783
2017-07-31 | 5:35 | 1.8981 | 8.6142 |  | 10
2017-07-31 | 5:40 | 1.8856 | 8.1034 |  | 10
2017-07-31 | 5:45 | 1.8263 | 8.0567 | 1 | 10 | 81.3036 | 82.148
2017-07-31 | 5:50 | 1.8513 | 7.5365 |  | 10
2017-07-31 | 5:55 | 1.8536 | 7.2108 |  | 10
2017-07-31 | 6:00 | 1.8287 | 6.8114 | 1 | 10 | 69.3888 | 79.7687
2017-07-31 | 6:05 | 1.7975 | 6.8081 |  | 10
2017-07-31 | 6:10 | 1.7928 | 7.0415 |  | 10
2017-07-31 | 6:15 | 1.7959 | 6.6309 | 1 | 10 | 67.6706 | 78.4512
2017-07-31 | 6:20 | 1.7858 | 6.5126 |  | 10
2017-07-31 | 6:25 | 1.7678 | 6.2175 |  | 10
2017-07-31 | 6:30 | 1.8162 | 6.2116 | 1 | 10 | 63.5158 | 77.5496
2017-07-31 | 6:35 | 1.7772 | 6.0175 |  | 10
2017-07-31 | 6:40 | 1.7733 | 5.7271 |  | 10
2017-07-31 | 6:45 | 1.7904 | 6.2747 | 1 | 10 | 63.8885 | 76.8391
2017-07-31 | 6:50 | 1.7655 | 5.9947 |  | 10
2017-07-31 | 6:55 | 1.778 | 5.8915 |  | 10
2017-07-31 | 7:00 | 1.76 | 5.9838 | 1 | 10 | 61.6183 | 76.6811
2017-07-31 | 7:05 | 1.785 | 5.777 |  | 10
2017-07-31 | 7:10 | 1.767 | 5.9734 |  | 10
2017-07-31 | 7:15 | 1.7429 | 5.8631 | 1 | 10 | 60.3356 | 76.6253
2017-07-31 | 7:20 | 1.7694 | 5.5437 |  | 10
2017-07-31 | 7:25 | 1.7733 | 4.9862 |  | 10
2017-07-31 | 7:30 | 1.7795 | 4.7433 | 1 | 10 | 48.8632 | 76.2231
2017-07-31 | 7:35 | 1.7561 | 4.9846 |  | 10
2017-07-31 | 7:40 | 1.7475 | 4.5757 |  | 10
2017-07-31 | 7:45 | 1.7124 | 5.6068 | 1 | 10 | 56.4089 | 76.383
2017-07-31 | 7:50 | 1.7491 | 5.138 |  | 10
2017-07-31 | 7:55 | 1.7171 | 5.5868 |  | 10
2017-07-31 | 8:00 | 1.7312 | 5.1955 | 1 | 10 | 53.8251 | 76.9894
2017-07-31 | 8:05 | 1.7304 | 5.2019 |  | 10
2017-07-31 | 8:10 | 1.7405 | 5.9202 |  | 10
2017-07-31 | 8:15 | 1.714 | 6.2345 | 1 | 10 | 63.2454 | 77.6568
2017-07-31 | 8:20 | 1.6968 | 7.1291 |  | 10
2017-07-31 | 8:25 | 1.6048 | 7.7913 |  | 10
2017-07-31 | 8:30 | 1.6805 | 7.4212 | 1 | 10 | 75.4539 | 80.0963
2017-07-31 | 8:35 | 1.6968 | 7.5231 |  | 10
2017-07-31 | 8:40 | 1.7 | 7.7819 |  | 10
2017-07-31 | 8:45 | 1.7195 | 7.9124 | 1 | 10 | 80.4229 | 81.4851
2017-07-31 | 8:50 | 1.7647 | 6.6647 |  | 10
2017-07-31 | 8:55 | 1.8084 | 4.6507 |  | 10
2017-07-31 | 9:00 |  |  | 0
2017-07-31 | 9:00 | 1.7343 | 2.9989 | 0 | 1.5 | 33.5989 | 80.9362
2017-07-31 | 9:05 | 1.6204 | 0 |  | 1.5
2017-07-31 | 9:10 | 1.6485 | 0 |  | 1.5
2017-07-31 | 9:15 | 1.682 | 0 | 0 | 1.5 | 25 | 84.1873
2017-07-31 | 9:20 | 1.7171 | 0 |  | 1.5
2017-07-31 | 9:25 | 1.7163 | 0 |  | 1.5
2017-07-31 | 9:30 | 1.7249 | 0 | 0 | 1.5 | 25 | 85.0411
2017-07-31 | 9:35 | 1.7491 | 0 |  | 1.5
2017-07-31 | 9:40 | 1.7257 | 0 |  | 1.5
2017-07-31 | 9:45 | 1.76 | 0 | 0 | 1.5 | 25 | 85.3095
2017-07-31 | 9:50 | 1.7218 | 0 |  | 1.5
2017-07-31 | 9:55 | 1.7327 | 0 |  | 1.5
2017-07-31 | 10:00 | 1.7093 | 0 | 0 | 1.5 | 25 | 85.7282
2017-07-31 | 10:05 | 1.7585 | 0 |  | 1.5
2017-07-31 | 10:10 | 1.7397 | 0 |  | 1.5
2017-07-31 | 10:15 | 1.7249 | 0 | 0 | 1.5 | 25 | 86.1228
2017-07-31 | 10:20 | 1.7179 | 0 |  | 1.5
2017-07-31 | 10:25 | 1.7343 | 0 |  | 1.5
2017-07-31 | 10:30 | 1.7241 | 0 | 0 | 1.5 | 25 | 86.854
2017-07-31 | 10:35 | 1.7007 | 0 |  | 1.5
2017-07-31 | 10:40 | 1.7413 | 0 |  | 1.5
2017-07-31 | 10:45 | 1.7093 | 0 | 0 | 1.5 | 25 | 87.5345
2017-07-31 | 10:50 | 1.7569 | 0 |  | 1.5
2017-07-31 | 10:55 | 1.7553 | 0 |  | 1.5
2017-07-31 | 11:00 | 1.728 | 0 | 0 | 1.5 | 25 | 87.6521
2017-07-31 | 11:05 | 1.7834 | 0 |  | 1.5
2017-07-31 | 11:10 | 1.7366 | 0 |  | 1.5
2017-07-31 | 11:15 | 1.7717 | 0 | 0 | 1.5 | 25 | 87.6467
2017-07-31 | 11:20 | 1.753 | 0 |  | 1.5
2017-07-31 | 11:25 | 1.7397 | 0 |  | 1.5
2017-07-31 | 11:30 | 1.7772 | 0 | 0 | 1.5 | 25 | 87.4757
2017-07-31 | 11:35 | 1.7249 | 0 |  | 1.5
2017-07-31 | 11:40 | 1.746 | 0 |  | 1.5
2017-07-31 | 11:45 | 1.7663 | 0 | 0 | 1.5 | 25 | 87.7042
2017-07-31 | 11:50 | 1.7288 | 0 |  | 1.5
2017-07-31 | 11:55 | 1.739 | 0 |  | 1.5
2017-07-31 | 12:00 | 1.7304 | 0 | 0 | 1.5 | 25 | 88.4914
2017-07-31 | 12:05 | 1.728 | 0 |  | 1.5
2017-07-31 | 12:10 | 1.7475 | 0 |  | 1.5
2017-07-31 | 12:15 | 1.7163 | 0 | 0 | 1.5 | 25 | 88.5343
2017-07-31 | 12:20 | 1.7421 | 0 |  | 1.5
2017-07-31 | 12:25 | 1.7631 | 0 |  | 1.5
2017-07-31 | 12:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 88.5778
2017-07-31 | 12:35 | 1.7265 | 0 |  | 1.5
2017-07-31 | 12:40 | 1.7655 | 0 |  | 1.5
2017-07-31 | 12:45 | 1.7522 | 0 | 0 | 1.5 | 25 | 88.2294
2017-07-31 | 12:50 | 1.746 | 0 |  | 1.5
2017-07-31 | 12:55 | 1.7257 | 0 |  | 1.5
2017-07-31 | 13:00 | 1.7413 | 0 | 0 | 1.5 | 25 | 88.3282
2017-07-31 | 13:05 | 1.7163 | 0 |  | 1.5
2017-07-31 | 13:10 | 1.7265 | 0 |  | 1.5
2017-07-31 | 13:15 | 1.7241 | 0 | 0 | 1.5 | 25 | 89.2026
2017-07-31 | 13:20 | 1.7421 | 0 |  | 1.5
2017-07-31 | 13:25 | 1.6953 | 0 |  | 1.5
2017-07-31 | 13:30 | 1.7288 | 0 | 0 | 1.5 | 25 | 89.8177
2017-07-31 | 13:35 | 1.7553 | 0 |  | 1.5
2017-07-31 | 13:40 | 1.7366 | 0 |  | 1.5
2017-07-31 | 13:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 90.143
2017-07-31 | 13:50 | 1.7452 | 0 |  | 1.5
2017-07-31 | 13:55 | 1.7702 | 0 |  | 1.5
2017-07-31 | 14:00 | 1.7475 | 0 | 0 | 1.5 | 25 | 90.224
2017-07-31 | 14:05 | 1.7561 | 0 |  | 1.5
2017-07-31 | 14:10 | 1.7273 | 0 |  | 1.5
2017-07-31 | 14:15 | 1.7265 | 0 | 0 | 1.5 | 25 | 90.58
2017-07-31 | 14:20 | 1.7163 | 0 |  | 1.5
2017-07-31 | 14:25 | 1.7397 | 0 |  | 1.5
2017-07-31 | 14:30 | 1.7304 | 0 | 0 | 1.5 | 25 | 91.0005
2017-07-31 | 14:35 | 1.7405 | 0 |  | 1.5
2017-07-31 | 14:40 | 1.7226 | 0 |  | 1.5
2017-07-31 | 14:45 | 1.7444 | 0 | 0 | 1.5 | 25 | 91.0632
2017-07-31 | 14:50 | 1.7273 | 0 |  | 1.5
2017-07-31 | 14:55 | 1.7351 | 0 |  | 1.5
2017-07-31 | 15:00 | 1.7156 | 0 | 0 | 1.5 | 25 | 91.4275
2017-07-31 | 15:05 | 1.7397 | 0 |  | 1.5
2017-07-31 | 15:10 | 1.7483 | 0 |  | 1.5
2017-07-31 | 15:15 | 1.7156 | 0 | 0 | 1.5 | 25 | 91.9228
2017-07-31 | 15:20 | 1.7343 | 0 |  | 1.5
2017-07-31 | 15:25 | 1.7382 | 0 |  | 1.5
2017-07-31 | 15:30 | 1.7202 | 0 | 0 | 1.5 | 25 | 92.2987
2017-07-31 | 15:35 | 1.7538 | 0 |  | 1.5
2017-07-31 | 15:40 | 1.767 | 0 |  | 1.5
2017-07-31 | 15:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 92.4759
2017-07-31 | 15:50 | 1.7288 | 0 |  | 1.5
2017-07-31 | 15:55 | 1.746 | 0 |  | 1.5
2017-07-31 | 16:00 | 1.7405 | 0 | 0 | 1.5 | 25 | 92.6899
2017-07-31 | 16:05 | 1.7288 | 0 |  | 1.5
2017-07-31 | 16:10 | 1.7647 | 0 |  | 1.5
2017-07-31 | 16:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 92.7199
2017-07-31 | 16:20 | 1.7764 | 0 |  | 1.5
2017-07-31 | 16:25 | 1.7912 | 0 |  | 1.5
2017-07-31 | 16:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 92.4511
2017-07-31 | 16:35 | 1.7639 | 0 |  | 1.5
2017-07-31 | 16:40 | 1.7436 | 0 |  | 1.5
2017-07-31 | 16:45 | 1.7694 | 0 | 0 | 1.5 | 25 | 92.346
2017-07-31 | 16:50 | 1.8084 | 0 |  | 1.5
2017-07-31 | 16:55 | 1.8037 | 0 |  | 1.5
2017-07-31 | 17:00 | 1.7842 | 0 | 0 | 1.5 | 25 | 91.5374
2017-07-31 | 17:05 | 1.8037 | 0 |  | 1.5
2017-07-31 | 17:10 | 1.7787 | 0 |  | 1.5
2017-07-31 | 17:15 | 1.8029 | 0 | 0 | 1.5 | 25 | 90.4388
2017-07-31 | 17:20 | 1.8209 | 0 |  | 1.5
2017-07-31 | 17:25 | 1.806 | 0 |  | 1.5
2017-07-31 | 17:30 | 1.7897 | 0 | 0 | 1.5 | 25 | 88.9877
2017-07-31 | 17:35 | 1.7826 | 0 |  | 1.5
2017-07-31 | 17:40 | 1.7592 | 0 |  | 1.5
2017-07-31 | 17:45 | 1.7748 | 0 | 0 | 1.5 | 25 | 88.4284
2017-07-31 | 17:50 | 1.7826 | 0 |  | 1.5
2017-07-31 | 17:55 | 1.7772 | 0 |  | 1.5
2017-07-31 | 18:00 | 1.7624 | 0 | 0 | 1.5 | 25 | 87.6144
2017-07-31 | 18:05 | 1.7772 | 0 |  | 1.5
2017-07-31 | 18:10 | 1.7795 | 0 |  | 1.5
2017-07-31 | 18:15 | 1.7975 | 0 | 0 | 1.5 | 25 | 86.7135
2017-07-31 | 18:20 | 1.8014 | 0 |  | 1.5
2017-07-31 | 18:25 | 1.767 | 0 |  | 1.5
2017-07-31 | 18:30 | 1.767 | 0 | 0 | 1.5 | 25 | 86.0623
2017-07-31 | 18:35 | 1.7686 | 0 |  | 1.5
2017-07-31 | 18:40 | 1.7811 | 0 |  | 1.5
2017-07-31 | 18:45 | 1.7655 | 0 | 0 | 1.5 | 25 | 85.4504
2017-07-31 | 18:50 | 1.7772 | 0 |  | 1.5
2017-07-31 | 18:55 | 1.7772 | 0 |  | 1.5
2017-07-31 | 19:00 | 1.8201 | 0 | 0 | 1.5 | 25 | 84.7316
2017-07-31 | 19:05 | 1.7787 | 0 |  | 1.5
2017-07-31 | 19:10 | 1.7834 | 0 |  | 1.5
2017-07-31 | 19:15 | 1.778 | 0 | 0 | 1.5 | 25 | 84.1323
2017-07-31 | 19:20 | 1.7725 | 0 |  | 1.5
2017-07-31 | 19:25 | 1.76 | 0 |  | 1.5
2017-07-31 | 19:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 83.703
2017-07-31 | 19:35 | 1.76 | 0 |  | 1.5
2017-07-31 | 19:40 | 1.7655 | 0 |  | 1.5
2017-07-31 | 19:45 | 1.7694 | 0.021182 | 0 | 1.5 | 25 | 83.2401
2017-07-31 | 19:50 | 1.7748 | 0 |  | 1.5
2017-07-31 | 19:55 | 1.7514 | 0 |  | 1.5
2017-07-31 | 20:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 82.6641
2017-07-31 | 20:05 | 1.7756 | 0 |  | 1.5
2017-07-31 | 20:10 | 1.7741 | 0 |  | 1.5
2017-07-31 | 20:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 82.1929
2017-07-31 | 20:20 | 1.7998 | 0 |  | 1.5
2017-07-31 | 20:25 | 1.7873 | 0 |  | 1.5
2017-07-31 | 20:30 | 1.7803 | 0 | 0 | 1.5 | 25 | 81.5973
2017-07-31 | 20:35 | 1.7717 | 0 |  | 1.5
2017-07-31 | 20:40 | 1.7647 | 0 |  | 1.5
2017-07-31 | 20:45 | 1.7795 | 0 | 0 | 1.5 | 25 | 80.9932
2017-07-31 | 20:50 | 1.7639 | 0 |  | 1.5
2017-07-31 | 20:55 | 1.7397 | 0 |  | 1.5
2017-07-31 | 21:00 | 1.7483 | 0 | 0 | 1.5 | 25 | 80.6808
2017-07-31 | 21:05 | -0.10418 | 0 |  | 1.5
2017-07-31 | 21:10 | -0.10418 | 0 |  | 1.5
2017-07-31 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 21:20 | -0.10574 | 0 |  | 1.5
2017-07-31 | 21:25 | -0.10574 | 0 |  | 1.5
2017-07-31 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 21:35 | -0.10652 | 0 |  | 1.5
2017-07-31 | 21:40 | -0.10652 | 0 |  | 1.5
2017-07-31 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 21:50 | -0.10574 | 0 |  | 1.5
2017-07-31 | 21:55 | -0.10652 | 0 |  | 1.5
2017-07-31 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 22:05 | -0.10574 | 0 |  | 1.5
2017-07-31 | 22:10 | -0.10496 | 0 |  | 1.5
2017-07-31 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 22:20 | -0.10496 | 0 |  | 1.5
2017-07-31 | 22:25 | -0.10574 | 0 |  | 1.5
2017-07-31 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 22:35 | -0.10496 | 0 |  | 1.5
2017-07-31 | 22:40 | -0.10418 | 0 |  | 1.5
2017-07-31 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 22:50 | -0.10496 | 0 |  | 1.5
2017-07-31 | 22:55 | -0.10496 | 0 |  | 1.5
2017-07-31 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 23:05 | -0.10496 | 0 |  | 1.5
2017-07-31 | 23:10 | -0.10496 | 0 |  | 1.5
2017-07-31 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 23:20 | -0.10496 | 0 |  | 1.5
2017-07-31 | 23:25 | -0.10496 | 0 |  | 1.5
2017-07-31 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 23:35 | -0.10496 | 0 |  | 1.5
2017-07-31 | 23:40 | -0.10418 | 0 |  | 1.5
2017-07-31 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-07-31 | 23:50 | -0.10418 | 0 |  | 1.5
2017-07-31 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-01 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-01 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-01 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-01 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-01 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 0:35 | -0.1034 | 0 |  | 1.5
2017-08-01 | 0:40 | -0.1034 | 0 |  | 1.5
2017-08-01 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 0:50 | -0.1034 | 0 |  | 1.5
2017-08-01 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-01 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 1:05 | -0.1034 | 0 |  | 1.5
2017-08-01 | 1:10 | -0.1034 | 0 |  | 1.5
2017-08-01 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 1:20 | -0.10574 | 0 |  | 1.5
2017-08-01 | 1:25 | -0.10652 | 0 |  | 1.5
2017-08-01 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 1:35 | -0.10652 | 0 |  | 1.5
2017-08-01 | 1:40 | -0.1073 | 0 |  | 1.5
2017-08-01 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 1:50 | -0.1073 | 0 |  | 1.5
2017-08-01 | 1:55 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:10 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:40 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-01 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-01 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-01 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-01 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-01 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-01 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-01 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-01 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-01 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-01 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-01 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-01 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 5:00 |  |  | 1
2017-08-01 | 5:05 | 2.168 | 6.1586 |  | 10
2017-08-01 | 5:10 | 2.0143 | 10 |  | 10
2017-08-01 | 5:15 | 1.9847 | 10 | 1 | 10 | 100 | 92.0382
2017-08-01 | 5:20 | 1.9527 | 10 |  | 10
2017-08-01 | 5:25 | 1.934 | 9.9491 |  | 10
2017-08-01 | 5:30 | 1.8536 | 9.5913 | 1 | 10 | 96.2925 | 86.8006
2017-08-01 | 5:35 | 1.8341 | 9.3224 |  | 10
2017-08-01 | 5:40 | 1.7998 | 9.0638 |  | 10
2017-08-01 | 5:45 | 1.8528 | 8.6043 | 1 | 10 | 87.0376 | 84.4518
2017-08-01 | 5:50 | 1.8216 | 8.4031 |  | 10
2017-08-01 | 5:55 | 1.8404 | 8.1752 |  | 10
2017-08-01 | 6:00 | 1.7936 | 7.8694 | 1 | 10 | 79.5614 | 82.5529
2017-08-01 | 6:05 | 1.7936 | 7.9195 |  | 10
2017-08-01 | 6:10 | 1.7741 | 8.0297 |  | 10
2017-08-01 | 6:15 | 1.7663 | 7.946 | 1 | 10 | 80 | 81.3588
2017-08-01 | 6:20 | 1.7663 | 8.09 |  | 10
2017-08-01 | 6:25 | 1.7709 | 7.6971 |  | 10
2017-08-01 | 6:30 | 1.7943 | 7.6084 | 1 | 10 | 77.4047 | 80.5
2017-08-01 | 6:35 | 1.7655 | 7.6361 |  | 10
2017-08-01 | 6:40 | 1.7865 | 7.6178 |  | 10
2017-08-01 | 6:45 | 1.7897 | 7.2758 | 1 | 10 | 73.6577 | 79.8817
2017-08-01 | 6:48 |  |  | 0
2017-08-01 | 6:50 | 1.4691 | 5.5687 |  | 1.5
2017-08-01 | 6:53 |  |  | 1
2017-08-01 | 6:55 | 1.9745 | 3.7081 |  | 10
2017-08-01 | 7:00 | 1.8333 | 3.9654 | 1 | 10 | 41.4011 | 79.4726
2017-08-01 | 7:05 | 1.7616 | 5.3324 |  | 10
2017-08-01 | 7:10 | 1.7764 | 6.4455 |  | 10
2017-08-01 | 7:15 | 1.7546 | 6.7673 | 1 | 10 | 68.3579 | 78.4708
2017-08-01 | 7:20 | 1.7686 | 6.2659 |  | 10
2017-08-01 | 7:25 | 1.7273 | 6.3314 |  | 10
2017-08-01 | 7:30 | 1.7507 | 6.2682 | 1 | 10 | 63.488 | 78.5271
2017-08-01 | 7:35 | 1.778 | 5.9577 |  | 10
2017-08-01 | 7:40 | 1.7436 | 5.7534 |  | 10
2017-08-01 | 7:45 | 1.7257 | 5.7867 | 1 | 10 | 58.9533 | 78.6309
2017-08-01 | 7:50 | 1.7678 | 4.9335 |  | 10
2017-08-01 | 7:55 | 1.7748 | 4.4695 |  | 10
2017-08-01 | 8:00 |  |  | 0
2017-08-01 | 8:00 | 1.7171 | 1.8687 | 0 | 1.5 | 25 | 78.1761
2017-08-01 | 8:05 | 1.5759 | 0 |  | 1.5
2017-08-01 | 8:10 | 1.6188 | 0 |  | 1.5
2017-08-01 | 8:15 | 1.7023 | 0 | 0 | 1.5 | 25 | 82.0485
2017-08-01 | 8:20 | 1.7015 | 0 |  | 1.5
2017-08-01 | 8:25 | 1.714 | 0 |  | 1.5
2017-08-01 | 8:30 | 1.7717 | 0 | 0 | 1.5 | 25 | 82.6312
2017-08-01 | 8:35 | 1.7507 | 0 |  | 1.5
2017-08-01 | 8:40 | 1.7491 | 0 |  | 1.5
2017-08-01 | 8:45 | 1.7366 | 0 | 0 | 1.5 | 25 | 82.9006
2017-08-01 | 8:50 | 1.714 | 0 |  | 1.5
2017-08-01 | 8:55 | 1.7491 | 0 |  | 1.5
2017-08-01 | 9:00 | 1.7499 | 0 | 0 | 1.5 | 25 | 82.8668
2017-08-01 | 9:05 | 1.7553 | 0 |  | 1.5
2017-08-01 | 9:10 | 1.753 | 0.010641 |  | 1.5
2017-08-01 | 9:15 | 1.7873 | 0 | 0 | 1.5 | 25 | 82.992
2017-08-01 | 9:20 | 1.7678 | 0 |  | 1.5
2017-08-01 | 9:25 | 1.7483 | 0 |  | 1.5
2017-08-01 | 9:30 | 1.7405 | 0 | 0 | 1.5 | 25 | 83.0568
2017-08-01 | 9:35 | 1.689 | 0 |  | 1.5
2017-08-01 | 9:40 | 1.7054 | 0 |  | 1.5
2017-08-01 | 9:45 | 1.7171 | 0 | 0 | 1.5 | 25 | 84.3153
2017-08-01 | 9:50 | 1.7054 | 0 |  | 1.5
2017-08-01 | 9:55 | 1.6929 | 0 |  | 1.5
2017-08-01 | 10:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 85.508
2017-08-01 | 10:05 | 1.6906 | 0 |  | 1.5
2017-08-01 | 10:10 | 1.7335 | 0 |  | 1.5
2017-08-01 | 10:15 | 1.7475 | 0 | 0 | 1.5 | 25 | 86.2703
2017-08-01 | 10:20 | 1.739 | 0 |  | 1.5
2017-08-01 | 10:25 | 1.7678 | 0 |  | 1.5
2017-08-01 | 10:30 | 1.7413 | 0 | 0 | 1.5 | 25 | 86.2861
2017-08-01 | 10:35 | 1.7717 | 0 |  | 1.5
2017-08-01 | 10:40 | 1.7748 | 0 |  | 1.5
2017-08-01 | 10:45 | 1.7436 | 0 | 0 | 1.5 | 25 | 85.872
2017-08-01 | 10:50 | 1.721 | 0 |  | 1.5
2017-08-01 | 10:55 | 1.7124 | 0 |  | 1.5
2017-08-01 | 11:00 | 1.7655 | 0 | 0 | 1.5 | 25 | 86.325
2017-08-01 | 11:05 | 1.7795 | 0 |  | 1.5
2017-08-01 | 11:10 | 1.7834 | 0 |  | 1.5
2017-08-01 | 11:15 | 1.7569 | 0 | 0 | 1.5 | 25 | 85.4867
2017-08-01 | 11:20 | 1.76 | 0 |  | 1.5
2017-08-01 | 11:25 | 1.7733 | 0 |  | 1.5
2017-08-01 | 11:30 | 1.7429 | 0 | 0 | 1.5 | 25 | 85.4142
2017-08-01 | 11:35 | 1.7234 | 0 |  | 1.5
2017-08-01 | 11:40 | 1.7514 | 0 |  | 1.5
2017-08-01 | 11:45 | 1.6828 | 0 | 0 | 1.5 | 25 | 86.1073
2017-08-01 | 11:50 | 1.7101 | 0 |  | 1.5
2017-08-01 | 11:55 | 1.7405 | 0 |  | 1.5
2017-08-01 | 12:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 87.0862
2017-08-01 | 12:05 | 1.7413 | 0 |  | 1.5
2017-08-01 | 12:10 | 1.7499 | 0 |  | 1.5
2017-08-01 | 12:15 | 1.7468 | 0 | 0 | 1.5 | 25 | 87.313
2017-08-01 | 12:20 | 1.7358 | 0 |  | 1.5
2017-08-01 | 12:25 | 1.7226 | 0 |  | 1.5
2017-08-01 | 12:30 | 1.7101 | 0 | 0 | 1.5 | 25 | 88.0457
2017-08-01 | 12:35 | 1.7351 | 0 |  | 1.5
2017-08-01 | 12:40 | 1.7343 | 0 |  | 1.5
2017-08-01 | 12:45 | 1.7546 | 0 | 0 | 1.5 | 25 | 88.1951
2017-08-01 | 12:50 | 1.7639 | 0 |  | 1.5
2017-08-01 | 12:55 | 1.7296 | 0 |  | 1.5
2017-08-01 | 13:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 88.3059
2017-08-01 | 13:05 | 1.746 | 0 |  | 1.5
2017-08-01 | 13:10 | 1.7694 | 0 |  | 1.5
2017-08-01 | 13:15 | 1.7413 | 0 | 0 | 1.5 | 25 | 88.6599
2017-08-01 | 13:20 | 1.7218 | 0 |  | 1.5
2017-08-01 | 13:25 | 1.7436 | 0 |  | 1.5
2017-08-01 | 13:30 | 1.6617 | 0 | 0 | 1.5 | 25 | 89.6688
2017-08-01 | 13:35 | 1.675 | 0 |  | 1.5
2017-08-01 | 13:40 | 1.7093 | 0 |  | 1.5
2017-08-01 | 13:45 | 1.6867 | 0 | 0 | 1.5 | 25 | 91.351
2017-08-01 | 13:50 | 1.707 | 0 |  | 1.5
2017-08-01 | 13:55 | 1.6836 | 0 |  | 1.5
2017-08-01 | 14:00 | 1.6766 | 0 | 0 | 1.5 | 25 | 92.6025
2017-08-01 | 14:05 | 1.7062 | 0 |  | 1.5
2017-08-01 | 14:10 | 1.7117 | 0 |  | 1.5
2017-08-01 | 14:15 | 1.7109 | 0 | 0 | 1.5 | 25 | 93.4381
2017-08-01 | 14:20 | 1.7421 | 0 |  | 1.5
2017-08-01 | 14:25 | 1.7436 | 0 |  | 1.5
2017-08-01 | 14:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 93.5646
2017-08-01 | 14:35 | 1.7241 | 0 |  | 1.5
2017-08-01 | 14:40 | 1.7624 | 0 |  | 1.5
2017-08-01 | 14:45 | 1.7483 | 0 | 0 | 1.5 | 25 | 93.907
2017-08-01 | 14:50 | 1.689 | 0 |  | 1.5
2017-08-01 | 14:55 | 1.7124 | 0 |  | 1.5
2017-08-01 | 15:00 | 1.7156 | 0 | 0 | 1.5 | 25 | 94.9852
2017-08-01 | 15:05 | 1.7257 | 0 |  | 1.5
2017-08-01 | 15:10 | 1.7226 | 0 |  | 1.5
2017-08-01 | 15:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 95.2819
2017-08-01 | 15:20 | 1.7241 | 0 |  | 1.5
2017-08-01 | 15:25 | 1.7179 | 0 |  | 1.5
2017-08-01 | 15:30 | 1.7241 | 0 | 0 | 1.5 | 25 | 95.6881
2017-08-01 | 15:35 | 1.7951 | 0 |  | 1.5
2017-08-01 | 15:40 | 1.7585 | 0 |  | 1.5
2017-08-01 | 15:45 | 1.7475 | 0 | 0 | 1.5 | 25 | 95.2824
2017-08-01 | 15:50 | 1.7748 | 0 |  | 1.5
2017-08-01 | 15:55 | 1.7538 | 0 |  | 1.5
2017-08-01 | 16:00 | 1.7546 | 0 | 0 | 1.5 | 25 | 95.0524
2017-08-01 | 16:05 | 1.7569 | 0 |  | 1.5
2017-08-01 | 16:10 | 1.8466 | 0 |  | 1.5
2017-08-01 | 16:15 | 1.8146 | 0 | 0 | 1.5 | 25 | 94.0322
2017-08-01 | 16:20 | 1.7382 | 0 |  | 1.5
2017-08-01 | 16:25 | 1.7514 | 0 |  | 1.5
2017-08-01 | 16:30 | 1.7663 | 0 | 0 | 1.5 | 25 | 93.7155
2017-08-01 | 16:35 | 1.7772 | 0 |  | 1.5
2017-08-01 | 16:40 | 1.7499 | 0 |  | 1.5
2017-08-01 | 16:45 | 1.7639 | 0 | 0 | 1.5 | 25 | 93.2327
2017-08-01 | 16:50 | 1.728 | 0 |  | 1.5
2017-08-01 | 16:55 | 1.7787 | 0 |  | 1.5
2017-08-01 | 17:00 | 1.7585 | 0 | 0 | 1.5 | 25 | 93.1071
2017-08-01 | 17:05 | 1.7904 | 0 |  | 1.5
2017-08-01 | 17:10 | 1.8014 | 0 |  | 1.5
2017-08-01 | 17:15 | 1.7803 | 0 | 0 | 1.5 | 25 | 91.9306
2017-08-01 | 17:20 | 1.8263 | 0 |  | 1.5
2017-08-01 | 17:25 | 1.7171 | 0 |  | 1.5
2017-08-01 | 17:30 | 1.7374 | 0 | 0 | 1.5 | 25 | 91.5545
2017-08-01 | 17:35 | 1.7507 | 0 |  | 1.5
2017-08-01 | 17:40 | 1.7733 | 0 |  | 1.5
2017-08-01 | 17:45 | 1.8029 | 0 | 0 | 1.5 | 25 | 90.8523
2017-08-01 | 17:50 | 1.8107 | 0 |  | 1.5
2017-08-01 | 17:55 | 1.8162 | 0 |  | 1.5
2017-08-01 | 18:00 | 1.7819 | 0 | 0 | 1.5 | 25 | 89.7294
2017-08-01 | 18:05 | 1.7881 | 0 |  | 1.5
2017-08-01 | 18:10 | 1.7819 | 0 |  | 1.5
2017-08-01 | 18:15 | 1.8255 | 0 | 0 | 1.5 | 25 | 88.7857
2017-08-01 | 18:20 | 1.7826 | 0 |  | 1.5
2017-08-01 | 18:25 | 1.7858 | 0 |  | 1.5
2017-08-01 | 18:30 | 1.7967 | 0 | 0 | 1.5 | 25 | 87.0606
2017-08-01 | 18:35 | 1.778 | 0 |  | 1.5
2017-08-01 | 18:40 | 1.7647 | 0 |  | 1.5
2017-08-01 | 18:45 | 1.8014 | 0 | 0 | 1.5 | 25 | 86.0179
2017-08-01 | 18:50 | 1.7787 | 0 |  | 1.5
2017-08-01 | 18:55 | 1.785 | 0 |  | 1.5
2017-08-01 | 19:00 | 1.7608 | 0 | 0 | 1.5 | 25 | 85.1957
2017-08-01 | 19:05 | 1.7733 | 0 |  | 1.5
2017-08-01 | 19:10 | 1.7468 | 0 |  | 1.5
2017-08-01 | 19:15 | 1.7639 | 0 | 0 | 1.5 | 25 | 84.6066
2017-08-01 | 19:20 | 1.7577 | 0 |  | 1.5
2017-08-01 | 19:25 | 1.7686 | 0 |  | 1.5
2017-08-01 | 19:30 | 1.7647 | 0 | 0 | 1.5 | 25 | 84.1053
2017-08-01 | 19:35 | 1.7382 | 0 |  | 1.5
2017-08-01 | 19:40 | 1.753 | 0 |  | 1.5
2017-08-01 | 19:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 84.1311
2017-08-01 | 19:50 | 1.7616 | 0 |  | 1.5
2017-08-01 | 19:55 | 1.7553 | 0 |  | 1.5
2017-08-01 | 20:00 | 1.8006 | 0 | 0 | 1.5 | 25 | 83.605
2017-08-01 | 20:05 | 1.785 | 0 |  | 1.5
2017-08-01 | 20:10 | 1.8053 | 0 |  | 1.5
2017-08-01 | 20:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 82.4189
2017-08-01 | 20:20 | 1.7748 | 0 |  | 1.5
2017-08-01 | 20:25 | 1.7585 | 0 |  | 1.5
2017-08-01 | 20:30 | 1.7756 | 0 | 0 | 1.5 | 25 | 81.9074
2017-08-01 | 20:35 | 1.7998 | 0 |  | 1.5
2017-08-01 | 20:40 | 1.7826 | 0 |  | 1.5
2017-08-01 | 20:45 | 1.7897 | 0 | 0 | 1.5 | 25 | 81.0514
2017-08-01 | 20:50 | 1.76 | 0 |  | 1.5
2017-08-01 | 20:55 | 1.7865 | 0 |  | 1.5
2017-08-01 | 21:00 | 1.7327 | 0 | 0 | 1.5 | 25 | 80.7623
2017-08-01 | 21:05 | -0.10262 | 0 |  | 1.5
2017-08-01 | 21:10 | -0.1034 | 0 |  | 1.5
2017-08-01 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-01 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-01 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-01 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-01 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-01 | 21:55 | -0.1073 | 0 |  | 1.5
2017-08-01 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-01 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-01 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-01 | 22:25 | -0.10574 | 0 |  | 1.5
2017-08-01 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-01 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-01 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-01 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-01 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-01 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-01 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-01 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-01 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-01 | 23:40 | -0.10418 | 0 |  | 1.5
2017-08-01 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-01 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-01 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-02 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-02 | 0:05 | -0.1034 | 0 |  | 1.5
2017-08-02 | 0:10 | -0.1034 | 0 |  | 1.5
2017-08-02 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-02 | 0:15 | -0.1034 | 0 |  | 1.5 |  | 0
2017-08-02 | 0:20 | -0.10262 | 0 |  | 1.5
2017-08-02 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-02 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-02 | 0:30 | -0.1034 | 0 |  | 1.5 |  | 0
2017-08-02 | 0:35 | -0.1034 | 0 |  | 1.5
2017-08-02 | 0:40 | -0.1034 | 0 |  | 1.5
2017-08-02 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-02 | 0:45 | -0.1034 | 0 |  | 1.5 |  | 0
2017-08-02 | 0:50 | -0.10262 | 0 |  | 1.5
2017-08-02 | 0:55 | -0.10262 | 0 |  | 1.5
2017-08-02 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0
2017-08-02 | 1:00 | -0.10262 | 0 |  | 1.5 |  | 0
2017-08-02 | 1:05 | -0.10262 | 0 |  | 1.5
2017-08-02 | 1:10 | -0.10262 | 0 |  | 1.5
2017-08-02 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0
2017-08-02 | 1:15 | -0.10262 | 0 |  | 1.5 |  | 0
2017-08-02 | 1:20 | -0.10496 | 0 |  | 1.5
2017-08-02 | 1:25 | -0.10574 | 0 |  | 1.5
2017-08-02 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-02 | 1:30 | -0.10574 | 0 |  | 1.5 |  | 0
2017-08-02 | 1:35 | -0.10574 | 0 |  | 1.5
2017-08-02 | 1:40 | -0.10574 | 0 |  | 1.5
2017-08-02 | 1:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-02 | 1:45 | -0.10574 | 0 |  | 1.5 |  | 0
2017-08-02 | 1:50 | -0.10574 | 0 |  | 1.5
2017-08-02 | 1:55 | -0.10574 | 0 |  | 1.5
2017-08-02 | 2:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-02 | 2:00 | -0.10574 | 0 |  | 1.5 |  | 0
2017-08-02 | 2:05 | -0.10574 | 0 |  | 1.5
2017-08-02 | 2:10 | -0.10574 | 0 |  | 1.5
2017-08-02 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 2:15 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 2:20 | -0.10652 | 0 |  | 1.5
2017-08-02 | 2:25 | -0.10574 | 0 |  | 1.5
2017-08-02 | 2:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-02 | 2:30 | -0.10574 | 0 |  | 1.5 |  | 0
2017-08-02 | 2:35 | -0.10574 | 0 |  | 1.5
2017-08-02 | 2:40 | -0.10652 | 0 |  | 1.5
2017-08-02 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 2:45 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 2:50 | -0.10652 | 0 |  | 1.5
2017-08-02 | 2:55 | -0.10652 | 0 |  | 1.5
2017-08-02 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 3:00 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 3:05 | -0.10652 | 0 |  | 1.5
2017-08-02 | 3:10 | -0.10652 | 0 |  | 1.5
2017-08-02 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 3:15 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 3:20 | -0.10652 | 0 |  | 1.5
2017-08-02 | 3:25 | -0.1073 | 0 |  | 1.5
2017-08-02 | 3:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 3:30 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 3:35 | -0.1073 | 0 |  | 1.5
2017-08-02 | 3:40 | -0.1073 | 0 |  | 1.5
2017-08-02 | 3:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 3:45 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-02 | 3:55 | -0.1073 | 0 |  | 1.5
2017-08-02 | 4:00 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-02 | 4:00 | -0.10652 | 0 |  | 1.5 |  | 0
2017-08-02 | 4:05 | -0.10652 | 0 |  | 1.5
2017-08-02 | 4:10 | -0.10652 | 0 |  | 1.5
2017-08-02 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-02 | 4:15 | -0.1073 | 0 |  | 1.5 |  | 0
2017-08-02 | 4:20 | -0.1073 | 0 |  | 1.5
2017-08-02 | 4:25 | -0.10652 | 0 |  | 1.5
2017-08-02 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-02 | 4:30 | -0.1073 | 0 |  | 1.5 |  | 0
2017-08-02 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-02 | 4:40 | -0.10652 | 0 |  | 1.5
2017-08-02 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-02 | 4:45 | -0.1073 | 0 |  | 1.5 |  | 0
2017-08-02 | 4:50 | -0.1073 | 0 |  | 1.5
2017-08-02 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-02 | 5:00 | -0.1073 | 0 | 1 | 0 | 0
2017-08-02 | 5:00 | -0.1073 | 0 |  | 0 |  | 25
2017-08-02 | 5:05 | 1.817 | 6.155 |  | 10
2017-08-02 | 5:10 | 1.8591 | 10 |  | 10
2017-08-02 | 5:15 | 1.845 | 10 | 1 | 10 | 100
2017-08-02 | 5:15 | 1.845 | 10 |  | 10 |  | 96.6519
2017-08-02 | 5:20 | 1.8248 | 10 |  | 10
2017-08-02 | 5:25 | 1.8934 | 10 |  | 10
2017-08-02 | 5:30 | 1.9168 | 10 | 1 | 10 | 100
2017-08-02 | 5:30 | 1.9168 | 10 |  | 10 |  | 93.4786
2017-08-02 | 5:35 | 1.9106 | 9.9981 |  | 10
2017-08-02 | 5:40 | 1.9269 | 10 |  | 10
2017-08-02 | 5:45 | 1.9067 | 10 | 1 | 10 | 100
2017-08-02 | 5:45 | 1.9067 | 10 |  | 10 |  | 89.021
2017-08-02 | 5:50 | 1.856 | 9.9041 |  | 10
2017-08-02 | 5:55 | 1.8934 | 9.7089 |  | 10
2017-08-02 | 6:00 | 1.8653 | 9.2436 | 1 | 10 | 92.913
2017-08-02 | 6:00 | 1.8653 | 9.2436 |  | 10 |  | 85.5763
2017-08-02 | 6:05 | 1.8809 | 8.8414 |  | 10
2017-08-02 | 6:10 | 1.8591 | 8.5388 |  | 10
2017-08-02 | 6:15 | 1.8263 | 8.2034 | 1 | 10 | 82.8439
2017-08-02 | 6:15 | 1.8263 | 8.2034 |  | 10 |  | 82.8372
2017-08-02 | 6:20 | 1.8271 | 7.8085 |  | 10
2017-08-02 | 6:25 | 1.8092 | 7.4602 |  | 10
2017-08-02 | 6:30 | 1.8107 | 7.0991 | 1 | 10 | 71.8695
2017-08-02 | 6:30 | 1.8107 | 7.0991 |  | 10 |  | 81.0179
2017-08-02 | 6:35 | 1.7998 | 6.9026 |  | 10
2017-08-02 | 6:36 |  |  | 0
2017-08-02 | 6:40 | 1.7366 | 2.6257 |  | 1.5
2017-08-02 | 6:45 | 1.7421 | 0 | 0 | 1.5 | 25
2017-08-02 | 6:45 | 1.7421 | 0 |  | 1.5 |  | 81.6787
2017-08-02 | 6:50 | 1.7304 | 0 |  | 1.5
2017-08-02 | 6:55 | 1.76 | 0 |  | 1.5
2017-08-02 | 7:00 | 1.7296 | 0 | 0 | 1.5 | 25
2017-08-02 | 7:00 | 1.7296 | 0 |  | 1.5 |  | 81.8751
2017-08-02 | 7:05 | 1.7795 | 0 |  | 1.5
2017-08-02 | 7:10 | 1.7546 | 0 |  | 1.5
2017-08-02 | 7:15 | 1.7647 | 0 | 0 | 1.5 | 25
2017-08-02 | 7:15 | 1.7647 | 0 |  | 1.5 |  | 81.5438
2017-08-02 | 7:20 | 1.7631 | 0 |  | 1.5
2017-08-02 | 7:25 | 1.7553 | 0 |  | 1.5
2017-08-02 | 7:30 | 1.7694 | 0 | 0 | 1.5 | 25
2017-08-02 | 7:30 | 1.7694 | 0 |  | 1.5 |  | 81.3318
2017-08-02 | 7:35 | 1.7772 | 0 |  | 1.5
2017-08-02 | 7:40 | 1.7686 | 0 |  | 1.5
2017-08-02 | 7:45 | 1.7616 | 0 | 0 | 1.5 | 25
2017-08-02 | 7:45 | 1.7616 | 0 |  | 1.5 |  | 80.9912
2017-08-02 | 7:50 | 1.7429 | 0 |  | 1.5
2017-08-02 | 7:55 | 1.7421 | 0 |  | 1.5
2017-08-02 | 8:00 | 1.7296 | 0 | 0 | 1.5 | 25
2017-08-02 | 8:00 | 1.7296 | 0 |  | 1.5 |  | 80.9655
2017-08-02 | 8:05 | 1.7413 | 0 |  | 1.5
2017-08-02 | 8:10 | 1.7093 | 0 |  | 1.5
2017-08-02 | 8:15 | 1.7507 | 0 | 0 | 1.5 | 25
2017-08-02 | 8:15 | 1.7507 | 0 |  | 1.5 |  | 81.3103
2017-08-02 | 8:20 | 1.7374 | 0 |  | 1.5
2017-08-02 | 8:25 | 1.7085 | 0 |  | 1.5
2017-08-02 | 8:30 | 1.7397 | 0 | 0 | 1.5 | 25
2017-08-02 | 8:30 | 1.7397 | 0 |  | 1.5 |  | 81.781
2017-08-02 | 8:35 | 1.7226 | 0 |  | 1.5
2017-08-02 | 8:40 | 1.7514 | 0 |  | 1.5
2017-08-02 | 8:45 | 1.7366 | 0 | 0 | 1.5 | 25
2017-08-02 | 8:45 | 1.7366 | 0 |  | 1.5 |  | 82.2213
2017-08-02 | 8:50 | 1.7499 | 0 |  | 1.5
2017-08-02 | 8:55 | 1.7288 | 0 |  | 1.5
2017-08-02 | 9:00 | 1.7273 | 0 | 0 | 1.5 | 25
2017-08-02 | 9:00 | 1.7273 | 0 |  | 1.5 |  | 82.5992
2017-08-02 | 9:05 | 1.7343 | 0 |  | 1.5
2017-08-02 | 9:10 | 1.7366 | 0 |  | 1.5
2017-08-02 | 9:15 | 1.7249 | 0 | 0 | 1.5 | 25
2017-08-02 | 9:15 | 1.7249 | 0 |  | 1.5 |  | 83.1348
2017-08-02 | 9:20 | 1.6758 | 0 |  | 1.5
2017-08-02 | 9:25 | 1.7156 | 0 |  | 1.5
2017-08-02 | 9:30 | 1.7483 | 0 | 0 | 1.5 | 25
2017-08-02 | 9:30 | 1.7483 | 0 |  | 1.5 |  | 83.7738
2017-08-02 | 9:35 | 1.8014 | 0 |  | 1.5
2017-08-02 | 9:40 | 1.7811 | 0 |  | 1.5
2017-08-02 | 9:45 | 1.7382 | 0 | 0 | 1.5 | 25
2017-08-02 | 9:45 | 1.7382 | 0 |  | 1.5 |  | 83.4092
2017-08-02 | 9:50 | 1.7374 | 0 |  | 1.5
2017-08-02 | 9:55 | 1.7522 | 0 |  | 1.5
2017-08-02 | 10:00 | 1.7577 | 0 | 0 | 1.5 | 25
2017-08-02 | 10:00 | 1.7577 | 0 |  | 1.5 |  | 83.6775
2017-08-02 | 10:05 | 1.7577 | 0 |  | 1.5
2017-08-02 | 10:10 | 1.7624 | 0 |  | 1.5
2017-08-02 | 10:15 | 1.739 | 0 | 0 | 1.5 | 25
2017-08-02 | 10:15 | 1.739 | 0 |  | 1.5 |  | 83.2681
2017-08-02 | 10:20 | 1.7507 | 0 |  | 1.5
2017-08-02 | 10:25 | 1.7163 | 0 |  | 1.5
2017-08-02 | 10:30 | 1.7343 | 0 | 0 | 1.5 | 25
2017-08-02 | 10:30 | 1.7343 | 0 |  | 1.5 |  | 83.4818
2017-08-02 | 10:35 | 1.7202 | 0 |  | 1.5
2017-08-02 | 10:40 | 1.7249 | 0 |  | 1.5
2017-08-02 | 10:45 | 1.7117 | 0 | 0 | 1.5 | 25
2017-08-02 | 10:45 | 1.7117 | 0 |  | 1.5 |  | 84.172
2017-08-02 | 10:50 | 1.7382 | 0 |  | 1.5
2017-08-02 | 10:55 | 1.7007 | 0 |  | 1.5
2017-08-02 | 11:00 | 1.7093 | 0 | 0 | 1.5 | 25
2017-08-02 | 11:00 | 1.7093 | 0 |  | 1.5 |  | 84.9162
2017-08-02 | 11:05 | 1.7179 | 0 |  | 1.5
2017-08-02 | 11:10 | 1.714 | 0 |  | 1.5
2017-08-02 | 11:15 | 1.7312 | 0 | 0 | 1.5 | 25
2017-08-02 | 11:15 | 1.7312 | 0 |  | 1.5 |  | 85.7554
2017-08-02 | 11:20 | 1.739 | 0 |  | 1.5
2017-08-02 | 11:25 | 1.7202 | 0 |  | 1.5
2017-08-02 | 11:30 | 1.7374 | 0 | 0 | 1.5 | 25
2017-08-02 | 11:30 | 1.7374 | 0 |  | 1.5 |  | 86.311
2017-08-02 | 11:35 | 1.7234 | 0 |  | 1.5
2017-08-02 | 11:40 | 1.7327 | 0 |  | 1.5
2017-08-02 | 11:45 | 1.7171 | 0 | 0 | 1.5 | 25
2017-08-02 | 11:45 | 1.7171 | 0 |  | 1.5 |  | 87.0654
2017-08-02 | 11:50 | 1.6929 | 0 |  | 1.5
2017-08-02 | 11:55 | 1.6922 | 0 |  | 1.5
2017-08-02 | 12:00 | 1.6914 | 0 | 0 | 1.5 | 25
2017-08-02 | 12:00 | 1.6914 | 0 |  | 1.5 |  | 88.3955
2017-08-02 | 12:05 | 1.6766 | 0 |  | 1.5
2017-08-02 | 12:10 | 1.7249 | 0 |  | 1.5
2017-08-02 | 12:15 | 1.7046 | 0 | 0 | 1.5 | 25
2017-08-02 | 12:15 | 1.7046 | 0 |  | 1.5 |  | 89.5546
2017-08-02 | 12:20 | 1.7 | 0 |  | 1.5
2017-08-02 | 12:25 | 1.7054 | 0 |  | 1.5
2017-08-02 | 12:30 | 1.7358 | 0 | 0 | 1.5 | 25
2017-08-02 | 12:30 | 1.7358 | 0 |  | 1.5 |  | 90.6011
2017-08-02 | 12:35 | 1.7327 | 0 |  | 1.5
2017-08-02 | 12:40 | 1.7148 | 0 |  | 1.5
2017-08-02 | 12:45 | 1.7616 | 0 | 0 | 1.5 | 25
2017-08-02 | 12:45 | 1.7616 | 0 |  | 1.5 |  | 91.1319
2017-08-02 | 12:50 | 1.7202 | 0 |  | 1.5
2017-08-02 | 12:55 | 1.7507 | 0 |  | 1.5
2017-08-02 | 13:00 | 1.7405 | 0 | 0 | 1.5 | 25
2017-08-02 | 13:00 | 1.7405 | 0 |  | 1.5 |  | 91.3976
2017-08-02 | 13:05 | 1.7078 | 0 |  | 1.5
2017-08-02 | 13:10 | 1.7468 | 0 |  | 1.5
2017-08-02 | 13:15 | 1.7132 | 0 | 0 | 1.5 | 25
2017-08-02 | 13:15 | 1.7132 | 0 |  | 1.5 |  | 92.1563
2017-08-02 | 13:20 | 1.7241 | 0 |  | 1.5
2017-08-02 | 13:25 | 1.7335 | 0 |  | 1.5
2017-08-02 | 13:30 | 1.7366 | 0 | 0 | 1.5 | 25
2017-08-02 | 13:30 | 1.7366 | 0 |  | 1.5 |  | 92.7969
2017-08-02 | 13:35 | 1.7241 | 0 |  | 1.5
2017-08-02 | 13:40 | 1.7429 | 0 |  | 1.5
2017-08-02 | 13:45 | 1.7257 | 0 | 0 | 1.5 | 25
2017-08-02 | 13:45 | 1.7257 | 0 |  | 1.5 |  | 93.3866
2017-08-02 | 13:50 | 1.7195 | 0 |  | 1.5
2017-08-02 | 13:55 | 1.7413 | 0 |  | 1.5
2017-08-02 | 14:00 | 1.7249 | 0 | 0 | 1.5 | 25
2017-08-02 | 14:00 | 1.7249 | 0 |  | 1.5 |  | 93.8356
2017-08-02 | 14:05 | 1.7288 | 0 |  | 1.5
2017-08-02 | 14:10 | 1.7148 | 0 |  | 1.5
2017-08-02 | 14:15 | 1.7062 | 0 | 0 | 1.5 | 25
2017-08-02 | 14:15 | 1.7062 | 0 |  | 1.5 |  | 94.5011
2017-08-02 | 14:20 | 1.6976 | 0 |  | 1.5
2017-08-02 | 14:25 | 1.6976 | 0 |  | 1.5
2017-08-02 | 14:30 | 1.7335 | 0 | 0 | 1.5 | 25
2017-08-02 | 14:30 | 1.7335 | 0 |  | 1.5 |  | 95.6518
2017-08-02 | 14:35 | 1.707 | 0 |  | 1.5
2017-08-02 | 14:40 | 1.7312 | 0 |  | 1.5
2017-08-02 | 14:45 | 1.7031 | 0 | 0 | 1.5 | 25
2017-08-02 | 14:45 | 1.7031 | 0 |  | 1.5 |  | 96.7943
2017-08-02 | 14:50 | 1.7772 | 0 |  | 1.5
2017-08-02 | 14:55 | 1.707 | 0 |  | 1.5
2017-08-02 | 15:00 | 1.7015 | 0 | 0 | 1.5 | 25
2017-08-02 | 15:00 | 1.7015 | 0 |  | 1.5 |  | 97.4892
2017-08-02 | 15:05 | 1.7078 | 0 |  | 1.5
2017-08-02 | 15:10 | 1.6828 | 0 |  | 1.5
2017-08-02 | 15:15 | 1.7046 | 0 | 0 | 1.5 | 25
2017-08-02 | 15:15 | 1.7046 | 0 |  | 1.5 |  | 98.4682
2017-08-02 | 15:20 | 1.6103 | 0 |  | 1.5
2017-08-02 | 15:25 | 1.5198 | 0 |  | 1.5
2017-08-02 | 15:30 | 1.441 | 0 | 0 | 1.5 | 25
2017-08-02 | 15:30 | 1.441 | 0 |  | 1.5 |  | 100
2017-08-02 | 15:35 | 1.3919 | 0 |  | 1.5
2017-08-02 | 15:40 |  |  | 0
2017-08-02 | 15:40 | 1.3326 | 0 |  | 1.5
2017-08-02 | 15:45 | 1.3287 | 0 | 0 | 1.5 | 25
2017-08-02 | 15:45 | 1.3287 | 0 |  | 1.5 |  | 100
2017-08-02 | 15:50 | 1.3224 | 0 |  | 1.5
2017-08-02 | 15:55 | 1.2983 | 0 |  | 1.5
2017-08-02 | 16:00 | 1.2834 | 0 | 0 | 1.5 | 25
2017-08-02 | 16:00 | 1.2834 | 0 |  | 1.5 |  | 100
2017-08-02 | 16:05 | 1.2967 | 0 |  | 1.5
2017-08-02 | 16:10 | 1.2554 | 0 |  | 1.5
2017-08-02 | 16:15 | 1.2756 | 0 | 0 | 1.5 | 25
2017-08-02 | 16:15 | 1.2756 | 0 |  | 1.5 |  | 100
2017-08-02 | 16:20 | 1.299 | 0 |  | 1.5
2017-08-02 | 16:25 | 1.2483 | 0 |  | 1.5
2017-08-02 | 16:30 | 1.2359 | 0 | 0 | 1.5 | 25
2017-08-02 | 16:30 | 1.2359 | 0 |  | 1.5 |  | 100
2017-08-02 | 16:35 | 1.2008 | 0 |  | 1.5
2017-08-02 | 16:40 | 1.2351 | 0 |  | 1.5
2017-08-02 | 16:45 | 1.2086 | 0 | 0 | 1.5 | 25
2017-08-02 | 16:45 | 1.2086 | 0 |  | 1.5 |  | 100
2017-08-02 | 16:50 | 1.2047 | 0 |  | 1.5
2017-08-02 | 16:55 | 1.1368 | 0 |  | 1.5
2017-08-02 | 17:00 | 1.1641 | 0 | 0 | 1.5 | 25
2017-08-02 | 17:00 | 1.1641 | 0 |  | 1.5 |  | 100
2017-08-02 | 17:05 | 1.1313 | 0 |  | 1.5
2017-08-02 | 17:10 | 1.104 | 0 |  | 1.5
2017-08-02 | 17:15 | 1.1048 | 0 | 0 | 1.5 | 25
2017-08-02 | 17:15 | 1.1048 | 0 |  | 1.5 |  | 100
2017-08-02 | 17:20 | 1.1282 | 0 |  | 1.5
2017-08-02 | 17:25 | 1.1095 | 0 |  | 1.5
2017-08-02 | 17:30 | 1.1282 | 0 | 0 | 1.5 | 25
2017-08-02 | 17:30 | 1.1282 | 0 |  | 1.5 |  | 100
2017-08-02 | 17:35 | 1.1103 | 0 |  | 1.5
2017-08-02 | 17:40 | 1.0939 | 0 |  | 1.5
2017-08-02 | 17:45 | 1.0908 | 0 | 0 | 1.5 | 25
2017-08-02 | 17:45 | 1.0908 | 0 |  | 1.5 |  | 100
2017-08-02 | 17:50 | 1.1134 | 0 |  | 1.5
2017-08-02 | 17:55 | 1.0697 | 0 |  | 1.5
2017-08-02 | 18:00 | 1.0814 | 0 | 0 | 1.5 | 25
2017-08-02 | 18:00 | 1.0814 | 0 |  | 1.5 |  | 100
2017-08-02 | 18:05 | 1.0986 | 0.1421 |  | 1.5
2017-08-02 | 18:10 | 1.0393 | 0 |  | 1.5
2017-08-02 | 18:15 | 1.0471 | 0 | 0 | 1.5 | 25
2017-08-02 | 18:15 | 1.0471 | 0 |  | 1.5 |  | 100
2017-08-02 | 18:20 | 1.0081 | 0 |  | 1.5
2017-08-02 | 18:25 | 1.0097 | 0 |  | 1.5
2017-08-02 | 18:30 | 1.0151 | 0 | 0 | 1.5 | 25
2017-08-02 | 18:30 | 1.0151 | 0 |  | 1.5 |  | 100
2017-08-02 | 18:35 | 1.0081 | 0 |  | 1.5
2017-08-02 | 18:40 | 1.0151 | 0 |  | 1.5
2017-08-02 | 18:45 | 1.0159 | 0 | 0 | 1.5 | 25
2017-08-02 | 18:45 | 1.0159 | 0 |  | 1.5 |  | 100
2017-08-02 | 18:50 | 1.0221 | 0 |  | 1.5
2017-08-02 | 18:55 | 0.99562 | 0 |  | 1.5
2017-08-02 | 19:00 | 0.99562 | 0 | 0 | 1.5 | 25
2017-08-02 | 19:00 | 0.99562 | 0 |  | 1.5 |  | 100
2017-08-02 | 19:05 | 1.0221 | 0 |  | 1.5
2017-08-02 | 19:10 | 1.0229 | 0 |  | 1.5
2017-08-02 | 19:15 | 1.0214 | 0 | 0 | 1.5 | 25
2017-08-02 | 19:15 | 1.0214 | 0 |  | 1.5 |  | 100
2017-08-02 | 19:20 | 0.99172 | 0 |  | 1.5
2017-08-02 | 19:25 | 1.037 | 0 |  | 1.5
2017-08-02 | 19:30 | 1.0416 | 0 | 0 | 1.5 | 25
2017-08-02 | 19:30 | 1.0416 | 0 |  | 1.5 |  | 100
2017-08-02 | 19:35 | 1.0206 | 0 |  | 1.5
2017-08-02 | 19:40 | 1.0136 | 0 |  | 1.5
2017-08-02 | 19:45 | 1.0206 | 0 | 0 | 1.5 | 25
2017-08-02 | 19:45 | 1.0206 | 0 |  | 1.5 |  | 100
2017-08-02 | 19:50 | 1.0097 | 0 |  | 1.5
2017-08-02 | 19:55 | 1.0182 | 0 |  | 1.5
2017-08-02 | 20:00 | 1.0323 | 0 | 0 | 1.5 | 25
2017-08-02 | 20:00 | 1.0323 | 0 |  | 1.5 |  | 100
2017-08-02 | 20:05 | 1.0307 | 0 |  | 1.5
2017-08-02 | 20:10 | 1.012 | 0 |  | 1.5
2017-08-02 | 20:15 | 1.0315 | 0 | 0 | 1.5 | 25
2017-08-02 | 20:15 | 1.0315 | 0 |  | 1.5 |  | 100
2017-08-02 | 20:20 | 1.044 | 0 |  | 1.5
2017-08-02 | 20:25 | 1.0128 | 0 |  | 1.5
2017-08-02 | 20:30 | 1.0471 | 0 | 0 | 1.5 | 25
2017-08-02 | 20:30 | 1.0471 | 0 |  | 1.5 |  | 100
2017-08-02 | 20:35 | 1.0104 | 0 |  | 1.5
2017-08-02 | 20:40 | 1.0354 | 0 |  | 1.5
2017-08-02 | 20:45 | 1.0385 | 0 | 0 | 1.5 | 25
2017-08-02 | 20:45 | 1.0385 | 0 |  | 1.5 |  | 100
2017-08-02 | 20:50 | 1.0307 | 0 |  | 1.5
2017-08-02 | 20:55 | 1.0432 | 0 |  | 1.5
2017-08-02 | 21:00 | 1.058 | 0 | 0 | 1.5 | 25
2017-08-02 | 21:00 | 1.058 | 0 |  | 1.5 |  | 0
2017-08-02 | 21:05 | -0.10184 | 0 |  | 1.5
2017-08-02 | 21:10 | -0.10106 | 0 |  | 1.5
2017-08-02 | 21:15 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 21:15 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 21:20 | -0.10106 | 0 |  | 1.5
2017-08-02 | 21:25 | -0.10106 | 0 |  | 1.5
2017-08-02 | 21:30 | -0.10262 | 0 | 0 | 1.5 | 0
2017-08-02 | 21:30 | -0.10262 | 0 |  | 1.5 |  | 0
2017-08-02 | 21:35 | -0.10106 | 0 |  | 1.5
2017-08-02 | 21:40 | -0.10106 | 0 |  | 1.5
2017-08-02 | 21:45 | -0.10184 | 0 | 0 | 1.5 | 0
2017-08-02 | 21:45 | -0.10184 | 0 |  | 1.5 |  | 0
2017-08-02 | 21:50 | -0.10106 | 0 |  | 1.5
2017-08-02 | 21:55 | -0.10184 | 0 |  | 1.5
2017-08-02 | 22:00 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 22:00 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 22:05 | -0.10184 | 0 |  | 1.5
2017-08-02 | 22:10 | -0.10106 | 0 |  | 1.5
2017-08-02 | 22:15 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 22:15 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 22:20 | -0.10106 | 0 |  | 1.5
2017-08-02 | 22:25 | -0.10106 | 0 |  | 1.5
2017-08-02 | 22:30 | -0.10262 | 0 | 0 | 1.5 | 0
2017-08-02 | 22:30 | -0.10262 | 0 |  | 1.5 |  | 0
2017-08-02 | 22:35 | -0.10106 | 0 |  | 1.5
2017-08-02 | 22:40 | -0.10106 | 0 |  | 1.5
2017-08-02 | 22:45 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 22:45 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 22:50 | -0.10184 | 0 |  | 1.5
2017-08-02 | 22:55 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:00 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 23:00 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 23:05 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:10 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:15 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 23:15 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 23:20 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:25 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:30 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 23:30 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 23:35 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:40 | -0.10028 | 0 |  | 1.5
2017-08-02 | 23:45 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-02 | 23:45 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-02 | 23:50 | -0.10106 | 0 |  | 1.5
2017-08-02 | 23:55 | -0.10106 | 0 |  | 1.5
2017-08-03 | 0:00 | -0.10106 | 0 | 0 | 1.5 | 0
2017-08-03 | 0:00 | -0.10106 | 0 |  | 1.5 |  | 0
2017-08-03 | 0:05 | -0.10106 | 0 |  | 1.5
2017-08-03 | 0:10 | -0.10106 | 0 |  | 1.5
2017-08-03 | 0:15 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 0:20 | -0.10184 | 0 |  | 1.5
2017-08-03 | 0:25 | -0.10106 | 0 |  | 1.5
2017-08-03 | 0:30 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 0:35 | -0.10106 | 0 |  | 1.5
2017-08-03 | 0:40 | -0.10184 | 0 |  | 1.5
2017-08-03 | 0:45 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 0:50 | -0.10106 | 0 |  | 1.5
2017-08-03 | 0:55 | -0.10106 | 0 |  | 1.5
2017-08-03 | 1:00 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 1:05 | -0.10184 | 0 |  | 1.5
2017-08-03 | 1:10 | -0.10184 | 0 |  | 1.5
2017-08-03 | 1:15 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 1:20 | -0.10418 | 0 |  | 1.5
2017-08-03 | 1:25 | -0.10418 | 0 |  | 1.5
2017-08-03 | 1:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 1:35 | -0.10418 | 0 |  | 1.5
2017-08-03 | 1:40 | -0.10418 | 0 |  | 1.5
2017-08-03 | 1:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 1:50 | -0.10418 | 0 |  | 1.5
2017-08-03 | 1:55 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 2:05 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:10 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 2:20 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:25 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 2:35 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:40 | -0.1034 | 0 |  | 1.5
2017-08-03 | 2:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 2:50 | -0.10418 | 0 |  | 1.5
2017-08-03 | 2:55 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 3:05 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:10 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 3:20 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:25 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 3:35 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:40 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 3:50 | -0.10418 | 0 |  | 1.5
2017-08-03 | 3:55 | -0.10418 | 0 |  | 1.5
2017-08-03 | 4:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 4:05 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:10 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 4:20 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:25 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 4:35 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:40 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 4:50 | -0.10496 | 0 |  | 1.5
2017-08-03 | 4:55 | -0.10496 | 0 |  | 1.5
2017-08-03 | 5:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 25
2017-08-03 | 5:05 | 1.122 | 0 |  | 1.5
2017-08-03 | 5:10 | 1.3373 | 0 |  | 1.5
2017-08-03 | 5:15 | 1.3326 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 5:20 | 1.3154 | 0 |  | 1.5
2017-08-03 | 5:25 | 1.2546 | 0 |  | 1.5
2017-08-03 | 5:30 | 1.2195 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 5:35 | 1.1937 | 0 |  | 1.5
2017-08-03 | 5:40 | 1.1891 | 0 |  | 1.5
2017-08-03 | 5:45 | 1.2281 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 5:50 | 1.2281 | 0 |  | 1.5
2017-08-03 | 5:55 | 1.2717 | 0 |  | 1.5
2017-08-03 | 6:00 | 1.2242 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 6:05 | 1.2694 | 0 |  | 1.5
2017-08-03 | 6:10 | 1.3068 | 0 |  | 1.5
2017-08-03 | 6:15 | 1.2842 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 6:20 | 1.2764 | 0 |  | 1.5
2017-08-03 | 6:25 | 1.2608 | 0 |  | 1.5
2017-08-03 | 6:30 | 1.3458 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 6:35 | 1.3887 | 0 |  | 1.5
2017-08-03 | 6:40 | 1.4667 | 0 |  | 1.5
2017-08-03 | 6:45 | 1.5471 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 6:50 | 1.6391 | 0 |  | 1.5
2017-08-03 | 6:55 | 1.6937 | 0 |  | 1.5
2017-08-03 | 7:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 99.8994
2017-08-03 | 7:05 | 1.8271 | 0 |  | 1.5
2017-08-03 | 7:10 | 1.8474 | 0 |  | 1.5
2017-08-03 | 7:15 | 1.8575 | 0 | 0 | 1.5 | 0 | 97.7285
2017-08-03 | 7:20 | 1.9199 | 0 |  | 1.5
2017-08-03 | 7:25 | 1.9145 | 0 |  | 1.5
2017-08-03 | 7:30 | 1.9121 | 0 | 0 | 1.5 | 0 | 93.43
2017-08-03 | 7:35 | 1.8918 | 0 |  | 1.5
2017-08-03 | 7:40 | 1.8669 | 0 |  | 1.5
2017-08-03 | 7:45 | 1.8684 | 0 | 0 | 1.5 | 0 | 90.0232
2017-08-03 | 7:50 | 1.8006 | 0 |  | 1.5
2017-08-03 | 7:55 | 1.8014 | 0 |  | 1.5
2017-08-03 | 8:00 | 1.8411 | 0 | 0 | 1.5 | 0 | 87.9144
2017-08-03 | 8:05 | 1.8131 | 0 |  | 1.5
2017-08-03 | 8:10 | 1.785 | 0 |  | 1.5
2017-08-03 | 8:15 | 1.7335 | 0 | 0 | 1.5 | 0 | 86.9547
2017-08-03 | 8:20 | 1.7366 | 0 |  | 1.5
2017-08-03 | 8:25 | 1.6656 | 0 |  | 1.5
2017-08-03 | 8:30 | 1.6625 | 0 | 0 | 1.5 | 0 | 88.5465
2017-08-03 | 8:35 | 1.7374 | 0 |  | 1.5
2017-08-03 | 8:40 | 1.7733 | 0 |  | 1.5
2017-08-03 | 8:45 | 1.7655 | 0 | 0 | 1.5 | 0 | 88.5243
2017-08-03 | 8:50 | 1.7546 | 0 |  | 1.5
2017-08-03 | 8:55 | 1.7421 | 0 |  | 1.5
2017-08-03 | 9:00 | 1.7444 | 0 | 0 | 1.5 | 0 | 88.5565
2017-08-03 | 9:05 | 1.7374 | 0 |  | 1.5
2017-08-03 | 9:10 | 1.7538 | 0 |  | 1.5
2017-08-03 | 9:15 | 1.7655 | 0 | 0 | 1.5 | 0 | 88.6945
2017-08-03 | 9:20 | 1.7475 | 0 |  | 1.5
2017-08-03 | 9:25 | 1.7429 | 0 |  | 1.5
2017-08-03 | 9:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 88.7579
2017-08-03 | 9:35 | 1.7351 | 0 |  | 1.5
2017-08-03 | 9:40 | 1.7522 | 0 |  | 1.5
2017-08-03 | 9:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 88.5084
2017-08-03 | 9:50 | 1.7522 | 0 |  | 1.5
2017-08-03 | 9:55 | 1.753 | 0 |  | 1.5
2017-08-03 | 10:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 88.5299
2017-08-03 | 10:05 | 1.7319 | 0 |  | 1.5
2017-08-03 | 10:10 | 1.7085 | 0 |  | 1.5
2017-08-03 | 10:15 | 1.6992 | 0 | 0 | 1.5 | 0 | 89.1302
2017-08-03 | 10:20 | 1.7444 | 0 |  | 1.5
2017-08-03 | 10:25 | 1.7202 | 0 |  | 1.5
2017-08-03 | 10:30 | 1.728 | 0 | 0 | 1.5 | 0 | 89.5999
2017-08-03 | 10:35 | 1.7296 | 0 |  | 1.5
2017-08-03 | 10:40 | 1.7663 | 0 |  | 1.5
2017-08-03 | 10:45 | 1.7304 | 0 | 0 | 1.5 | 0 | 89.9124
2017-08-03 | 10:50 | 1.8021 | 0 |  | 1.5
2017-08-03 | 10:55 | 1.7538 | 0 |  | 1.5
2017-08-03 | 11:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 89.6441
2017-08-03 | 11:05 | 1.7117 | 0 |  | 1.5
2017-08-03 | 11:10 | 1.7085 | 0 |  | 1.5
2017-08-03 | 11:15 | 1.7078 | 0 | 0 | 1.5 | 0 | 90.512
2017-08-03 | 11:20 | 1.7062 | 0 |  | 1.5
2017-08-03 | 11:25 | 1.7436 | 0 |  | 1.5
2017-08-03 | 11:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 91.0523
2017-08-03 | 11:35 | 1.7631 | 0 |  | 1.5
2017-08-03 | 11:40 | 1.721 | 0 |  | 1.5
2017-08-03 | 11:45 | 1.6922 | 0 | 0 | 1.5 | 0 | 91.7476
2017-08-03 | 11:50 | 1.6844 | 0 |  | 1.5
2017-08-03 | 11:55 | 1.682 | 0 |  | 1.5
2017-08-03 | 12:00 | 1.6734 | 0 | 0 | 1.5 | 0 | 93.3439
2017-08-03 | 12:05 | 1.739 | 0 |  | 1.5
2017-08-03 | 12:10 | 1.7452 | 0 |  | 1.5
2017-08-03 | 12:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 93.5774
2017-08-03 | 12:20 | 1.7218 | 0 |  | 1.5
2017-08-03 | 12:25 | 1.7327 | 0 |  | 1.5
2017-08-03 | 12:30 | 1.7163 | 0 | 0 | 1.5 | 0 | 94.0438
2017-08-03 | 12:35 | 1.721 | 0 |  | 1.5
2017-08-03 | 12:40 | 1.7234 | 0 |  | 1.5
2017-08-03 | 12:45 | 1.76 | 0 | 0 | 1.5 | 0 | 94.3516
2017-08-03 | 12:50 | 1.7257 | 0 |  | 1.5
2017-08-03 | 12:55 | 1.7234 | 0 |  | 1.5
2017-08-03 | 13:00 | 1.739 | 0 | 0 | 1.5 | 0 | 94.6309
2017-08-03 | 13:05 | 1.7343 | 0 |  | 1.5
2017-08-03 | 13:10 | 1.6945 | 0 |  | 1.5
2017-08-03 | 13:15 | 1.7234 | 0 | 0 | 1.5 | 0 | 95.6133
2017-08-03 | 13:20 | 1.6992 | 0 |  | 1.5
2017-08-03 | 13:25 | 1.6953 | 0 |  | 1.5
2017-08-03 | 13:30 | 1.6992 | 0 | 0 | 1.5 | 0 | 96.77
2017-08-03 | 13:35 | 1.6953 | 0 |  | 1.5
2017-08-03 | 13:40 | 1.7046 | 0 |  | 1.5
2017-08-03 | 13:45 | 1.6914 | 0 | 0 | 1.5 | 0 | 98.2361
2017-08-03 | 13:50 | 1.7163 | 0 |  | 1.5
2017-08-03 | 13:55 | 1.6812 | 0 |  | 1.5
2017-08-03 | 14:00 | 1.6797 | 0 | 0 | 1.5 | 0 | 99.9399
2017-08-03 | 14:05 | 1.6984 | 0 |  | 1.5
2017-08-03 | 14:10 | 1.6711 | 0 |  | 1.5
2017-08-03 | 14:15 | 1.6867 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 14:20 | 1.6313 | 0 |  | 1.5
2017-08-03 | 14:25 | 1.636 | 0 |  | 1.5
2017-08-03 | 14:30 | 1.6134 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 14:35 | 1.6157 | 0 |  | 1.5
2017-08-03 | 14:40 | 1.5962 | 0 |  | 1.5
2017-08-03 | 14:45 | 1.5486 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 14:50 | 1.5057 | 0 |  | 1.5
2017-08-03 | 14:55 | 1.5065 | 0 |  | 1.5
2017-08-03 | 15:00 | 1.494 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 15:05 | 1.4972 | 0 |  | 1.5
2017-08-03 | 15:10 | 1.5026 | 0 |  | 1.5
2017-08-03 | 15:15 | 1.4823 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 15:20 | 1.5206 | 0 |  | 1.5
2017-08-03 | 15:25 | 1.5026 | 0 |  | 1.5
2017-08-03 | 15:30 | 1.5455 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 15:35 | 1.5354 | 0 |  | 1.5
2017-08-03 | 15:40 | 1.4917 | 0 |  | 1.5
2017-08-03 | 15:45 | 1.5291 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 15:50 | 1.5245 | 0 |  | 1.5
2017-08-03 | 15:55 | 1.519 | 0 |  | 1.5
2017-08-03 | 16:00 | 1.5354 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 16:05 | 1.5221 | 0 |  | 1.5
2017-08-03 | 16:10 | 1.5463 | 0 |  | 1.5
2017-08-03 | 16:15 | 1.5346 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 16:20 | 1.551 | 0 |  | 1.5
2017-08-03 | 16:25 | 1.5572 | 0 |  | 1.5
2017-08-03 | 16:30 | 1.6048 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 16:35 | 1.5525 | 0 |  | 1.5
2017-08-03 | 16:40 | 1.5736 | 0 |  | 1.5
2017-08-03 | 16:45 | 1.5502 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 16:50 | 1.5853 | 0 |  | 1.5
2017-08-03 | 16:55 | 1.604 | 0 |  | 1.5
2017-08-03 | 17:00 | 1.604 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 17:05 | 1.59 | 0 |  | 1.5
2017-08-03 | 17:10 | 1.6204 | 0 |  | 1.5
2017-08-03 | 17:15 | 1.6071 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 17:20 | 1.622 | 0 |  | 1.5
2017-08-03 | 17:25 | 1.6703 | 0 |  | 1.5
2017-08-03 | 17:30 | 1.6781 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 17:35 | 1.7023 | 0 |  | 1.5
2017-08-03 | 17:40 | 1.6906 | 0 |  | 1.5
2017-08-03 | 17:45 | 1.7117 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 17:50 | 1.6976 | 0 |  | 1.5
2017-08-03 | 17:55 | 1.7265 | 0 |  | 1.5
2017-08-03 | 18:00 | 1.7234 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 18:05 | 1.7561 | 0 |  | 1.5
2017-08-03 | 18:10 | 1.7491 | 0 |  | 1.5
2017-08-03 | 18:15 | 1.6812 | 0 | 0 | 1.5 | 0 | 100
2017-08-03 | 18:20 | 1.7475 | 0 |  | 1.5
2017-08-03 | 18:25 | 1.76 | 0 |  | 1.5
2017-08-03 | 18:30 | 1.7374 | 0 | 0 | 1.5 | 0 | 99.9526
2017-08-03 | 18:35 | 1.8092 | 0 |  | 1.5
2017-08-03 | 18:40 | 1.7772 | 0 |  | 1.5
2017-08-03 | 18:45 | 1.7873 | 0 | 0 | 1.5 | 0 | 99.4281
2017-08-03 | 18:50 | 1.7436 | 0 |  | 1.5
2017-08-03 | 18:55 | 1.7865 | 0 |  | 1.5
2017-08-03 | 19:00 | 1.785 | 0 | 0 | 1.5 | 0 | 98.7502
2017-08-03 | 19:05 | 1.7967 | 0 |  | 1.5
2017-08-03 | 19:10 | 1.8154 | 0 |  | 1.5
2017-08-03 | 19:15 | 1.7982 | 0 | 0 | 1.5 | 0 | 97.3512
2017-08-03 | 19:20 | 1.8053 | 0 |  | 1.5
2017-08-03 | 19:25 | 1.8107 | 0 |  | 1.5
2017-08-03 | 19:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 96.0896
2017-08-03 | 19:35 | 1.8201 | 0 |  | 1.5
2017-08-03 | 19:40 | 1.7928 | 0 |  | 1.5
2017-08-03 | 19:45 | 1.7834 | 0 | 0 | 1.5 | 0 | 95.013
2017-08-03 | 19:50 | 1.8138 | 0 |  | 1.5
2017-08-03 | 19:55 | 1.7842 | 0 |  | 1.5
2017-08-03 | 20:00 | 1.7787 | 0 | 0 | 1.5 | 0 | 93.8804
2017-08-03 | 20:05 | 1.7686 | 0 |  | 1.5
2017-08-03 | 20:10 | 1.7795 | 0 |  | 1.5
2017-08-03 | 20:15 | 1.7897 | 0 | 0 | 1.5 | 0 | 93.0208
2017-08-03 | 20:20 | 1.7717 | 0 |  | 1.5
2017-08-03 | 20:25 | 1.8162 | 0 |  | 1.5
2017-08-03 | 20:30 | 1.8131 | 0 | 0 | 1.5 | 0 | 91.766
2017-08-03 | 20:35 | 1.8255 | 0 |  | 1.5
2017-08-03 | 20:40 | 1.8224 | 0 |  | 1.5
2017-08-03 | 20:45 | 1.7904 | 0 | 0 | 1.5 | 0 | 90.2224
2017-08-03 | 20:50 | 1.7748 | 0 |  | 1.5
2017-08-03 | 20:55 | 1.7725 | 0 |  | 1.5
2017-08-03 | 21:00 | 1.767 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 21:05 | -0.10184 | 0 |  | 1.5
2017-08-03 | 21:10 | -0.10262 | 0 |  | 1.5
2017-08-03 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 21:20 | -0.1034 | 0 |  | 1.5
2017-08-03 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-03 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-03 | 21:40 | -0.10418 | 0 |  | 1.5
2017-08-03 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 21:50 | -0.10418 | 0 |  | 1.5
2017-08-03 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-03 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 22:05 | -0.10418 | 0 |  | 1.5
2017-08-03 | 22:10 | -0.10418 | 0 |  | 1.5
2017-08-03 | 22:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 22:20 | -0.10418 | 0 |  | 1.5
2017-08-03 | 22:25 | -0.10418 | 0 |  | 1.5
2017-08-03 | 22:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 22:35 | -0.10418 | 0 |  | 1.5
2017-08-03 | 22:40 | -0.10418 | 0 |  | 1.5
2017-08-03 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-03 | 22:55 | -0.1034 | 0 |  | 1.5
2017-08-03 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 23:05 | -0.1034 | 0 |  | 1.5
2017-08-03 | 23:10 | -0.1034 | 0 |  | 1.5
2017-08-03 | 23:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 23:20 | -0.1034 | 0 |  | 1.5
2017-08-03 | 23:25 | -0.1034 | 0 |  | 1.5
2017-08-03 | 23:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 23:35 | -0.10262 | 0 |  | 1.5
2017-08-03 | 23:40 | -0.10262 | 0 |  | 1.5
2017-08-03 | 23:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-03 | 23:50 | -0.10184 | 0 |  | 1.5
2017-08-03 | 23:55 | -0.10184 | 0 |  | 1.5
2017-08-04 | 0:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 0:05 | -0.10262 | 0 |  | 1.5
2017-08-04 | 0:10 | -0.10262 | 0 |  | 1.5
2017-08-04 | 0:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 0:20 | -0.10262 | 0 |  | 1.5
2017-08-04 | 0:25 | -0.10184 | 0 |  | 1.5
2017-08-04 | 0:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 0:35 | -0.10262 | 0 |  | 1.5
2017-08-04 | 0:40 | -0.10262 | 0 |  | 1.5
2017-08-04 | 0:45 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 0:50 | -0.10262 | 0 |  | 1.5
2017-08-04 | 0:55 | -0.10262 | 0 |  | 1.5
2017-08-04 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 1:05 | -0.10262 | 0 |  | 1.5
2017-08-04 | 1:10 | -0.10262 | 0 |  | 1.5
2017-08-04 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 1:20 | -0.10496 | 0 |  | 1.5
2017-08-04 | 1:25 | -0.1073 | 0 |  | 1.5
2017-08-04 | 1:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 1:35 | -0.10496 | 0 |  | 1.5
2017-08-04 | 1:40 | -0.10496 | 0 |  | 1.5
2017-08-04 | 1:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 1:50 | -0.10496 | 0 |  | 1.5
2017-08-04 | 1:55 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 2:05 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:10 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 2:20 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:25 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 2:35 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:40 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 2:50 | -0.10496 | 0 |  | 1.5
2017-08-04 | 2:55 | -0.10496 | 0 |  | 1.5
2017-08-04 | 3:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 3:05 | -0.10496 | 0 |  | 1.5
2017-08-04 | 3:10 | -0.10496 | 0 |  | 1.5
2017-08-04 | 3:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 3:20 | -0.10496 | 0 |  | 1.5
2017-08-04 | 3:25 | -0.10496 | 0 |  | 1.5
2017-08-04 | 3:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 3:35 | -0.10574 | 0 |  | 1.5
2017-08-04 | 3:40 | -0.10496 | 0 |  | 1.5
2017-08-04 | 3:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 3:50 | -0.10574 | 0 |  | 1.5
2017-08-04 | 3:55 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 4:05 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:10 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 4:20 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:25 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 4:35 | -0.10652 | 0 |  | 1.5
2017-08-04 | 4:40 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 4:50 | -0.10574 | 0 |  | 1.5
2017-08-04 | 4:55 | -0.10574 | 0 |  | 1.5
2017-08-04 | 5:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 5:05 | 1.2218 | 0 |  | 1.5
2017-08-04 | 5:10 | 1.5471 | 0 |  | 1.5
2017-08-04 | 5:15 | 1.5588 | 0 | 0 | 1.5 | 0 | 100
2017-08-04 | 5:20 | 1.4839 | 0 |  | 1.5
2017-08-04 | 5:25 | 1.5081 | 0 |  | 1.5
2017-08-04 | 5:30 | 1.5549 | 0 | 0 | 1.5 | 0 | 100
2017-08-04 | 5:35 | 1.5775 | 0 |  | 1.5
2017-08-04 | 5:40 | 1.6649 | 0 |  | 1.5
2017-08-04 | 5:45 | 1.7507 | 0 | 0 | 1.5 | 0 | 99.9684
2017-08-04 | 5:50 | 1.8131 | 0 |  | 1.5
2017-08-04 | 5:55 | 1.8599 | 0 |  | 1.5
2017-08-04 | 6:00 | 1.8879 | 0 | 0 | 1.5 | 0 | 97.2587
2017-08-04 | 6:05 | 1.9207 | 0 |  | 1.5
2017-08-04 | 6:10 | 1.9262 | 0 |  | 1.5
2017-08-04 | 6:15 | 1.9386 | 0 | 0 | 1.5 | 0 | 92.4246
2017-08-04 | 6:20 | 1.9074 | 0 |  | 1.5
2017-08-04 | 6:25 | 1.8973 | 0 |  | 1.5
2017-08-04 | 6:30 | 1.8653 | 0 | 0 | 1.5 | 0 | 88.0617
2017-08-04 | 6:32 |  |  | 0
2017-08-04 | 6:35 | 2.0065 | 3.3485 |  | 10
2017-08-04 | 6:40 | 1.8903 | 8.2247 |  | 10
2017-08-04 | 6:45 | 1.7413 | 8.9572 | 1 | 10 | 92.1 | 84.1519
2017-08-04 | 6:50 | 1.7733 | 8.0479 |  | 10
2017-08-04 | 6:55 | 1.7943 | 7.3886 |  | 10
2017-08-04 | 7:00 | 1.7842 | 7.116 | 1 | 10 | 74.6591 | 83.1078
2017-08-04 | 7:05 | 1.7951 | 7.1372 |  | 10
2017-08-04 | 7:10 | 1.7546 | 7.1905 |  | 10
2017-08-04 | 7:15 | 1.8131 | 6.9419 | 1 | 10 | 72.4363 | 82.0644
2017-08-04 | 7:20 | 1.7787 | 6.5462 |  | 10
2017-08-04 | 7:25 | 1.7795 | 6.5775 |  | 10
2017-08-04 | 7:30 | 1.7795 | 6.1712 | 1 | 10 | 64.7371 | 81.2615
2017-08-04 | 7:35 | 1.7787 | 6.1096 |  | 10
2017-08-04 | 7:40 | 1.7881 | 6.2475 |  | 10
2017-08-04 | 7:45 | 1.8045 | 4.4426 | 1 | 10 | 49.6595 | 80.5072
2017-08-04 | 7:50 | 1.8396 | 1.6923 |  | 10
2017-08-04 | 7:52 |  |  | 0
2017-08-04 | 7:55 | 1.6298 | 0 |  | 1.5
2017-08-04 | 8:00 | 1.6805 | 0 | 0 | 1.5 | 25 | 80.965
2017-08-04 | 8:05 | 1.7179 | 0 |  | 1.5
2017-08-04 | 8:10 | 1.7382 | 0 |  | 1.5
2017-08-04 | 8:15 | 1.7202 | 0 | 0 | 1.5 | 25 | 81.868
2017-08-04 | 8:20 | 1.728 | 0 |  | 1.5
2017-08-04 | 8:25 | 1.7241 | 0 |  | 1.5
2017-08-04 | 8:30 | 1.7865 | 0 | 0 | 1.5 | 25 | 82.0988
2017-08-04 | 8:35 | 1.7631 | 0 |  | 1.5
2017-08-04 | 8:40 | 1.7538 | 0 |  | 1.5
2017-08-04 | 8:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 82.0827
2017-08-04 | 8:50 | 1.7249 | 0 |  | 1.5
2017-08-04 | 8:55 | 1.7335 | 0 |  | 1.5
2017-08-04 | 9:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 82.4124
2017-08-04 | 9:05 | 1.7397 | 0 |  | 1.5
2017-08-04 | 9:10 | 1.7101 | 0 |  | 1.5
2017-08-04 | 9:15 | 1.7093 | 0 | 0 | 1.5 | 25 | 82.8439
2017-08-04 | 9:20 | 1.7483 | 0 |  | 1.5
2017-08-04 | 9:25 | 1.767 | 0 |  | 1.5
2017-08-04 | 9:30 | 1.739 | 0 | 0 | 1.5 | 25 | 83.0051
2017-08-04 | 9:35 | 1.7452 | 0 |  | 1.5
2017-08-04 | 9:40 | 1.7514 | 0 |  | 1.5
2017-08-04 | 9:45 | 1.7374 | 0 | 0 | 1.5 | 25 | 83.0246
2017-08-04 | 9:50 | 1.721 | 0 |  | 1.5
2017-08-04 | 9:55 | 1.7491 | 0 |  | 1.5
2017-08-04 | 10:00 | 1.7397 | 0 | 0 | 1.5 | 25 | 83.2095
2017-08-04 | 10:05 | 1.7078 | 0 |  | 1.5
2017-08-04 | 10:10 | 1.6758 | 0 |  | 1.5
2017-08-04 | 10:15 | 1.7101 | 0 | 0 | 1.5 | 25 | 84.5444
2017-08-04 | 10:20 | 1.7468 | 0 |  | 1.5
2017-08-04 | 10:25 | 1.753 | 0 |  | 1.5
2017-08-04 | 10:30 | 1.7553 | 0 | 0 | 1.5 | 25 | 84.785
2017-08-04 | 10:35 | 1.7273 | 0 |  | 1.5
2017-08-04 | 10:40 | 1.7429 | 0 |  | 1.5
2017-08-04 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 25 | 84.918
2017-08-04 | 10:50 | 1.7826 | 0 |  | 1.5
2017-08-04 | 10:55 | 1.7639 | 0 |  | 1.5
2017-08-04 | 11:00 | 1.7312 | 0 | 0 | 1.5 | 25 | 84.8353
2017-08-04 | 11:05 | 1.7468 | 0 |  | 1.5
2017-08-04 | 11:10 | 1.7546 | 0 |  | 1.5
2017-08-04 | 11:15 | 1.721 | 0 | 0 | 1.5 | 25 | 84.8446
2017-08-04 | 11:20 | 1.7117 | 0 |  | 1.5
2017-08-04 | 11:25 | 1.7241 | 0 |  | 1.5
2017-08-04 | 11:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 85.2903
2017-08-04 | 11:35 | 1.6961 | 0 |  | 1.5
2017-08-04 | 11:40 | 1.6875 | 0 |  | 1.5
2017-08-04 | 11:45 | 1.6664 | 0 | 0 | 1.5 | 25 | 86.6584
2017-08-04 | 11:50 | 1.714 | 0 |  | 1.5
2017-08-04 | 11:55 | 1.6992 | 0 |  | 1.5
2017-08-04 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 25 | 87.7192
2017-08-04 | 12:05 | 1.6656 | 0 |  | 1.5
2017-08-04 | 12:10 | 1.7046 | 0 |  | 1.5
2017-08-04 | 12:15 | 1.728 | 0 | 0 | 1.5 | 25 | 89.5441
2017-08-04 | 12:20 | 1.7187 | 0 |  | 1.5
2017-08-04 | 12:25 | 1.7405 | 0 |  | 1.5
2017-08-04 | 12:30 | 1.7647 | 0 | 0 | 1.5 | 25 | 90.3187
2017-08-04 | 12:35 | 1.7569 | 0 |  | 1.5
2017-08-04 | 12:40 | 1.7257 | 0 |  | 1.5
2017-08-04 | 12:45 | 1.7358 | 0 | 0 | 1.5 | 25 | 90.8103
2017-08-04 | 12:50 | 1.7241 | 0 |  | 1.5
2017-08-04 | 12:55 | 1.7382 | 0 |  | 1.5
2017-08-04 | 13:00 | 1.7546 | 0 | 0 | 1.5 | 25 | 91.2046
2017-08-04 | 13:05 | 1.7202 | 0 |  | 1.5
2017-08-04 | 13:10 | 1.7296 | 0 |  | 1.5
2017-08-04 | 13:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 91.5823
2017-08-04 | 13:20 | 1.8084 | 0 |  | 1.5
2017-08-04 | 13:25 | 1.7663 | 0 |  | 1.5
2017-08-04 | 13:30 | 1.7647 | 0 | 0 | 1.5 | 25 | 90.6274
2017-08-04 | 13:35 | 1.7366 | 0 |  | 1.5
2017-08-04 | 13:40 | 1.7117 | 0 |  | 1.5
2017-08-04 | 13:45 | 1.7335 | 0 | 0 | 1.5 | 25 | 91.0444
2017-08-04 | 13:50 | 1.7234 | 0 |  | 1.5
2017-08-04 | 13:55 | 1.7507 | 0 |  | 1.5
2017-08-04 | 14:00 | 1.7592 | 0 | 0 | 1.5 | 25 | 91.0399
2017-08-04 | 14:05 | 1.7234 | 0 |  | 1.5
2017-08-04 | 14:10 | 1.7795 | 0 |  | 1.5
2017-08-04 | 14:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 91.3092
2017-08-04 | 14:20 | 1.7873 | 0 |  | 1.5
2017-08-04 | 14:25 | 1.7592 | 0 |  | 1.5
2017-08-04 | 14:30 | 1.7616 | 0 | 0 | 1.5 | 25 | 91.0303
2017-08-04 | 14:35 | 1.7522 | 0 |  | 1.5
2017-08-04 | 14:40 | 1.7499 | 0 |  | 1.5
2017-08-04 | 14:45 | 1.7475 | 0 | 0 | 1.5 | 25 | 90.9119
2017-08-04 | 14:50 | 1.746 | 0 |  | 1.5
2017-08-04 | 14:55 | 1.7109 | 0 |  | 1.5
2017-08-04 | 15:00 | 1.7631 | 0 | 0 | 1.5 | 25 | 90.7855
2017-08-04 | 15:05 | 1.7616 | 0 |  | 1.5
2017-08-04 | 15:10 | 1.746 | 0 |  | 1.5
2017-08-04 | 15:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 90.6405
2017-08-04 | 15:20 | 1.7741 | 0 |  | 1.5
2017-08-04 | 15:25 | 1.7405 | 0 |  | 1.5
2017-08-04 | 15:30 | 1.7124 | 0 | 0 | 1.5 | 25 | 90.7599
2017-08-04 | 15:35 | 1.6961 | 0 |  | 1.5
2017-08-04 | 15:40 | 1.7078 | 0 |  | 1.5
2017-08-04 | 15:45 | 1.7296 | 0 | 0 | 1.5 | 25 | 91.2765
2017-08-04 | 15:50 | 1.7156 | 0 |  | 1.5
2017-08-04 | 15:55 | 1.6688 | 0 |  | 1.5
2017-08-04 | 16:00 | 1.7187 | 0 | 0 | 1.5 | 25 | 92.4038
2017-08-04 | 16:05 | 1.714 | 0 |  | 1.5
2017-08-04 | 16:10 | 1.6992 | 0 |  | 1.5
2017-08-04 | 16:15 | 1.7351 | 0 | 0 | 1.5 | 25 | 93.2213
2017-08-04 | 16:20 | 1.7475 | 0 |  | 1.5
2017-08-04 | 16:25 | 1.7499 | 0 |  | 1.5
2017-08-04 | 16:30 | 1.7702 | 0 | 0 | 1.5 | 25 | 92.9893
2017-08-04 | 16:35 | 1.767 | 0 |  | 1.5
2017-08-04 | 16:40 | 1.7858 | 0 |  | 1.5
2017-08-04 | 16:45 | 1.7795 | 0 | 0 | 1.5 | 25 | 92.2962
2017-08-04 | 16:50 | 1.76 | 0 |  | 1.5
2017-08-04 | 16:55 | 1.7756 | 0 |  | 1.5
2017-08-04 | 17:00 | 1.7865 | 0 | 0 | 1.5 | 25 | 91.4941
2017-08-04 | 17:05 | 1.753 | 0 |  | 1.5
2017-08-04 | 17:10 | 1.7686 | 0 |  | 1.5
2017-08-04 | 17:15 | 1.7647 | 0 | 0 | 1.5 | 25 | 90.9776
2017-08-04 | 17:20 | 1.7959 | 0 |  | 1.5
2017-08-04 | 17:25 | 1.8146 | 0 |  | 1.5
2017-08-04 | 17:30 | 1.7967 | 0 | 0 | 1.5 | 25 | 90.074
2017-08-04 | 17:35 | 1.7741 | 0 |  | 1.5
2017-08-04 | 17:40 | 1.799 | 0 |  | 1.5
2017-08-04 | 17:45 | 1.7756 | 0 | 0 | 1.5 | 25 | 89.0349
2017-08-04 | 17:50 | 1.785 | 0 |  | 1.5
2017-08-04 | 17:55 | 1.7725 | 0 |  | 1.5
2017-08-04 | 18:00 | 1.76 | 0 | 0 | 1.5 | 25 | 88.4061
2017-08-04 | 18:05 | 1.739 | 0 |  | 1.5
2017-08-04 | 18:10 | 1.7553 | 0 |  | 1.5
2017-08-04 | 18:15 | 1.7694 | 0 | 0 | 1.5 | 25 | 87.8927
2017-08-04 | 18:20 | 1.7741 | 0 |  | 1.5
2017-08-04 | 18:25 | 1.7717 | 0 |  | 1.5
2017-08-04 | 18:30 | 1.7678 | 0 | 0 | 1.5 | 25 | 87.2368
2017-08-04 | 18:35 | 1.7936 | 0 |  | 1.5
2017-08-04 | 18:40 | 1.7975 | 0 |  | 1.5
2017-08-04 | 18:45 | 1.778 | 0 | 0 | 1.5 | 25 | 86.5041
2017-08-04 | 18:50 | 1.7655 | 0 |  | 1.5
2017-08-04 | 18:55 | 1.7842 | 0 |  | 1.5
2017-08-04 | 19:00 | 1.7819 | 0 | 0 | 1.5 | 25 | 85.8374
2017-08-04 | 19:05 | 1.7834 | 0 |  | 1.5
2017-08-04 | 19:10 | 1.7686 | 0 |  | 1.5
2017-08-04 | 19:15 | 1.7756 | 0 | 0 | 1.5 | 25 | 85.1694
2017-08-04 | 19:20 | 1.7787 | 0 |  | 1.5
2017-08-04 | 19:25 | 1.7725 | 0 |  | 1.5
2017-08-04 | 19:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 84.5824
2017-08-04 | 19:35 | 1.7546 | 0 |  | 1.5
2017-08-04 | 19:40 | 1.7733 | 0 |  | 1.5
2017-08-04 | 19:45 | 1.7904 | 0 | 0 | 1.5 | 25 | 83.9806
2017-08-04 | 19:50 | 1.7647 | 0 |  | 1.5
2017-08-04 | 19:55 | 1.8123 | 0 |  | 1.5
2017-08-04 | 20:00 | 1.7725 | 0 | 0 | 1.5 | 25 | 83.1481
2017-08-04 | 20:05 | 1.7772 | 0 |  | 1.5
2017-08-04 | 20:10 | 1.7834 | 0 |  | 1.5
2017-08-04 | 20:15 | 1.7834 | 0 | 0 | 1.5 | 25 | 82.2217
2017-08-04 | 20:20 | 1.7912 | 0 |  | 1.5
2017-08-04 | 20:25 | 1.7655 | 0 |  | 1.5
2017-08-04 | 20:30 | 1.76 | 0 | 0 | 1.5 | 25 | 81.4052
2017-08-04 | 20:35 | 1.7397 | 0 |  | 1.5
2017-08-04 | 20:40 | 1.767 | 0 |  | 1.5
2017-08-04 | 20:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 81.0784
2017-08-04 | 20:50 | 1.728 | 0 |  | 1.5
2017-08-04 | 20:55 | 1.7335 | 0 |  | 1.5
2017-08-04 | 21:00 | 1.7592 | 0 | 0 | 1.5 | 25 | 81.024
2017-08-04 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-04 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-04 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-04 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-04 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 21:35 | -0.10496 | 0 |  | 1.5
2017-08-04 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-04 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-04 | 21:55 | -0.10574 | 0 |  | 1.5
2017-08-04 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-04 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-04 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-04 | 22:25 | -0.10574 | 0 |  | 1.5
2017-08-04 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-04 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-04 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-04 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-04 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 23:05 | -0.10574 | 0 |  | 1.5
2017-08-04 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-04 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-04 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-04 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-04 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-04 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-04 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-04 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-05 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-05 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-05 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 0:20 | -0.10496 | 0 |  | 1.5
2017-08-05 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-05 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-05 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-05 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-05 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-05 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-05 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-05 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 1:20 | -0.10808 | 0 |  | 1.5
2017-08-05 | 1:25 | -0.10808 | 0 |  | 1.5
2017-08-05 | 1:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-05 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-05 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 1:50 | -0.1073 | 0 |  | 1.5
2017-08-05 | 1:55 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:10 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:25 | -0.10808 | 0 |  | 1.5
2017-08-05 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:40 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-05 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-05 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 3:05 | -0.1073 | 0 |  | 1.5
2017-08-05 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-05 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-05 | 3:25 | -0.1073 | 0 |  | 1.5
2017-08-05 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 3:35 | -0.1073 | 0 |  | 1.5
2017-08-05 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-05 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-05 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-05 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 4:05 | -0.1073 | 0 |  | 1.5
2017-08-05 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-05 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-05 | 4:25 | -0.1073 | 0 |  | 1.5
2017-08-05 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-05 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-05 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-05 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-05 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 5:00 |  |  | 1
2017-08-05 | 5:05 | 2.0049 | 6.5084 |  | 10
2017-08-05 | 5:10 | 1.9652 | 10 |  | 10
2017-08-05 | 5:15 | 1.9488 | 10 | 1 | 10 | 100 | 94.2843
2017-08-05 | 5:20 | 1.9152 | 10 |  | 10
2017-08-05 | 5:25 | 1.9012 | 10 |  | 10
2017-08-05 | 5:30 | 1.9371 | 10 | 1 | 10 | 100 | 89.4741
2017-08-05 | 5:35 | 1.9199 | 9.9953 |  | 10
2017-08-05 | 5:40 | 1.8801 | 9.8814 |  | 10
2017-08-05 | 5:45 | 1.8723 | 9.5828 | 1 | 10 | 96.1838 | 85.8344
2017-08-05 | 5:50 | 1.8489 | 9.2901 |  | 10
2017-08-05 | 5:55 | 1.8497 | 9.0736 |  | 10
2017-08-05 | 6:00 | 1.8287 | 9.0392 | 1 | 10 | 90.7085 | 83.4
2017-08-05 | 6:05 | 1.7975 | 9.1159 |  | 10
2017-08-05 | 6:10 | 1.778 | 9.2369 |  | 10
2017-08-05 | 6:15 | 1.778 | 9.0656 | 1 | 10 | 91.0715 | 82.5069
2017-08-05 | 6:20 | 1.7585 | 8.9897 |  | 10
2017-08-05 | 6:25 | 1.7702 | 8.9438 |  | 10
2017-08-05 | 6:30 | 1.7561 | 8.9294 | 1 | 10 | 89.6454 | 81.9194
2017-08-05 | 6:35 | 1.7522 | 8.9612 |  | 10
2017-08-05 | 6:40 | 1.7343 | 8.8716 |  | 10
2017-08-05 | 6:45 | 1.7795 | 8.7984 | 1 | 10 | 88.4163 | 81.5692
2017-08-05 | 6:50 | 1.7842 | 8.8136 |  | 10
2017-08-05 | 6:55 | 1.7171 | 8.697 |  | 10
2017-08-05 | 7:00 | 1.76 | 8.5746 | 1 | 10 | 86.2316 | 81.1807
2017-08-05 | 7:05 | 1.7733 | 8.5794 |  | 10
2017-08-05 | 7:10 | 1.7452 | 8.4119 |  | 10
2017-08-05 | 7:15 | 1.7569 | 8.1993 | 1 | 10 | 82.6698 | 80.9214
2017-08-05 | 7:20 | 1.7585 | 8.1231 |  | 10
2017-08-05 | 7:25 | 1.746 | 8.1444 |  | 10
2017-08-05 | 7:30 | 1.7351 | 8.1078 | 1 | 10 | 81.6334 | 80.6409
2017-08-05 | 7:35 | 1.7764 | 8.0298 |  | 10
2017-08-05 | 7:40 | 1.7585 | 7.9408 |  | 10
2017-08-05 | 7:45 | 1.7561 | 7.8953 | 1 | 10 | 79.616 | 80.3331
2017-08-05 | 7:50 | 1.7561 | 7.7772 |  | 10
2017-08-05 | 7:55 | 1.7452 | 7.7373 |  | 10
2017-08-05 | 8:00 | 1.7631 | 7.6128 | 1 | 10 | 76.7822 | 80.0646
2017-08-05 | 8:05 | 1.7624 | 7.6843 |  | 10
2017-08-05 | 8:10 | 1.753 | 7.8175 |  | 10
2017-08-05 | 8:15 | 1.7616 | 7.8489 | 1 | 10 | 79.0874 | 80.036
2017-08-05 | 8:20 | 1.7491 | 7.7938 |  | 10
2017-08-05 | 8:25 | 1.7631 | 7.645 |  | 10
2017-08-05 | 8:30 | 1.7522 | 7.4412 | 1 | 10 | 75.2412 | 80.0568
2017-08-05 | 8:35 | 1.7475 | 7.2929 |  | 10
2017-08-05 | 8:40 | 1.753 | 7.2041 |  | 10
2017-08-05 | 8:45 | 1.7655 | 7.1191 | 1 | 10 | 72.0705 | 79.7722
2017-08-05 | 8:50 | 1.7585 | 7.0665 |  | 10
2017-08-05 | 8:55 | 1.7351 | 7.0294 |  | 10
2017-08-05 | 9:00 | 1.7304 | 6.9009 | 1 | 10 | 69.9215 | 79.6765
2017-08-05 | 9:05 | 1.7553 | 6.7973 |  | 10
2017-08-05 | 9:10 | 1.7436 | 6.7814 |  | 10
2017-08-05 | 9:15 | 1.7608 | 6.8075 | 1 | 10 | 69.0303 | 79.6542
2017-08-05 | 9:20 | 1.7592 | 6.8296 |  | 10
2017-08-05 | 9:25 | 1.8162 | 5.1297 |  | 10
2017-08-05 | 9:30 | 1.8146 | 2.7147 | 1 | 10 | 30.4536 | 78.6949
2017-08-05 | 9:35 | 1.7975 | 0.95006 |  | 10
2017-08-05 | 9:40 |  |  | 0
2017-08-05 | 9:40 | 1.7327 | 0 |  | 1.5
2017-08-05 | 9:45 | 1.6095 | 0 | 0 | 1.5 | 25 | 79.4166
2017-08-05 | 9:50 | 1.6695 | 0 |  | 1.5
2017-08-05 | 9:55 | 1.6914 | 0 |  | 1.5
2017-08-05 | 10:00 | 1.7304 | 0 | 0 | 1.5 | 25 | 81.093
2017-08-05 | 10:05 | 1.746 | 0 |  | 1.5
2017-08-05 | 10:10 | 1.7124 | 0 |  | 1.5
2017-08-05 | 10:15 | 1.7265 | 0 | 0 | 1.5 | 25 | 81.576
2017-08-05 | 10:20 | 1.7546 | 0 |  | 1.5
2017-08-05 | 10:25 | 1.7405 | 0 |  | 1.5
2017-08-05 | 10:30 | 1.746 | 0 | 0 | 1.5 | 25 | 81.6665
2017-08-05 | 10:35 | 1.7491 | 0 |  | 1.5
2017-08-05 | 10:40 | 1.7678 | 0 |  | 1.5
2017-08-05 | 10:45 | 1.7475 | 0 | 0 | 1.5 | 25 | 81.6928
2017-08-05 | 10:50 | 1.7468 | 0 |  | 1.5
2017-08-05 | 10:55 | 1.7288 | 0 |  | 1.5
2017-08-05 | 11:00 | 1.7561 | 0 | 0 | 1.5 | 25 | 81.9303
2017-08-05 | 11:05 | 1.7358 | 0 |  | 1.5
2017-08-05 | 11:10 | 1.7468 | 0 |  | 1.5
2017-08-05 | 11:15 | 1.7187 | 0 | 0 | 1.5 | 25 | 82.0743
2017-08-05 | 11:20 | 1.7741 | 0 |  | 1.5
2017-08-05 | 11:25 | 1.7546 | 0 |  | 1.5
2017-08-05 | 11:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 82.2727
2017-08-05 | 11:35 | 1.7468 | 0 |  | 1.5
2017-08-05 | 11:40 | 1.7132 | 0 |  | 1.5
2017-08-05 | 11:45 | 1.7358 | 0 | 0 | 1.5 | 25 | 82.7398
2017-08-05 | 11:50 | 1.7429 | 0 |  | 1.5
2017-08-05 | 11:55 | 1.7148 | 0 |  | 1.5
2017-08-05 | 12:00 | 1.7452 | 0 | 0 | 1.5 | 25 | 83.1373
2017-08-05 | 12:05 | 1.7351 | 0 |  | 1.5
2017-08-05 | 12:10 | 1.7319 | 0 |  | 1.5
2017-08-05 | 12:15 | 1.7444 | 0 | 0 | 1.5 | 25 | 83.4886
2017-08-05 | 12:20 | 1.7078 | 0 |  | 1.5
2017-08-05 | 12:25 | 1.7374 | 0 |  | 1.5
2017-08-05 | 12:30 | 1.7288 | 0 | 0 | 1.5 | 25 | 83.8172
2017-08-05 | 12:35 | 1.7273 | 0 |  | 1.5
2017-08-05 | 12:40 | 1.7296 | 0 |  | 1.5
2017-08-05 | 12:45 | 1.7327 | 0 | 0 | 1.5 | 25 | 84.0894
2017-08-05 | 12:50 | 1.7546 | 0 |  | 1.5
2017-08-05 | 12:55 | 1.7491 | 0 |  | 1.5
2017-08-05 | 13:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 84.2851
2017-08-05 | 13:05 | 1.7577 | 0 |  | 1.5
2017-08-05 | 13:10 | 1.7655 | 0 |  | 1.5
2017-08-05 | 13:15 | 1.7522 | 0 | 0 | 1.5 | 25 | 84.4766
2017-08-05 | 13:20 | 1.7405 | 0 |  | 1.5
2017-08-05 | 13:25 | 1.7694 | 0 |  | 1.5
2017-08-05 | 13:30 | 1.7616 | 0 | 0 | 1.5 | 25 | 84.4447
2017-08-05 | 13:35 | 1.7374 | 0 |  | 1.5
2017-08-05 | 13:40 | 1.7257 | 0 |  | 1.5
2017-08-05 | 13:45 | 1.7678 | 0 | 0 | 1.5 | 25 | 84.4062
2017-08-05 | 13:50 | 1.739 | 0 |  | 1.5
2017-08-05 | 13:55 | 1.7483 | 0 |  | 1.5
2017-08-05 | 14:00 | 1.7538 | 0 | 0 | 1.5 | 25 | 84.3653
2017-08-05 | 14:05 | 1.7616 | 0 |  | 1.5
2017-08-05 | 14:10 | 1.746 | 0 |  | 1.5
2017-08-05 | 14:15 | 1.739 | 0 | 0 | 1.5 | 25 | 84.431
2017-08-05 | 14:20 | 1.7577 | 0 |  | 1.5
2017-08-05 | 14:25 | 1.7538 | 0 |  | 1.5
2017-08-05 | 14:30 | 1.7561 | 0 | 0 | 1.5 | 25 | 84.5074
2017-08-05 | 14:35 | 1.7436 | 0 |  | 1.5
2017-08-05 | 14:40 | 1.7413 | 0 |  | 1.5
2017-08-05 | 14:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 84.5599
2017-08-05 | 14:50 | 1.7436 | 0 |  | 1.5
2017-08-05 | 14:55 | 1.7873 | 0 |  | 1.5
2017-08-05 | 15:00 | 1.778 | 0 | 0 | 1.5 | 25 | 84.536
2017-08-05 | 15:05 | 1.7803 | 0 |  | 1.5
2017-08-05 | 15:10 | 1.7717 | 0 |  | 1.5
2017-08-05 | 15:15 | 1.7858 | 0 | 0 | 1.5 | 25 | 84.5024
2017-08-05 | 15:20 | 1.7507 | 0 |  | 1.5
2017-08-05 | 15:25 | 1.7031 | 0 |  | 1.5
2017-08-05 | 15:30 | 1.7397 | 0 | 0 | 1.5 | 25 | 84.5489
2017-08-05 | 15:35 | 1.7452 | 0 |  | 1.5
2017-08-05 | 15:40 | 1.7717 | 0 |  | 1.5
2017-08-05 | 15:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 84.373
2017-08-05 | 15:50 | 1.7514 | 0 |  | 1.5
2017-08-05 | 15:55 | 1.785 | 0 |  | 1.5
2017-08-05 | 16:00 | 1.7663 | 0 | 0 | 1.5 | 25 | 84.2215
2017-08-05 | 16:05 | 1.7273 | 0 |  | 1.5
2017-08-05 | 16:10 | 1.7709 | 0 |  | 1.5
2017-08-05 | 16:15 | 1.7491 | 0 | 0 | 1.5 | 25 | 84.1148
2017-08-05 | 16:20 | 1.7561 | 0 |  | 1.5
2017-08-05 | 16:25 | 1.7624 | 0 |  | 1.5
2017-08-05 | 16:30 | 1.7741 | 0 | 0 | 1.5 | 25 | 83.81
2017-08-05 | 16:35 | 1.746 | 0 |  | 1.5
2017-08-05 | 16:40 | 1.7483 | 0 |  | 1.5
2017-08-05 | 16:45 | 1.7702 | 0 | 0 | 1.5 | 25 | 83.5559
2017-08-05 | 16:50 | 1.7889 | 0 |  | 1.5
2017-08-05 | 16:55 | 1.7561 | 0 |  | 1.5
2017-08-05 | 17:00 | 1.753 | 0 | 0 | 1.5 | 25 | 83.3869
2017-08-05 | 17:05 | 1.7421 | 0 |  | 1.5
2017-08-05 | 17:10 | 1.7725 | 0 |  | 1.5
2017-08-05 | 17:15 | 1.7772 | 0 | 0 | 1.5 | 25 | 82.7978
2017-08-05 | 17:20 | 1.7702 | 0 |  | 1.5
2017-08-05 | 17:25 | 1.7702 | 0 |  | 1.5
2017-08-05 | 17:30 | 1.7655 | 0 | 0 | 1.5 | 25 | 82.3217
2017-08-05 | 17:35 | 1.7522 | 0 |  | 1.5
2017-08-05 | 17:40 | 1.7702 | 0 |  | 1.5
2017-08-05 | 17:45 | 1.7881 | 0 | 0 | 1.5 | 25 | 82.0473
2017-08-05 | 17:50 | 1.7865 | 0 |  | 1.5
2017-08-05 | 17:55 | 1.7733 | 0 |  | 1.5
2017-08-05 | 18:00 | 1.7803 | 0 | 0 | 1.5 | 25 | 81.8473
2017-08-05 | 18:05 | 1.7803 | 0 |  | 1.5
2017-08-05 | 18:10 | 1.753 | 0 |  | 1.5
2017-08-05 | 18:15 | 1.7881 | 0 | 0 | 1.5 | 25 | 81.5691
2017-08-05 | 18:20 | 1.7312 | 0 |  | 1.5
2017-08-05 | 18:25 | 1.7436 | 0 |  | 1.5
2017-08-05 | 18:30 | 1.7522 | 0 | 0 | 1.5 | 25 | 81.3796
2017-08-05 | 18:35 | 1.7772 | 0 |  | 1.5
2017-08-05 | 18:40 | 1.7507 | 0 |  | 1.5
2017-08-05 | 18:45 | 1.7405 | 0 | 0 | 1.5 | 25 | 81.1266
2017-08-05 | 18:50 | 1.7538 | 0 |  | 1.5
2017-08-05 | 18:55 | 1.7819 | 0 |  | 1.5
2017-08-05 | 19:00 | 1.7452 | 0 | 0 | 1.5 | 25 | 80.9499
2017-08-05 | 19:05 | 1.7171 | 0 |  | 1.5
2017-08-05 | 19:10 | 1.7585 | 0 |  | 1.5
2017-08-05 | 19:15 | 1.767 | 0 | 0 | 1.5 | 25 | 80.6241
2017-08-05 | 19:20 | 1.7592 | 0 |  | 1.5
2017-08-05 | 19:25 | 1.7608 | 0 |  | 1.5
2017-08-05 | 19:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 80.3349
2017-08-05 | 19:35 | 1.7639 | 0 |  | 1.5
2017-08-05 | 19:40 | 1.7826 | 0 |  | 1.5
2017-08-05 | 19:45 | 1.7475 | 0 | 0 | 1.5 | 25 | 80.1208
2017-08-05 | 19:50 | 1.7647 | 0 |  | 1.5
2017-08-05 | 19:55 | 1.7507 | 0 |  | 1.5
2017-08-05 | 20:00 | 1.7741 | 0 | 0 | 1.5 | 25 | 79.9968
2017-08-05 | 20:05 | 1.7702 | 0 |  | 1.5
2017-08-05 | 20:10 | 1.7491 | 0 |  | 1.5
2017-08-05 | 20:15 | 1.7616 | 0 | 0 | 1.5 | 25 | 79.7137
2017-08-05 | 20:20 | 1.7304 | 0 |  | 1.5
2017-08-05 | 20:25 | 1.7265 | 0 |  | 1.5
2017-08-05 | 20:30 | 1.7319 | 0 | 0 | 1.5 | 25 | 79.9337
2017-08-05 | 20:35 | 1.7538 | 0 |  | 1.5
2017-08-05 | 20:40 | 1.7616 | 0 |  | 1.5
2017-08-05 | 20:45 | 1.7491 | 0 | 0 | 1.5 | 25 | 80.1777
2017-08-05 | 20:50 | 1.7429 | 0 |  | 1.5
2017-08-05 | 20:55 | 1.7429 | 0 |  | 1.5
2017-08-05 | 21:00 | 1.7616 | 0 | 0 | 1.5 | 25 | 80.2777
2017-08-05 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-05 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-05 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-05 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-05 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-05 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-05 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-05 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-05 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 22:05 | -0.10652 | 0 |  | 1.5
2017-08-05 | 22:10 | -0.10652 | 0 |  | 1.5
2017-08-05 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 22:20 | -0.10652 | 0 |  | 1.5
2017-08-05 | 22:25 | -0.10652 | 0 |  | 1.5
2017-08-05 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 22:35 | -0.10574 | 0 |  | 1.5
2017-08-05 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-05 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-05 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-05 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 23:05 | -0.10574 | 0 |  | 1.5
2017-08-05 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-05 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 23:20 | -0.10574 | 0 |  | 1.5
2017-08-05 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-05 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-05 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-05 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-05 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-05 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-06 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-06 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-06 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-06 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 1:20 | -0.1073 | 0 |  | 1.5
2017-08-06 | 1:25 | -0.1073 | 0 |  | 1.5
2017-08-06 | 1:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 1:35 | -0.1073 | 0 |  | 1.5
2017-08-06 | 1:40 | -0.1073 | 0 |  | 1.5
2017-08-06 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 1:50 | -0.1073 | 0 |  | 1.5
2017-08-06 | 1:55 | -0.10652 | 0 |  | 1.5
2017-08-06 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 2:05 | -0.10652 | 0 |  | 1.5
2017-08-06 | 2:10 | -0.10652 | 0 |  | 1.5
2017-08-06 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-06 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-06 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-06 | 2:40 | -0.1073 | 0 |  | 1.5
2017-08-06 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-06 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-06 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-06 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-06 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 3:20 | -0.1073 | 0 |  | 1.5
2017-08-06 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-06 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-06 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-06 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-06 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-06 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-06 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 5:00 |  |  | 1
2017-08-06 | 5:05 | 2.1836 | 5.9127 |  | 10
2017-08-06 | 5:10 | 1.9496 | 10 |  | 10
2017-08-06 | 5:15 | 1.9098 | 10 | 1 | 10 | 100 | 92.9461
2017-08-06 | 5:20 | 1.8981 | 10 |  | 10
2017-08-06 | 5:25 | 1.9238 | 9.9857 |  | 10
2017-08-06 | 5:30 | 1.9402 | 9.6199 | 1 | 10 | 96.6852 | 88.4763
2017-08-06 | 5:35 | 1.9566 | 9.0947 |  | 10
2017-08-06 | 5:40 | 1.8833 | 8.7726 |  | 10
2017-08-06 | 5:45 | 1.8677 | 8.5341 | 1 | 10 | 85.9435 | 84.4585
2017-08-06 | 5:50 | 1.8482 | 8.4172 |  | 10
2017-08-06 | 5:55 | 1.8513 | 8.1893 |  | 10
2017-08-06 | 6:00 | 1.7881 | 7.9402 | 1 | 10 | 80.1388 | 82.5652
2017-08-06 | 6:05 | 1.7803 | 8.0133 |  | 10
2017-08-06 | 6:10 | 1.7982 | 8.1802 |  | 10
2017-08-06 | 6:15 | 1.7655 | 8.2868 | 1 | 10 | 83.3436 | 81.5343
2017-08-06 | 6:20 | 1.7577 | 8.4041 |  | 10
2017-08-06 | 6:25 | 1.7483 | 8.3103 |  | 10
2017-08-06 | 6:30 | 1.7421 | 8.1386 | 1 | 10 | 82.0904 | 81.2283
2017-08-06 | 6:35 | 1.7561 | 8.0924 |  | 10
2017-08-06 | 6:40 | 1.7639 | 8.0568 |  | 10
2017-08-06 | 6:45 | 1.7631 | 7.9123 | 1 | 10 | 79.9054 | 80.7785
2017-08-06 | 6:50 | 1.7897 | 7.762 |  | 10
2017-08-06 | 6:55 | 1.7725 | 7.6524 |  | 10
2017-08-06 | 7:00 | 1.7647 | 7.5278 | 1 | 10 | 76.0705 | 80.3185
2017-08-06 | 7:05 | 1.7647 | 7.4491 |  | 10
2017-08-06 | 7:10 | 1.746 | 7.4343 |  | 10
2017-08-06 | 7:15 | 1.7499 | 7.323 | 1 | 10 | 74.0775 | 79.9844
2017-08-06 | 7:20 | 1.7819 | 7.2395 |  | 10
2017-08-06 | 7:25 | 1.7717 | 7.1809 |  | 10
2017-08-06 | 7:30 | 1.7608 | 7.2269 | 1 | 10 | 73.0053 | 79.7012
2017-08-06 | 7:35 | 1.739 | 7.3357 |  | 10
2017-08-06 | 7:40 | 1.7694 | 6.9893 |  | 10
2017-08-06 | 7:45 | 1.7296 | 7.2202 | 1 | 10 | 72.8928 | 79.4982
2017-08-06 | 7:50 | 1.7475 | 7.3556 |  | 10
2017-08-06 | 7:55 | 1.7483 | 7.3739 |  | 10
2017-08-06 | 8:00 | 1.7491 | 7.3713 | 1 | 10 | 74.5914 | 79.6291
2017-08-06 | 8:05 | 1.7655 | 7.163 |  | 10
2017-08-06 | 8:10 | 1.7327 | 7.3015 |  | 10
2017-08-06 | 8:15 | 1.767 | 7.1095 | 1 | 10 | 72.1676 | 79.6372
2017-08-06 | 8:20 | 1.7663 | 7.0347 |  | 10
2017-08-06 | 8:25 | 1.767 | 7.0774 |  | 10
2017-08-06 | 8:30 | 1.7686 | 6.6219 | 1 | 10 | 67.2516 | 79.4124
2017-08-06 | 8:35 | 1.7647 | 6.8232 |  | 10
2017-08-06 | 8:40 | 1.7663 | 6.5663 |  | 10
2017-08-06 | 8:45 | 1.7553 | 6.6927 | 1 | 10 | 67.7684 | 79.133
2017-08-06 | 8:50 | 1.7499 | 6.5226 |  | 10
2017-08-06 | 8:55 | 1.7507 | 6.2402 |  | 10
2017-08-06 | 9:00 | 1.7865 | 4.9843 | 1 | 10 | 53.046 | 78.8167
2017-08-06 | 9:05 | 1.7943 | 2.592 |  | 10
2017-08-06 | 9:10 | 1.7842 | 0.53632 |  | 10
2017-08-06 | 9:14 |  |  | 0
2017-08-06 | 9:15 | 1.5783 | 0 | 0 | 1.5 | 25 | 78.1306
2017-08-06 | 9:20 | 1.622 | 0 |  | 1.5
2017-08-06 | 9:25 | 1.6805 | 0 |  | 1.5
2017-08-06 | 9:30 | 1.6961 | 0 | 0 | 1.5 | 25 | 80.7165
2017-08-06 | 9:35 | 1.7312 | 0 |  | 1.5
2017-08-06 | 9:40 | 1.7093 | 0 |  | 1.5
2017-08-06 | 9:45 | 1.7421 | 0 | 0 | 1.5 | 25 | 81.3391
2017-08-06 | 9:50 | 1.7366 | 0 |  | 1.5
2017-08-06 | 9:55 | 1.7741 | 0 |  | 1.5
2017-08-06 | 10:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 81.4466
2017-08-06 | 10:05 | 1.7499 | 0 |  | 1.5
2017-08-06 | 10:10 | 1.7483 | 0 |  | 1.5
2017-08-06 | 10:15 | 1.7647 | 0 | 0 | 1.5 | 25 | 81.552
2017-08-06 | 10:20 | 1.7413 | 0 |  | 1.5
2017-08-06 | 10:25 | 1.7366 | 0 |  | 1.5
2017-08-06 | 10:30 | 1.7444 | 0 | 0 | 1.5 | 25 | 81.7085
2017-08-06 | 10:35 | 1.7553 | 0 |  | 1.5
2017-08-06 | 10:40 | 1.7507 | 0 |  | 1.5
2017-08-06 | 10:45 | 1.753 | 0 | 0 | 1.5 | 25 | 81.8781
2017-08-06 | 10:50 | 1.7748 | 0 |  | 1.5
2017-08-06 | 10:55 | 1.7397 | 0 |  | 1.5
2017-08-06 | 11:00 | 1.7335 | 0 | 0 | 1.5 | 25 | 81.9412
2017-08-06 | 11:05 | 1.7553 | 0 |  | 1.5
2017-08-06 | 11:10 | 1.7569 | 0 |  | 1.5
2017-08-06 | 11:15 | 1.7195 | 0 | 0 | 1.5 | 25 | 82.0579
2017-08-06 | 11:20 | 1.7514 | 0 |  | 1.5
2017-08-06 | 11:25 | 1.7468 | 0 |  | 1.5
2017-08-06 | 11:30 | 1.7226 | 0 | 0 | 1.5 | 25 | 82.2287
2017-08-06 | 11:35 | 1.7358 | 0 |  | 1.5
2017-08-06 | 11:40 | 1.7514 | 0 |  | 1.5
2017-08-06 | 11:45 | 1.7312 | 0 | 0 | 1.5 | 25 | 82.3145
2017-08-06 | 11:50 | 1.7624 | 0 |  | 1.5
2017-08-06 | 11:55 | 1.7429 | 0 |  | 1.5
2017-08-06 | 12:00 | 1.7748 | 0 | 0 | 1.5 | 25 | 82.3572
2017-08-06 | 12:05 | 1.7546 | 0 |  | 1.5
2017-08-06 | 12:10 | 1.746 | 0 |  | 1.5
2017-08-06 | 12:15 | 1.7327 | 0 | 0 | 1.5 | 25 | 82.5458
2017-08-06 | 12:20 | 1.7358 | 0 |  | 1.5
2017-08-06 | 12:25 | 1.7444 | 0 |  | 1.5
2017-08-06 | 12:30 | 1.7335 | 0 | 0 | 1.5 | 25 | 82.6851
2017-08-06 | 12:35 | 1.7405 | 0 |  | 1.5
2017-08-06 | 12:40 | 1.7421 | 0 |  | 1.5
2017-08-06 | 12:45 | 1.739 | 0 | 0 | 1.5 | 25 | 82.9995
2017-08-06 | 12:50 | 1.7538 | 0 |  | 1.5
2017-08-06 | 12:55 | 1.7296 | 0 |  | 1.5
2017-08-06 | 13:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 83.1939
2017-08-06 | 13:05 | 1.7343 | 0 |  | 1.5
2017-08-06 | 13:10 | 1.7358 | 0 |  | 1.5
2017-08-06 | 13:15 | 1.7397 | 0 | 0 | 1.5 | 25 | 83.8333
2017-08-06 | 13:20 | 1.7382 | 0 |  | 1.5
2017-08-06 | 13:25 | 1.7624 | 0 |  | 1.5
2017-08-06 | 13:30 | 1.7234 | 0 | 0 | 1.5 | 25 | 84.119
2017-08-06 | 13:35 | 1.7507 | 0 |  | 1.5
2017-08-06 | 13:40 | 1.7561 | 0 |  | 1.5
2017-08-06 | 13:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 84.2848
2017-08-06 | 13:50 | 1.7218 | 0 |  | 1.5
2017-08-06 | 13:55 | 1.7514 | 0 |  | 1.5
2017-08-06 | 14:00 | 1.7249 | 0 | 0 | 1.5 | 25 | 84.4758
2017-08-06 | 14:05 | 1.7273 | 0 |  | 1.5
2017-08-06 | 14:10 | 1.7631 | 0 |  | 1.5
2017-08-06 | 14:15 | 1.7522 | 0 | 0 | 1.5 | 25 | 84.9256
2017-08-06 | 14:20 | 1.7514 | 0 |  | 1.5
2017-08-06 | 14:25 | 1.7483 | 0 |  | 1.5
2017-08-06 | 14:30 | 1.7507 | 0 | 0 | 1.5 | 25 | 84.9605
2017-08-06 | 14:35 | 1.7491 | 0 |  | 1.5
2017-08-06 | 14:40 | 1.7304 | 0 |  | 1.5
2017-08-06 | 14:45 | 1.7343 | 0 | 0 | 1.5 | 25 | 85.0947
2017-08-06 | 14:50 | 1.76 | 0 |  | 1.5
2017-08-06 | 14:55 | 1.7335 | 0 |  | 1.5
2017-08-06 | 15:00 | 1.7452 | 0 | 0 | 1.5 | 25 | 85.275
2017-08-06 | 15:05 | 1.7413 | 0 |  | 1.5
2017-08-06 | 15:10 | 1.7413 | 0 |  | 1.5
2017-08-06 | 15:15 | 1.7624 | 0 | 0 | 1.5 | 25 | 85.279
2017-08-06 | 15:20 | 1.7358 | 0 |  | 1.5
2017-08-06 | 15:25 | 1.7514 | 0 |  | 1.5
2017-08-06 | 15:30 | 1.7468 | 0 | 0 | 1.5 | 25 | 85.2773
2017-08-06 | 15:35 | 1.7546 | 0 |  | 1.5
2017-08-06 | 15:40 | 1.746 | 0 |  | 1.5
2017-08-06 | 15:45 | 1.7304 | 0 | 0 | 1.5 | 25 | 85.4716
2017-08-06 | 15:50 | 1.7468 | 0 |  | 1.5
2017-08-06 | 15:55 | 1.7514 | 0 |  | 1.5
2017-08-06 | 16:00 | 1.7631 | 0 | 0 | 1.5 | 25 | 85.4656
2017-08-06 | 16:05 | 1.7592 | 0 |  | 1.5
2017-08-06 | 16:10 | 1.7561 | 0 |  | 1.5
2017-08-06 | 16:15 | 1.7218 | 0 | 0 | 1.5 | 25 | 85.3919
2017-08-06 | 16:20 | 1.7733 | 0 |  | 1.5
2017-08-06 | 16:25 | 1.7358 | 0 |  | 1.5
2017-08-06 | 16:30 | 1.7592 | 0 | 0 | 1.5 | 25 | 85.1348
2017-08-06 | 16:35 | 1.7709 | 0 |  | 1.5
2017-08-06 | 16:40 | 1.7756 | 0 |  | 1.5
2017-08-06 | 16:45 | 1.739 | 0 | 0 | 1.5 | 25 | 84.7338
2017-08-06 | 16:50 | 1.7756 | 0 |  | 1.5
2017-08-06 | 16:55 | 1.7569 | 0 |  | 1.5
2017-08-06 | 17:00 | 1.7468 | 0 | 0 | 1.5 | 25 | 84.4504
2017-08-06 | 17:05 | 1.7553 | 0 |  | 1.5
2017-08-06 | 17:10 | 1.7507 | 0 |  | 1.5
2017-08-06 | 17:15 | 1.7647 | 0 | 0 | 1.5 | 25 | 84.0245
2017-08-06 | 17:20 | 1.7585 | 0 |  | 1.5
2017-08-06 | 17:25 | 1.7491 | 0 |  | 1.5
2017-08-06 | 17:30 | 1.7772 | 0 | 0 | 1.5 | 25 | 83.8427
2017-08-06 | 17:35 | 1.7475 | 0 |  | 1.5
2017-08-06 | 17:40 | 1.7514 | 0 |  | 1.5
2017-08-06 | 17:45 | 1.7631 | 0 | 0 | 1.5 | 25 | 83.8115
2017-08-06 | 17:50 | 1.7546 | 0 |  | 1.5
2017-08-06 | 17:55 | 1.7592 | 0 |  | 1.5
2017-08-06 | 18:00 | 1.7429 | 0 | 0 | 1.5 | 25 | 83.7119
2017-08-06 | 18:05 | 1.7748 | 0 |  | 1.5
2017-08-06 | 18:10 | 1.7499 | 0 |  | 1.5
2017-08-06 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 25 | 83.6648
2017-08-06 | 18:20 | 1.7826 | 0 |  | 1.5
2017-08-06 | 18:25 | 1.7764 | 0 |  | 1.5
2017-08-06 | 18:30 | 1.7577 | 0 | 0 | 1.5 | 25 | 83.5574
2017-08-06 | 18:35 | 1.7826 | 0 |  | 1.5
2017-08-06 | 18:40 | 1.7444 | 0 |  | 1.5
2017-08-06 | 18:45 | 1.7499 | 0 | 0 | 1.5 | 25 | 83.4523
2017-08-06 | 18:50 | 1.7561 | 0 |  | 1.5
2017-08-06 | 18:55 | 1.7624 | 0 |  | 1.5
2017-08-06 | 19:00 | 1.7491 | 0 | 0 | 1.5 | 25 | 83.1694
2017-08-06 | 19:05 | 1.7709 | 0 |  | 1.5
2017-08-06 | 19:10 | 1.7873 | 0 |  | 1.5
2017-08-06 | 19:15 | 1.7686 | 0 | 0 | 1.5 | 25 | 82.7466
2017-08-06 | 19:20 | 1.7577 | 0 |  | 1.5
2017-08-06 | 19:25 | 1.7702 | 0 |  | 1.5
2017-08-06 | 19:30 | 1.7351 | 0 | 0 | 1.5 | 25 | 82.3563
2017-08-06 | 19:35 | 1.753 | 0 |  | 1.5
2017-08-06 | 19:40 | 1.7764 | 0 |  | 1.5
2017-08-06 | 19:45 | 1.7624 | 0 | 0 | 1.5 | 25 | 82.1816
2017-08-06 | 19:50 | 1.7787 | 0 |  | 1.5
2017-08-06 | 19:55 | 1.7546 | 0 |  | 1.5
2017-08-06 | 20:00 | 1.76 | 0 | 0 | 1.5 | 25 | 81.8914
2017-08-06 | 20:05 | 1.7663 | 0 |  | 1.5
2017-08-06 | 20:10 | 1.778 | 0 |  | 1.5
2017-08-06 | 20:15 | 1.7538 | 0 | 0 | 1.5 | 25 | 81.7394
2017-08-06 | 20:20 | 1.7296 | 0 |  | 1.5
2017-08-06 | 20:25 | 1.7663 | 0 |  | 1.5
2017-08-06 | 20:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 81.5103
2017-08-06 | 20:35 | 1.7639 | 0 |  | 1.5
2017-08-06 | 20:40 | 1.739 | 0 |  | 1.5
2017-08-06 | 20:45 | 1.7538 | 0 | 0 | 1.5 | 25 | 81.2424
2017-08-06 | 20:50 | 1.7608 | 0 |  | 1.5
2017-08-06 | 20:55 | 1.7546 | 0 |  | 1.5
2017-08-06 | 21:00 | 1.7366 | 0 | 0 | 1.5 | 25 | 80.9376
2017-08-06 | 21:05 | -0.10496 | 0 |  | 1.5
2017-08-06 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-06 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-06 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-06 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 21:35 | -0.10496 | 0 |  | 1.5
2017-08-06 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-06 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-06 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-06 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-06 | 22:55 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 23:05 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-06 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 23:20 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:25 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 23:35 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:40 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-06 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-06 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-07 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-07 | 0:10 | -0.1034 | 0 |  | 1.5
2017-08-07 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 0:20 | -0.1034 | 0 |  | 1.5
2017-08-07 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-07 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 0:35 | -0.1034 | 0 |  | 1.5
2017-08-07 | 0:40 | -0.10262 | 0 |  | 1.5
2017-08-07 | 0:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 0:50 | -0.10262 | 0 |  | 1.5
2017-08-07 | 0:55 | -0.10262 | 0 |  | 1.5
2017-08-07 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 1:05 | -0.10184 | 0 |  | 1.5
2017-08-07 | 1:10 | -0.10262 | 0 |  | 1.5
2017-08-07 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 1:20 | -0.10574 | 0 |  | 1.5
2017-08-07 | 1:25 | -0.10496 | 0 |  | 1.5
2017-08-07 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 1:35 | -0.10496 | 0 |  | 1.5
2017-08-07 | 1:40 | -0.10496 | 0 |  | 1.5
2017-08-07 | 1:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 1:50 | -0.10496 | 0 |  | 1.5
2017-08-07 | 1:55 | -0.10496 | 0 |  | 1.5
2017-08-07 | 2:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 2:05 | -0.10496 | 0 |  | 1.5
2017-08-07 | 2:10 | -0.10574 | 0 |  | 1.5
2017-08-07 | 2:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 2:20 | -0.10574 | 0 |  | 1.5
2017-08-07 | 2:25 | -0.10652 | 0 |  | 1.5
2017-08-07 | 2:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 2:35 | -0.10574 | 0 |  | 1.5
2017-08-07 | 2:40 | -0.10574 | 0 |  | 1.5
2017-08-07 | 2:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 2:50 | -0.10574 | 0 |  | 1.5
2017-08-07 | 2:55 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 3:05 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:10 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 3:20 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:25 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 3:35 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:40 | -0.10652 | 0 |  | 1.5
2017-08-07 | 3:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 3:50 | -0.10574 | 0 |  | 1.5
2017-08-07 | 3:55 | -0.10652 | 0 |  | 1.5
2017-08-07 | 4:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 4:05 | -0.10574 | 0 |  | 1.5
2017-08-07 | 4:10 | -0.10574 | 0 |  | 1.5
2017-08-07 | 4:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 4:20 | -0.10574 | 0 |  | 1.5
2017-08-07 | 4:25 | -0.10574 | 0 |  | 1.5
2017-08-07 | 4:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 4:35 | -0.10652 | 0 |  | 1.5
2017-08-07 | 4:40 | -0.10574 | 0 |  | 1.5
2017-08-07 | 4:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 4:50 | -0.10652 | 0 |  | 1.5
2017-08-07 | 4:55 | -0.10574 | 0 |  | 1.5
2017-08-07 | 5:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 5:00 |  |  | 1
2017-08-07 | 5:05 | 1.9761 | 7.2824 |  | 10
2017-08-07 | 5:10 | 1.9956 | 10 |  | 10
2017-08-07 | 5:15 | 1.9168 | 10 | 1 | 10 | 100 | 94.6156
2017-08-07 | 5:20 | 1.8739 | 10 |  | 10
2017-08-07 | 5:25 | 1.8115 | 10 |  | 10
2017-08-07 | 5:30 | 1.8458 | 10 | 1 | 10 | 100 | 92.0204
2017-08-07 | 5:35 | 1.8677 | 10 |  | 10
2017-08-07 | 5:40 | 1.856 | 10 |  | 10
2017-08-07 | 5:45 | 1.8887 | 9.8786 | 1 | 10 | 98.8972 | 89.0545
2017-08-07 | 5:50 | 1.9074 | 9.5328 |  | 10
2017-08-07 | 5:55 | 1.863 | 9.2754 |  | 10
2017-08-07 | 6:00 | 1.8497 | 8.8539 | 1 | 10 | 89.0418 | 85.7145
2017-08-07 | 6:05 | 1.8606 | 8.742 |  | 10
2017-08-07 | 6:10 | 1.8396 | 8.7209 |  | 10
2017-08-07 | 6:15 | 1.8372 | 8.6877 | 1 | 10 | 87.1483 | 83.3414
2017-08-07 | 6:20 | 1.7819 | 8.6026 |  | 10
2017-08-07 | 6:25 | 1.8099 | 8.3404 |  | 10
2017-08-07 | 6:30 | 1.8029 | 8.1574 | 1 | 10 | 82.0393 | 82.0782
2017-08-07 | 6:35 | 1.7772 | 8.1724 |  | 10
2017-08-07 | 6:40 | 1.7826 | 7.938 |  | 10
2017-08-07 | 6:45 | 1.778 | 7.5759 | 1 | 10 | 76.8359 | 81.2399
2017-08-07 | 6:50 | 1.7865 | 7.1837 |  | 10
2017-08-07 | 6:55 | 1.7647 | 6.9129 |  | 10
2017-08-07 | 7:00 | 1.7897 | 6.7323 | 1 | 10 | 68.5019 | 80.1898
2017-08-07 | 7:05 | 1.7889 | 6.2376 |  | 10
2017-08-07 | 7:10 | 1.817 | 6.0797 |  | 10
2017-08-07 | 7:15 | 1.7928 | 6.3681 | 1 | 10 | 64.4416 | 79.3025
2017-08-07 | 7:20 | 1.7702 | 6.3894 |  | 10
2017-08-07 | 7:25 | 1.7351 | 6.3453 |  | 10
2017-08-07 | 7:30 | 1.7249 | 6.0823 | 1 | 10 | 62.0321 | 79.4973
2017-08-07 | 7:35 | 1.7405 | 6.6301 |  | 10
2017-08-07 | 7:40 | 1.7787 | 6.745 |  | 10
2017-08-07 | 7:45 | 1.7702 | 6.1362 | 1 | 10 | 62.963 | 79.3474
2017-08-07 | 7:50 | 1.7967 | 5.2908 |  | 10
2017-08-07 | 7:55 | 1.7725 | 5.1538 |  | 10
2017-08-07 | 8:00 | 1.7663 | 4.8986 | 1 | 10 | 50.5712 | 78.605
2017-08-07 | 8:05 | 1.7702 | 4.9388 |  | 10
2017-08-07 | 8:10 | 1.7405 | 4.8148 |  | 10
2017-08-07 | 8:15 | 1.7702 | 5.1161 | 1 | 10 | 51.8673 | 78.1085
2017-08-07 | 8:20 | 1.7756 | 4.7442 |  | 10
2017-08-07 | 8:25 | 1.7624 | 5.3019 |  | 10
2017-08-07 | 8:30 | 1.7444 | 5.3386 | 1 | 10 | 54.2891 | 77.9633
2017-08-07 | 8:35 | 1.7421 | 5.4426 |  | 10
2017-08-07 | 8:40 | 1.728 | 5.2902 |  | 10
2017-08-07 | 8:45 | 1.7631 | 3.0345 | 1 | 10 | 33.837 | 78.0155
2017-08-07 | 8:46 |  |  | 0
2017-08-07 | 8:50 | 1.6079 | 0 |  | 1.5
2017-08-07 | 8:55 | 1.6571 | 0 |  | 1.5
2017-08-07 | 9:00 | 1.6773 | 0 | 0 | 1.5 | 25 | 80.666
2017-08-07 | 9:05 | 1.7296 | 0 |  | 1.5
2017-08-07 | 9:10 | 1.7296 | 0 |  | 1.5
2017-08-07 | 9:15 | 1.7444 | 0 | 0 | 1.5 | 25 | 81.2756
2017-08-07 | 9:20 | 1.7265 | 0 |  | 1.5
2017-08-07 | 9:25 | 1.739 | 0 |  | 1.5
2017-08-07 | 9:30 | 1.7663 | 0 | 0 | 1.5 | 25 | 81.4134
2017-08-07 | 9:35 | 1.6313 | 0 |  | 1.5
2017-08-07 | 9:40 | 1.6524 | 0 |  | 1.5
2017-08-07 | 9:45 | 1.6539 | 0 | 0 | 1.5 | 25 | 84.2194
2017-08-07 | 9:50 | 1.6812 | 0 |  | 1.5
2017-08-07 | 9:55 | 1.7234 | 0 |  | 1.5
2017-08-07 | 10:00 | 1.7444 | 0 | 0 | 1.5 | 25 | 85.4875
2017-08-07 | 10:05 | 1.785 | 0 |  | 1.5
2017-08-07 | 10:10 | 1.7608 | 0 |  | 1.5
2017-08-07 | 10:15 | 1.8146 | 0 | 0 | 1.5 | 25 | 84.9404
2017-08-07 | 10:20 | 1.7764 | 0 |  | 1.5
2017-08-07 | 10:25 | 1.76 | 0 |  | 1.5
2017-08-07 | 10:30 | 1.7343 | 0 | 0 | 1.5 | 25 | 84.5385
2017-08-07 | 10:35 | 1.7148 | 0 |  | 1.5
2017-08-07 | 10:40 | 1.7288 | 0 |  | 1.5
2017-08-07 | 10:45 | 1.7655 | 0 | 0 | 1.5 | 25 | 85.0291
2017-08-07 | 10:50 | 1.7522 | 0 |  | 1.5
2017-08-07 | 10:55 | 1.7195 | 0 |  | 1.5
2017-08-07 | 11:00 | 1.7507 | 0 | 0 | 1.5 | 25 | 85.1493
2017-08-07 | 11:05 | 1.7702 | 0 |  | 1.5
2017-08-07 | 11:10 | 1.7101 | 0 |  | 1.5
2017-08-07 | 11:15 | 1.7421 | 0 | 0 | 1.5 | 25 | 85.4179
2017-08-07 | 11:20 | 1.7273 | 0 |  | 1.5
2017-08-07 | 11:25 | 1.707 | 0 |  | 1.5
2017-08-07 | 11:30 | 1.7124 | 0 | 0 | 1.5 | 25 | 86.1013
2017-08-07 | 11:35 | 1.7249 | 0 |  | 1.5
2017-08-07 | 11:40 | 1.7499 | 0 |  | 1.5
2017-08-07 | 11:45 | 1.7592 | 0 | 0 | 1.5 | 25 | 86.4617
2017-08-07 | 11:50 | 1.6688 | 0 |  | 1.5
2017-08-07 | 11:55 | 1.6812 | 0 |  | 1.5
2017-08-07 | 12:00 | 1.7132 | 0 | 0 | 1.5 | 25 | 87.8467
2017-08-07 | 12:05 | 1.7538 | 0 |  | 1.5
2017-08-07 | 12:10 | 1.7304 | 0 |  | 1.5
2017-08-07 | 12:15 | 1.7397 | 0 | 0 | 1.5 | 25 | 88.5014
2017-08-07 | 12:20 | 1.7054 | 0 |  | 1.5
2017-08-07 | 12:25 | 1.7319 | 0 |  | 1.5
2017-08-07 | 12:30 | 1.7257 | 0 | 0 | 1.5 | 25 | 89.1342
2017-08-07 | 12:35 | 1.7444 | 0 |  | 1.5
2017-08-07 | 12:40 | 1.7319 | 0 |  | 1.5
2017-08-07 | 12:45 | 1.7319 | 0 | 0 | 1.5 | 25 | 89.6344
2017-08-07 | 12:50 | 1.7382 | 0 |  | 1.5
2017-08-07 | 12:55 | 1.7483 | 0 |  | 1.5
2017-08-07 | 13:00 | 1.7218 | 0 | 0 | 1.5 | 25 | 90.037
2017-08-07 | 13:05 | 1.7265 | 0 |  | 1.5
2017-08-07 | 13:10 | 1.7382 | 0 |  | 1.5
2017-08-07 | 13:15 | 1.7327 | 0 | 0 | 1.5 | 25 | 90.4102
2017-08-07 | 13:20 | 1.7397 | 0 |  | 1.5
2017-08-07 | 13:25 | 1.7124 | 0 |  | 1.5
2017-08-07 | 13:30 | 1.7241 | 0 | 0 | 1.5 | 25 | 91.1049
2017-08-07 | 13:35 | 1.7421 | 0 |  | 1.5
2017-08-07 | 13:40 | 1.7335 | 0 |  | 1.5
2017-08-07 | 13:45 | 1.7577 | 0 | 0 | 1.5 | 25 | 91.3112
2017-08-07 | 13:50 | 1.7312 | 0 |  | 1.5
2017-08-07 | 13:55 | 1.7436 | 0 |  | 1.5
2017-08-07 | 14:00 | 1.7312 | 0 | 0 | 1.5 | 25 | 91.2013
2017-08-07 | 14:05 | 1.7608 | 0 |  | 1.5
2017-08-07 | 14:10 | 1.7725 | 0 |  | 1.5
2017-08-07 | 14:15 | 1.7405 | 0 | 0 | 1.5 | 25 | 91.1333
2017-08-07 | 14:20 | 1.739 | 0 |  | 1.5
2017-08-07 | 14:25 | 1.7234 | 0 |  | 1.5
2017-08-07 | 14:30 | 1.746 | 0 | 0 | 1.5 | 25 | 91.3566
2017-08-07 | 14:35 | 1.7093 | 0 |  | 1.5
2017-08-07 | 14:40 | 1.7273 | 0 |  | 1.5
2017-08-07 | 14:45 | 1.7335 | 0 | 0 | 1.5 | 25 | 91.9683
2017-08-07 | 14:50 | 1.7312 | 0 |  | 1.5
2017-08-07 | 14:55 | 1.7748 | 0 |  | 1.5
2017-08-07 | 15:00 | 1.7928 | 0 | 0 | 1.5 | 25 | 91.7438
2017-08-07 | 15:05 | 1.7468 | 0 |  | 1.5
2017-08-07 | 15:10 | 1.7397 | 0 |  | 1.5
2017-08-07 | 15:15 | 1.7405 | 0 | 0 | 1.5 | 25 | 91.7629
2017-08-07 | 15:20 | 1.7748 | 0 |  | 1.5
2017-08-07 | 15:25 | 1.739 | 0 |  | 1.5
2017-08-07 | 15:30 | 1.7764 | 0 | 0 | 1.5 | 25 | 91.6522
2017-08-07 | 15:35 | 1.7725 | 0 |  | 1.5
2017-08-07 | 15:40 | 1.7452 | 0 |  | 1.5
2017-08-07 | 15:45 | 1.7647 | 0 | 0 | 1.5 | 25 | 91.2624
2017-08-07 | 15:50 | 1.7764 | 0 |  | 1.5
2017-08-07 | 15:55 | 1.7639 | 0 |  | 1.5
2017-08-07 | 16:00 | 1.7741 | 0 | 0 | 1.5 | 25 | 90.8147
2017-08-07 | 16:05 | 1.7741 | 0 |  | 1.5
2017-08-07 | 16:10 | 1.7491 | 0 |  | 1.5
2017-08-07 | 16:15 | 1.7499 | 0 | 0 | 1.5 | 25 | 90.6641
2017-08-07 | 16:20 | 1.7522 | 0 |  | 1.5
2017-08-07 | 16:25 | 1.7374 | 0 |  | 1.5
2017-08-07 | 16:30 | 1.7499 | 0 | 0 | 1.5 | 25 | 90.5618
2017-08-07 | 16:35 | 1.728 | 0 |  | 1.5
2017-08-07 | 16:40 | 1.7507 | 0 |  | 1.5
2017-08-07 | 16:45 | 1.728 | 0 | 0 | 1.5 | 25 | 90.8262
2017-08-07 | 16:50 | 1.7717 | 0 |  | 1.5
2017-08-07 | 16:55 | 1.7561 | 0 |  | 1.5
2017-08-07 | 17:00 | 1.7803 | 0 | 0 | 1.5 | 25 | 90.1587
2017-08-07 | 17:05 | 1.7959 | 0 |  | 1.5
2017-08-07 | 17:10 | 1.767 | 0 |  | 1.5
2017-08-07 | 17:15 | 1.799 | 0 | 0 | 1.5 | 25 | 89.0177
2017-08-07 | 17:20 | 1.8177 | 0 |  | 1.5
2017-08-07 | 17:25 | 1.7967 | 0 |  | 1.5
2017-08-07 | 17:30 | 1.7928 | 0 | 0 | 1.5 | 25 | 87.9007
2017-08-07 | 17:35 | 1.7889 | 0 |  | 1.5
2017-08-07 | 17:40 | 1.792 | 0 |  | 1.5
2017-08-07 | 17:45 | 1.778 | 0 | 0 | 1.5 | 25 | 86.7823
2017-08-07 | 17:50 | 1.7655 | 0 |  | 1.5
2017-08-07 | 17:55 | 1.7904 | 0 |  | 1.5
2017-08-07 | 18:00 | 1.8076 | 0 | 0 | 1.5 | 25 | 85.6702
2017-08-07 | 18:05 | 1.7936 | 0 |  | 1.5
2017-08-07 | 18:10 | 1.7748 | 0 |  | 1.5
2017-08-07 | 18:15 | 1.7553 | 0 | 0 | 1.5 | 25 | 84.9605
2017-08-07 | 18:20 | 1.792 | 0 |  | 1.5
2017-08-07 | 18:25 | 1.7709 | 0 |  | 1.5
2017-08-07 | 18:30 | 1.7624 | 0 | 0 | 1.5 | 25 | 84.2827
2017-08-07 | 18:35 | 1.7647 | 0 |  | 1.5
2017-08-07 | 18:40 | 1.7444 | 0 |  | 1.5
2017-08-07 | 18:45 | 1.7413 | 0 | 0 | 1.5 | 25 | 84.0442
2017-08-07 | 18:50 | 1.7413 | 0 |  | 1.5
2017-08-07 | 18:55 | 1.7647 | 0 |  | 1.5
2017-08-07 | 19:00 | 1.7429 | 0 | 0 | 1.5 | 25 | 83.9683
2017-08-07 | 19:05 | 1.7826 | 0 |  | 1.5
2017-08-07 | 19:10 | 1.7678 | 0 |  | 1.5
2017-08-07 | 19:15 | 1.7764 | 0 | 0 | 1.5 | 25 | 83.5705
2017-08-07 | 19:20 | 1.7748 | 0 |  | 1.5
2017-08-07 | 19:25 | 1.7694 | 0 |  | 1.5
2017-08-07 | 19:30 | 1.7694 | 0 | 0 | 1.5 | 25 | 82.995
2017-08-07 | 19:35 | 1.7881 | 0 |  | 1.5
2017-08-07 | 19:40 | 1.7741 | 0 |  | 1.5
2017-08-07 | 19:45 | 1.76 | 0 | 0 | 1.5 | 25 | 82.5301
2017-08-07 | 19:50 | 1.753 | 0 |  | 1.5
2017-08-07 | 19:55 | 1.7546 | 0 |  | 1.5
2017-08-07 | 20:00 | 1.7226 | 0 | 0 | 1.5 | 25 | 82.3356
2017-08-07 | 20:05 | 1.7624 | 0 |  | 1.5
2017-08-07 | 20:10 | 1.7405 | 0 |  | 1.5
2017-08-07 | 20:15 | 1.7522 | 0 | 0 | 1.5 | 25 | 82.0468
2017-08-07 | 20:20 | 1.7608 | 0 |  | 1.5
2017-08-07 | 20:25 | 1.7546 | 0 |  | 1.5
2017-08-07 | 20:30 | 1.7772 | 0 | 0 | 1.5 | 25 | 81.7272
2017-08-07 | 20:35 | 1.7772 | 0 |  | 1.5
2017-08-07 | 20:40 | 1.7694 | 0 |  | 1.5
2017-08-07 | 20:45 | 1.7491 | 0 | 0 | 1.5 | 25 | 81.3506
2017-08-07 | 20:50 | 1.7639 | 0 |  | 1.5
2017-08-07 | 20:55 | 1.739 | 0 |  | 1.5
2017-08-07 | 21:00 | 1.7296 | 0 | 0 | 1.5 | 25 | 81.0958
2017-08-07 | 21:05 | -0.10574 | 0 |  | 1.5
2017-08-07 | 21:10 | -0.10652 | 0 |  | 1.5
2017-08-07 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 21:20 | -0.10652 | 0 |  | 1.5
2017-08-07 | 21:25 | -0.10652 | 0 |  | 1.5
2017-08-07 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 21:35 | -0.10652 | 0 |  | 1.5
2017-08-07 | 21:40 | -0.1073 | 0 |  | 1.5
2017-08-07 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-07 | 21:55 | -0.10574 | 0 |  | 1.5
2017-08-07 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-07 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-07 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-07 | 22:25 | -0.1073 | 0 |  | 1.5
2017-08-07 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 22:35 | -0.10574 | 0 |  | 1.5
2017-08-07 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-07 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-07 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-07 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-07 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-07 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-08 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-08 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-08 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-08 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-08 | 0:15 | [5 empty] | 0
2017-08-08 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-08 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-08 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-08 | 0:30 | [5 empty] | 0
2017-08-08 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-08 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-08 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-08 | 0:45 | [5 empty] | 0
2017-08-08 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-08 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-08 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-08 | 1:00 | [5 empty] | 0
2017-08-08 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-08 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-08 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-08 | 1:15 | [5 empty] | 0
2017-08-08 | 1:20 | -0.1073 | 0 |  | 1.5
2017-08-08 | 1:25 | -0.11354 | 0 |  | 1.5
2017-08-08 | 1:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 1:30 | [5 empty] | 0
2017-08-08 | 1:35 | -0.1073 | 0 |  | 1.5
2017-08-08 | 1:40 | -0.1073 | 0 |  | 1.5
2017-08-08 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 1:45 | [5 empty] | 0
2017-08-08 | 1:50 | -0.1073 | 0 |  | 1.5
2017-08-08 | 1:55 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 2:00 | [5 empty] | 0
2017-08-08 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:10 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 2:15 | [5 empty] | 0
2017-08-08 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-08 | 2:30 | [5 empty] | 0
2017-08-08 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:40 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 2:45 | [5 empty] | 0
2017-08-08 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-08 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 3:00 | [5 empty] | 0
2017-08-08 | 3:05 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 3:15 |  |  |  | 1.5 |  | 0
2017-08-08 | 3:20 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:25 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 3:30 | [5 empty] | 0
2017-08-08 | 3:35 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:40 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 3:45 | [5 empty] | 0
2017-08-08 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-08 | 3:55 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 4:00 | [5 empty] | 0
2017-08-08 | 4:05 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:10 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 4:15 | [5 empty] | 0
2017-08-08 | 4:20 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:25 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-08-08 | 4:30 | [5 empty] | 0
2017-08-08 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:40 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 4:45 | [5 empty] | 0
2017-08-08 | 4:50 | -0.1073 | 0 |  | 1.5
2017-08-08 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-08 | 5:00 | -0.1073 | 0 | 1 | 0 | 0
2017-08-08 | 5:00 | [5 empty] | 25
2017-08-08 | 5:05 | 2.0283 | 6.2566 |  | 10
2017-08-08 | 5:10 | 1.9628 | 9.9994 |  | 10
2017-08-08 | 5:15 | 1.9012 | 10 | 1 | 10 | 100
2017-08-08 | 5:15 | [5 empty] | 94.2832
2017-08-08 | 5:20 | 1.8684 | 10 |  | 10
2017-08-08 | 5:25 | 1.8567 | 10 |  | 10
2017-08-08 | 5:30 | 1.8521 | 10 | 1 | 10 | 100
2017-08-08 | 5:30 | [5 empty] | 91.2534
2017-08-08 | 5:35 | 1.8996 | 10 |  | 10
2017-08-08 | 5:40 | 1.916 | 10 |  | 10
2017-08-08 | 5:45 | 1.8864 | 9.9793 | 1 | 10 | 99.922
2017-08-08 | 5:45 |  |  |  | 10 |  | 87.5328
2017-08-08 | 5:50 | 1.8591 | 9.7834 |  | 10
2017-08-08 | 5:55 | 1.8474 | 9.6774 |  | 10
2017-08-08 | 6:00 | 1.8318 | 9.4722 | 1 | 10 | 95.1944
2017-08-08 | 6:00 |  |  |  | 10 |  | 84.8638
2017-08-08 | 6:05 | 1.8053 | 9.4822 |  | 10
2017-08-08 | 6:10 | 1.785 | 9.5255 |  | 10
2017-08-08 | 6:15 | 1.767 | 9.3503 | 1 | 10 | 93.9148
2017-08-08 | 6:15 | [5 empty] | 83.5788
2017-08-08 | 6:20 | 1.7904 | 9.155 |  | 10
2017-08-08 | 6:25 | 1.7865 | 8.9072 |  | 10
2017-08-08 | 6:30 | 1.7787 | 8.6801 | 1 | 10 | 87.3068
2017-08-08 | 6:30 | [5 empty] | 82.4451
2017-08-08 | 6:35 | 1.8115 | 8.2491 |  | 10
2017-08-08 | 6:40 | 1.785 | 8.2358 |  | 10
2017-08-08 | 6:45 | 1.8045 | 7.9079 | 1 | 10 | 80.2646
2017-08-08 | 6:45 | [5 empty] | 81.5641
2017-08-08 | 6:50 | 1.7936 | 7.2075 |  | 10
2017-08-08 | 6:55 | 1.7811 | 6.9253 |  | 10
2017-08-08 | 7:00 | 1.799 | 6.493 | 1 | 10 | 66.9056
2017-08-08 | 7:00 | [5 empty] | 80.379
2017-08-08 | 7:05 | 1.7764 | 6.6126 |  | 10
2017-08-08 | 7:10 | 1.7764 | 6.6768 |  | 10
2017-08-08 | 7:15 | 1.7553 | 6.8904 | 1 | 10 | 69.7741
2017-08-08 | 7:15 | [5 empty] | 79.8815
2017-08-08 | 7:20 | 1.7538 | 6.9681 |  | 10
2017-08-08 | 7:25 | 1.7195 | 6.3527 |  | 10
2017-08-08 | 7:30 | 1.6797 | 5.9329 | 1 | 10 | 60.898
2017-08-08 | 7:30 | [5 empty] | 80.5879
2017-08-08 | 7:35 | 1.7382 | 5.5583 |  | 10
2017-08-08 | 7:40 | 1.7889 | 5.9788 |  | 10
2017-08-08 | 7:45 | 1.714 | 5.6577 | 1 | 10 | 58.0361
2017-08-08 | 7:45 | [5 empty] | 80.1896
2017-08-08 | 7:50 | 1.8099 | 5.4055 |  | 10
2017-08-08 | 7:55 | 1.7507 | 5.2171 |  | 10
2017-08-08 | 8:00 | 1.7748 | 4.9005 | 1 | 10 | 51.0803
2017-08-08 | 8:00 | [5 empty] | 79.9561
2017-08-08 | 8:05 | 1.8302 | 4.8512 |  | 10
2017-08-08 | 8:10 | 1.7748 | 4.809 |  | 10
2017-08-08 | 8:15 | 1.7881 | 4.2373 | 1 | 10 | 44.5806
2017-08-08 | 8:15 | [5 empty] | 79.6884
2017-08-08 | 8:20 | 1.7421 | 4.4425 |  | 10
2017-08-08 | 8:25 | 1.6625 | 4.5167 |  | 10
2017-08-08 | 8:30 | 1.6516 | 2.0919 | 1 | 10 | 25
2017-08-08 | 8:30 | [5 empty] | 81.0758
2017-08-08 | 8:35 | 1.6828 | 0.004795 |  | 10
2017-08-08 | 8:40 | 1.6641 | 0 |  | 10
2017-08-08 | 8:45 | 1.6812 | 0 | 1 | 10 | 25
2017-08-08 | 8:45 | [5 empty] | 83.1086
2017-08-08 | 8:50 | 1.714 | 0 |  | 10
2017-08-08 | 8:52 |  |  | 0
2017-08-08 | 8:55 | 1.6235 | 0 |  | 1.5
2017-08-08 | 9:00 | 1.6469 | 0 | 0 | 1.5 | 25
2017-08-08 | 9:00 | [5 empty] | 84.9565
2017-08-08 | 9:05 | 1.668 | 0 |  | 1.5
2017-08-08 | 9:10 | 1.7553 | 0 |  | 1.5
2017-08-08 | 9:15 | 1.7304 | 0 | 0 | 1.5 | 25
2017-08-08 | 9:15 | [5 empty] | 85.7413
2017-08-08 | 9:20 | 1.785 | 0 |  | 1.5
2017-08-08 | 9:25 | 1.7865 | 0 |  | 1.5
2017-08-08 | 9:30 | 1.7397 | 0 | 0 | 1.5 | 25
2017-08-08 | 9:30 | [5 empty] | 85.6793
2017-08-08 | 9:35 | 1.7702 | 0 |  | 1.5
2017-08-08 | 9:40 | 1.7468 | 0 |  | 1.5
2017-08-08 | 9:45 | 1.7592 | 0 | 0 | 1.5 | 25
2017-08-08 | 9:45 | [5 empty] | 85.3316
2017-08-08 | 9:50 | 1.778 | 0 |  | 1.5
2017-08-08 | 9:55 | 1.7577 | 0 |  | 1.5
2017-08-08 | 10:00 | 1.7709 | 0 | 0 | 1.5 | 25
2017-08-08 | 10:00 | [5 empty] | 84.7222
2017-08-08 | 10:05 | 1.7569 | 0 |  | 1.5
2017-08-08 | 10:10 | 1.7397 | 0 |  | 1.5
2017-08-08 | 10:15 | 1.7101 | 0 | 0 | 1.5 | 25
2017-08-08 | 10:15 | [5 empty] | 84.5579
2017-08-08 | 10:20 | 1.7366 | 0 |  | 1.5
2017-08-08 | 10:25 | 1.7335 | 0 |  | 1.5
2017-08-08 | 10:30 | 1.6937 | 0 | 0 | 1.5 | 25
2017-08-08 | 10:30 | [5 empty] | 85.1105
2017-08-08 | 10:35 | 1.7319 | 0 |  | 1.5
2017-08-08 | 10:40 | 1.7717 | 0 |  | 1.5
2017-08-08 | 10:45 | 1.7265 | 0 | 0 | 1.5 | 25 | 85.6324
2017-08-08 | 10:50 | 1.7273 | 0 |  | 1.5
2017-08-08 | 10:55 | 1.7234 | 0 |  | 1.5
2017-08-08 | 11:00 | 1.7358 | 0 | 0 | 1.5 | 25
2017-08-08 | 11:00 | [5 empty] | 86.2804
2017-08-08 | 11:05 | 1.6961 | 0 |  | 1.5
2017-08-08 | 11:10 | 1.7163 | 0 |  | 1.5
2017-08-08 | 11:15 | 1.7475 | 0 | 0 | 1.5 | 25
2017-08-08 | 11:15 | [5 empty] | 87.1292
2017-08-08 | 11:20 | 1.7366 | 0 |  | 1.5
2017-08-08 | 11:25 | 1.7374 | 0 |  | 1.5
2017-08-08 | 11:30 | 1.7007 | 0 | 0 | 1.5 | 25
2017-08-08 | 11:30 | [5 empty] | 88.0105
2017-08-08 | 11:35 | 1.7249 | 0 |  | 1.5
2017-08-08 | 11:40 | 1.7327 | 0 |  | 1.5
2017-08-08 | 11:45 | 1.7202 | 0 | 0 | 1.5 | 25
2017-08-08 | 11:45 | [5 empty] | 88.775
2017-08-08 | 11:50 | 1.6937 | 0 |  | 1.5
2017-08-08 | 11:55 | 1.6968 | 0 |  | 1.5
2017-08-08 | 12:00 | 1.7288 | 0 | 0 | 1.5 | 25
2017-08-08 | 12:00 | [5 empty] | 89.5663
2017-08-08 | 12:05 | 1.7421 | 0 |  | 1.5
2017-08-08 | 12:10 | 1.7179 | 0 |  | 1.5
2017-08-08 | 12:15 | 1.7039 | 0 | 0 | 1.5 | 25
2017-08-08 | 12:15 | [5 empty] | 90.3793
2017-08-08 | 12:20 | 1.7093 | 0 |  | 1.5
2017-08-08 | 12:25 | 1.7319 | 0 |  | 1.5
2017-08-08 | 12:30 | 1.7436 | 0 | 0 | 1.5 | 25
2017-08-08 | 12:30 | [5 empty] | 91.0335
2017-08-08 | 12:35 | 1.728 | 0 |  | 1.5
2017-08-08 | 12:40 | 1.721 | 0 |  | 1.5
2017-08-08 | 12:45 | 1.76 | 0 | 0 | 1.5 | 25
2017-08-08 | 12:45 | [5 empty] | 91.3736
2017-08-08 | 12:50 | 1.7421 | 0 |  | 1.5
2017-08-08 | 12:55 | 1.7319 | 0 |  | 1.5
2017-08-08 | 13:00 | 1.7397 | 0 | 0 | 1.5 | 25
2017-08-08 | 13:00 | [5 empty] | 91.628
2017-08-08 | 13:05 | 1.7585 | 0 |  | 1.5
2017-08-08 | 13:10 | 1.714 | 0 |  | 1.5
2017-08-08 | 13:15 | 1.7514 | 0 | 0 | 1.5 | 25
2017-08-08 | 13:15 | [5 empty] | 91.7177
2017-08-08 | 13:20 | 1.7405 | 0 |  | 1.5
2017-08-08 | 13:25 | 1.7249 | 0 |  | 1.5
2017-08-08 | 13:30 | 1.7148 | 0 | 0 | 1.5 | 25
2017-08-08 | 13:30 | [5 empty] | 92.1663
2017-08-08 | 13:35 | 1.7124 | 0 |  | 1.5
2017-08-08 | 13:40 | 1.7296 | 0 |  | 1.5
2017-08-08 | 13:45 | 1.7312 | 0 | 0 | 1.5 | 25
2017-08-08 | 13:45 | [5 empty] | 93.0035
2017-08-08 | 13:50 | 1.7452 | 0 |  | 1.5
2017-08-08 | 13:55 | 1.7561 | 0 |  | 1.5
2017-08-08 | 14:00 | 1.7655 | 0 | 0 | 1.5 | 25
2017-08-08 | 14:00 | [5 empty] | 92.9431
2017-08-08 | 14:05 | 1.7678 | 0 |  | 1.5
2017-08-08 | 14:10 | 1.7148 | 0 |  | 1.5
2017-08-08 | 14:15 | 1.7491 | 0 | 0 | 1.5 | 25
2017-08-08 | 14:15 | [5 empty] | 93.1622
2017-08-08 | 14:20 | 1.7265 | 0 |  | 1.5
2017-08-08 | 14:25 | 1.7499 | 0 |  | 1.5
2017-08-08 | 14:30 | 1.7655 | 0 | 0 | 1.5 | 25
2017-08-08 | 14:30 | [5 empty] | 93.3148
2017-08-08 | 14:35 | 1.7499 | 0 |  | 1.5
2017-08-08 | 14:40 | 1.7538 | 0 |  | 1.5
2017-08-08 | 14:45 | 1.728 | 0 | 0 | 1.5 | 25
2017-08-08 | 14:45 | [5 empty] | 93.4197
2017-08-08 | 14:50 | 1.7585 | 0 |  | 1.5
2017-08-08 | 14:55 | 1.7491 | 0 |  | 1.5
2017-08-08 | 15:00 | 1.7702 | 0 | 0 | 1.5 | 25
2017-08-08 | 15:00 | [5 empty] | 93.5254
2017-08-08 | 15:05 | 1.7569 | 0 |  | 1.5
2017-08-08 | 15:10 | 1.7546 | 0 |  | 1.5
2017-08-08 | 15:15 | 1.7296 | 0 | 0 | 1.5 | 25 | 93.3712
2017-08-08 | 15:20 | 1.7382 | 0 |  | 1.5
2017-08-08 | 15:25 | 1.7195 | 0 |  | 1.5
2017-08-08 | 15:30 | 1.7031 | 0 | 0 | 1.5 | 25
2017-08-08 | 15:30 | [5 empty] | 93.9724
2017-08-08 | 15:35 | 1.7 | 0 |  | 1.5
2017-08-08 | 15:40 | 1.7304 | 0 |  | 1.5
2017-08-08 | 15:45 | 1.7608 | 0 | 0 | 1.5 | 25
2017-08-08 | 15:45 | [5 empty] | 94.9824
2017-08-08 | 15:50 | 1.7499 | 0 |  | 1.5
2017-08-08 | 15:55 | 1.7327 | 0 |  | 1.5
2017-08-08 | 16:00 | 1.7943 | 0 | 0 | 1.5 | 25
2017-08-08 | 16:00 | [5 empty] | 94.991
2017-08-08 | 16:05 | 1.8279 | 0 |  | 1.5
2017-08-08 | 16:10 | 1.7764 | 0 |  | 1.5
2017-08-08 | 16:15 | 1.7561 | 0 | 0 | 1.5 | 25
2017-08-08 | 16:15 | [5 empty] | 94.1379
2017-08-08 | 16:20 | 1.7374 | 0 |  | 1.5
2017-08-08 | 16:25 | 1.7717 | 0 |  | 1.5
2017-08-08 | 16:30 | 1.7663 | 0 | 0 | 1.5 | 25
2017-08-08 | 16:30 | [5 empty] | 94.1829
2017-08-08 | 16:35 | 1.7585 | 0 |  | 1.5
2017-08-08 | 16:40 | 1.7756 | 0 |  | 1.5
2017-08-08 | 16:45 | 1.7811 | 0 | 0 | 1.5 | 25
2017-08-08 | 16:45 | [5 empty] | 93.9293
2017-08-08 | 16:50 | 1.7756 | 0 |  | 1.5
2017-08-08 | 16:55 | 1.7546 | 0 |  | 1.5
2017-08-08 | 17:00 | 1.7889 | 0 | 0 | 1.5 | 25
2017-08-08 | 17:00 | [5 empty] | 93.5115
2017-08-08 | 17:05 | 1.7772 | 0 |  | 1.5
2017-08-08 | 17:10 | 1.753 | 0 |  | 1.5
2017-08-08 | 17:15 | 1.7522 | 0 | 0 | 1.5 | 25
2017-08-08 | 17:15 | [5 empty] | 93.0504
2017-08-08 | 17:20 | 1.7725 | 0 |  | 1.5
2017-08-08 | 17:25 | 1.7725 | 0 |  | 1.5
2017-08-08 | 17:30 | 1.8029 | 0 | 0 | 1.5 | 25
2017-08-08 | 17:30 |  |  |  | 1.5 |  | 91.9383
2017-08-08 | 17:35 | 1.7811 | 0 |  | 1.5
2017-08-08 | 17:40 | 1.7756 | 0 |  | 1.5
2017-08-08 | 17:45 | 1.7889 | 0 | 0 | 1.5 | 25
2017-08-08 | 17:45 | [5 empty] | 90.7766
2017-08-08 | 17:50 | 1.8154 | 0 |  | 1.5
2017-08-08 | 17:55 | 1.8006 | 0 |  | 1.5
2017-08-08 | 18:00 | 1.8037 | 0 | 0 | 1.5 | 25
2017-08-08 | 18:00 | [5 empty] | 89.5586
2017-08-08 | 18:05 | 1.7865 | 0 |  | 1.5
2017-08-08 | 18:10 | 1.7803 | 0 |  | 1.5
2017-08-08 | 18:15 | 1.7897 | 0 | 0 | 1.5 | 25
2017-08-08 | 18:15 | [5 empty] | 88.9128
2017-08-08 | 18:20 | 1.7678 | 0 |  | 1.5
2017-08-08 | 18:25 | 1.7639 | 0 |  | 1.5
2017-08-08 | 18:30 | 1.7709 | 0 | 0 | 1.5 | 25
2017-08-08 | 18:30 | [5 empty] | 88.3048
2017-08-08 | 18:35 | 1.7678 | 0 |  | 1.5
2017-08-08 | 18:40 | 1.7647 | 0 |  | 1.5
2017-08-08 | 18:45 | 1.8092 | 0 | 0 | 1.5 | 25
2017-08-08 | 18:45 | [5 empty] | 87.6444
2017-08-08 | 18:50 | 1.7514 | 0 |  | 1.5
2017-08-08 | 18:55 | 1.7897 | 0 |  | 1.5
2017-08-08 | 19:00 | 1.7912 | 0 | 0 | 1.5 | 25
2017-08-08 | 19:00 | [5 empty] | 87.0828
2017-08-08 | 19:05 | 1.7943 | 0 |  | 1.5
2017-08-08 | 19:10 | 1.7663 | 0 |  | 1.5
2017-08-08 | 19:15 | 1.7819 | 0 | 0 | 1.5 | 25
2017-08-08 | 19:15 | [5 empty] | 86.4409
2017-08-08 | 19:20 | 1.7889 | 0 |  | 1.5
2017-08-08 | 19:25 | 1.7912 | 0 |  | 1.5
2017-08-08 | 19:30 | 1.7967 | 0 | 0 | 1.5 | 25
2017-08-08 | 19:30 | [5 empty] | 85.7114
2017-08-08 | 19:35 | 1.7889 | 0 |  | 1.5
2017-08-08 | 19:40 | 1.7834 | 0 |  | 1.5
2017-08-08 | 19:45 | 1.8045 | 0 | 0 | 1.5 | 25
2017-08-08 | 19:45 | [5 empty] | 84.9288
2017-08-08 | 19:50 | 1.7616 | 0 |  | 1.5
2017-08-08 | 19:55 | 1.7585 | 0 |  | 1.5
2017-08-08 | 20:00 | 1.7397 | 0 | 0 | 1.5 | 25
2017-08-08 | 20:00 | [5 empty] | 84.417
2017-08-08 | 20:05 | 1.7624 | 0 |  | 1.5
2017-08-08 | 20:10 | 1.7452 | 0 |  | 1.5
2017-08-08 | 20:15 | 1.7585 | 0 | 0 | 1.5 | 25
2017-08-08 | 20:15 | [5 empty] | 83.9247
2017-08-08 | 20:20 | 1.7912 | 0 |  | 1.5
2017-08-08 | 20:25 | 1.7553 | 0 |  | 1.5
2017-08-08 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 25
2017-08-08 | 20:30 | [5 empty] | 83.5566
2017-08-08 | 20:35 | 1.8115 | 0 |  | 1.5
2017-08-08 | 20:40 | 1.8029 | 0 |  | 1.5
2017-08-08 | 20:45 | 1.7772 | 0 | 0 | 1.5 | 25
2017-08-08 | 20:45 | [5 empty] | 82.8694
2017-08-08 | 20:50 | 1.7756 | 0 |  | 1.5
2017-08-08 | 20:53 |  |  | 0
2017-08-08 | 20:55 | 1.7873 | 0 |  | 1.5
2017-08-08 | 21:00 | 1.7694 | 0 | 0 | 1.5 | 25
2017-08-08 | 21:00 | [5 empty] | 0
2017-08-08 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-08 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-08 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-08 | 21:15 | [5 empty] | 0
2017-08-08 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-08 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-08 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-08 | 21:30 | [5 empty] | 0
2017-08-08 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-08 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-08 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-08 | 21:45 | [5 empty] | 0
2017-08-08 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-08 | 21:55 | -0.1073 | 0 |  | 1.5
2017-08-08 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-08 | 22:00 | [5 empty] | 0
2017-08-08 | 22:05 | -0.1073 | 0 |  | 1.5
2017-08-08 | 22:10 | -0.1073 | 0 |  | 1.5
2017-08-08 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 22:15 | [5 empty] | 0
2017-08-08 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-08 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-08 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 22:30 | [5 empty] | 0
2017-08-08 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-08 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-08 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 22:45 | [5 empty] | 0
2017-08-08 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-08 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 23:00 | [5 empty] | 0
2017-08-08 | 23:05 | -0.1034 | 0 |  | 1.5
2017-08-08 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 23:15 | [5 empty] | 0
2017-08-08 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 23:30 | [5 empty] | 0
2017-08-08 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-08 | 23:45 | [5 empty] | 0
2017-08-08 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-08 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-09 | 0:00 | [5 empty] | 0
2017-08-09 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-09 | 0:55 | -0.1034 | 0 |  | 1.5
2017-08-09 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 1:05 | -0.1034 | 0 |  | 1.5
2017-08-09 | 1:10 | -0.1034 | 0 |  | 1.5
2017-08-09 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 1:20 | -0.10652 | 0 |  | 1.5
2017-08-09 | 1:25 | -0.10652 | 0 |  | 1.5
2017-08-09 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 1:35 | -0.10652 | 0 |  | 1.5
2017-08-09 | 1:40 | -0.10652 | 0 |  | 1.5
2017-08-09 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 1:50 | -0.10652 | 0 |  | 1.5
2017-08-09 | 1:55 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 2:05 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:10 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 2:20 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:25 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 2:35 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:40 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 2:50 | -0.10652 | 0 |  | 1.5
2017-08-09 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 3:05 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 3:20 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:25 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 3:35 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:40 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-09 | 3:55 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 4:05 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:10 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 4:20 | -0.1112 | 0 |  | 1.5
2017-08-09 | 4:25 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:40 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 4:50 | -0.1073 | 0 |  | 1.5
2017-08-09 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-09 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 5:05 | 1.505 | 0 |  | 1.5
2017-08-09 | 5:10 | 1.8006 | 0 |  | 1.5
2017-08-09 | 5:15 | 1.845 | 0 | 0 | 1.5 | 0 | 98.6437
2017-08-09 | 5:20 | 1.7811 | 0 |  | 1.5
2017-08-09 | 5:25 | 1.817 | 0 |  | 1.5
2017-08-09 | 5:30 | 1.838 | 0 | 0 | 1.5 | 0 | 96.8596
2017-08-09 | 5:35 | 1.9285 | 0 |  | 1.5
2017-08-09 | 5:40 | 2.0026 | 0 |  | 1.5
2017-08-09 | 5:45 | 2.0432 | 0 | 0 | 1.5 | 0 | 91.1328
2017-08-09 | 5:50 | 2.0026 | 0 |  | 1.5
2017-08-09 | 5:55 | 1.9425 | 0 |  | 1.5
2017-08-09 | 6:00 | 1.8708 | 0 | 0 | 1.5 | 0 | 85.6326
2017-08-09 | 6:05 | 1.8427 | 0 |  | 1.5
2017-08-09 | 6:10 | 1.8131 | 0 |  | 1.5
2017-08-09 | 6:15 | 1.8014 | 0 | 0 | 1.5 | 0 | 83.3656
2017-08-09 | 6:20 | 1.7873 | 0 |  | 1.5
2017-08-09 | 6:25 | 1.7936 | 0 |  | 1.5
2017-08-09 | 6:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 82.2182
2017-08-09 | 6:35 | 1.7647 | 0 |  | 1.5
2017-08-09 | 6:40 | 1.8021 | 0 |  | 1.5
2017-08-09 | 6:45 | 1.767 | 0 | 0 | 1.5 | 0 | 81.6358
2017-08-09 | 6:50 | 1.7507 | 0 |  | 1.5
2017-08-09 | 6:55 | 1.7748 | 0 |  | 1.5
2017-08-09 | 7:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.2669
2017-08-09 | 7:05 | 1.7452 | 0 |  | 1.5
2017-08-09 | 7:10 | 1.767 | 0 |  | 1.5
2017-08-09 | 7:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 80.9774
2017-08-09 | 7:20 | 1.7171 | 0 |  | 1.5
2017-08-09 | 7:25 | 1.7085 | 0 |  | 1.5
2017-08-09 | 7:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 81.1797
2017-08-09 | 7:35 | 1.76 | 0 |  | 1.5
2017-08-09 | 7:40 | 1.7195 | 0 |  | 1.5
2017-08-09 | 7:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 81.2609
2017-08-09 | 7:50 | 1.7444 | 0 |  | 1.5
2017-08-09 | 7:55 | 1.7491 | 0 |  | 1.5
2017-08-09 | 8:00 | 1.7811 | 0 | 0 | 1.5 | 0 | 81.3606
2017-08-09 | 8:05 | 1.7475 | 0 |  | 1.5
2017-08-09 | 8:10 | 1.7226 | 0 |  | 1.5
2017-08-09 | 8:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 81.7854
2017-08-09 | 8:20 | 1.7546 | 0 |  | 1.5
2017-08-09 | 8:25 | 1.7335 | 0 |  | 1.5
2017-08-09 | 8:30 | 1.739 | 0 | 0 | 1.5 | 0 | 82.3971
2017-08-09 | 8:35 | 1.7304 | 0 |  | 1.5
2017-08-09 | 8:40 | 1.7218 | 0 |  | 1.5
2017-08-09 | 8:45 | 1.7343 | 0 | 0 | 1.5 | 0 | 82.9607
2017-08-09 | 8:50 | 1.7343 | 0 |  | 1.5
2017-08-09 | 8:55 | 1.7717 | 0 |  | 1.5
2017-08-09 | 9:00 | 1.7725 | 0 | 0 | 1.5 | 0 | 82.8028
2017-08-09 | 9:05 | 1.7507 | 0 |  | 1.5
2017-08-09 | 9:10 | 1.7101 | 0 |  | 1.5
2017-08-09 | 9:15 | 1.7234 | 0 | 0 | 1.5 | 0 | 82.9893
2017-08-09 | 9:20 | 1.7561 | 0 |  | 1.5
2017-08-09 | 9:25 | 1.7764 | 0 |  | 1.5
2017-08-09 | 9:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 83.063
2017-08-09 | 9:35 | 1.7507 | 0 |  | 1.5
2017-08-09 | 9:40 | 1.739 | 0 |  | 1.5
2017-08-09 | 9:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 82.9514
2017-08-09 | 9:50 | 1.746 | 0 |  | 1.5
2017-08-09 | 9:55 | 1.753 | 0 |  | 1.5
2017-08-09 | 10:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 82.8787
2017-08-09 | 10:05 | 1.728 | 0 |  | 1.5
2017-08-09 | 10:10 | 1.7046 | 0 |  | 1.5
2017-08-09 | 10:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 83.3229
2017-08-09 | 10:20 | 1.7226 | 0 |  | 1.5
2017-08-09 | 10:25 | 1.7117 | 0 |  | 1.5
2017-08-09 | 10:30 | 1.7304 | 0 | 0 | 1.5 | 0 | 84.2314
2017-08-09 | 10:35 | 1.7093 | 0 |  | 1.5
2017-08-09 | 10:40 | 1.7538 | 0 |  | 1.5
2017-08-09 | 10:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 84.5602
2017-08-09 | 10:50 | 1.7429 | 0 |  | 1.5
2017-08-09 | 10:55 | 1.7366 | 0 |  | 1.5
2017-08-09 | 11:00 | 1.7202 | 0 | 0 | 1.5 | 0 | 84.9968
2017-08-09 | 11:05 | 1.7343 | 0 |  | 1.5
2017-08-09 | 11:10 | 1.7257 | 0 |  | 1.5
2017-08-09 | 11:15 | 1.7343 | 0 | 0 | 1.5 | 0 | 85.4629
2017-08-09 | 11:20 | 1.7475 | 0 |  | 1.5
2017-08-09 | 11:25 | 1.7429 | 0 |  | 1.5
2017-08-09 | 11:30 | 1.7351 | 0 | 0 | 1.5 | 0 | 85.6693
2017-08-09 | 11:35 | 1.7304 | 0 |  | 1.5
2017-08-09 | 11:40 | 1.7327 | 0 |  | 1.5
2017-08-09 | 11:45 | 1.7163 | 0 | 0 | 1.5 | 0 | 86.4039
2017-08-09 | 11:50 | 1.7 | 0 |  | 1.5
2017-08-09 | 11:55 | 1.7226 | 0 |  | 1.5
2017-08-09 | 12:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 87.1814
2017-08-09 | 12:05 | 1.6883 | 0 |  | 1.5
2017-08-09 | 12:10 | 1.682 | 0 |  | 1.5
2017-08-09 | 12:15 | 1.7023 | 0 | 0 | 1.5 | 0 | 88.8547
2017-08-09 | 12:20 | 1.6976 | 0 |  | 1.5
2017-08-09 | 12:25 | 1.7234 | 0 |  | 1.5
2017-08-09 | 12:30 | 1.7148 | 0 | 0 | 1.5 | 0 | 89.9976
2017-08-09 | 12:35 | 1.7475 | 0 |  | 1.5
2017-08-09 | 12:40 | 1.739 | 0 |  | 1.5
2017-08-09 | 12:45 | 1.7327 | 0 | 0 | 1.5 | 0 | 90.1952
2017-08-09 | 12:50 | 1.7234 | 0 |  | 1.5
2017-08-09 | 12:55 | 1.7234 | 0 |  | 1.5
2017-08-09 | 13:00 | 1.714 | 0 | 0 | 1.5 | 0 | 90.8771
2017-08-09 | 13:05 | 1.7304 | 0 |  | 1.5
2017-08-09 | 13:10 | 1.7288 | 0 |  | 1.5
2017-08-09 | 13:15 | 1.7405 | 0 | 0 | 1.5 | 0 | 91.3524
2017-08-09 | 13:20 | 1.7148 | 0 |  | 1.5
2017-08-09 | 13:25 | 1.7319 | 0 |  | 1.5
2017-08-09 | 13:30 | 1.7265 | 0 | 0 | 1.5 | 0 | 92.1316
2017-08-09 | 13:35 | 1.7561 | 0 |  | 1.5
2017-08-09 | 13:40 | 1.728 | 0 |  | 1.5
2017-08-09 | 13:45 | 1.7234 | 0 | 0 | 1.5 | 0 | 92.3181
2017-08-09 | 13:50 | 1.7312 | 0 |  | 1.5
2017-08-09 | 13:55 | 1.7015 | 0 |  | 1.5
2017-08-09 | 14:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 92.9183
2017-08-09 | 14:05 | 1.721 | 0 |  | 1.5
2017-08-09 | 14:10 | 1.7358 | 0 |  | 1.5
2017-08-09 | 14:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 93.4331
2017-08-09 | 14:20 | 1.721 | 0 |  | 1.5
2017-08-09 | 14:25 | 1.7218 | 0 |  | 1.5
2017-08-09 | 14:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 94.1113
2017-08-09 | 14:35 | 1.7522 | 0 |  | 1.5
2017-08-09 | 14:40 | 1.7405 | 0 |  | 1.5
2017-08-09 | 14:45 | 1.7257 | 0 | 0 | 1.5 | 0 | 94.3686
2017-08-09 | 14:50 | 1.7686 | 0 |  | 1.5
2017-08-09 | 14:55 | 1.7444 | 0 |  | 1.5
2017-08-09 | 15:00 | 1.739 | 0 | 0 | 1.5 | 0 | 94.821
2017-08-09 | 15:05 | 1.7585 | 0 |  | 1.5
2017-08-09 | 15:10 | 1.7686 | 0 |  | 1.5
2017-08-09 | 15:15 | 1.739 | 0 | 0 | 1.5 | 0 | 95.0448
2017-08-09 | 15:20 | 1.7608 | 0 |  | 1.5
2017-08-09 | 15:25 | 1.7569 | 0 |  | 1.5
2017-08-09 | 15:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 94.8767
2017-08-09 | 15:35 | 1.7592 | 0 |  | 1.5
2017-08-09 | 15:40 | 1.7444 | 0 |  | 1.5
2017-08-09 | 15:45 | 1.7741 | 0 | 0 | 1.5 | 0 | 94.9071
2017-08-09 | 15:50 | 1.7733 | 0 |  | 1.5
2017-08-09 | 15:55 | 1.7655 | 0 |  | 1.5
2017-08-09 | 16:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 94.7738
2017-08-09 | 16:05 | 1.7319 | 0 |  | 1.5
2017-08-09 | 16:10 | 1.7444 | 0 |  | 1.5
2017-08-09 | 16:15 | 1.7803 | 0 | 0 | 1.5 | 0 | 94.5359
2017-08-09 | 16:20 | 1.7491 | 0 |  | 1.5
2017-08-09 | 16:25 | 1.806 | 0 |  | 1.5
2017-08-09 | 16:30 | 1.7678 | 0 | 0 | 1.5 | 0 | 93.8863
2017-08-09 | 16:35 | 1.7834 | 0 |  | 1.5
2017-08-09 | 16:40 | 1.7468 | 0 |  | 1.5
2017-08-09 | 16:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 93.6315
2017-08-09 | 16:50 | 1.7374 | 0 |  | 1.5
2017-08-09 | 16:55 | 1.6898 | 0 |  | 1.5
2017-08-09 | 17:00 | 1.7967 | 0 | 0 | 1.5 | 0 | 93.9633
2017-08-09 | 17:05 | 1.7452 | 0 |  | 1.5
2017-08-09 | 17:10 | 1.7756 | 0 |  | 1.5
2017-08-09 | 17:15 | 1.7912 | 0 | 0 | 1.5 | 0 | 93.2331
2017-08-09 | 17:20 | 1.785 | 0 |  | 1.5
2017-08-09 | 17:25 | 1.8107 | 0 |  | 1.5
2017-08-09 | 17:30 | 1.7975 | 0 | 0 | 1.5 | 0 | 92.2596
2017-08-09 | 17:35 | 1.8279 | 0 |  | 1.5
2017-08-09 | 17:40 | 1.778 | 0 |  | 1.5
2017-08-09 | 17:45 | 1.7897 | 0 | 0 | 1.5 | 0 | 91
2017-08-09 | 17:50 | 1.7842 | 0 |  | 1.5
2017-08-09 | 17:55 | 1.7834 | 0 |  | 1.5
2017-08-09 | 18:00 | 1.7881 | 0 | 0 | 1.5 | 0 | 90.0152
2017-08-09 | 18:05 | 1.7811 | 0 |  | 1.5
2017-08-09 | 18:10 | 1.7795 | 0 |  | 1.5
2017-08-09 | 18:15 | 1.8021 | 0 | 0 | 1.5 | 0 | 89.0809
2017-08-09 | 18:20 | 1.7928 | 0 |  | 1.5
2017-08-09 | 18:25 | 1.785 | 0 |  | 1.5
2017-08-09 | 18:30 | 1.7928 | 0 | 0 | 1.5 | 0 | 87.8217
2017-08-09 | 18:35 | 1.8131 | 0 |  | 1.5
2017-08-09 | 18:40 | 1.7873 | 0 |  | 1.5
2017-08-09 | 18:45 | 1.799 | 0 | 0 | 1.5 | 0 | 86.5648
2017-08-09 | 18:50 | 1.7873 | 0 |  | 1.5
2017-08-09 | 18:55 | 1.7881 | 0 |  | 1.5
2017-08-09 | 19:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 85.7608
2017-08-09 | 19:05 | 1.76 | 0 |  | 1.5
2017-08-09 | 19:10 | 1.7764 | 0 |  | 1.5
2017-08-09 | 19:15 | 1.7873 | 0 | 0 | 1.5 | 0 | 85.411
2017-08-09 | 19:20 | 1.7616 | 0 |  | 1.5
2017-08-09 | 19:25 | 1.7975 | 0 |  | 1.5
2017-08-09 | 19:30 | 1.7725 | 0 | 0 | 1.5 | 0 | 84.9946
2017-08-09 | 19:35 | 1.7624 | 0 |  | 1.5
2017-08-09 | 19:40 | 1.7741 | 0 |  | 1.5
2017-08-09 | 19:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 84.2867
2017-08-09 | 19:50 | 1.8037 | 0 |  | 1.5
2017-08-09 | 19:55 | 1.7787 | 0 |  | 1.5
2017-08-09 | 20:00 | 1.7873 | 0 | 0 | 1.5 | 0 | 83.3036
2017-08-09 | 20:05 | 1.739 | 0 |  | 1.5
2017-08-09 | 20:10 | 1.785 | 0 |  | 1.5
2017-08-09 | 20:15 | 1.7717 | 0 | 0 | 1.5 | 0 | 82.8871
2017-08-09 | 20:20 | 1.7647 | 0 |  | 1.5
2017-08-09 | 20:25 | 1.7647 | 0 |  | 1.5
2017-08-09 | 20:30 | 1.7819 | 0 | 0 | 1.5 | 0 | 82.4597
2017-08-09 | 20:35 | 1.76 | 0 |  | 1.5
2017-08-09 | 20:40 | 1.7624 | 0 |  | 1.5
2017-08-09 | 20:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 82.2442
2017-08-09 | 20:50 | 1.7663 | 0 |  | 1.5
2017-08-09 | 20:55 | 1.7429 | 0 |  | 1.5
2017-08-09 | 21:00 | 1.778 | 0 | 0 | 1.5 | 0 | 81.8705
2017-08-09 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-09 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-09 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 21:20 | -0.10574 | 0 |  | 1.5
2017-08-09 | 21:25 | -0.10574 | 0 |  | 1.5
2017-08-09 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-09 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-09 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-09 | 21:55 | -0.10808 | 0 |  | 1.5
2017-08-09 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:25 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 22:35 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-09 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-09 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 23:05 | -0.10574 | 0 |  | 1.5
2017-08-09 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-09 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-09 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-09 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-09 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-09 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-09 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-09 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-10 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-10 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-10 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-10 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-10 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-10 | 0:40 | -0.1034 | 0 |  | 1.5
2017-08-10 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 0:50 | -0.1034 | 0 |  | 1.5
2017-08-10 | 0:55 | -0.1034 | 0 |  | 1.5
2017-08-10 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 1:05 | -0.1034 | 0 |  | 1.5
2017-08-10 | 1:10 | -0.1034 | 0 |  | 1.5
2017-08-10 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 1:20 | -0.10574 | 0 |  | 1.5
2017-08-10 | 1:25 | -0.10574 | 0 |  | 1.5
2017-08-10 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 1:35 | -0.10652 | 0 |  | 1.5
2017-08-10 | 1:40 | -0.10652 | 0 |  | 1.5
2017-08-10 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 1:50 | -0.10652 | 0 |  | 1.5
2017-08-10 | 1:55 | -0.10652 | 0 |  | 1.5
2017-08-10 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 2:05 | -0.10652 | 0 |  | 1.5
2017-08-10 | 2:10 | -0.10652 | 0 |  | 1.5
2017-08-10 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 2:20 | -0.10652 | 0 |  | 1.5
2017-08-10 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-10 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 2:35 | -0.10652 | 0 |  | 1.5
2017-08-10 | 2:40 | -0.10652 | 0 |  | 1.5
2017-08-10 | 2:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-10 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 3:05 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 3:20 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:25 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 3:35 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:40 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-10 | 3:55 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 4:05 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:10 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 4:20 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:25 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:40 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 4:50 | -0.1073 | 0 |  | 1.5
2017-08-10 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-10 | 5:00 | -0.11354 | 0 | 0 | 1.5 | 0 | 25
2017-08-10 | 5:05 | 1.4855 | 0 |  | 1.5
2017-08-10 | 5:10 | 1.8677 | 0 |  | 1.5
2017-08-10 | 5:15 | 1.8513 | 0 | 0 | 1.5 | 0 | 98.124
2017-08-10 | 5:20 | 1.8318 | 0 |  | 1.5
2017-08-10 | 5:25 | 1.785 | 0 |  | 1.5
2017-08-10 | 5:30 | 1.8411 | 0 | 0 | 1.5 | 0 | 96.3499
2017-08-10 | 5:35 | 1.9043 | 0 |  | 1.5
2017-08-10 | 5:40 | 1.955 | 0 |  | 1.5
2017-08-10 | 5:45 | 1.9597 | 0 | 0 | 1.5 | 0 | 91.7371
2017-08-10 | 5:50 | 1.9589 | 0 |  | 1.5
2017-08-10 | 5:55 | 1.9277 | 0 |  | 1.5
2017-08-10 | 6:00 | 1.9184 | 0 | 0 | 1.5 | 0 | 86.4607
2017-08-10 | 6:05 | 1.8786 | 0 |  | 1.5
2017-08-10 | 6:10 | 1.8216 | 0 |  | 1.5
2017-08-10 | 6:15 | 1.8365 | 0 | 0 | 1.5 | 0 | 83.8353
2017-08-10 | 6:20 | 1.7717 | 0 |  | 1.5
2017-08-10 | 6:25 | 1.7772 | 0 |  | 1.5
2017-08-10 | 6:30 | 1.7756 | 0 | 0 | 1.5 | 0 | 82.7029
2017-08-10 | 6:35 | 1.8123 | 0 |  | 1.5
2017-08-10 | 6:40 | 1.7702 | 0 |  | 1.5
2017-08-10 | 6:45 | 1.7764 | 0 | 0 | 1.5 | 0 | 81.9487
2017-08-10 | 6:50 | 1.7569 | 0 |  | 1.5
2017-08-10 | 6:55 | 1.7405 | 0 |  | 1.5
2017-08-10 | 7:00 | 1.7468 | 0 | 0 | 1.5 | 0 | 81.6259
2017-08-10 | 7:05 | 1.753 | 0 |  | 1.5
2017-08-10 | 7:10 | 1.7787 | 0 |  | 1.5
2017-08-10 | 7:15 | 1.7787 | 0 | 0 | 1.5 | 0 | 81.3225
2017-08-10 | 7:20 | 1.7483 | 0 |  | 1.5
2017-08-10 | 7:25 | 1.7631 | 0 |  | 1.5
2017-08-10 | 7:30 | 1.778 | 0 | 0 | 1.5 | 0 | 81.1614
2017-08-10 | 7:35 | 1.739 | 0 |  | 1.5
2017-08-10 | 7:40 | 1.7647 | 0 |  | 1.5
2017-08-10 | 7:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 81.2746
2017-08-10 | 7:50 | 1.7741 | 0 |  | 1.5
2017-08-10 | 7:55 | 1.7702 | 0 |  | 1.5
2017-08-10 | 8:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.1779
2017-08-10 | 8:05 | 1.7631 | 0 |  | 1.5
2017-08-10 | 8:10 | 1.7491 | 0 |  | 1.5
2017-08-10 | 8:15 | 1.7312 | 0 | 0 | 1.5 | 0 | 81.3471
2017-08-10 | 8:20 | 1.7319 | 0 |  | 1.5
2017-08-10 | 8:25 | 1.7296 | 0 |  | 1.5
2017-08-10 | 8:30 | 1.6867 | 0 | 0 | 1.5 | 0 | 81.7979
2017-08-10 | 8:35 | 1.7475 | 0 |  | 1.5
2017-08-10 | 8:40 | 1.7553 | 0 |  | 1.5
2017-08-10 | 8:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 82.1286
2017-08-10 | 8:50 | 1.7304 | 0 |  | 1.5
2017-08-10 | 8:55 | 1.7655 | 0 |  | 1.5
2017-08-10 | 9:00 | 1.7444 | 0 | 0 | 1.5 | 0 | 81.9877
2017-08-10 | 9:05 | 1.7561 | 0 |  | 1.5
2017-08-10 | 9:10 | 1.6883 | 0 |  | 1.5
2017-08-10 | 9:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 82.1672
2017-08-10 | 9:20 | 1.7085 | 0 |  | 1.5
2017-08-10 | 9:25 | 1.7351 | 0 |  | 1.5
2017-08-10 | 9:30 | 1.7249 | 0 | 0 | 1.5 | 0 | 82.655
2017-08-10 | 9:35 | 1.7124 | 0 |  | 1.5
2017-08-10 | 9:40 | 1.7265 | 0 |  | 1.5
2017-08-10 | 9:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 83.5905
2017-08-10 | 9:50 | 1.728 | 0 |  | 1.5
2017-08-10 | 9:55 | 1.7109 | 0 |  | 1.5
2017-08-10 | 10:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 84.1719
2017-08-10 | 10:05 | 1.7351 | 0 |  | 1.5
2017-08-10 | 10:10 | 1.7639 | 0 |  | 1.5
2017-08-10 | 10:15 | 1.7772 | 0 | 0 | 1.5 | 0 | 84.5079
2017-08-10 | 10:20 | 1.7413 | 0 |  | 1.5
2017-08-10 | 10:25 | 1.7436 | 0 |  | 1.5
2017-08-10 | 10:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 84.8866
2017-08-10 | 10:35 | 1.7444 | 0 |  | 1.5
2017-08-10 | 10:40 | 1.7468 | 0 |  | 1.5
2017-08-10 | 10:45 | 1.7241 | 0 | 0 | 1.5 | 0 | 85.4362
2017-08-10 | 10:50 | 1.7249 | 0 |  | 1.5
2017-08-10 | 10:55 | 1.7304 | 0 |  | 1.5
2017-08-10 | 11:00 | 1.7109 | 0 | 0 | 1.5 | 0 | 86.0439
2017-08-10 | 11:05 | 1.714 | 0 |  | 1.5
2017-08-10 | 11:10 | 1.6812 | 0 |  | 1.5
2017-08-10 | 11:15 | 1.739 | 0 | 0 | 1.5 | 0 | 87.2958
2017-08-10 | 11:20 | 1.7163 | 0 |  | 1.5
2017-08-10 | 11:25 | 1.7366 | 0 |  | 1.5
2017-08-10 | 11:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 87.7237
2017-08-10 | 11:35 | 1.7397 | 0 |  | 1.5
2017-08-10 | 11:40 | 1.7663 | 0 |  | 1.5
2017-08-10 | 11:45 | 1.7553 | 0 | 0 | 1.5 | 0 | 87.5642
2017-08-10 | 11:50 | 1.7624 | 0 |  | 1.5
2017-08-10 | 11:55 | 1.7405 | 0 |  | 1.5
2017-08-10 | 12:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 87.8462
2017-08-10 | 12:05 | 1.7327 | 0 |  | 1.5
2017-08-10 | 12:10 | 1.7241 | 0 |  | 1.5
2017-08-10 | 12:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 88.1281
2017-08-10 | 12:20 | 1.7366 | 0 |  | 1.5
2017-08-10 | 12:25 | 1.7655 | 0 |  | 1.5
2017-08-10 | 12:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 88.2063
2017-08-10 | 12:35 | 1.7343 | 0 |  | 1.5
2017-08-10 | 12:40 | 1.753 | 0 |  | 1.5
2017-08-10 | 12:45 | 1.6633 | 0 | 0 | 1.5 | 0 | 89.127
2017-08-10 | 12:50 | 1.6883 | 0 |  | 1.5
2017-08-10 | 12:55 | 1.7436 | 0 |  | 1.5
2017-08-10 | 13:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 89.629
2017-08-10 | 13:05 | 1.739 | 0 |  | 1.5
2017-08-10 | 13:10 | 1.7265 | 0 |  | 1.5
2017-08-10 | 13:15 | 1.721 | 0 | 0 | 1.5 | 0 | 90.2212
2017-08-10 | 13:20 | 1.7304 | 0 |  | 1.5
2017-08-10 | 13:25 | 1.7 | 0 |  | 1.5
2017-08-10 | 13:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 91.2375
2017-08-10 | 13:35 | 1.7296 | 0 |  | 1.5
2017-08-10 | 13:40 | 1.7405 | 0 |  | 1.5
2017-08-10 | 13:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 91.5114
2017-08-10 | 13:50 | 1.7499 | 0 |  | 1.5
2017-08-10 | 13:55 | 1.7163 | 0 |  | 1.5
2017-08-10 | 14:00 | 1.7234 | 0 | 0 | 1.5 | 0 | 92.1617
2017-08-10 | 14:05 | 1.689 | 0 |  | 1.5
2017-08-10 | 14:10 | 1.7468 | 0 |  | 1.5
2017-08-10 | 14:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 92.8569
2017-08-10 | 14:20 | 1.7491 | 0 |  | 1.5
2017-08-10 | 14:25 | 1.7475 | 0 |  | 1.5
2017-08-10 | 14:30 | 1.785 | 0 | 0 | 1.5 | 0 | 93.0815
2017-08-10 | 14:35 | 1.7546 | 0 |  | 1.5
2017-08-10 | 14:40 | 1.7702 | 0 |  | 1.5
2017-08-10 | 14:45 | 1.7553 | 0 | 0 | 1.5 | 0 | 92.7755
2017-08-10 | 14:50 | 1.7351 | 0 |  | 1.5
2017-08-10 | 14:55 | 1.7195 | 0 |  | 1.5
2017-08-10 | 15:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 92.8605
2017-08-10 | 15:05 | 1.7585 | 0 |  | 1.5
2017-08-10 | 15:10 | 1.7304 | 0 |  | 1.5
2017-08-10 | 15:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 93.0807
2017-08-10 | 15:20 | 1.7007 | 0 |  | 1.5
2017-08-10 | 15:25 | 1.7296 | 0 |  | 1.5
2017-08-10 | 15:30 | 1.7195 | 0 | 0 | 1.5 | 0 | 93.4417
2017-08-10 | 15:35 | 1.7577 | 0 |  | 1.5
2017-08-10 | 15:40 | 1.7507 | 0 |  | 1.5
2017-08-10 | 15:45 | 1.7811 | 0 | 0 | 1.5 | 0 | 93.1121
2017-08-10 | 15:50 | 1.7709 | 0 |  | 1.5
2017-08-10 | 15:55 | 1.7522 | 0 |  | 1.5
2017-08-10 | 16:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 92.6041
2017-08-10 | 16:05 | 1.7795 | 0 |  | 1.5
2017-08-10 | 16:10 | 1.7608 | 0 |  | 1.5
2017-08-10 | 16:15 | 1.7928 | 0 | 0 | 1.5 | 0 | 91.9366
2017-08-10 | 16:20 | 1.7179 | 0 |  | 1.5
2017-08-10 | 16:25 | 1.7655 | 0 |  | 1.5
2017-08-10 | 16:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 92.1831
2017-08-10 | 16:35 | 1.7897 | 0 |  | 1.5
2017-08-10 | 16:40 | 1.8326 | 0 |  | 1.5
2017-08-10 | 16:45 | 1.8489 | 0 | 0 | 1.5 | 0 | 90.4997
2017-08-10 | 16:50 | 1.8411 | 0 |  | 1.5
2017-08-10 | 16:55 | 1.8209 | 0 |  | 1.5
2017-08-10 | 17:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 88.7995
2017-08-10 | 17:05 | 1.7483 | 0 |  | 1.5
2017-08-10 | 17:10 | 1.7725 | 0 |  | 1.5
2017-08-10 | 17:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 88.1953
2017-08-10 | 17:20 | 1.7881 | 0 |  | 1.5
2017-08-10 | 17:25 | 1.7569 | 0 |  | 1.5
2017-08-10 | 17:30 | 1.721 | 0 | 0 | 1.5 | 0 | 87.9523
2017-08-10 | 17:35 | 1.7538 | 0 |  | 1.5
2017-08-10 | 17:40 | 1.7507 | 0 |  | 1.5
2017-08-10 | 17:45 | 1.7717 | 0 | 0 | 1.5 | 0 | 87.6315
2017-08-10 | 17:50 | 1.7912 | 0 |  | 1.5
2017-08-10 | 17:55 | 1.7647 | 0 |  | 1.5
2017-08-10 | 18:00 | 1.8014 | 0 | 0 | 1.5 | 0 | 86.7818
2017-08-10 | 18:05 | 1.7998 | 0 |  | 1.5
2017-08-10 | 18:10 | 1.7889 | 0 |  | 1.5
2017-08-10 | 18:15 | 1.7982 | 0 | 0 | 1.5 | 0 | 86.0823
2017-08-10 | 18:20 | 1.7733 | 0 |  | 1.5
2017-08-10 | 18:25 | 1.7585 | 0 |  | 1.5
2017-08-10 | 18:30 | 1.7678 | 0 | 0 | 1.5 | 0 | 85.73
2017-08-10 | 18:35 | 1.7725 | 0 |  | 1.5
2017-08-10 | 18:40 | 1.7795 | 0 |  | 1.5
2017-08-10 | 18:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 85.2371
2017-08-10 | 18:50 | 1.7733 | 0 |  | 1.5
2017-08-10 | 18:55 | 1.7904 | 0 |  | 1.5
2017-08-10 | 19:00 | 1.7842 | 0 | 0 | 1.5 | 0 | 84.6629
2017-08-10 | 19:05 | 1.7538 | 0 |  | 1.5
2017-08-10 | 19:10 | 1.7694 | 0 |  | 1.5
2017-08-10 | 19:15 | 1.7803 | 0 | 0 | 1.5 | 0 | 84.1388
2017-08-10 | 19:20 | 1.7686 | 0 |  | 1.5
2017-08-10 | 19:25 | 1.7514 | 0 |  | 1.5
2017-08-10 | 19:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 83.5455
2017-08-10 | 19:35 | 1.7577 | 0 |  | 1.5
2017-08-10 | 19:40 | 1.7475 | 0 |  | 1.5
2017-08-10 | 19:45 | 1.7748 | 0 | 0 | 1.5 | 0 | 83.094
2017-08-10 | 19:50 | 1.7717 | 0 |  | 1.5
2017-08-10 | 19:55 | 1.7514 | 0 |  | 1.5
2017-08-10 | 20:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 82.7778
2017-08-10 | 20:05 | 1.7312 | 0 |  | 1.5
2017-08-10 | 20:10 | 1.7624 | 0 |  | 1.5
2017-08-10 | 20:15 | 1.7764 | 0 | 0 | 1.5 | 0 | 82.5626
2017-08-10 | 20:20 | 1.7741 | 0 |  | 1.5
2017-08-10 | 20:25 | 1.7795 | 0 |  | 1.5
2017-08-10 | 20:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 82.3412
2017-08-10 | 20:35 | 1.8162 | 0 |  | 1.5
2017-08-10 | 20:40 | 1.7709 | 0 |  | 1.5
2017-08-10 | 20:45 | 1.7655 | 0 | 0 | 1.5 | 0 | 81.8645
2017-08-10 | 20:50 | 1.7616 | 0 |  | 1.5
2017-08-10 | 20:55 | 1.7709 | 0 |  | 1.5
2017-08-10 | 21:00 | 1.7748 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-10 | 21:10 | -0.10574 | 0 |  | 1.5
2017-08-10 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 21:20 | -0.10652 | 0 |  | 1.5
2017-08-10 | 21:25 | -0.10886 | 0 |  | 1.5
2017-08-10 | 21:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 21:35 | -0.10652 | 0 |  | 1.5
2017-08-10 | 21:40 | -0.10652 | 0 |  | 1.5
2017-08-10 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 21:50 | -0.10652 | 0 |  | 1.5
2017-08-10 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 22:05 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:10 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 22:20 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:25 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 22:35 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:40 | -0.10652 | 0 |  | 1.5
2017-08-10 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-10 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-10 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 23:05 | -0.10964 | 0 |  | 1.5
2017-08-10 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-10 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 23:20 | -0.10574 | 0 |  | 1.5
2017-08-10 | 23:25 | -0.10574 | 0 |  | 1.5
2017-08-10 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-10 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-10 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-10 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-10 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-11 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-11 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-11 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-11 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-11 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-11 | 0:40 | -0.10574 | 0 |  | 1.5
2017-08-11 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 0:50 | -0.10574 | 0 |  | 1.5
2017-08-11 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-11 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-11 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-11 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 1:20 | -0.11198 | 0 |  | 1.5
2017-08-11 | 1:25 | -0.1073 | 0 |  | 1.5
2017-08-11 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-11 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-11 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-11 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-11 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-11 | 2:10 | -0.10886 | 0 |  | 1.5
2017-08-11 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 2:20 | -0.10886 | 0 |  | 1.5
2017-08-11 | 2:25 | -0.10886 | 0 |  | 1.5
2017-08-11 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 2:35 | -0.10808 | 0 |  | 1.5
2017-08-11 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-11 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 2:50 | -0.10808 | 0 |  | 1.5
2017-08-11 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-11 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-11 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-11 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 4:05 | -0.10886 | 0 |  | 1.5
2017-08-11 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-11 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-11 | 4:25 | -0.11042 | 0 |  | 1.5
2017-08-11 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-11 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-11 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-11 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-11 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 5:05 | 1.3692 | 0 |  | 1.5
2017-08-11 | 5:10 | 1.6906 | 0 |  | 1.5
2017-08-11 | 5:15 | 1.7436 | 0 | 0 | 1.5 | 0 | 99.9822
2017-08-11 | 5:20 | 1.7124 | 0 |  | 1.5
2017-08-11 | 5:25 | 1.753 | 0 |  | 1.5
2017-08-11 | 5:30 | 1.799 | 0 | 0 | 1.5 | 0 | 99.6961
2017-08-11 | 5:35 | 1.863 | 0 |  | 1.5
2017-08-11 | 5:40 | 1.9659 | 0 |  | 1.5
2017-08-11 | 5:45 | 2.04 | 0 | 0 | 1.5 | 0 | 94.8776
2017-08-11 | 5:50 | 2.0354 | 0 |  | 1.5
2017-08-11 | 5:55 | 1.9932 | 0 |  | 1.5
2017-08-11 | 6:00 | 1.9301 | 0 | 0 | 1.5 | 0 | 88.0489
2017-08-11 | 6:05 | 1.9394 | 0 |  | 1.5
2017-08-11 | 6:10 | 1.863 | 0 |  | 1.5
2017-08-11 | 6:15 | 1.8404 | 0 | 0 | 1.5 | 0 | 84.2587
2017-08-11 | 6:20 | 1.7811 | 0 |  | 1.5
2017-08-11 | 6:25 | 1.8232 | 0 |  | 1.5
2017-08-11 | 6:30 | 1.785 | 0 | 0 | 1.5 | 0 | 82.8874
2017-08-11 | 6:35 | 1.7819 | 0 |  | 1.5
2017-08-11 | 6:40 | 1.7795 | 0 |  | 1.5
2017-08-11 | 6:45 | 1.7741 | 0 | 0 | 1.5 | 0 | 82.0607
2017-08-11 | 6:50 | 1.7616 | 0 |  | 1.5
2017-08-11 | 6:55 | 1.7686 | 0 |  | 1.5
2017-08-11 | 7:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 81.7687
2017-08-11 | 7:05 | 1.7694 | 0 |  | 1.5
2017-08-11 | 7:10 | 1.753 | 0 |  | 1.5
2017-08-11 | 7:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 81.3832
2017-08-11 | 7:20 | 1.7483 | 0 |  | 1.5
2017-08-11 | 7:25 | 1.7499 | 0 |  | 1.5
2017-08-11 | 7:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 81.231
2017-08-11 | 7:35 | 1.7421 | 0 |  | 1.5
2017-08-11 | 7:40 | 1.7296 | 0 |  | 1.5
2017-08-11 | 7:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 81.2907
2017-08-11 | 7:50 | 1.7787 | 0 |  | 1.5
2017-08-11 | 7:55 | 1.7507 | 0 |  | 1.5
2017-08-11 | 8:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 81.3206
2017-08-11 | 8:05 | 1.7873 | 0 |  | 1.5
2017-08-11 | 8:10 | 1.7795 | 0 |  | 1.5
2017-08-11 | 8:15 | 1.7351 | 0 | 0 | 1.5 | 0 | 81.3642
2017-08-11 | 8:20 | 1.76 | 0 |  | 1.5
2017-08-11 | 8:25 | 1.7436 | 0 |  | 1.5
2017-08-11 | 8:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 81.3318
2017-08-11 | 8:35 | 1.7592 | 0 |  | 1.5
2017-08-11 | 8:40 | 1.76 | 0 |  | 1.5
2017-08-11 | 8:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 81.3978
2017-08-11 | 8:50 | 1.7639 | 0 |  | 1.5
2017-08-11 | 8:55 | 1.7811 | 0 |  | 1.5
2017-08-11 | 9:00 | 1.7257 | 0 | 0 | 1.5 | 0 | 81.5048
2017-08-11 | 9:05 | 1.7429 | 0 |  | 1.5
2017-08-11 | 9:10 | 1.7444 | 0 |  | 1.5
2017-08-11 | 9:15 | 1.7288 | 0 | 0 | 1.5 | 0 | 81.8053
2017-08-11 | 9:20 | 1.7429 | 0 |  | 1.5
2017-08-11 | 9:25 | 1.7444 | 0 |  | 1.5
2017-08-11 | 9:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 81.9812
2017-08-11 | 9:35 | 1.7273 | 0 |  | 1.5
2017-08-11 | 9:40 | 1.714 | 0 |  | 1.5
2017-08-11 | 9:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 82.174
2017-08-11 | 9:50 | 1.7312 | 0 |  | 1.5
2017-08-11 | 9:55 | 1.7132 | 0 |  | 1.5
2017-08-11 | 10:00 | 1.7296 | 0 | 0 | 1.5 | 0 | 82.4782
2017-08-11 | 10:05 | 1.7335 | 0 |  | 1.5
2017-08-11 | 10:10 | 1.7374 | 0 |  | 1.5
2017-08-11 | 10:15 | 1.739 | 0 | 0 | 1.5 | 0 | 82.7039
2017-08-11 | 10:20 | 1.7234 | 0 |  | 1.5
2017-08-11 | 10:25 | 1.753 | 0 |  | 1.5
2017-08-11 | 10:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 82.9399
2017-08-11 | 10:35 | 1.7319 | 0 |  | 1.5
2017-08-11 | 10:40 | 1.7101 | 0 |  | 1.5
2017-08-11 | 10:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 83.3369
2017-08-11 | 10:50 | 1.7351 | 0 |  | 1.5
2017-08-11 | 10:55 | 1.7202 | 0 |  | 1.5
2017-08-11 | 11:00 | 1.7405 | 0 | 0 | 1.5 | 0 | 83.9188
2017-08-11 | 11:05 | 1.7124 | 0 |  | 1.5
2017-08-11 | 11:10 | 1.7234 | 0 |  | 1.5
2017-08-11 | 11:15 | 1.7023 | 0 | 0 | 1.5 | 0 | 84.5684
2017-08-11 | 11:20 | 1.7148 | 0 |  | 1.5
2017-08-11 | 11:25 | 1.7163 | 0 |  | 1.5
2017-08-11 | 11:30 | 1.6844 | 0 | 0 | 1.5 | 0 | 85.8274
2017-08-11 | 11:35 | 1.7078 | 0 |  | 1.5
2017-08-11 | 11:40 | 1.7179 | 0 |  | 1.5
2017-08-11 | 11:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 86.5641
2017-08-11 | 11:50 | 1.7421 | 0 |  | 1.5
2017-08-11 | 11:55 | 1.7444 | 0 |  | 1.5
2017-08-11 | 12:00 | 1.7631 | 0 | 0 | 1.5 | 0 | 86.534
2017-08-11 | 12:05 | 1.76 | 0 |  | 1.5
2017-08-11 | 12:10 | 1.7468 | 0 |  | 1.5
2017-08-11 | 12:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 86.726
2017-08-11 | 12:20 | 1.7296 | 0 |  | 1.5
2017-08-11 | 12:25 | 1.7553 | 0 |  | 1.5
2017-08-11 | 12:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 87.1614
2017-08-11 | 12:35 | 1.7249 | 0 |  | 1.5
2017-08-11 | 12:40 | 1.7343 | 0 |  | 1.5
2017-08-11 | 12:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 87.4869
2017-08-11 | 12:50 | 1.7234 | 0 |  | 1.5
2017-08-11 | 12:55 | 1.7351 | 0 |  | 1.5
2017-08-11 | 13:00 | 1.7312 | 0 | 0 | 1.5 | 0 | 87.8942
2017-08-11 | 13:05 | 1.7327 | 0 |  | 1.5
2017-08-11 | 13:10 | 1.7351 | 0 |  | 1.5
2017-08-11 | 13:15 | 1.746 | 0 | 0 | 1.5 | 0 | 88.129
2017-08-11 | 13:20 | 1.7241 | 0 |  | 1.5
2017-08-11 | 13:25 | 1.7405 | 0 |  | 1.5
2017-08-11 | 13:30 | 1.7912 | 0 | 0 | 1.5 | 0 | 88.2606
2017-08-11 | 13:35 | 1.7507 | 0 |  | 1.5
2017-08-11 | 13:40 | 1.7195 | 0 |  | 1.5
2017-08-11 | 13:45 | 1.7507 | 0 | 0 | 1.5 | 0 | 88.2688
2017-08-11 | 13:50 | 1.7569 | 0 |  | 1.5
2017-08-11 | 13:55 | 1.7694 | 0 |  | 1.5
2017-08-11 | 14:00 | 1.76 | 0 | 0 | 1.5 | 0 | 88.0468
2017-08-11 | 14:05 | 1.7483 | 0 |  | 1.5
2017-08-11 | 14:10 | 1.7663 | 0 |  | 1.5
2017-08-11 | 14:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 87.8411
2017-08-11 | 14:20 | 1.7171 | 0 |  | 1.5
2017-08-11 | 14:25 | 1.778 | 0 |  | 1.5
2017-08-11 | 14:30 | 1.7803 | 0 | 0 | 1.5 | 0 | 87.7614
2017-08-11 | 14:35 | 1.7608 | 0 |  | 1.5
2017-08-11 | 14:40 | 1.7553 | 0 |  | 1.5
2017-08-11 | 14:45 | 1.6727 | 0 | 0 | 1.5 | 0 | 88.2906
2017-08-11 | 14:50 | 1.7195 | 0 |  | 1.5
2017-08-11 | 14:55 | 1.7234 | 0 |  | 1.5
2017-08-11 | 15:00 | 1.7015 | 0 | 0 | 1.5 | 0 | 89.343
2017-08-11 | 15:05 | 1.7351 | 0 |  | 1.5
2017-08-11 | 15:10 | 1.7475 | 0 |  | 1.5
2017-08-11 | 15:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 89.4036
2017-08-11 | 15:20 | 1.7546 | 0 |  | 1.5
2017-08-11 | 15:25 | 1.7468 | 0 |  | 1.5
2017-08-11 | 15:30 | 1.753 | 0 | 0 | 1.5 | 0 | 89.2216
2017-08-11 | 15:35 | 1.7725 | 0 |  | 1.5
2017-08-11 | 15:40 | 1.7631 | 0 |  | 1.5
2017-08-11 | 15:45 | 1.76 | 0 | 0 | 1.5 | 0 | 89.1097
2017-08-11 | 15:50 | 1.7312 | 0 |  | 1.5
2017-08-11 | 15:55 | 1.7429 | 0 |  | 1.5
2017-08-11 | 16:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 89.0202
2017-08-11 | 16:05 | 1.739 | 0 |  | 1.5
2017-08-11 | 16:10 | 1.728 | 0 |  | 1.5
2017-08-11 | 16:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 89.3765
2017-08-11 | 16:20 | 1.7327 | 0 |  | 1.5
2017-08-11 | 16:25 | 1.728 | 0 |  | 1.5
2017-08-11 | 16:30 | 1.739 | 0 | 0 | 1.5 | 0 | 89.981
2017-08-11 | 16:35 | 1.7436 | 0 |  | 1.5
2017-08-11 | 16:40 | 1.7678 | 0 |  | 1.5
2017-08-11 | 16:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 89.7515
2017-08-11 | 16:50 | 1.728 | 0 |  | 1.5
2017-08-11 | 16:55 | 1.7382 | 0 |  | 1.5
2017-08-11 | 17:00 | 1.7561 | 0 | 0 | 1.5 | 0 | 89.5631
2017-08-11 | 17:05 | 1.7881 | 0 |  | 1.5
2017-08-11 | 17:10 | 1.7561 | 0 |  | 1.5
2017-08-11 | 17:15 | 1.7936 | 0 | 0 | 1.5 | 0 | 88.6491
2017-08-11 | 17:20 | 1.8162 | 0 |  | 1.5
2017-08-11 | 17:25 | 1.7936 | 0 |  | 1.5
2017-08-11 | 17:30 | 1.7912 | 0 | 0 | 1.5 | 0 | 87.2161
2017-08-11 | 17:35 | 1.7873 | 0 |  | 1.5
2017-08-11 | 17:40 | 1.7608 | 0 |  | 1.5
2017-08-11 | 17:45 | 1.7756 | 0 | 0 | 1.5 | 0 | 86.3052
2017-08-11 | 17:50 | 1.7787 | 0 |  | 1.5
2017-08-11 | 17:55 | 1.7569 | 0 |  | 1.5
2017-08-11 | 18:00 | 1.7756 | 0 | 0 | 1.5 | 0 | 85.4769
2017-08-11 | 18:05 | 1.7858 | 0 |  | 1.5
2017-08-11 | 18:10 | 1.7608 | 0 |  | 1.5
2017-08-11 | 18:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 85.0401
2017-08-11 | 18:20 | 1.7647 | 0 |  | 1.5
2017-08-11 | 18:25 | 1.7639 | 0 |  | 1.5
2017-08-11 | 18:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 84.6628
2017-08-11 | 18:35 | 1.7694 | 0 |  | 1.5
2017-08-11 | 18:40 | 1.7468 | 0 |  | 1.5
2017-08-11 | 18:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 84.384
2017-08-11 | 18:50 | 1.7733 | 0 |  | 1.5
2017-08-11 | 18:55 | 1.7694 | 0 |  | 1.5
2017-08-11 | 19:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 84.0077
2017-08-11 | 19:05 | 1.7569 | 0 |  | 1.5
2017-08-11 | 19:10 | 1.7444 | 0 |  | 1.5
2017-08-11 | 19:15 | 1.7709 | 0 | 0 | 1.5 | 0 | 83.7258
2017-08-11 | 19:20 | 1.7686 | 0 |  | 1.5
2017-08-11 | 19:25 | 1.7351 | 0 |  | 1.5
2017-08-11 | 19:30 | 1.7795 | 0 | 0 | 1.5 | 0 | 83.0676
2017-08-11 | 19:35 | 1.76 | 0 |  | 1.5
2017-08-11 | 19:40 | 1.7686 | 0 |  | 1.5
2017-08-11 | 19:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 82.7826
2017-08-11 | 19:50 | 1.7756 | 0 |  | 1.5
2017-08-11 | 19:55 | 1.785 | 0 |  | 1.5
2017-08-11 | 20:00 | 1.7795 | 0 | 0 | 1.5 | 0 | 82.4781
2017-08-11 | 20:05 | 1.7943 | 0 |  | 1.5
2017-08-11 | 20:10 | 1.7725 | 0 |  | 1.5
2017-08-11 | 20:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 82.2534
2017-08-11 | 20:20 | 1.7507 | 0 |  | 1.5
2017-08-11 | 20:25 | 1.7881 | 0 |  | 1.5
2017-08-11 | 20:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 81.8758
2017-08-11 | 20:35 | 1.7842 | 0 |  | 1.5
2017-08-11 | 20:40 | 1.7475 | 0 |  | 1.5
2017-08-11 | 20:45 | 1.7873 | 0 | 0 | 1.5 | 0 | 81.3691
2017-08-11 | 20:50 | 1.7569 | 0 |  | 1.5
2017-08-11 | 20:55 | 1.7343 | 0 |  | 1.5
2017-08-11 | 21:00 | 1.767 | 0 | 0 | 1.5 | 0 | 80.9294
2017-08-11 | 21:05 | -0.10496 | 0 |  | 1.5
2017-08-11 | 21:10 | -0.10574 | 0 |  | 1.5
2017-08-11 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 21:20 | -0.10574 | 0 |  | 1.5
2017-08-11 | 21:25 | -0.10574 | 0 |  | 1.5
2017-08-11 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-11 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-11 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-11 | 21:55 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 22:05 | -0.10886 | 0 |  | 1.5
2017-08-11 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:25 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 22:35 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-11 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 23:05 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 23:20 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:25 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 23:35 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:40 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-11 | 23:50 | -0.10574 | 0 |  | 1.5
2017-08-11 | 23:55 | -0.10574 | 0 |  | 1.5
2017-08-12 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 0:05 | -0.10574 | 0 |  | 1.5
2017-08-12 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-12 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 0:20 | -0.10496 | 0 |  | 1.5
2017-08-12 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-12 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-12 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-12 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 0:50 | -0.10496 | 0 |  | 1.5
2017-08-12 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-12 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-12 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-12 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 1:20 | -0.10808 | 0 |  | 1.5
2017-08-12 | 1:25 | -0.10808 | 0 |  | 1.5
2017-08-12 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-12 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-12 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-12 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-12 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-12 | 2:10 | -0.10808 | 0 |  | 1.5
2017-08-12 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-12 | 2:25 | -0.10886 | 0 |  | 1.5
2017-08-12 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 2:35 | -0.10886 | 0 |  | 1.5
2017-08-12 | 2:40 | -0.10886 | 0 |  | 1.5
2017-08-12 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 2:50 | -0.10886 | 0 |  | 1.5
2017-08-12 | 2:55 | -0.10886 | 0 |  | 1.5
2017-08-12 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 3:05 | -0.10886 | 0 |  | 1.5
2017-08-12 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-12 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-12 | 3:25 | -0.10886 | 0 |  | 1.5
2017-08-12 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-12 | 3:40 | -0.10886 | 0 |  | 1.5
2017-08-12 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-12 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-12 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 4:05 | -0.10886 | 0 |  | 1.5
2017-08-12 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-12 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-12 | 4:25 | -0.10886 | 0 |  | 1.5
2017-08-12 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-12 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-12 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 4:50 | -0.10886 | 0 |  | 1.5
2017-08-12 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-12 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 5:05 | 1.7296 | 0 |  | 1.5
2017-08-12 | 5:10 | 1.9332 | 0 |  | 1.5
2017-08-12 | 5:15 | 1.8942 | 0 | 0 | 1.5 | 0 | 96.1908
2017-08-12 | 5:20 | 1.8544 | 0 |  | 1.5
2017-08-12 | 5:25 | 1.8692 | 0 |  | 1.5
2017-08-12 | 5:30 | 2.0026 | 0 | 0 | 1.5 | 0 | 92.5533
2017-08-12 | 5:35 | 2.0112 | 0 |  | 1.5
2017-08-12 | 5:40 | 2.0026 | 0 |  | 1.5
2017-08-12 | 5:45 | 1.9277 | 0 | 0 | 1.5 | 0 | 85.911
2017-08-12 | 5:50 | 1.8833 | 0 |  | 1.5
2017-08-12 | 5:55 | 1.8513 | 0 |  | 1.5
2017-08-12 | 6:00 | 1.8053 | 0 | 0 | 1.5 | 0 | 82.8251
2017-08-12 | 6:05 | 1.7889 | 0 |  | 1.5
2017-08-12 | 6:10 | 1.7787 | 0 |  | 1.5
2017-08-12 | 6:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.7794
2017-08-12 | 6:20 | 1.7678 | 0 |  | 1.5
2017-08-12 | 6:25 | 1.7858 | 0 |  | 1.5
2017-08-12 | 6:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 81.3045
2017-08-12 | 6:35 | 1.7522 | 0 |  | 1.5
2017-08-12 | 6:40 | 1.7616 | 0 |  | 1.5
2017-08-12 | 6:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 81.0219
2017-08-12 | 6:50 | 1.7725 | 0 |  | 1.5
2017-08-12 | 6:55 | 1.7756 | 0 |  | 1.5
2017-08-12 | 7:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 80.7247
2017-08-12 | 7:05 | 1.7678 | 0 |  | 1.5
2017-08-12 | 7:10 | 1.7624 | 0 |  | 1.5
2017-08-12 | 7:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 80.5238
2017-08-12 | 7:20 | 1.7288 | 0 |  | 1.5
2017-08-12 | 7:25 | 1.7475 | 0 |  | 1.5
2017-08-12 | 7:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 80.2366
2017-08-12 | 7:35 | 1.7351 | 0 |  | 1.5
2017-08-12 | 7:40 | 1.7538 | 0 |  | 1.5
2017-08-12 | 7:45 | 1.7897 | 0 | 0 | 1.5 | 0 | 80.2029
2017-08-12 | 7:50 | 1.7522 | 0 |  | 1.5
2017-08-12 | 7:55 | 1.7397 | 0 |  | 1.5
2017-08-12 | 8:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 80.0581
2017-08-12 | 8:05 | 1.7468 | 0 |  | 1.5
2017-08-12 | 8:10 | 1.7709 | 0 |  | 1.5
2017-08-12 | 8:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.8888
2017-08-12 | 8:20 | 1.7702 | 0 |  | 1.5
2017-08-12 | 8:25 | 1.7686 | 0 |  | 1.5
2017-08-12 | 8:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 79.8187
2017-08-12 | 8:35 | 1.7795 | 0 |  | 1.5
2017-08-12 | 8:40 | 1.7514 | 0 |  | 1.5
2017-08-12 | 8:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.787
2017-08-12 | 8:50 | 1.7405 | 0 |  | 1.5
2017-08-12 | 8:55 | 1.7483 | 0 |  | 1.5
2017-08-12 | 9:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.6681
2017-08-12 | 9:05 | 1.7639 | 0 |  | 1.5
2017-08-12 | 9:10 | 1.746 | 0 |  | 1.5
2017-08-12 | 9:15 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.5372
2017-08-12 | 9:20 | 1.7522 | 0 |  | 1.5
2017-08-12 | 9:25 | 1.7499 | 0 |  | 1.5
2017-08-12 | 9:30 | 1.7374 | 0 | 0 | 1.5 | 0 | 79.3628
2017-08-12 | 9:35 | 1.7319 | 0 |  | 1.5
2017-08-12 | 9:40 | 1.7514 | 0 |  | 1.5
2017-08-12 | 9:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 79.42
2017-08-12 | 9:50 | 1.7421 | 0 |  | 1.5
2017-08-12 | 9:55 | 1.7343 | 0 |  | 1.5
2017-08-12 | 10:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 79.5564
2017-08-12 | 10:05 | 1.7273 | 0 |  | 1.5
2017-08-12 | 10:10 | 1.7421 | 0 |  | 1.5
2017-08-12 | 10:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 79.487
2017-08-12 | 10:20 | 1.7351 | 0 |  | 1.5
2017-08-12 | 10:25 | 1.7475 | 0 |  | 1.5
2017-08-12 | 10:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 79.6328
2017-08-12 | 10:35 | 1.7234 | 0 |  | 1.5
2017-08-12 | 10:40 | 1.7592 | 0 |  | 1.5
2017-08-12 | 10:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 79.6959
2017-08-12 | 10:50 | 1.7631 | 0 |  | 1.5
2017-08-12 | 10:55 | 1.728 | 0 |  | 1.5
2017-08-12 | 11:00 | 1.7358 | 0 | 0 | 1.5 | 0 | 79.7663
2017-08-12 | 11:05 | 1.7421 | 0 |  | 1.5
2017-08-12 | 11:10 | 1.7655 | 0 |  | 1.5
2017-08-12 | 11:15 | 1.7795 | 0 | 0 | 1.5 | 0 | 79.6597
2017-08-12 | 11:20 | 1.7514 | 0 |  | 1.5
2017-08-12 | 11:25 | 1.7444 | 0 |  | 1.5
2017-08-12 | 11:30 | 1.746 | 0 | 0 | 1.5 | 0 | 79.6659
2017-08-12 | 11:35 | 1.7538 | 0 |  | 1.5
2017-08-12 | 11:40 | 1.7304 | 0 |  | 1.5
2017-08-12 | 11:45 | 1.7358 | 0 | 0 | 1.5 | 0 | 79.8201
2017-08-12 | 11:50 | 1.7436 | 0 |  | 1.5
2017-08-12 | 11:55 | 1.7499 | 0 |  | 1.5
2017-08-12 | 12:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 80.0062
2017-08-12 | 12:05 | 1.76 | 0 |  | 1.5
2017-08-12 | 12:10 | 1.7241 | 0 |  | 1.5
2017-08-12 | 12:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 80.1346
2017-08-12 | 12:20 | 1.7787 | 0 |  | 1.5
2017-08-12 | 12:25 | 1.7819 | 0 |  | 1.5
2017-08-12 | 12:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 80.1913
2017-08-12 | 12:35 | 1.7483 | 0 |  | 1.5
2017-08-12 | 12:40 | 1.7335 | 0 |  | 1.5
2017-08-12 | 12:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 80.2205
2017-08-12 | 12:50 | 1.7429 | 0 |  | 1.5
2017-08-12 | 12:55 | 1.7577 | 0 |  | 1.5
2017-08-12 | 13:00 | 1.7249 | 0 | 0 | 1.5 | 0 | 80.4087
2017-08-12 | 13:05 | 1.7273 | 0 |  | 1.5
2017-08-12 | 13:10 | 1.728 | 0 |  | 1.5
2017-08-12 | 13:15 | 1.7312 | 0 | 0 | 1.5 | 0 | 80.6
2017-08-12 | 13:20 | 1.7468 | 0 |  | 1.5
2017-08-12 | 13:25 | 1.7538 | 0 |  | 1.5
2017-08-12 | 13:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 80.7926
2017-08-12 | 13:35 | 1.7444 | 0 |  | 1.5
2017-08-12 | 13:40 | 1.7491 | 0 |  | 1.5
2017-08-12 | 13:45 | 1.7273 | 0 | 0 | 1.5 | 0 | 81.2276
2017-08-12 | 13:50 | 1.7312 | 0 |  | 1.5
2017-08-12 | 13:55 | 1.7358 | 0 |  | 1.5
2017-08-12 | 14:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 81.7671
2017-08-12 | 14:05 | 1.7179 | 0 |  | 1.5
2017-08-12 | 14:10 | 1.7413 | 0 |  | 1.5
2017-08-12 | 14:15 | 1.728 | 0 | 0 | 1.5 | 0 | 82.0859
2017-08-12 | 14:20 | 1.728 | 0 |  | 1.5
2017-08-12 | 14:25 | 1.7553 | 0 |  | 1.5
2017-08-12 | 14:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 82.256
2017-08-12 | 14:35 | 1.7397 | 0 |  | 1.5
2017-08-12 | 14:40 | 1.7374 | 0 |  | 1.5
2017-08-12 | 14:45 | 1.7241 | 0 | 0 | 1.5 | 0 | 82.4558
2017-08-12 | 14:50 | 1.7436 | 0 |  | 1.5
2017-08-12 | 14:55 | 1.739 | 0 |  | 1.5
2017-08-12 | 15:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 82.6423
2017-08-12 | 15:05 | 1.7436 | 0 |  | 1.5
2017-08-12 | 15:10 | 1.7296 | 0 |  | 1.5
2017-08-12 | 15:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 82.9332
2017-08-12 | 15:20 | 1.7444 | 0 |  | 1.5
2017-08-12 | 15:25 | 1.7561 | 0 |  | 1.5
2017-08-12 | 15:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 83.1318
2017-08-12 | 15:35 | 1.746 | 0 |  | 1.5
2017-08-12 | 15:40 | 1.7577 | 0 |  | 1.5
2017-08-12 | 15:45 | 1.7717 | 0 | 0 | 1.5 | 0 | 83.1606
2017-08-12 | 15:50 | 1.739 | 0 |  | 1.5
2017-08-12 | 15:55 | 1.746 | 0 |  | 1.5
2017-08-12 | 16:00 | 1.7405 | 0 | 0 | 1.5 | 0 | 83.1583
2017-08-12 | 16:05 | 1.7585 | 0 |  | 1.5
2017-08-12 | 16:10 | 1.7468 | 0 |  | 1.5
2017-08-12 | 16:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 83.1786
2017-08-12 | 16:20 | 1.7733 | 0 |  | 1.5
2017-08-12 | 16:25 | 1.753 | 0 |  | 1.5
2017-08-12 | 16:30 | 1.76 | 0 | 0 | 1.5 | 0 | 83.012
2017-08-12 | 16:35 | 1.76 | 0 |  | 1.5
2017-08-12 | 16:40 | 1.7577 | 0 |  | 1.5
2017-08-12 | 16:45 | 1.76 | 0 | 0 | 1.5 | 0 | 82.7679
2017-08-12 | 16:50 | 1.7483 | 0 |  | 1.5
2017-08-12 | 16:55 | 1.7733 | 0 |  | 1.5
2017-08-12 | 17:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 82.748
2017-08-12 | 17:05 | 1.7592 | 0 |  | 1.5
2017-08-12 | 17:10 | 1.7444 | 0 |  | 1.5
2017-08-12 | 17:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 82.7355
2017-08-12 | 17:20 | 1.7678 | 0 |  | 1.5
2017-08-12 | 17:25 | 1.7842 | 0 |  | 1.5
2017-08-12 | 17:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 82.4677
2017-08-12 | 17:35 | 1.746 | 0 |  | 1.5
2017-08-12 | 17:40 | 1.767 | 0 |  | 1.5
2017-08-12 | 17:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.2358
2017-08-12 | 17:50 | 1.7663 | 0 |  | 1.5
2017-08-12 | 17:55 | 1.7561 | 0 |  | 1.5
2017-08-12 | 18:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 82.0475
2017-08-12 | 18:05 | 1.7546 | 0 |  | 1.5
2017-08-12 | 18:10 | 1.7663 | 0 |  | 1.5
2017-08-12 | 18:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 81.9342
2017-08-12 | 18:20 | 1.7561 | 0 |  | 1.5
2017-08-12 | 18:25 | 1.76 | 0 |  | 1.5
2017-08-12 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.8285
2017-08-12 | 18:35 | 1.7608 | 0 |  | 1.5
2017-08-12 | 18:40 | 1.7585 | 0 |  | 1.5
2017-08-12 | 18:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 81.6677
2017-08-12 | 18:50 | 1.7546 | 0 |  | 1.5
2017-08-12 | 18:55 | 1.76 | 0 |  | 1.5
2017-08-12 | 19:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.3802
2017-08-12 | 19:05 | 1.7296 | 0 |  | 1.5
2017-08-12 | 19:10 | 1.7436 | 0 |  | 1.5
2017-08-12 | 19:15 | 1.7686 | 0 | 0 | 1.5 | 0 | 81.2186
2017-08-12 | 19:20 | 1.7624 | 0 |  | 1.5
2017-08-12 | 19:25 | 1.7702 | 0 |  | 1.5
2017-08-12 | 19:30 | 1.7335 | 0 | 0 | 1.5 | 0 | 81.0487
2017-08-12 | 19:35 | 1.7413 | 0 |  | 1.5
2017-08-12 | 19:40 | 1.7663 | 0 |  | 1.5
2017-08-12 | 19:45 | 1.753 | 0 | 0 | 1.5 | 0 | 80.8512
2017-08-12 | 19:50 | 1.7553 | 0 |  | 1.5
2017-08-12 | 19:55 | 1.778 | 0 |  | 1.5
2017-08-12 | 20:00 | 1.739 | 0 | 0 | 1.5 | 0 | 80.6529
2017-08-12 | 20:05 | 1.7491 | 0 |  | 1.5
2017-08-12 | 20:10 | 1.7374 | 0 |  | 1.5
2017-08-12 | 20:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 80.6031
2017-08-12 | 20:20 | 1.7639 | 0 |  | 1.5
2017-08-12 | 20:25 | 1.7343 | 0 |  | 1.5
2017-08-12 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 80.3485
2017-08-12 | 20:35 | 1.7405 | 0 |  | 1.5
2017-08-12 | 20:40 | 1.7678 | 0 |  | 1.5
2017-08-12 | 20:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 80.1323
2017-08-12 | 20:50 | 1.7608 | 0 |  | 1.5
2017-08-12 | 20:55 | 1.7631 | 0 |  | 1.5
2017-08-12 | 21:00 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.9272
2017-08-12 | 21:05 | -0.10496 | 0 |  | 1.5
2017-08-12 | 21:10 | -0.10652 | 0 |  | 1.5
2017-08-12 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 21:20 | -0.10652 | 0 |  | 1.5
2017-08-12 | 21:25 | -0.10652 | 0 |  | 1.5
2017-08-12 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 21:35 | -0.10652 | 0 |  | 1.5
2017-08-12 | 21:40 | -0.10652 | 0 |  | 1.5
2017-08-12 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 21:50 | -0.10652 | 0 |  | 1.5
2017-08-12 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-12 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 22:05 | -0.10652 | 0 |  | 1.5
2017-08-12 | 22:10 | -0.10652 | 0 |  | 1.5
2017-08-12 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 22:20 | -0.1073 | 0 |  | 1.5
2017-08-12 | 22:25 | -0.1073 | 0 |  | 1.5
2017-08-12 | 22:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 22:35 | -0.1073 | 0 |  | 1.5
2017-08-12 | 22:40 | -0.10808 | 0 |  | 1.5
2017-08-12 | 22:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 22:50 | -0.10808 | 0 |  | 1.5
2017-08-12 | 22:55 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 23:05 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:10 | -0.1073 | 0 |  | 1.5
2017-08-12 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 23:20 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:25 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 23:35 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:40 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-12 | 23:50 | -0.10808 | 0 |  | 1.5
2017-08-12 | 23:55 | -0.10808 | 0 |  | 1.5
2017-08-13 | 0:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 0:05 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:10 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 0:20 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:25 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 0:35 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:40 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 0:50 | -0.1073 | 0 |  | 1.5
2017-08-13 | 0:55 | -0.1073 | 0 |  | 1.5
2017-08-13 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 1:05 | -0.1073 | 0 |  | 1.5
2017-08-13 | 1:10 | -0.1073 | 0 |  | 1.5
2017-08-13 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 1:20 | -0.1112 | 0 |  | 1.5
2017-08-13 | 1:25 | -0.1112 | 0 |  | 1.5
2017-08-13 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 1:35 | -0.11042 | 0 |  | 1.5
2017-08-13 | 1:40 | -0.1112 | 0 |  | 1.5
2017-08-13 | 1:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 1:50 | -0.10964 | 0 |  | 1.5
2017-08-13 | 1:55 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 2:05 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:10 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 2:20 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:25 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 2:35 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:40 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 2:50 | -0.10964 | 0 |  | 1.5
2017-08-13 | 2:55 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 3:05 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:10 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 3:20 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:25 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 3:35 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:40 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 3:50 | -0.10964 | 0 |  | 1.5
2017-08-13 | 3:55 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 4:05 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:10 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 4:20 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:25 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 4:35 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:40 | -0.10964 | 0 |  | 1.5
2017-08-13 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 4:50 | -0.11276 | 0 |  | 1.5
2017-08-13 | 4:55 | -0.10964 | 0 |  | 1.5
2017-08-13 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 5:05 | 1.9893 | 0 |  | 1.5
2017-08-13 | 5:10 | 2.1344 | 0 |  | 1.5
2017-08-13 | 5:15 | 2.0112 | 0 | 0 | 1.5 | 0 | 92.4059
2017-08-13 | 5:20 | 1.9199 | 0 |  | 1.5
2017-08-13 | 5:25 | 1.9402 | 0 |  | 1.5
2017-08-13 | 5:30 | 1.9776 | 0 | 0 | 1.5 | 0 | 87.0757
2017-08-13 | 5:35 | 1.9246 | 0 |  | 1.5
2017-08-13 | 5:40 | 1.9121 | 0 |  | 1.5
2017-08-13 | 5:45 | 1.8505 | 0 | 0 | 1.5 | 0 | 82.8019
2017-08-13 | 5:50 | 1.8021 | 0 |  | 1.5
2017-08-13 | 5:55 | 1.7959 | 0 |  | 1.5
2017-08-13 | 6:00 | 1.767 | 0 | 0 | 1.5 | 0 | 81.3282
2017-08-13 | 6:05 | 1.7819 | 0 |  | 1.5
2017-08-13 | 6:10 | 1.7803 | 0 |  | 1.5
2017-08-13 | 6:15 | 1.785 | 0 | 0 | 1.5 | 0 | 80.6403
2017-08-13 | 6:20 | 1.7351 | 0 |  | 1.5
2017-08-13 | 6:25 | 1.7483 | 0 |  | 1.5
2017-08-13 | 6:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 80.4013
2017-08-13 | 6:35 | 1.7904 | 0 |  | 1.5
2017-08-13 | 6:40 | 1.767 | 0 |  | 1.5
2017-08-13 | 6:45 | 1.7452 | 0 | 0 | 1.5 | 0 | 80.2569
2017-08-13 | 6:50 | 1.7561 | 0 |  | 1.5
2017-08-13 | 6:55 | 1.7733 | 0 |  | 1.5
2017-08-13 | 7:00 | 1.753 | 0 | 0 | 1.5 | 0 | 80.0331
2017-08-13 | 7:05 | 1.7499 | 0 |  | 1.5
2017-08-13 | 7:10 | 1.7897 | 0 |  | 1.5
2017-08-13 | 7:15 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.7718
2017-08-13 | 7:20 | 1.7429 | 0 |  | 1.5
2017-08-13 | 7:25 | 1.7795 | 0 |  | 1.5
2017-08-13 | 7:30 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.5667
2017-08-13 | 7:35 | 1.7288 | 0 |  | 1.5
2017-08-13 | 7:40 | 1.7444 | 0 |  | 1.5
2017-08-13 | 7:45 | 1.7312 | 0 | 0 | 1.5 | 0 | 79.4516
2017-08-13 | 7:50 | 1.7608 | 0 |  | 1.5
2017-08-13 | 7:55 | 1.7842 | 0 |  | 1.5
2017-08-13 | 8:00 | 1.7865 | 0 | 0 | 1.5 | 0 | 79.2554
2017-08-13 | 8:05 | 1.76 | 0 |  | 1.5
2017-08-13 | 8:10 | 1.6961 | 0 |  | 1.5
2017-08-13 | 8:15 | 1.7585 | 0 | 0 | 1.5 | 0 | 79.2035
2017-08-13 | 8:20 | 1.7577 | 0 |  | 1.5
2017-08-13 | 8:25 | 1.7725 | 0 |  | 1.5
2017-08-13 | 8:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 79.0892
2017-08-13 | 8:35 | 1.746 | 0 |  | 1.5
2017-08-13 | 8:40 | 1.7413 | 0 |  | 1.5
2017-08-13 | 8:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.2692
2017-08-13 | 8:50 | 1.7811 | 0 |  | 1.5
2017-08-13 | 8:55 | 1.7756 | 0 |  | 1.5
2017-08-13 | 9:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 79.2191
2017-08-13 | 9:05 | 1.7522 | 0 |  | 1.5
2017-08-13 | 9:10 | 1.7335 | 0 |  | 1.5
2017-08-13 | 9:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.2717
2017-08-13 | 9:20 | 1.7397 | 0 |  | 1.5
2017-08-13 | 9:25 | 1.7795 | 0 |  | 1.5
2017-08-13 | 9:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 79.2609
2017-08-13 | 9:35 | 1.7413 | 0 |  | 1.5
2017-08-13 | 9:40 | 1.7577 | 0 |  | 1.5
2017-08-13 | 9:45 | 1.767 | 0 | 0 | 1.5 | 0 | 79.3314
2017-08-13 | 9:50 | 1.7491 | 0 |  | 1.5
2017-08-13 | 9:55 | 1.7397 | 0 |  | 1.5
2017-08-13 | 10:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.387
2017-08-13 | 10:05 | 1.7507 | 0 |  | 1.5
2017-08-13 | 10:10 | 1.7514 | 0 |  | 1.5
2017-08-13 | 10:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 79.4193
2017-08-13 | 10:20 | 1.7327 | 0 |  | 1.5
2017-08-13 | 10:25 | 1.7421 | 0 |  | 1.5
2017-08-13 | 10:30 | 1.7304 | 0 | 0 | 1.5 | 0 | 79.5577
2017-08-13 | 10:35 | 1.7569 | 0 |  | 1.5
2017-08-13 | 10:40 | 1.7764 | 0 |  | 1.5
2017-08-13 | 10:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 79.4398
2017-08-13 | 10:50 | 1.7171 | 0 |  | 1.5
2017-08-13 | 10:55 | 1.7514 | 0 |  | 1.5
2017-08-13 | 11:00 | 1.7475 | 0 | 0 | 1.5 | 0 | 79.5123
2017-08-13 | 11:05 | 1.7639 | 0 |  | 1.5
2017-08-13 | 11:10 | 1.739 | 0 |  | 1.5
2017-08-13 | 11:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 79.5992
2017-08-13 | 11:20 | 1.7475 | 0 |  | 1.5
2017-08-13 | 11:25 | 1.7577 | 0 |  | 1.5
2017-08-13 | 11:30 | 1.7304 | 0 | 0 | 1.5 | 0 | 79.6411
2017-08-13 | 11:35 | 1.7507 | 0 |  | 1.5
2017-08-13 | 11:40 | 1.7678 | 0 |  | 1.5
2017-08-13 | 11:45 | 1.746 | 0 | 0 | 1.5 | 0 | 79.7425
2017-08-13 | 11:50 | 1.7382 | 0 |  | 1.5
2017-08-13 | 11:55 | 1.7468 | 0 |  | 1.5
2017-08-13 | 12:00 | 1.7444 | 0 | 0 | 1.5 | 0 | 79.8558
2017-08-13 | 12:05 | 1.7663 | 0 |  | 1.5
2017-08-13 | 12:10 | 1.7366 | 0 |  | 1.5
2017-08-13 | 12:15 | 1.7249 | 0 | 0 | 1.5 | 0 | 80.001
2017-08-13 | 12:20 | 1.746 | 0 |  | 1.5
2017-08-13 | 12:25 | 1.728 | 0 |  | 1.5
2017-08-13 | 12:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.9238
2017-08-13 | 12:35 | 1.7436 | 0 |  | 1.5
2017-08-13 | 12:40 | 1.7538 | 0 |  | 1.5
2017-08-13 | 12:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 80.0602
2017-08-13 | 12:50 | 1.7475 | 0 |  | 1.5
2017-08-13 | 12:55 | 1.7522 | 0 |  | 1.5
2017-08-13 | 13:00 | 1.7319 | 0 | 0 | 1.5 | 0 | 80.0931
2017-08-13 | 13:05 | 1.7444 | 0 |  | 1.5
2017-08-13 | 13:10 | 1.7226 | 0 |  | 1.5
2017-08-13 | 13:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 80.3079
2017-08-13 | 13:20 | 1.7382 | 0 |  | 1.5
2017-08-13 | 13:25 | 1.746 | 0 |  | 1.5
2017-08-13 | 13:30 | 1.7296 | 0 | 0 | 1.5 | 0 | 80.4884
2017-08-13 | 13:35 | 1.7265 | 0 |  | 1.5
2017-08-13 | 13:40 | 1.7429 | 0 |  | 1.5
2017-08-13 | 13:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 80.534
2017-08-13 | 13:50 | 1.7616 | 0 |  | 1.5
2017-08-13 | 13:55 | 1.7631 | 0 |  | 1.5
2017-08-13 | 14:00 | 1.7608 | 0 | 0 | 1.5 | 0 | 80.5161
2017-08-13 | 14:05 | 1.7631 | 0 |  | 1.5
2017-08-13 | 14:10 | 1.7546 | 0 |  | 1.5
2017-08-13 | 14:15 | 1.7405 | 0 | 0 | 1.5 | 0 | 80.4789
2017-08-13 | 14:20 | 1.7312 | 0 |  | 1.5
2017-08-13 | 14:25 | 1.7538 | 0 |  | 1.5
2017-08-13 | 14:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 80.7531
2017-08-13 | 14:35 | 1.7553 | 0 |  | 1.5
2017-08-13 | 14:40 | 1.7335 | 0 |  | 1.5
2017-08-13 | 14:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 80.8731
2017-08-13 | 14:50 | 1.7374 | 0 |  | 1.5
2017-08-13 | 14:55 | 1.7382 | 0 |  | 1.5
2017-08-13 | 15:00 | 1.7569 | 0 | 0 | 1.5 | 0 | 80.9952
2017-08-13 | 15:05 | 1.7343 | 0 |  | 1.5
2017-08-13 | 15:10 | 1.7491 | 0 |  | 1.5
2017-08-13 | 15:15 | 1.7514 | 0 | 0 | 1.5 | 0 | 81.1162
2017-08-13 | 15:20 | 1.7522 | 0 |  | 1.5
2017-08-13 | 15:25 | 1.7288 | 0 |  | 1.5
2017-08-13 | 15:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.2193
2017-08-13 | 15:35 | 1.7624 | 0 |  | 1.5
2017-08-13 | 15:40 | 1.7663 | 0 |  | 1.5
2017-08-13 | 15:45 | 1.7507 | 0 | 0 | 1.5 | 0 | 81.0725
2017-08-13 | 15:50 | 1.7335 | 0 |  | 1.5
2017-08-13 | 15:55 | 1.7569 | 0 |  | 1.5
2017-08-13 | 16:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 81.0186
2017-08-13 | 16:05 | 1.7553 | 0 |  | 1.5
2017-08-13 | 16:10 | 1.7592 | 0 |  | 1.5
2017-08-13 | 16:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 80.8663
2017-08-13 | 16:20 | 1.7592 | 0 |  | 1.5
2017-08-13 | 16:25 | 1.7382 | 0 |  | 1.5
2017-08-13 | 16:30 | 1.7366 | 0 | 0 | 1.5 | 0 | 80.8007
2017-08-13 | 16:35 | 1.7592 | 0 |  | 1.5
2017-08-13 | 16:40 | 1.7351 | 0 |  | 1.5
2017-08-13 | 16:45 | 1.7374 | 0 | 0 | 1.5 | 0 | 80.8275
2017-08-13 | 16:50 | 1.7553 | 0 |  | 1.5
2017-08-13 | 16:55 | 1.7608 | 0 |  | 1.5
2017-08-13 | 17:00 | 1.7382 | 0 | 0 | 1.5 | 0 | 80.7451
2017-08-13 | 17:05 | 1.7678 | 0 |  | 1.5
2017-08-13 | 17:10 | 1.7499 | 0 |  | 1.5
2017-08-13 | 17:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 80.6911
2017-08-13 | 17:20 | 1.767 | 0 |  | 1.5
2017-08-13 | 17:25 | 1.7585 | 0 |  | 1.5
2017-08-13 | 17:30 | 1.7702 | 0 | 0 | 1.5 | 0 | 80.3185
2017-08-13 | 17:35 | 1.7569 | 0 |  | 1.5
2017-08-13 | 17:40 | 1.7538 | 0 |  | 1.5
2017-08-13 | 17:45 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.9179
2017-08-13 | 17:50 | 1.7468 | 0 |  | 1.5
2017-08-13 | 17:55 | 1.7748 | 0 |  | 1.5
2017-08-13 | 18:00 | 1.7569 | 0 | 0 | 1.5 | 0 | 79.7824
2017-08-13 | 18:05 | 1.7553 | 0 |  | 1.5
2017-08-13 | 18:10 | 1.7569 | 0 |  | 1.5
2017-08-13 | 18:15 | 1.7928 | 0 | 0 | 1.5 | 0 | 79.5818
2017-08-13 | 18:20 | 1.7483 | 0 |  | 1.5
2017-08-13 | 18:25 | 1.7413 | 0 |  | 1.5
2017-08-13 | 18:30 | 1.7803 | 0 | 0 | 1.5 | 0 | 79.3416
2017-08-13 | 18:35 | 1.7553 | 0 |  | 1.5
2017-08-13 | 18:40 | 1.7452 | 0 |  | 1.5
2017-08-13 | 18:45 | 1.7795 | 0 | 0 | 1.5 | 0 | 79.2334
2017-08-13 | 18:50 | 1.7382 | 0 |  | 1.5
2017-08-13 | 18:55 | 1.7538 | 0 |  | 1.5
2017-08-13 | 19:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.1953
2017-08-13 | 19:05 | 1.7608 | 0 |  | 1.5
2017-08-13 | 19:10 | 1.7655 | 0 |  | 1.5
2017-08-13 | 19:15 | 1.7234 | 0 | 0 | 1.5 | 0 | 79.0941
2017-08-13 | 19:20 | 1.7733 | 0 |  | 1.5
2017-08-13 | 19:25 | 1.7553 | 0 |  | 1.5
2017-08-13 | 19:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 78.9539
2017-08-13 | 19:35 | 1.7756 | 0 |  | 1.5
2017-08-13 | 19:40 | 1.7709 | 0 |  | 1.5
2017-08-13 | 19:45 | 1.7452 | 0 | 0 | 1.5 | 0 | 78.7324
2017-08-13 | 19:50 | 1.7655 | 0 |  | 1.5
2017-08-13 | 19:55 | 1.7553 | 0 |  | 1.5
2017-08-13 | 20:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 78.5377
2017-08-13 | 20:05 | 1.7561 | 0 |  | 1.5
2017-08-13 | 20:10 | 1.7475 | 0 |  | 1.5
2017-08-13 | 20:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 78.3358
2017-08-13 | 20:20 | 1.7639 | 0 |  | 1.5
2017-08-13 | 20:25 | 1.7803 | 0 |  | 1.5
2017-08-13 | 20:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 77.9529
2017-08-13 | 20:35 | 1.7413 | 0 |  | 1.5
2017-08-13 | 20:40 | 1.767 | 0 |  | 1.5
2017-08-13 | 20:45 | 1.7561 | 0 | 0 | 1.5 | 0 | 77.6712
2017-08-13 | 20:50 | 1.7678 | 0 |  | 1.5
2017-08-13 | 20:55 | 1.7694 | 0 |  | 1.5
2017-08-13 | 21:00 | 1.7694 | 0 | 0 | 1.5 | 0 | 77.3824
2017-08-13 | 21:05 | -0.10652 | 0 |  | 1.5
2017-08-13 | 21:10 | -0.1073 | 0 |  | 1.5
2017-08-13 | 21:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 21:20 | -0.10808 | 0 |  | 1.5
2017-08-13 | 21:25 | -0.10808 | 0 |  | 1.5
2017-08-13 | 21:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 21:35 | -0.10808 | 0 |  | 1.5
2017-08-13 | 21:40 | -0.10964 | 0 |  | 1.5
2017-08-13 | 21:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 21:50 | -0.10964 | 0 |  | 1.5
2017-08-13 | 21:55 | -0.10886 | 0 |  | 1.5
2017-08-13 | 22:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 22:05 | -0.10964 | 0 |  | 1.5
2017-08-13 | 22:10 | -0.11042 | 0 |  | 1.5
2017-08-13 | 22:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 22:20 | -0.11042 | 0 |  | 1.5
2017-08-13 | 22:25 | -0.11042 | 0 |  | 1.5
2017-08-13 | 22:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 22:35 | -0.1112 | 0 |  | 1.5
2017-08-13 | 22:40 | -0.1112 | 0 |  | 1.5
2017-08-13 | 22:45 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 22:50 | -0.1112 | 0 |  | 1.5
2017-08-13 | 22:55 | -0.1112 | 0 |  | 1.5
2017-08-13 | 23:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 23:05 | -0.11042 | 0 |  | 1.5
2017-08-13 | 23:10 | -0.11042 | 0 |  | 1.5
2017-08-13 | 23:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 23:20 | -0.10886 | 0 |  | 1.5
2017-08-13 | 23:25 | -0.10808 | 0 |  | 1.5
2017-08-13 | 23:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 23:35 | -0.10808 | 0 |  | 1.5
2017-08-13 | 23:40 | -0.10808 | 0 |  | 1.5
2017-08-13 | 23:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-13 | 23:50 | -0.10808 | 0 |  | 1.5
2017-08-13 | 23:55 | -0.10808 | 0 |  | 1.5
2017-08-14 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 0:05 | -0.1073 | 0 |  | 1.5
2017-08-14 | 0:10 | -0.10808 | 0 |  | 1.5
2017-08-14 | 0:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 0:20 | -0.10808 | 0 |  | 1.5
2017-08-14 | 0:25 | -0.1073 | 0 |  | 1.5
2017-08-14 | 0:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-14 | 0:30 | [5 empty] | 0
2017-08-14 | 0:35 | -0.10808 | 0 |  | 1.5
2017-08-14 | 0:40 | -0.10808 | 0 |  | 1.5
2017-08-14 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 0:50 | -0.10808 | 0 |  | 1.5
2017-08-14 | 0:55 | -0.10808 | 0 |  | 1.5
2017-08-14 | 1:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-14 | 1:00 | [5 empty] | 0
2017-08-14 | 1:05 | -0.1073 | 0 |  | 1.5
2017-08-14 | 1:10 | -0.10808 | 0 |  | 1.5
2017-08-14 | 1:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 1:20 | -0.11198 | 0 |  | 1.5
2017-08-14 | 1:25 | -0.1112 | 0 |  | 1.5
2017-08-14 | 1:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-08-14 | 1:30 | [5 empty] | 0
2017-08-14 | 1:35 | -0.1112 | 0 |  | 1.5
2017-08-14 | 1:40 | -0.1112 | 0 |  | 1.5
2017-08-14 | 1:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 1:50 | -0.1112 | 0 |  | 1.5
2017-08-14 | 1:55 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:00 | -0.1112 | 0 | 0 | 1.5 | 0
2017-08-14 | 2:00 | [5 empty] | 0
2017-08-14 | 2:05 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:10 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:15 | -0.11198 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 2:20 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:25 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:30 | -0.1112 | 0 | 0 | 1.5 | 0
2017-08-14 | 2:30 | [5 empty] | 0
2017-08-14 | 2:35 | -0.11198 | 0 |  | 1.5
2017-08-14 | 2:40 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:45 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 2:50 | -0.1112 | 0 |  | 1.5
2017-08-14 | 2:55 | -0.11354 | 0 |  | 1.5
2017-08-14 | 3:00 | -0.11276 | 0 | 0 | 1.5 | 0
2017-08-14 | 3:00 | [5 empty] | 0
2017-08-14 | 3:05 | -0.11276 | 0 |  | 1.5
2017-08-14 | 3:10 | -0.11276 | 0 |  | 1.5
2017-08-14 | 3:15 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 3:20 | -0.11276 | 0 |  | 1.5
2017-08-14 | 3:25 | -0.11354 | 0 |  | 1.5
2017-08-14 | 3:30 | -0.11276 | 0 | 0 | 1.5 | 0
2017-08-14 | 3:30 | [5 empty] | 0
2017-08-14 | 3:35 | -0.11276 | 0 |  | 1.5
2017-08-14 | 3:40 | -0.11276 | 0 |  | 1.5
2017-08-14 | 3:45 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 3:50 | -0.11276 | 0 |  | 1.5
2017-08-14 | 3:55 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:00 | -0.11276 | 0 | 0 | 1.5 | 0
2017-08-14 | 4:00 | [5 empty] | 0
2017-08-14 | 4:05 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:10 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:15 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 4:20 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:25 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:30 | -0.11198 | 0 | 0 | 1.5 | 0
2017-08-14 | 4:30 | [5 empty] | 0
2017-08-14 | 4:35 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:40 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:45 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 4:50 | -0.11276 | 0 |  | 1.5
2017-08-14 | 4:55 | -0.11276 | 0 |  | 1.5
2017-08-14 | 5:00 | -0.11276 | 0 | 0 | 1.5 | 0
2017-08-14 | 5:00 | [5 empty] | 25.4
2017-08-14 | 5:05 | 2.4433 | 0 |  | 1.5
2017-08-14 | 5:10 | 2.3302 | 0 |  | 1.5
2017-08-14 | 5:15 | 2.0736 | 0 | 0 | 1.5 | 0
2017-08-14 | 5:15 | [5 empty] | 87.2668
2017-08-14 | 5:20 | 1.9472 | 0 |  | 1.5
2017-08-14 | 5:25 | 1.856 | 0 |  | 1.5
2017-08-14 | 5:30 | 1.8115 | 0 | 0 | 1.5 | 0
2017-08-14 | 5:30 | [5 empty] | 83.1511
2017-08-14 | 5:35 | 1.785 | 0 |  | 1.5
2017-08-14 | 5:40 | 1.7702 | 0 |  | 1.5
2017-08-14 | 5:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 82.287
2017-08-14 | 5:50 | 1.7577 | 0 |  | 1.5
2017-08-14 | 5:55 | 1.7343 | 0 |  | 1.5
2017-08-14 | 6:00 | 1.7741 | 0 | 0 | 1.5 | 0
2017-08-14 | 6:00 | [5 empty] | 82.1014
2017-08-14 | 6:05 | 1.76 | 0 |  | 1.5
2017-08-14 | 6:10 | 1.7631 | 0 |  | 1.5
2017-08-14 | 6:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 82.0694
2017-08-14 | 6:20 | 1.7405 | 0 |  | 1.5
2017-08-14 | 6:25 | 1.7514 | 0 |  | 1.5
2017-08-14 | 6:30 | 1.7569 | 0 | 0 | 1.5 | 0
2017-08-14 | 6:30 | [5 empty] | 82.0925
2017-08-14 | 6:35 | 1.7444 | 0 |  | 1.5
2017-08-14 | 6:40 | 1.7624 | 0 |  | 1.5
2017-08-14 | 6:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.0918
2017-08-14 | 6:50 | 1.7507 | 0 |  | 1.5
2017-08-14 | 6:55 | 1.7483 | 0 |  | 1.5
2017-08-14 | 7:00 | 1.7382 | 0 | 0 | 1.5 | 0
2017-08-14 | 7:00 | [5 empty] | 82.1594
2017-08-14 | 7:05 | 1.7546 | 0 |  | 1.5
2017-08-14 | 7:10 | 1.7319 | 0 |  | 1.5
2017-08-14 | 7:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.1616
2017-08-14 | 7:20 | 1.7811 | 0 |  | 1.5
2017-08-14 | 7:25 | 1.76 | 0 |  | 1.5
2017-08-14 | 7:30 | 1.7592 | 0 | 0 | 1.5 | 0
2017-08-14 | 7:30 | [5 empty] | 82.0884
2017-08-14 | 7:35 | 1.7405 | 0 |  | 1.5
2017-08-14 | 7:40 | 1.7546 | 0 |  | 1.5
2017-08-14 | 7:45 | 1.7241 | 0 | 0 | 1.5 | 0 | 82.3172
2017-08-14 | 7:50 | 1.746 | 0 |  | 1.5
2017-08-14 | 7:55 | 1.7366 | 0 |  | 1.5
2017-08-14 | 8:00 | 1.7585 | 0 | 0 | 1.5 | 0
2017-08-14 | 8:00 | [5 empty] | 82.6056
2017-08-14 | 8:05 | 1.7413 | 0 |  | 1.5
2017-08-14 | 8:10 | 1.7608 | 0 |  | 1.5
2017-08-14 | 8:15 | 1.7959 | 0 | 0 | 1.5 | 0
2017-08-14 | 8:15 | [5 empty] | 82.6391
2017-08-14 | 8:20 | 1.8193 | 0 |  | 1.5
2017-08-14 | 8:25 | 1.7811 | 0 |  | 1.5
2017-08-14 | 8:30 | 1.7631 | 0 | 0 | 1.5 | 0
2017-08-14 | 8:30 | [5 empty] | 81.4771
2017-08-14 | 8:35 | 1.7717 | 0 |  | 1.5
2017-08-14 | 8:40 | 1.7553 | 0 |  | 1.5
2017-08-14 | 8:45 | 1.7928 | 0 | 0 | 1.5 | 0 | 80.8444
2017-08-14 | 8:50 | 1.767 | 0 |  | 1.5
2017-08-14 | 8:55 | 1.7725 | 0 |  | 1.5
2017-08-14 | 9:00 | 1.7468 | 0 | 0 | 1.5 | 0
2017-08-14 | 9:00 | [5 empty] | 80.4373
2017-08-14 | 9:05 | 1.7436 | 0 |  | 1.5
2017-08-14 | 9:10 | 1.7327 | 0 |  | 1.5
2017-08-14 | 9:15 | 1.785 | 0 | 0 | 1.5 | 0 | 80.29
2017-08-14 | 9:20 | 1.7709 | 0 |  | 1.5
2017-08-14 | 9:25 | 1.7756 | 0 |  | 1.5
2017-08-14 | 9:30 | 1.7787 | 0 | 0 | 1.5 | 0
2017-08-14 | 9:30 | [5 empty] | 80.0656
2017-08-14 | 9:35 | 1.7873 | 0 |  | 1.5
2017-08-14 | 9:40 | 1.7647 | 0 |  | 1.5
2017-08-14 | 9:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 79.7795
2017-08-14 | 9:50 | 1.7397 | 0 |  | 1.5
2017-08-14 | 9:55 | 1.7889 | 0 |  | 1.5
2017-08-14 | 10:00 | 1.7351 | 0 | 0 | 1.5 | 0
2017-08-14 | 10:00 | [5 empty] | 79.6617
2017-08-14 | 10:05 | 1.767 | 0 |  | 1.5
2017-08-14 | 10:10 | 1.7366 | 0 |  | 1.5
2017-08-14 | 10:15 | 1.7179 | 0 | 0 | 1.5 | 0 | 79.8945
2017-08-14 | 10:20 | 1.7436 | 0 |  | 1.5
2017-08-14 | 10:25 | 1.7343 | 0 |  | 1.5
2017-08-14 | 10:30 | 1.7374 | 0 | 0 | 1.5 | 0
2017-08-14 | 10:30 | [5 empty] | 79.9744
2017-08-14 | 10:35 | 1.7 | 0 |  | 1.5
2017-08-14 | 10:40 | 1.7202 | 0 |  | 1.5
2017-08-14 | 10:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 80.2284
2017-08-14 | 10:50 | 1.7429 | 0 |  | 1.5
2017-08-14 | 10:55 | 1.7522 | 0 |  | 1.5
2017-08-14 | 11:00 | 1.7343 | 0 | 0 | 1.5 | 0
2017-08-14 | 11:00 | [5 empty] | 80.1728
2017-08-14 | 11:05 | 1.7382 | 0 |  | 1.5
2017-08-14 | 11:10 | 1.7553 | 0 |  | 1.5
2017-08-14 | 11:15 | 1.7764 | 0 | 0 | 1.5 | 0 | 80.0309
2017-08-14 | 11:20 | 1.7397 | 0 |  | 1.5
2017-08-14 | 11:25 | 1.7241 | 0 |  | 1.5
2017-08-14 | 11:30 | 1.7538 | 0 | 0 | 1.5 | 0
2017-08-14 | 11:30 | [5 empty] | 80.4329
2017-08-14 | 11:35 | 1.7366 | 0 |  | 1.5
2017-08-14 | 11:40 | 1.7561 | 0 |  | 1.5
2017-08-14 | 11:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 80.3154
2017-08-14 | 11:50 | 1.7756 | 0 |  | 1.5
2017-08-14 | 11:55 | 1.7663 | 0 |  | 1.5
2017-08-14 | 12:00 | 1.739 | 0 | 0 | 1.5 | 0
2017-08-14 | 12:00 | [5 empty] | 80.2223
2017-08-14 | 12:05 | 1.7429 | 0 |  | 1.5
2017-08-14 | 12:10 | 1.7366 | 0 |  | 1.5
2017-08-14 | 12:15 | 1.7312 | 0 | 0 | 1.5 | 0 | 80.6129
2017-08-14 | 12:20 | 1.6828 | 0 |  | 1.5
2017-08-14 | 12:25 | 1.7 | 0 |  | 1.5
2017-08-14 | 12:30 | 1.7631 | 0 | 0 | 1.5 | 0
2017-08-14 | 12:30 | [5 empty] | 81.7883
2017-08-14 | 12:35 | 1.7514 | 0 |  | 1.5
2017-08-14 | 12:40 | 1.7834 | 0 |  | 1.5
2017-08-14 | 12:45 | 1.785 | 0 | 0 | 1.5 | 0 | 81.4364
2017-08-14 | 12:50 | 1.7413 | 0 |  | 1.5
2017-08-14 | 12:55 | 1.739 | 0 |  | 1.5
2017-08-14 | 13:00 | 1.7585 | 0 | 0 | 1.5 | 0
2017-08-14 | 13:00 | [5 empty] | 81.4041
2017-08-14 | 13:05 | 1.7288 | 0 |  | 1.5
2017-08-14 | 13:10 | 1.7148 | 0 |  | 1.5
2017-08-14 | 13:15 | 1.7163 | 0 | 0 | 1.5 | 0
2017-08-14 | 13:15 | [5 empty] | 82.2014
2017-08-14 | 13:20 | 1.7007 | 0 |  | 1.5
2017-08-14 | 13:25 | 1.6797 | 0 |  | 1.5
2017-08-14 | 13:30 | 1.7023 | 0 | 0 | 1.5 | 0
2017-08-14 | 13:30 | [5 empty] | 83.5115
2017-08-14 | 13:35 | 1.7195 | 0 |  | 1.5
2017-08-14 | 13:40 | 1.7156 | 0 |  | 1.5
2017-08-14 | 13:45 | 1.7171 | 0 | 0 | 1.5 | 0 | 84.3486
2017-08-14 | 13:50 | 1.7171 | 0 |  | 1.5
2017-08-14 | 13:55 | 1.7093 | 0 |  | 1.5
2017-08-14 | 14:00 | 1.7538 | 0 | 0 | 1.5 | 0
2017-08-14 | 14:00 | [5 empty] | 85.2098
2017-08-14 | 14:05 | 1.7522 | 0 |  | 1.5
2017-08-14 | 14:10 | 1.728 | 0 |  | 1.5
2017-08-14 | 14:15 | 1.7491 | 0 | 0 | 1.5 | 0 | 85.5502
2017-08-14 | 14:20 | 1.7296 | 0 |  | 1.5
2017-08-14 | 14:25 | 1.707 | 0 |  | 1.5
2017-08-14 | 14:30 | 1.721 | 0 | 0 | 1.5 | 0
2017-08-14 | 14:30 | [5 empty] | 86.3655
2017-08-14 | 14:35 | 1.7405 | 0 |  | 1.5
2017-08-14 | 14:40 | 1.7943 | 0 |  | 1.5
2017-08-14 | 14:45 | 1.792 | 0 | 0 | 1.5 | 0 | 85.8829
2017-08-14 | 14:50 | 1.8014 | 0 |  | 1.5
2017-08-14 | 14:55 | 1.8146 | 0 |  | 1.5
2017-08-14 | 15:00 | 1.7842 | 0 | 0 | 1.5 | 0
2017-08-14 | 15:00 | [5 empty] | 84.4856
2017-08-14 | 15:05 | 1.7694 | 0 |  | 1.5
2017-08-14 | 15:10 | 1.746 | 0 |  | 1.5
2017-08-14 | 15:15 | 1.7452 | 0 | 0 | 1.5 | 0
2017-08-14 | 15:15 | [5 empty] | 84.2539
2017-08-14 | 15:20 | 1.7265 | 0 |  | 1.5
2017-08-14 | 15:25 | 1.7592 | 0 |  | 1.5
2017-08-14 | 15:30 | 1.7327 | 0 | 0 | 1.5 | 0
2017-08-14 | 15:30 | [5 empty] | 84.8867
2017-08-14 | 15:35 | 1.7475 | 0 |  | 1.5
2017-08-14 | 15:40 | 1.7296 | 0 |  | 1.5
2017-08-14 | 15:45 | 1.76 | 0 | 0 | 1.5 | 0 | 85.1394
2017-08-14 | 15:50 | 1.7444 | 0 |  | 1.5
2017-08-14 | 15:55 | 1.7811 | 0 |  | 1.5
2017-08-14 | 16:00 | 1.7647 | 0 | 0 | 1.5 | 0
2017-08-14 | 16:00 | [5 empty] | 84.9208
2017-08-14 | 16:05 | 1.7546 | 0 |  | 1.5
2017-08-14 | 16:10 | 1.7358 | 0 |  | 1.5
2017-08-14 | 16:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 84.6999
2017-08-14 | 16:20 | 1.7764 | 0 |  | 1.5
2017-08-14 | 16:25 | 1.746 | 0 |  | 1.5
2017-08-14 | 16:30 | 1.7686 | 0 | 0 | 1.5 | 0
2017-08-14 | 16:30 | [5 empty] | 84.3367
2017-08-14 | 16:35 | 1.7686 | 0 |  | 1.5
2017-08-14 | 16:40 | 1.76 | 0 |  | 1.5
2017-08-14 | 16:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 84.0956
2017-08-14 | 16:50 | 1.7585 | 0 |  | 1.5
2017-08-14 | 16:55 | 1.7312 | 0 |  | 1.5
2017-08-14 | 17:00 | 1.7413 | 0 | 0 | 1.5 | 0
2017-08-14 | 17:00 | [5 empty] | 84.065
2017-08-14 | 17:05 | 1.7655 | 0 |  | 1.5
2017-08-14 | 17:10 | 1.7756 | 0 |  | 1.5
2017-08-14 | 17:15 | 1.7756 | 0 | 0 | 1.5 | 0
2017-08-14 | 17:15 | [5 empty] | 83.6595
2017-08-14 | 17:20 | 1.7975 | 0 |  | 1.5
2017-08-14 | 17:25 | 1.7748 | 0 |  | 1.5
2017-08-14 | 17:30 | 1.8006 | 0 | 0 | 1.5 | 0 | 82.9313
2017-08-14 | 17:35 | 1.7819 | 0 |  | 1.5
2017-08-14 | 17:40 | 1.7694 | 0 |  | 1.5
2017-08-14 | 17:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 82.1867
2017-08-14 | 17:50 | 1.7795 | 0 |  | 1.5
2017-08-14 | 17:55 | 1.7647 | 0 |  | 1.5
2017-08-14 | 18:00 | 1.7608 | 0 | 0 | 1.5 | 0
2017-08-14 | 18:00 | [5 empty] | 81.7093
2017-08-14 | 18:05 | 1.7858 | 0 |  | 1.5
2017-08-14 | 18:10 | 1.7452 | 0 |  | 1.5
2017-08-14 | 18:15 | 1.7491 | 0 | 0 | 1.5 | 0 | 81.5053
2017-08-14 | 18:20 | 1.767 | 0 |  | 1.5
2017-08-14 | 18:25 | 1.7569 | 0 |  | 1.5
2017-08-14 | 18:30 | 1.76 | 0 | 0 | 1.5 | 0
2017-08-14 | 18:30 | [5 empty] | 81.1664
2017-08-14 | 18:35 | 1.7725 | 0 |  | 1.5
2017-08-14 | 18:40 | 1.7772 | 0 |  | 1.5
2017-08-14 | 18:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 80.6981
2017-08-14 | 18:50 | 1.746 | 0 |  | 1.5
2017-08-14 | 18:55 | 1.7561 | 0 |  | 1.5
2017-08-14 | 19:00 | 1.7585 | 0 | 0 | 1.5 | 0
2017-08-14 | 19:00 | [5 empty] | 80.503
2017-08-14 | 19:05 | 1.7624 | 0 |  | 1.5
2017-08-14 | 19:10 | 1.753 | 0 |  | 1.5
2017-08-14 | 19:15 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.1112
2017-08-14 | 19:20 | 1.7577 | 0 |  | 1.5
2017-08-14 | 19:25 | 1.7592 | 0 |  | 1.5
2017-08-14 | 19:30 | 1.7678 | 0 | 0 | 1.5 | 0
2017-08-14 | 19:30 | [5 empty] | 79.7992
2017-08-14 | 19:35 | 1.7374 | 0 |  | 1.5
2017-08-14 | 19:40 | 1.7592 | 0 |  | 1.5
2017-08-14 | 19:45 | 1.7249 | 0 | 0 | 1.5 | 0 | 79.722
2017-08-14 | 19:50 | 1.7522 | 0 |  | 1.5
2017-08-14 | 19:55 | 1.7694 | 0 |  | 1.5
2017-08-14 | 20:00 | 1.7647 | 0 | 0 | 1.5 | 0
2017-08-14 | 20:00 | [5 empty] | 79.4106
2017-08-14 | 20:05 | 1.7897 | 0 |  | 1.5
2017-08-14 | 20:10 | 1.7639 | 0 |  | 1.5
2017-08-14 | 20:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 79.1145
2017-08-14 | 20:20 | 1.7631 | 0 |  | 1.5
2017-08-14 | 20:25 | 1.7663 | 0 |  | 1.5
2017-08-14 | 20:30 | 1.7577 | 0 | 0 | 1.5 | 0
2017-08-14 | 20:30 | [5 empty] | 78.9721
2017-08-14 | 20:35 | 1.7546 | 0 |  | 1.5
2017-08-14 | 20:40 | 1.7553 | 0 |  | 1.5
2017-08-14 | 20:45 | 1.7764 | 0 | 0 | 1.5 | 0 | 78.9141
2017-08-14 | 20:50 | 1.7624 | 0 |  | 1.5
2017-08-14 | 20:55 | 1.7397 | 0 |  | 1.5
2017-08-14 | 21:00 | 1.7546 | 0 | 0 | 1.5 | 0
2017-08-14 | 21:00 | [5 empty] | 0
2017-08-14 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-14 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-14 | 21:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-14 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-14 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-14 | 21:30 | [5 empty] | 0
2017-08-14 | 21:35 | -0.10808 | 0 |  | 1.5
2017-08-14 | 21:40 | -0.10418 | 0 |  | 1.5
2017-08-14 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-14 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-14 | 22:30 | [5 empty] | 0
2017-08-14 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:40 | -0.10418 | 0 |  | 1.5
2017-08-14 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-14 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-14 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-14 | 23:00 | [5 empty] | 0
2017-08-14 | 23:05 | -0.10886 | 0 |  | 1.5
2017-08-14 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-14 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-14 | 23:15 | [5 empty] | 0
2017-08-14 | 23:20 | -0.10574 | 0 |  | 1.5
2017-08-14 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-14 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-14 | 23:30 | [5 empty] | 0
2017-08-14 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-14 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-14 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-14 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-14 | 23:55 | -0.10574 | 0 |  | 1.5
2017-08-15 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-15 | 0:00 | [5 empty] | 0
2017-08-15 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-15 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-15 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 0:20 | -0.10496 | 0 |  | 1.5
2017-08-15 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-15 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-15 | 0:40 | -0.10574 | 0 |  | 1.5
2017-08-15 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 0:50 | -0.10574 | 0 |  | 1.5
2017-08-15 | 0:55 | -0.10574 | 0 |  | 1.5
2017-08-15 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-15 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-15 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 1:20 | -0.10886 | 0 |  | 1.5
2017-08-15 | 1:25 | -0.10886 | 0 |  | 1.5
2017-08-15 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 1:35 | -0.10886 | 0 |  | 1.5
2017-08-15 | 1:40 | -0.10886 | 0 |  | 1.5
2017-08-15 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 1:50 | -0.10886 | 0 |  | 1.5
2017-08-15 | 1:55 | -0.10886 | 0 |  | 1.5
2017-08-15 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 2:05 | -0.10886 | 0 |  | 1.5
2017-08-15 | 2:10 | -0.11198 | 0 |  | 1.5
2017-08-15 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 2:20 | -0.10886 | 0 |  | 1.5
2017-08-15 | 2:25 | -0.10886 | 0 |  | 1.5
2017-08-15 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 2:35 | -0.10886 | 0 |  | 1.5
2017-08-15 | 2:40 | -0.10964 | 0 |  | 1.5
2017-08-15 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 2:50 | -0.10886 | 0 |  | 1.5
2017-08-15 | 2:55 | -0.10964 | 0 |  | 1.5
2017-08-15 | 3:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 3:05 | -0.10964 | 0 |  | 1.5
2017-08-15 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-15 | 3:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-15 | 3:25 | -0.10886 | 0 |  | 1.5
2017-08-15 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 3:35 | -0.10886 | 0 |  | 1.5
2017-08-15 | 3:40 | -0.10886 | 0 |  | 1.5
2017-08-15 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 3:50 | -0.10964 | 0 |  | 1.5
2017-08-15 | 3:55 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 4:05 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:10 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 4:20 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:25 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 4:35 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:40 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 4:50 | -0.10964 | 0 |  | 1.5
2017-08-15 | 4:55 | -0.10964 | 0 |  | 1.5
2017-08-15 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 5:05 | 2.3567 | 0 |  | 1.5
2017-08-15 | 5:10 | 2.3513 | 0 |  | 1.5
2017-08-15 | 5:15 | 2.1344 | 0 | 0 | 1.5 | 0 | 87.5476
2017-08-15 | 5:20 | 1.9652 | 0 |  | 1.5
2017-08-15 | 5:25 | 1.9012 | 0 |  | 1.5
2017-08-15 | 5:30 | 1.8302 | 0 | 0 | 1.5 | 0 | 83.0353
2017-08-15 | 5:35 | 1.8029 | 0 |  | 1.5
2017-08-15 | 5:40 | 1.7764 | 0 |  | 1.5
2017-08-15 | 5:45 | 1.76 | 0 | 0 | 1.5 | 0 | 82.0016
2017-08-15 | 5:50 | 1.7507 | 0 |  | 1.5
2017-08-15 | 5:55 | 1.7444 | 0 |  | 1.5
2017-08-15 | 6:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 81.7779
2017-08-15 | 6:05 | 1.753 | 0 |  | 1.5
2017-08-15 | 6:10 | 1.739 | 0 |  | 1.5
2017-08-15 | 6:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 81.7485
2017-08-15 | 6:20 | 1.76 | 0 |  | 1.5
2017-08-15 | 6:25 | 1.7163 | 0 |  | 1.5
2017-08-15 | 6:30 | 1.7374 | 0 | 0 | 1.5 | 0 | 81.7892
2017-08-15 | 6:35 | 1.7265 | 0 |  | 1.5
2017-08-15 | 6:40 | 1.7491 | 0 |  | 1.5
2017-08-15 | 6:45 | 1.778 | 0 | 0 | 1.5 | 0 | 81.8973
2017-08-15 | 6:50 | 1.7483 | 0 |  | 1.5
2017-08-15 | 6:55 | 1.746 | 0 |  | 1.5
2017-08-15 | 7:00 | 1.7475 | 0 | 0 | 1.5 | 0 | 82.0418
2017-08-15 | 7:05 | 1.7756 | 0 |  | 1.5
2017-08-15 | 7:10 | 1.7553 | 0 |  | 1.5
2017-08-15 | 7:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 82.0706
2017-08-15 | 7:20 | 1.7499 | 0 |  | 1.5
2017-08-15 | 7:25 | 1.7413 | 0 |  | 1.5
2017-08-15 | 7:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 82.164
2017-08-15 | 7:35 | 1.7577 | 0 |  | 1.5
2017-08-15 | 7:40 | 1.7522 | 0 |  | 1.5
2017-08-15 | 7:45 | 1.7709 | 0 | 0 | 1.5 | 0 | 82.3645
2017-08-15 | 7:50 | 1.8037 | 0 |  | 1.5
2017-08-15 | 7:55 | 1.8263 | 0 |  | 1.5
2017-08-15 | 8:00 | 1.7982 | 0 | 0 | 1.5 | 0 | 80.6801
2017-08-15 | 8:05 | 1.7811 | 0 |  | 1.5
2017-08-15 | 8:10 | 1.7592 | 0 |  | 1.5
2017-08-15 | 8:15 | 1.7842 | 0 | 0 | 1.5 | 0 | 79.8304
2017-08-15 | 8:20 | 1.767 | 0 |  | 1.5
2017-08-15 | 8:25 | 1.7647 | 0 |  | 1.5
2017-08-15 | 8:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 79.5357
2017-08-15 | 8:35 | 1.7631 | 0 |  | 1.5
2017-08-15 | 8:40 | 1.7569 | 0 |  | 1.5
2017-08-15 | 8:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.5395
2017-08-15 | 8:50 | 1.7382 | 0 |  | 1.5
2017-08-15 | 8:55 | 1.7725 | 0 |  | 1.5
2017-08-15 | 9:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.5882
2017-08-15 | 9:05 | 1.7234 | 0 |  | 1.5
2017-08-15 | 9:10 | 1.7366 | 0 |  | 1.5
2017-08-15 | 9:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 79.9265
2017-08-15 | 9:20 | 1.785 | 0 |  | 1.5
2017-08-15 | 9:25 | 1.746 | 0 |  | 1.5
2017-08-15 | 9:30 | 1.7553 | 0 | 0 | 1.5 | 0 | 80.0871
2017-08-15 | 9:35 | 1.7709 | 0 |  | 1.5
2017-08-15 | 9:40 | 1.7483 | 0 |  | 1.5
2017-08-15 | 9:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 80.1177
2017-08-15 | 9:50 | 1.7631 | 0 |  | 1.5
2017-08-15 | 9:55 | 1.7078 | 0 |  | 1.5
2017-08-15 | 10:00 | 1.6797 | 0 | 0 | 1.5 | 0 | 80.7504
2017-08-15 | 10:05 | 1.7265 | 0 |  | 1.5
2017-08-15 | 10:10 | 1.7093 | 0 |  | 1.5
2017-08-15 | 10:15 | 1.7031 | 0 | 0 | 1.5 | 0 | 81.8781
2017-08-15 | 10:20 | 1.7109 | 0 |  | 1.5
2017-08-15 | 10:25 | 1.7085 | 0 |  | 1.5
2017-08-15 | 10:30 | 1.7171 | 0 | 0 | 1.5 | 0 | 82.6796
2017-08-15 | 10:35 | 1.7483 | 0 |  | 1.5
2017-08-15 | 10:40 | 1.7436 | 0 |  | 1.5
2017-08-15 | 10:45 | 1.8084 | 0 | 0 | 1.5 | 0 | 82.3748
2017-08-15 | 10:50 | 1.7631 | 0 |  | 1.5
2017-08-15 | 10:55 | 1.7397 | 0 |  | 1.5
2017-08-15 | 11:00 | 1.7468 | 0 | 0 | 1.5 | 0 | 81.7343
2017-08-15 | 11:05 | 1.7507 | 0 |  | 1.5
2017-08-15 | 11:10 | 1.7522 | 0 |  | 1.5
2017-08-15 | 11:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 81.8885
2017-08-15 | 11:20 | 1.7179 | 0 |  | 1.5
2017-08-15 | 11:25 | 1.7538 | 0 |  | 1.5
2017-08-15 | 11:30 | 1.7335 | 0 | 0 | 1.5 | 0 | 82.1241
2017-08-15 | 11:35 | 1.7468 | 0 |  | 1.5
2017-08-15 | 11:40 | 1.6937 | 0 |  | 1.5
2017-08-15 | 11:45 | 1.6649 | 0 | 0 | 1.5 | 0 | 83.3482
2017-08-15 | 11:50 | 1.6688 | 0 |  | 1.5
2017-08-15 | 11:55 | 1.7109 | 0 |  | 1.5
2017-08-15 | 12:00 | 1.7304 | 0 | 0 | 1.5 | 0 | 84.9784
2017-08-15 | 12:05 | 1.7195 | 0 |  | 1.5
2017-08-15 | 12:10 | 1.7405 | 0 |  | 1.5
2017-08-15 | 12:15 | 1.7039 | 0 | 0 | 1.5 | 0 | 86.0874
2017-08-15 | 12:20 | 1.7171 | 0 |  | 1.5
2017-08-15 | 12:25 | 1.7007 | 0 |  | 1.5
2017-08-15 | 12:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 87.1084
2017-08-15 | 12:35 | 1.7444 | 0 |  | 1.5
2017-08-15 | 12:40 | 1.7577 | 0 |  | 1.5
2017-08-15 | 12:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 86.9129
2017-08-15 | 12:50 | 1.767 | 0 |  | 1.5
2017-08-15 | 12:55 | 1.7538 | 0 |  | 1.5
2017-08-15 | 13:00 | 1.7101 | 0 | 0 | 1.5 | 0 | 86.8516
2017-08-15 | 13:05 | 1.6851 | 0 |  | 1.5
2017-08-15 | 13:10 | 1.7046 | 0 |  | 1.5
2017-08-15 | 13:15 | 1.7226 | 0 | 0 | 1.5 | 0 | 88.1221
2017-08-15 | 13:20 | 1.7187 | 0 |  | 1.5
2017-08-15 | 13:25 | 1.728 | 0 |  | 1.5
2017-08-15 | 13:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 88.5763
2017-08-15 | 13:35 | 1.7663 | 0 |  | 1.5
2017-08-15 | 13:40 | 1.7577 | 0 |  | 1.5
2017-08-15 | 13:45 | 1.7686 | 0 | 0 | 1.5 | 0 | 88.5494
2017-08-15 | 13:50 | 1.7889 | 0 |  | 1.5
2017-08-15 | 13:55 | 1.7865 | 0 |  | 1.5
2017-08-15 | 14:00 | 1.7943 | 0 | 0 | 1.5 | 0 | 87.6559
2017-08-15 | 14:05 | 1.7936 | 0 |  | 1.5
2017-08-15 | 14:10 | 1.8014 | 0 |  | 1.5
2017-08-15 | 14:15 | 1.7928 | 0 | 0 | 1.5 | 0 | 86.1874
2017-08-15 | 14:20 | 1.8053 | 0 |  | 1.5
2017-08-15 | 14:25 | 1.8185 | 0 |  | 1.5
2017-08-15 | 14:30 | 1.7725 | 0 | 0 | 1.5 | 0 | 85.2136
2017-08-15 | 14:35 | 1.7351 | 0 |  | 1.5
2017-08-15 | 14:40 | 1.7686 | 0 |  | 1.5
2017-08-15 | 14:45 | 1.7366 | 0 | 0 | 1.5 | 0 | 85.1085
2017-08-15 | 14:50 | 1.7639 | 0 |  | 1.5
2017-08-15 | 14:55 | 1.714 | 0 |  | 1.5
2017-08-15 | 15:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 85.7252
2017-08-15 | 15:05 | 1.753 | 0 |  | 1.5
2017-08-15 | 15:10 | 1.7452 | 0 |  | 1.5
2017-08-15 | 15:15 | 1.7343 | 0 | 0 | 1.5 | 0 | 86.4558
2017-08-15 | 15:20 | 1.7397 | 0 |  | 1.5
2017-08-15 | 15:25 | 1.6867 | 0 |  | 1.5
2017-08-15 | 15:30 | 1.7179 | 0 | 0 | 1.5 | 0 | 87.3427
2017-08-15 | 15:35 | 1.7499 | 0 |  | 1.5
2017-08-15 | 15:40 | 1.7522 | 0 |  | 1.5
2017-08-15 | 15:45 | 1.7795 | 0 | 0 | 1.5 | 0 | 87.3679
2017-08-15 | 15:50 | 1.7647 | 0 |  | 1.5
2017-08-15 | 15:55 | 1.8123 | 0 |  | 1.5
2017-08-15 | 16:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 86.5572
2017-08-15 | 16:05 | 1.7577 | 0 |  | 1.5
2017-08-15 | 16:10 | 1.7631 | 0 |  | 1.5
2017-08-15 | 16:15 | 1.8287 | 0 | 0 | 1.5 | 0 | 85.7252
2017-08-15 | 16:20 | 1.7873 | 0 |  | 1.5
2017-08-15 | 16:25 | 1.7998 | 0 |  | 1.5
2017-08-15 | 16:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 84.4217
2017-08-15 | 16:35 | 1.7686 | 0 |  | 1.5
2017-08-15 | 16:40 | 1.7592 | 0 |  | 1.5
2017-08-15 | 16:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 83.8105
2017-08-15 | 16:50 | 1.7413 | 0 |  | 1.5
2017-08-15 | 16:55 | 1.7655 | 0 |  | 1.5
2017-08-15 | 17:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 83.4466
2017-08-15 | 17:05 | 1.7296 | 0 |  | 1.5
2017-08-15 | 17:10 | 1.7304 | 0 |  | 1.5
2017-08-15 | 17:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 84.0289
2017-08-15 | 17:20 | 1.7865 | 0 |  | 1.5
2017-08-15 | 17:25 | 1.7998 | 0 |  | 1.5
2017-08-15 | 17:30 | 1.7928 | 0 | 0 | 1.5 | 0 | 83.3793
2017-08-15 | 17:35 | 1.7569 | 0 |  | 1.5
2017-08-15 | 17:40 | 1.7943 | 0 |  | 1.5
2017-08-15 | 17:45 | 1.7561 | 0 | 0 | 1.5 | 0 | 82.8957
2017-08-15 | 17:50 | 1.7741 | 0 |  | 1.5
2017-08-15 | 17:55 | 1.7608 | 0 |  | 1.5
2017-08-15 | 18:00 | 1.7553 | 0 | 0 | 1.5 | 0 | 82.3567
2017-08-15 | 18:05 | 1.7881 | 0 |  | 1.5
2017-08-15 | 18:10 | 1.7858 | 0 |  | 1.5
2017-08-15 | 18:15 | 1.785 | 0 | 0 | 1.5 | 0 | 81.625
2017-08-15 | 18:20 | 1.7655 | 0 |  | 1.5
2017-08-15 | 18:25 | 1.7647 | 0 |  | 1.5
2017-08-15 | 18:30 | 1.7889 | 0 | 0 | 1.5 | 0 | 81.0896
2017-08-15 | 18:35 | 1.767 | 0 |  | 1.5
2017-08-15 | 18:40 | 1.76 | 0 |  | 1.5
2017-08-15 | 18:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 80.5904
2017-08-15 | 18:50 | 1.7483 | 0 |  | 1.5
2017-08-15 | 18:55 | 1.7819 | 0 |  | 1.5
2017-08-15 | 19:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 80.2405
2017-08-15 | 19:05 | 1.7663 | 0 |  | 1.5
2017-08-15 | 19:10 | 1.7585 | 0 |  | 1.5
2017-08-15 | 19:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 79.8143
2017-08-15 | 19:20 | 1.7514 | 0 |  | 1.5
2017-08-15 | 19:25 | 1.7655 | 0 |  | 1.5
2017-08-15 | 19:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.8298
2017-08-15 | 19:35 | 1.7468 | 0 |  | 1.5
2017-08-15 | 19:40 | 1.7288 | 0 |  | 1.5
2017-08-15 | 19:45 | 1.7491 | 0 | 0 | 1.5 | 0 | 79.9801
2017-08-15 | 19:50 | 1.739 | 0 |  | 1.5
2017-08-15 | 19:55 | 1.7374 | 0 |  | 1.5
2017-08-15 | 20:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 79.9691
2017-08-15 | 20:05 | 1.7374 | 0 |  | 1.5
2017-08-15 | 20:10 | 1.753 | 0 |  | 1.5
2017-08-15 | 20:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.7343
2017-08-15 | 20:20 | 1.7374 | 0 |  | 1.5
2017-08-15 | 20:25 | 1.7725 | 0 |  | 1.5
2017-08-15 | 20:30 | 1.739 | 0 | 0 | 1.5 | 0 | 79.8717
2017-08-15 | 20:35 | 1.7569 | 0 |  | 1.5
2017-08-15 | 20:40 | 1.76 | 0 |  | 1.5
2017-08-15 | 20:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 79.7103
2017-08-15 | 20:50 | 1.7499 | 0 |  | 1.5
2017-08-15 | 20:55 | 1.7382 | 0 |  | 1.5
2017-08-15 | 21:00 | 1.7826 | 0 | 0 | 1.5 | 0 | 79.4539
2017-08-15 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-15 | 21:10 | -0.1034 | 0 |  | 1.5
2017-08-15 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 21:20 | -0.1034 | 0 |  | 1.5
2017-08-15 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-15 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-15 | 21:40 | -0.10418 | 0 |  | 1.5
2017-08-15 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-15 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-15 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 22:50 | -0.10418 | 0 |  | 1.5
2017-08-15 | 22:55 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 23:05 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:10 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 23:20 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:25 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 23:35 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:40 | -0.1034 | 0 |  | 1.5
2017-08-15 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-15 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-15 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-16 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-16 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-16 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-16 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 1:20 | -0.1073 | 0 |  | 1.5
2017-08-16 | 1:25 | -0.1073 | 0 |  | 1.5
2017-08-16 | 1:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 1:35 | -0.1073 | 0 |  | 1.5
2017-08-16 | 1:40 | -0.1073 | 0 |  | 1.5
2017-08-16 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 1:50 | -0.1073 | 0 |  | 1.5
2017-08-16 | 1:55 | -0.1073 | 0 |  | 1.5
2017-08-16 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-16 | 2:10 | -0.10808 | 0 |  | 1.5
2017-08-16 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-16 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-16 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-16 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-16 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-16 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-16 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-16 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-16 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-16 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-16 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-16 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-16 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-16 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-16 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-16 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 5:05 | 2.1024 | 0 |  | 1.5
2017-08-16 | 5:10 | 2.2818 | 0 |  | 1.5
2017-08-16 | 5:15 | 2.0486 | 0 | 0 | 1.5 | 0 | 89.6607
2017-08-16 | 5:20 | 1.9511 | 0 |  | 1.5
2017-08-16 | 5:25 | 1.8583 | 0 |  | 1.5
2017-08-16 | 5:30 | 1.7826 | 0 | 0 | 1.5 | 0 | 86.1516
2017-08-16 | 5:35 | 1.7546 | 0 |  | 1.5
2017-08-16 | 5:40 | 1.7608 | 0 |  | 1.5
2017-08-16 | 5:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 85.8921
2017-08-16 | 5:50 | 1.7522 | 0 |  | 1.5
2017-08-16 | 5:55 | 1.7553 | 0 |  | 1.5
2017-08-16 | 6:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 86.043
2017-08-16 | 6:05 | 1.7507 | 0 |  | 1.5
2017-08-16 | 6:10 | 1.7475 | 0 |  | 1.5
2017-08-16 | 6:15 | 1.7382 | 0 | 0 | 1.5 | 0 | 86.2149
2017-08-16 | 6:20 | 1.7468 | 0 |  | 1.5
2017-08-16 | 6:25 | 1.7522 | 0 |  | 1.5
2017-08-16 | 6:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 86.3622
2017-08-16 | 6:35 | 1.7522 | 0 |  | 1.5
2017-08-16 | 6:40 | 1.7577 | 0 |  | 1.5
2017-08-16 | 6:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 86.4818
2017-08-16 | 6:50 | 1.7569 | 0 |  | 1.5
2017-08-16 | 6:55 | 1.7553 | 0 |  | 1.5
2017-08-16 | 7:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 86.507
2017-08-16 | 7:05 | 1.7452 | 0 |  | 1.5
2017-08-16 | 7:10 | 1.7507 | 0 |  | 1.5
2017-08-16 | 7:15 | 1.8076 | 0 | 0 | 1.5 | 0 | 86.5263
2017-08-16 | 7:20 | 1.7967 | 0 |  | 1.5
2017-08-16 | 7:25 | 1.895 | 0 |  | 1.5
2017-08-16 | 7:30 | 1.9394 | 0 | 0 | 1.5 | 0 | 83.7139
2017-08-16 | 7:35 | 1.884 | 0 |  | 1.5
2017-08-16 | 7:40 | 1.8482 | 0 |  | 1.5
2017-08-16 | 7:45 | 1.8107 | 0 | 0 | 1.5 | 0 | 80.9208
2017-08-16 | 7:50 | 1.8014 | 0 |  | 1.5
2017-08-16 | 7:55 | 1.806 | 0 |  | 1.5
2017-08-16 | 8:00 | 1.7772 | 0 | 0 | 1.5 | 0 | 79.7957
2017-08-16 | 8:05 | 1.7795 | 0 |  | 1.5
2017-08-16 | 8:10 | 1.7226 | 0 |  | 1.5
2017-08-16 | 8:15 | 1.7335 | 0 | 0 | 1.5 | 0 | 79.6527
2017-08-16 | 8:20 | 1.7132 | 0 |  | 1.5
2017-08-16 | 8:25 | 1.7663 | 0 |  | 1.5
2017-08-16 | 8:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 80.0475
2017-08-16 | 8:35 | 1.7132 | 0 |  | 1.5
2017-08-16 | 8:40 | 1.7335 | 0 |  | 1.5
2017-08-16 | 8:45 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.9015
2017-08-16 | 8:50 | 1.7218 | 0 |  | 1.5
2017-08-16 | 8:55 | 1.7382 | 0 |  | 1.5
2017-08-16 | 9:00 | 1.7288 | 0 | 0 | 1.5 | 0 | 80.0928
2017-08-16 | 9:05 | 1.7655 | 0 |  | 1.5
2017-08-16 | 9:10 | 1.7366 | 0 |  | 1.5
2017-08-16 | 9:15 | 1.7733 | 0 | 0 | 1.5 | 0 | 80.0812
2017-08-16 | 9:20 | 1.7741 | 0 |  | 1.5
2017-08-16 | 9:25 | 1.7288 | 0 |  | 1.5
2017-08-16 | 9:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 80.124
2017-08-16 | 9:35 | 1.7507 | 0 |  | 1.5
2017-08-16 | 9:40 | 1.7241 | 0 |  | 1.5
2017-08-16 | 9:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 80.308
2017-08-16 | 9:50 | 1.7546 | 0 |  | 1.5
2017-08-16 | 9:55 | 1.7585 | 0 |  | 1.5
2017-08-16 | 10:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 80.3881
2017-08-16 | 10:05 | 1.7522 | 0 |  | 1.5
2017-08-16 | 10:10 | 1.7709 | 0 |  | 1.5
2017-08-16 | 10:15 | 1.7787 | 0 | 0 | 1.5 | 0 | 80.4579
2017-08-16 | 10:20 | 1.7273 | 0 |  | 1.5
2017-08-16 | 10:25 | 1.7444 | 0 |  | 1.5
2017-08-16 | 10:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 80.6649
2017-08-16 | 10:35 | 1.7101 | 0 |  | 1.5
2017-08-16 | 10:40 | 1.7335 | 0 |  | 1.5
2017-08-16 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 80.9658
2017-08-16 | 10:50 | 1.7351 | 0 |  | 1.5
2017-08-16 | 10:55 | 1.7374 | 0 |  | 1.5
2017-08-16 | 11:00 | 1.7319 | 0 | 0 | 1.5 | 0 | 81.325
2017-08-16 | 11:05 | 1.6937 | 0 |  | 1.5
2017-08-16 | 11:10 | 1.7234 | 0 |  | 1.5
2017-08-16 | 11:15 | 1.7241 | 0 | 0 | 1.5 | 0 | 82.0278
2017-08-16 | 11:20 | 1.7257 | 0 |  | 1.5
2017-08-16 | 11:25 | 1.6781 | 0 |  | 1.5
2017-08-16 | 11:30 | 1.7078 | 0 | 0 | 1.5 | 0 | 83.0013
2017-08-16 | 11:35 | 1.7085 | 0 |  | 1.5
2017-08-16 | 11:40 | 1.6742 | 0 |  | 1.5
2017-08-16 | 11:45 | 1.7015 | 0 | 0 | 1.5 | 0 | 84.4016
2017-08-16 | 11:50 | 1.6844 | 0 |  | 1.5
2017-08-16 | 11:55 | 1.7093 | 0 |  | 1.5
2017-08-16 | 12:00 | 1.6766 | 0 | 0 | 1.5 | 0 | 85.7709
2017-08-16 | 12:05 | 1.6805 | 0 |  | 1.5
2017-08-16 | 12:10 | 1.714 | 0 |  | 1.5
2017-08-16 | 12:15 | 1.7093 | 0 | 0 | 1.5 | 0 | 86.9831
2017-08-16 | 12:20 | 1.7031 | 0 |  | 1.5
2017-08-16 | 12:25 | 1.728 | 0 |  | 1.5
2017-08-16 | 12:30 | 1.7335 | 0 | 0 | 1.5 | 0 | 88.0239
2017-08-16 | 12:35 | 1.7577 | 0 |  | 1.5
2017-08-16 | 12:40 | 1.7491 | 0 |  | 1.5
2017-08-16 | 12:45 | 1.76 | 0 | 0 | 1.5 | 0 | 88.0308
2017-08-16 | 12:50 | 1.7686 | 0 |  | 1.5
2017-08-16 | 12:55 | 1.7444 | 0 |  | 1.5
2017-08-16 | 13:00 | 1.7421 | 0 | 0 | 1.5 | 0 | 87.8934
2017-08-16 | 13:05 | 1.753 | 0 |  | 1.5
2017-08-16 | 13:10 | 1.7358 | 0 |  | 1.5
2017-08-16 | 13:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 87.8362
2017-08-16 | 13:20 | 1.7413 | 0 |  | 1.5
2017-08-16 | 13:25 | 1.7577 | 0 |  | 1.5
2017-08-16 | 13:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 87.7118
2017-08-16 | 13:35 | 1.714 | 0 |  | 1.5
2017-08-16 | 13:40 | 1.7397 | 0 |  | 1.5
2017-08-16 | 13:45 | 1.7343 | 0 | 0 | 1.5 | 0 | 87.9487
2017-08-16 | 13:50 | 1.7756 | 0 |  | 1.5
2017-08-16 | 13:55 | 1.7709 | 0 |  | 1.5
2017-08-16 | 14:00 | 1.7382 | 0 | 0 | 1.5 | 0 | 87.8508
2017-08-16 | 14:05 | 1.76 | 0 |  | 1.5
2017-08-16 | 14:10 | 1.817 | 0 |  | 1.5
2017-08-16 | 14:15 | 1.7982 | 0 | 0 | 1.5 | 0 | 87.141
2017-08-16 | 14:20 | 1.7858 | 0 |  | 1.5
2017-08-16 | 14:25 | 1.7678 | 0 |  | 1.5
2017-08-16 | 14:30 | 1.7725 | 0 | 0 | 1.5 | 0 | 86.3192
2017-08-16 | 14:35 | 1.7678 | 0 |  | 1.5
2017-08-16 | 14:40 | 1.7624 | 0 |  | 1.5
2017-08-16 | 14:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 86.0112
2017-08-16 | 14:50 | 1.7717 | 0 |  | 1.5
2017-08-16 | 14:55 | 1.753 | 0 |  | 1.5
2017-08-16 | 15:00 | 1.7663 | 0 | 0 | 1.5 | 0 | 85.6736
2017-08-16 | 15:05 | 1.7585 | 0 |  | 1.5
2017-08-16 | 15:10 | 1.7358 | 0 |  | 1.5
2017-08-16 | 15:15 | 1.7491 | 0 | 0 | 1.5 | 0 | 85.5632
2017-08-16 | 15:20 | 1.7717 | 0 |  | 1.5
2017-08-16 | 15:25 | 1.7975 | 0 |  | 1.5
2017-08-16 | 15:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 85.0736
2017-08-16 | 15:35 | 1.8021 | 0 |  | 1.5
2017-08-16 | 15:40 | 1.7569 | 0 |  | 1.5
2017-08-16 | 15:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 84.4092
2017-08-16 | 15:50 | 1.7686 | 0 |  | 1.5
2017-08-16 | 15:55 | 1.778 | 0 |  | 1.5
2017-08-16 | 16:00 | 1.7351 | 0 | 0 | 1.5 | 0 | 83.9384
2017-08-16 | 16:05 | 1.7811 | 0 |  | 1.5
2017-08-16 | 16:10 | 1.6898 | 0 |  | 1.5
2017-08-16 | 16:15 | 1.6992 | 0 | 0 | 1.5 | 0 | 84.5819
2017-08-16 | 16:20 | 1.7202 | 0 |  | 1.5
2017-08-16 | 16:25 | 1.7421 | 0 |  | 1.5
2017-08-16 | 16:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 85.1089
2017-08-16 | 16:35 | 1.7561 | 0 |  | 1.5
2017-08-16 | 16:40 | 1.7499 | 0 |  | 1.5
2017-08-16 | 16:45 | 1.7327 | 0 | 0 | 1.5 | 0 | 85.133
2017-08-16 | 16:50 | 1.7522 | 0 |  | 1.5
2017-08-16 | 16:55 | 1.8279 | 0 |  | 1.5
2017-08-16 | 17:00 | 1.8146 | 0 | 0 | 1.5 | 0 | 83.9281
2017-08-16 | 17:05 | 1.8029 | 0 |  | 1.5
2017-08-16 | 17:10 | 1.7764 | 0 |  | 1.5
2017-08-16 | 17:15 | 1.7733 | 0 | 0 | 1.5 | 0 | 83.0749
2017-08-16 | 17:20 | 1.7834 | 0 |  | 1.5
2017-08-16 | 17:25 | 1.8138 | 0 |  | 1.5
2017-08-16 | 17:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.1733
2017-08-16 | 17:35 | 1.7686 | 0 |  | 1.5
2017-08-16 | 17:40 | 1.7756 | 0 |  | 1.5
2017-08-16 | 17:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.4622
2017-08-16 | 17:50 | 1.7748 | 0 |  | 1.5
2017-08-16 | 17:55 | 1.7405 | 0 |  | 1.5
2017-08-16 | 18:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 81.1494
2017-08-16 | 18:05 | 1.7538 | 0 |  | 1.5
2017-08-16 | 18:10 | 1.7748 | 0 |  | 1.5
2017-08-16 | 18:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 81.0165
2017-08-16 | 18:20 | 1.7585 | 0 |  | 1.5
2017-08-16 | 18:25 | 1.76 | 0 |  | 1.5
2017-08-16 | 18:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 80.9468
2017-08-16 | 18:35 | 1.7241 | 0 |  | 1.5
2017-08-16 | 18:40 | 1.7795 | 0 |  | 1.5
2017-08-16 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 80.8177
2017-08-16 | 18:50 | 1.7499 | 0 |  | 1.5
2017-08-16 | 18:55 | 1.7358 | 0 |  | 1.5
2017-08-16 | 19:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 80.8093
2017-08-16 | 19:05 | 1.7218 | 0 |  | 1.5
2017-08-16 | 19:10 | 1.7475 | 0 |  | 1.5
2017-08-16 | 19:15 | 1.7967 | 0 | 0 | 1.5 | 0 | 80.5149
2017-08-16 | 19:20 | 1.7585 | 0 |  | 1.5
2017-08-16 | 19:25 | 1.7655 | 0 |  | 1.5
2017-08-16 | 19:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 80.1717
2017-08-16 | 19:35 | 1.7553 | 0 |  | 1.5
2017-08-16 | 19:40 | 1.7468 | 0 |  | 1.5
2017-08-16 | 19:45 | 1.7748 | 0 | 0 | 1.5 | 0 | 79.958
2017-08-16 | 19:50 | 1.7678 | 0 |  | 1.5
2017-08-16 | 19:55 | 1.7514 | 0 |  | 1.5
2017-08-16 | 20:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.6341
2017-08-16 | 20:05 | 1.7429 | 0 |  | 1.5
2017-08-16 | 20:10 | 1.7483 | 0 |  | 1.5
2017-08-16 | 20:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.4604
2017-08-16 | 20:20 | 1.7421 | 0 |  | 1.5
2017-08-16 | 20:25 | 1.7343 | 0 |  | 1.5
2017-08-16 | 20:30 | 1.778 | 0 | 0 | 1.5 | 0 | 79.1168
2017-08-16 | 20:35 | 1.753 | 0 |  | 1.5
2017-08-16 | 20:40 | 1.7655 | 0 |  | 1.5
2017-08-16 | 20:45 | 1.7678 | 0 | 0 | 1.5 | 0 | 79.0157
2017-08-16 | 20:50 | 1.746 | 0 |  | 1.5
2017-08-16 | 20:55 | 1.7117 | 0 |  | 1.5
2017-08-16 | 21:00 | 1.7561 | 0 | 0 | 1.5 | 0 | 79.3194
2017-08-16 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-16 | 21:10 | -0.10262 | 0 |  | 1.5
2017-08-16 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 21:20 | -0.1034 | 0 |  | 1.5
2017-08-16 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-16 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-16 | 21:40 | -0.1034 | 0 |  | 1.5
2017-08-16 | 21:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 21:50 | -0.10418 | 0 |  | 1.5
2017-08-16 | 21:55 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 22:05 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:10 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-16 | 22:25 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 22:35 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:40 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 22:50 | -0.10418 | 0 |  | 1.5
2017-08-16 | 22:55 | -0.10262 | 0 |  | 1.5
2017-08-16 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 23:05 | -0.10418 | 0 |  | 1.5
2017-08-16 | 23:10 | -0.10418 | 0 |  | 1.5
2017-08-16 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 23:20 | -0.10418 | 0 |  | 1.5
2017-08-16 | 23:25 | -0.10418 | 0 |  | 1.5
2017-08-16 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 23:35 | -0.10418 | 0 |  | 1.5
2017-08-16 | 23:40 | -0.10262 | 0 |  | 1.5
2017-08-16 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-16 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-16 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-17 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-17 | 0:10 | -0.1034 | 0 |  | 1.5
2017-08-17 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 0:20 | -0.1034 | 0 |  | 1.5
2017-08-17 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-17 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 0:35 | -0.1034 | 0 |  | 1.5
2017-08-17 | 0:40 | -0.1034 | 0 |  | 1.5
2017-08-17 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 0:50 | -0.1034 | 0 |  | 1.5
2017-08-17 | 0:55 | -0.1034 | 0 |  | 1.5
2017-08-17 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 1:05 | -0.1034 | 0 |  | 1.5
2017-08-17 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-17 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 1:20 | -0.1073 | 0 |  | 1.5
2017-08-17 | 1:25 | -0.10652 | 0 |  | 1.5
2017-08-17 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 1:35 | -0.10652 | 0 |  | 1.5
2017-08-17 | 1:40 | -0.10652 | 0 |  | 1.5
2017-08-17 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 1:50 | -0.1112 | 0 |  | 1.5
2017-08-17 | 1:55 | -0.10652 | 0 |  | 1.5
2017-08-17 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 2:05 | -0.10652 | 0 |  | 1.5
2017-08-17 | 2:10 | -0.10652 | 0 |  | 1.5
2017-08-17 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-17 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-17 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-17 | 2:40 | -0.1073 | 0 |  | 1.5
2017-08-17 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-17 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 3:05 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 3:20 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:25 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 3:35 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:40 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-17 | 3:55 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 4:05 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:10 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 4:20 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:25 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:40 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 4:50 | -0.1073 | 0 |  | 1.5
2017-08-17 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-17 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 5:05 | 1.8521 | 0 |  | 1.5
2017-08-17 | 5:10 | 2.0424 | 0 |  | 1.5
2017-08-17 | 5:15 | 1.9488 | 0 | 0 | 1.5 | 0 | 94.3978
2017-08-17 | 5:20 | 1.8973 | 0 |  | 1.5
2017-08-17 | 5:25 | 1.9074 | 0 |  | 1.5
2017-08-17 | 5:30 | 1.9745 | 0 | 0 | 1.5 | 0 | 90.1187
2017-08-17 | 5:35 | 2.0159 | 0 |  | 1.5
2017-08-17 | 5:40 | 1.9909 | 0 |  | 1.5
2017-08-17 | 5:45 | 1.8973 | 0 | 0 | 1.5 | 0 | 83.977
2017-08-17 | 5:50 | 1.8747 | 0 |  | 1.5
2017-08-17 | 5:55 | 1.8458 | 0 |  | 1.5
2017-08-17 | 6:00 | 1.8396 | 0 | 0 | 1.5 | 0 | 81.2239
2017-08-17 | 6:05 | 1.7959 | 0 |  | 1.5
2017-08-17 | 6:10 | 1.7936 | 0 |  | 1.5
2017-08-17 | 6:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 79.9855
2017-08-17 | 6:20 | 1.7943 | 0 |  | 1.5
2017-08-17 | 6:25 | 1.7647 | 0 |  | 1.5
2017-08-17 | 6:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 79.5079
2017-08-17 | 6:35 | 1.7358 | 0 |  | 1.5
2017-08-17 | 6:40 | 1.7592 | 0 |  | 1.5
2017-08-17 | 6:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 79.3669
2017-08-17 | 6:50 | 1.7709 | 0 |  | 1.5
2017-08-17 | 6:55 | 1.7811 | 0 |  | 1.5
2017-08-17 | 7:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 79.1479
2017-08-17 | 7:05 | 1.721 | 0 |  | 1.5
2017-08-17 | 7:10 | 1.7546 | 0 |  | 1.5
2017-08-17 | 7:15 | 1.7514 | 0 | 0 | 1.5 | 0 | 79.2363
2017-08-17 | 7:20 | 1.7756 | 0 |  | 1.5
2017-08-17 | 7:25 | 1.7288 | 0 |  | 1.5
2017-08-17 | 7:30 | 1.7421 | 0 | 0 | 1.5 | 0 | 79.5455
2017-08-17 | 7:35 | 1.767 | 0 |  | 1.5
2017-08-17 | 7:40 | 1.7639 | 0 |  | 1.5
2017-08-17 | 7:45 | 1.7249 | 0 | 0 | 1.5 | 0 | 79.0912
2017-08-17 | 7:50 | 1.7078 | 0 |  | 1.5
2017-08-17 | 7:55 | 1.7358 | 0 |  | 1.5
2017-08-17 | 8:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 79.4537
2017-08-17 | 8:05 | 1.7085 | 0 |  | 1.5
2017-08-17 | 8:10 | 1.6992 | 0 |  | 1.5
2017-08-17 | 8:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 80.1203
2017-08-17 | 8:20 | 1.739 | 0 |  | 1.5
2017-08-17 | 8:25 | 1.7655 | 0 |  | 1.5
2017-08-17 | 8:30 | 1.7265 | 0 | 0 | 1.5 | 0 | 80.5521
2017-08-17 | 8:35 | 1.7483 | 0 |  | 1.5
2017-08-17 | 8:40 | 1.7795 | 0 |  | 1.5
2017-08-17 | 8:45 | 1.7772 | 0 | 0 | 1.5 | 0 | 80.1718
2017-08-17 | 8:50 | 1.76 | 0 |  | 1.5
2017-08-17 | 8:55 | 1.7772 | 0 |  | 1.5
2017-08-17 | 9:00 | 1.739 | 0 | 0 | 1.5 | 0 | 79.9867
2017-08-17 | 9:05 | 1.7475 | 0 |  | 1.5
2017-08-17 | 9:10 | 1.7686 | 0 |  | 1.5
2017-08-17 | 9:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.8634
2017-08-17 | 9:20 | 1.6383 | 0 |  | 1.5
2017-08-17 | 9:25 | 1.6235 | 0 |  | 1.5
2017-08-17 | 9:30 | 1.6851 | 0 | 0 | 1.5 | 0 | 81.9526
2017-08-17 | 9:35 | 1.7358 | 0 |  | 1.5
2017-08-17 | 9:40 | 1.7569 | 0 |  | 1.5
2017-08-17 | 9:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 82.1301
2017-08-17 | 9:50 | 1.7717 | 0 |  | 1.5
2017-08-17 | 9:55 | 1.7561 | 0 |  | 1.5
2017-08-17 | 10:00 | 1.7904 | 0 | 0 | 1.5 | 0 | 81.6737
2017-08-17 | 10:05 | 1.7452 | 0 |  | 1.5
2017-08-17 | 10:10 | 1.7507 | 0 |  | 1.5
2017-08-17 | 10:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 81.5838
2017-08-17 | 10:20 | 1.7382 | 0 |  | 1.5
2017-08-17 | 10:25 | 1.7179 | 0 |  | 1.5
2017-08-17 | 10:30 | 1.7592 | 0 | 0 | 1.5 | 0 | 81.8494
2017-08-17 | 10:35 | 1.7585 | 0 |  | 1.5
2017-08-17 | 10:40 | 1.7397 | 0 |  | 1.5
2017-08-17 | 10:45 | 1.7241 | 0 | 0 | 1.5 | 0 | 82.1795
2017-08-17 | 10:50 | 1.7241 | 0 |  | 1.5
2017-08-17 | 10:55 | 1.7226 | 0 |  | 1.5
2017-08-17 | 11:00 | 1.7296 | 0 | 0 | 1.5 | 0 | 82.7934
2017-08-17 | 11:05 | 1.6992 | 0 |  | 1.5
2017-08-17 | 11:10 | 1.7468 | 0 |  | 1.5
2017-08-17 | 11:15 | 1.7062 | 0 | 0 | 1.5 | 0 | 83.6455
2017-08-17 | 11:20 | 1.6578 | 0 |  | 1.5
2017-08-17 | 11:25 | 1.714 | 0 |  | 1.5
2017-08-17 | 11:30 | 1.6789 | 0 | 0 | 1.5 | 0 | 85.2601
2017-08-17 | 11:35 | 1.6867 | 0 |  | 1.5
2017-08-17 | 11:40 | 1.6914 | 0 |  | 1.5
2017-08-17 | 11:45 | 1.6953 | 0 | 0 | 1.5 | 0 | 86.7418
2017-08-17 | 11:50 | 1.6758 | 0 |  | 1.5
2017-08-17 | 11:55 | 1.7078 | 0 |  | 1.5
2017-08-17 | 12:00 | 1.6937 | 0 | 0 | 1.5 | 0 | 88.1115
2017-08-17 | 12:05 | 1.7288 | 0 |  | 1.5
2017-08-17 | 12:10 | 1.7257 | 0 |  | 1.5
2017-08-17 | 12:15 | 1.7436 | 0 | 0 | 1.5 | 0 | 88.6775
2017-08-17 | 12:20 | 1.7655 | 0 |  | 1.5
2017-08-17 | 12:25 | 1.7639 | 0 |  | 1.5
2017-08-17 | 12:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 88.5243
2017-08-17 | 12:35 | 1.7499 | 0 |  | 1.5
2017-08-17 | 12:40 | 1.7647 | 0 |  | 1.5
2017-08-17 | 12:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 88.436
2017-08-17 | 12:50 | 1.8294 | 0 |  | 1.5
2017-08-17 | 12:55 | 1.7951 | 0 |  | 1.5
2017-08-17 | 13:00 | 1.7873 | 0 | 0 | 1.5 | 0 | 87.2625
2017-08-17 | 13:05 | 1.7764 | 0 |  | 1.5
2017-08-17 | 13:10 | 1.7507 | 0 |  | 1.5
2017-08-17 | 13:15 | 1.7694 | 0 | 0 | 1.5 | 0 | 86.6636
2017-08-17 | 13:20 | 1.7616 | 0 |  | 1.5
2017-08-17 | 13:25 | 1.7663 | 0 |  | 1.5
2017-08-17 | 13:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 86.1066
2017-08-17 | 13:35 | 1.767 | 0 |  | 1.5
2017-08-17 | 13:40 | 1.767 | 0 |  | 1.5
2017-08-17 | 13:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 85.8818
2017-08-17 | 13:50 | 1.7421 | 0 |  | 1.5
2017-08-17 | 13:55 | 1.7273 | 0 |  | 1.5
2017-08-17 | 14:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 85.8994
2017-08-17 | 14:05 | 1.7421 | 0 |  | 1.5
2017-08-17 | 14:10 | 1.7468 | 0 |  | 1.5
2017-08-17 | 14:15 | 1.7312 | 0 | 0 | 1.5 | 0 | 86.423
2017-08-17 | 14:20 | 1.6914 | 0 |  | 1.5
2017-08-17 | 14:25 | 1.7062 | 0 |  | 1.5
2017-08-17 | 14:30 | 1.714 | 0 | 0 | 1.5 | 0 | 87.6099
2017-08-17 | 14:35 | 1.7421 | 0 |  | 1.5
2017-08-17 | 14:40 | 1.7257 | 0 |  | 1.5
2017-08-17 | 14:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 87.9372
2017-08-17 | 14:50 | 1.7569 | 0 |  | 1.5
2017-08-17 | 14:55 | 1.7663 | 0 |  | 1.5
2017-08-17 | 15:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 87.5189
2017-08-17 | 15:05 | 1.7811 | 0 |  | 1.5
2017-08-17 | 15:10 | 1.7717 | 0 |  | 1.5
2017-08-17 | 15:15 | 1.7709 | 0 | 0 | 1.5 | 0 | 86.9323
2017-08-17 | 15:20 | 1.7686 | 0 |  | 1.5
2017-08-17 | 15:25 | 1.7655 | 0 |  | 1.5
2017-08-17 | 15:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 86.4335
2017-08-17 | 15:35 | 1.7616 | 0 |  | 1.5
2017-08-17 | 15:40 | 1.7842 | 0 |  | 1.5
2017-08-17 | 15:45 | 1.7327 | 0 | 0 | 1.5 | 0 | 86.3248
2017-08-17 | 15:50 | 1.7507 | 0 |  | 1.5
2017-08-17 | 15:55 | 1.7756 | 0 |  | 1.5
2017-08-17 | 16:00 | 1.7124 | 0 | 0 | 1.5 | 0 | 86.4023
2017-08-17 | 16:05 | 1.7156 | 0 |  | 1.5
2017-08-17 | 16:10 | 1.7468 | 0 |  | 1.5
2017-08-17 | 16:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 86.5575
2017-08-17 | 16:20 | 1.7514 | 0 |  | 1.5
2017-08-17 | 16:25 | 1.7452 | 0 |  | 1.5
2017-08-17 | 16:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 86.4137
2017-08-17 | 16:35 | 1.7748 | 0 |  | 1.5
2017-08-17 | 16:40 | 1.7756 | 0 |  | 1.5
2017-08-17 | 16:45 | 1.778 | 0 | 0 | 1.5 | 0 | 86.0561
2017-08-17 | 16:50 | 1.7663 | 0 |  | 1.5
2017-08-17 | 16:55 | 1.7709 | 0 |  | 1.5
2017-08-17 | 17:00 | 1.8162 | 0 | 0 | 1.5 | 0 | 85.5895
2017-08-17 | 17:05 | 1.8021 | 0 |  | 1.5
2017-08-17 | 17:10 | 1.8115 | 0 |  | 1.5
2017-08-17 | 17:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 84.0136
2017-08-17 | 17:20 | 1.8014 | 0 |  | 1.5
2017-08-17 | 17:25 | 1.7998 | 0 |  | 1.5
2017-08-17 | 17:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 82.9354
2017-08-17 | 17:35 | 1.778 | 0 |  | 1.5
2017-08-17 | 17:40 | 1.792 | 0 |  | 1.5
2017-08-17 | 17:45 | 1.7756 | 0 | 0 | 1.5 | 0 | 82.1168
2017-08-17 | 17:50 | 1.7928 | 0 |  | 1.5
2017-08-17 | 17:55 | 1.7725 | 0 |  | 1.5
2017-08-17 | 18:00 | 1.7819 | 0 | 0 | 1.5 | 0 | 81.3753
2017-08-17 | 18:05 | 1.767 | 0 |  | 1.5
2017-08-17 | 18:10 | 1.7811 | 0 |  | 1.5
2017-08-17 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 80.8567
2017-08-17 | 18:20 | 1.7585 | 0 |  | 1.5
2017-08-17 | 18:25 | 1.7577 | 0 |  | 1.5
2017-08-17 | 18:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 80.572
2017-08-17 | 18:35 | 1.7241 | 0 |  | 1.5
2017-08-17 | 18:40 | 1.7678 | 0 |  | 1.5
2017-08-17 | 18:45 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.39
2017-08-17 | 18:50 | 1.7499 | 0 |  | 1.5
2017-08-17 | 18:55 | 1.7397 | 0 |  | 1.5
2017-08-17 | 19:00 | 1.7819 | 0 | 0 | 1.5 | 0 | 80.2262
2017-08-17 | 19:05 | 1.7608 | 0 |  | 1.5
2017-08-17 | 19:10 | 1.7772 | 0 |  | 1.5
2017-08-17 | 19:15 | 1.7764 | 0 | 0 | 1.5 | 0 | 79.8005
2017-08-17 | 19:20 | 1.7639 | 0 |  | 1.5
2017-08-17 | 19:25 | 1.7655 | 0 |  | 1.5
2017-08-17 | 19:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 79.3749
2017-08-17 | 19:35 | 1.7569 | 0 |  | 1.5
2017-08-17 | 19:40 | 1.7787 | 0 |  | 1.5
2017-08-17 | 19:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.0808
2017-08-17 | 19:50 | 1.7553 | 0 |  | 1.5
2017-08-17 | 19:55 | 1.7366 | 0 |  | 1.5
2017-08-17 | 20:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 79.1152
2017-08-17 | 20:05 | 1.7772 | 0 |  | 1.5
2017-08-17 | 20:10 | 1.7491 | 0 |  | 1.5
2017-08-17 | 20:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 78.9138
2017-08-17 | 20:20 | 1.7577 | 0 |  | 1.5
2017-08-17 | 20:25 | 1.7475 | 0 |  | 1.5
2017-08-17 | 20:30 | 1.76 | 0 | 0 | 1.5 | 0 | 78.9839
2017-08-17 | 20:35 | 1.7514 | 0 |  | 1.5
2017-08-17 | 20:40 | 1.7538 | 0 |  | 1.5
2017-08-17 | 20:45 | 1.7304 | 0 | 0 | 1.5 | 0 | 79.0758
2017-08-17 | 20:50 | 1.7475 | 0 |  | 1.5
2017-08-17 | 20:55 | 1.7218 | 0 |  | 1.5
2017-08-17 | 21:00 | 1.6844 | 0 | 0 | 1.5 | 0 | 79.7611
2017-08-17 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-17 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-17 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 21:20 | -0.1034 | 0 |  | 1.5
2017-08-17 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-17 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-17 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-17 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 21:50 | -0.10418 | 0 |  | 1.5
2017-08-17 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:10 | -0.10418 | 0 |  | 1.5
2017-08-17 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-17 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-17 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-17 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-17 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-18 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-18 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-18 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-18 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-18 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 1:20 | -0.10808 | 0 |  | 1.5
2017-08-18 | 1:25 | -0.1073 | 0 |  | 1.5
2017-08-18 | 1:30 | -0.11276 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 1:35 | -0.1073 | 0 |  | 1.5
2017-08-18 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-18 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-18 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:10 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-18 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 2:35 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 2:50 | -0.10808 | 0 |  | 1.5
2017-08-18 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-18 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 4:05 | -0.1112 | 0 |  | 1.5
2017-08-18 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-18 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-18 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 5:05 | 1.973 | 0 |  | 1.5
2017-08-18 | 5:10 | 2.1453 | 0 |  | 1.5
2017-08-18 | 5:15 | 2.0143 | 0 | 0 | 1.5 | 0 | 92.4604
2017-08-18 | 5:20 | 1.9503 | 0 |  | 1.5
2017-08-18 | 5:25 | 1.9995 | 0 |  | 1.5
2017-08-18 | 5:30 | 1.9769 | 0 | 0 | 1.5 | 0 | 86.4735
2017-08-18 | 5:35 | 1.9137 | 0 |  | 1.5
2017-08-18 | 5:40 | 1.902 | 0 |  | 1.5
2017-08-18 | 5:45 | 1.8692 | 0 | 0 | 1.5 | 0 | 82.215
2017-08-18 | 5:50 | 1.8357 | 0 |  | 1.5
2017-08-18 | 5:55 | 1.8255 | 0 |  | 1.5
2017-08-18 | 6:00 | 1.7943 | 0 | 0 | 1.5 | 0 | 80.2668
2017-08-18 | 6:05 | 1.778 | 0 |  | 1.5
2017-08-18 | 6:10 | 1.7733 | 0 |  | 1.5
2017-08-18 | 6:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 79.3607
2017-08-18 | 6:20 | 1.7452 | 0 |  | 1.5
2017-08-18 | 6:25 | 1.7553 | 0 |  | 1.5
2017-08-18 | 6:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 79.1215
2017-08-18 | 6:35 | 1.7631 | 0 |  | 1.5
2017-08-18 | 6:40 | 1.7733 | 0 |  | 1.5
2017-08-18 | 6:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 78.8389
2017-08-18 | 6:50 | 1.76 | 0 |  | 1.5
2017-08-18 | 6:55 | 1.7475 | 0 |  | 1.5
2017-08-18 | 7:00 | 1.7772 | 0 | 0 | 1.5 | 0 | 78.481
2017-08-18 | 7:05 | 1.739 | 0 |  | 1.5
2017-08-18 | 7:10 | 1.778 | 0 |  | 1.5
2017-08-18 | 7:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 78.1382
2017-08-18 | 7:20 | 1.7678 | 0 |  | 1.5
2017-08-18 | 7:25 | 1.753 | 0 |  | 1.5
2017-08-18 | 7:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 78.054
2017-08-18 | 7:35 | 1.7522 | 0 |  | 1.5
2017-08-18 | 7:40 | 1.7374 | 0 |  | 1.5
2017-08-18 | 7:45 | 1.7624 | 0 | 0 | 1.5 | 0 | 78.1481
2017-08-18 | 7:50 | 1.7873 | 0 |  | 1.5
2017-08-18 | 7:55 | 1.7881 | 0 |  | 1.5
2017-08-18 | 8:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 77.823
2017-08-18 | 8:05 | 1.7647 | 0 |  | 1.5
2017-08-18 | 8:10 | 1.6797 | 0 |  | 1.5
2017-08-18 | 8:15 | 1.7 | 0 | 0 | 1.5 | 0 | 78.8072
2017-08-18 | 8:20 | 1.6984 | 0 |  | 1.5
2017-08-18 | 8:25 | 1.6758 | 0 |  | 1.5
2017-08-18 | 8:30 | 1.6976 | 0 | 0 | 1.5 | 0 | 80.3614
2017-08-18 | 8:35 | 1.728 | 0 |  | 1.5
2017-08-18 | 8:40 | 1.7616 | 0 |  | 1.5
2017-08-18 | 8:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 80.6575
2017-08-18 | 8:50 | 1.7413 | 0 |  | 1.5
2017-08-18 | 8:55 | 1.7327 | 0 |  | 1.5
2017-08-18 | 9:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 80.9056
2017-08-18 | 9:05 | 1.7577 | 0 |  | 1.5
2017-08-18 | 9:10 | 1.7709 | 0 |  | 1.5
2017-08-18 | 9:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 80.7022
2017-08-18 | 9:20 | 1.7429 | 0 |  | 1.5
2017-08-18 | 9:25 | 1.7491 | 0 |  | 1.5
2017-08-18 | 9:30 | 1.6961 | 0 | 0 | 1.5 | 0 | 80.9627
2017-08-18 | 9:35 | 1.7163 | 0 |  | 1.5
2017-08-18 | 9:40 | 1.7382 | 0 |  | 1.5
2017-08-18 | 9:45 | 1.7546 | 0 | 0 | 1.5 | 0 | 81.3722
2017-08-18 | 9:50 | 1.7787 | 0 |  | 1.5
2017-08-18 | 9:55 | 1.7507 | 0 |  | 1.5
2017-08-18 | 10:00 | 1.7608 | 0 | 0 | 1.5 | 0 | 81.194
2017-08-18 | 10:05 | 1.7444 | 0 |  | 1.5
2017-08-18 | 10:10 | 1.753 | 0 |  | 1.5
2017-08-18 | 10:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.3664
2017-08-18 | 10:20 | 1.7296 | 0 |  | 1.5
2017-08-18 | 10:25 | 1.7195 | 0 |  | 1.5
2017-08-18 | 10:30 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.9183
2017-08-18 | 10:35 | 1.7639 | 0 |  | 1.5
2017-08-18 | 10:40 | 1.7826 | 0 |  | 1.5
2017-08-18 | 10:45 | 1.728 | 0 | 0 | 1.5 | 0 | 82.0523
2017-08-18 | 10:50 | 1.7631 | 0 |  | 1.5
2017-08-18 | 10:55 | 1.7429 | 0 |  | 1.5
2017-08-18 | 11:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 82.0863
2017-08-18 | 11:05 | 1.7475 | 0 |  | 1.5
2017-08-18 | 11:10 | 1.7296 | 0 |  | 1.5
2017-08-18 | 11:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 82.362
2017-08-18 | 11:20 | 1.7678 | 0 |  | 1.5
2017-08-18 | 11:25 | 1.7257 | 0 |  | 1.5
2017-08-18 | 11:30 | 1.7249 | 0 | 0 | 1.5 | 0 | 82.7238
2017-08-18 | 11:35 | 1.7078 | 0 |  | 1.5
2017-08-18 | 11:40 | 1.7234 | 0 |  | 1.5
2017-08-18 | 11:45 | 1.7257 | 0 | 0 | 1.5 | 0 | 83.5267
2017-08-18 | 11:50 | 1.7312 | 0 |  | 1.5
2017-08-18 | 11:55 | 1.7312 | 0 |  | 1.5
2017-08-18 | 12:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 83.8043
2017-08-18 | 12:05 | 1.7319 | 0 |  | 1.5
2017-08-18 | 12:10 | 1.7631 | 0 |  | 1.5
2017-08-18 | 12:15 | 1.7132 | 0 | 0 | 1.5 | 0 | 84.4251
2017-08-18 | 12:20 | 1.7109 | 0 |  | 1.5
2017-08-18 | 12:25 | 1.6992 | 0 |  | 1.5
2017-08-18 | 12:30 | 1.7179 | 0 | 0 | 1.5 | 0 | 85.1063
2017-08-18 | 12:35 | 1.6875 | 0 |  | 1.5
2017-08-18 | 12:40 | 1.728 | 0 |  | 1.5
2017-08-18 | 12:45 | 1.6945 | 0 | 0 | 1.5 | 0 | 86.2871
2017-08-18 | 12:50 | 1.721 | 0 |  | 1.5
2017-08-18 | 12:55 | 1.7241 | 0 |  | 1.5
2017-08-18 | 13:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 87.0891
2017-08-18 | 13:05 | 1.7475 | 0 |  | 1.5
2017-08-18 | 13:10 | 1.7397 | 0 |  | 1.5
2017-08-18 | 13:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 87.3885
2017-08-18 | 13:20 | 1.76 | 0 |  | 1.5
2017-08-18 | 13:25 | 1.7475 | 0 |  | 1.5
2017-08-18 | 13:30 | 1.7709 | 0 | 0 | 1.5 | 0 | 87.215
2017-08-18 | 13:35 | 1.7702 | 0 |  | 1.5
2017-08-18 | 13:40 | 1.721 | 0 |  | 1.5
2017-08-18 | 13:45 | 1.7218 | 0 | 0 | 1.5 | 0 | 87.5404
2017-08-18 | 13:50 | 1.7397 | 0 |  | 1.5
2017-08-18 | 13:55 | 1.7826 | 0 |  | 1.5
2017-08-18 | 14:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 87.2354
2017-08-18 | 14:05 | 1.7741 | 0 |  | 1.5
2017-08-18 | 14:10 | 1.7858 | 0 |  | 1.5
2017-08-18 | 14:15 | 1.7585 | 0 | 0 | 1.5 | 0 | 86.9969
2017-08-18 | 14:20 | 1.7709 | 0 |  | 1.5
2017-08-18 | 14:25 | 1.7881 | 0 |  | 1.5
2017-08-18 | 14:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 86.788
2017-08-18 | 14:35 | 1.7624 | 0 |  | 1.5
2017-08-18 | 14:40 | 1.7639 | 0 |  | 1.5
2017-08-18 | 14:45 | 1.721 | 0 | 0 | 1.5 | 0 | 86.9865
2017-08-18 | 14:50 | 1.7468 | 0 |  | 1.5
2017-08-18 | 14:55 | 1.7624 | 0 |  | 1.5
2017-08-18 | 15:00 | 1.7468 | 0 | 0 | 1.5 | 0 | 87.1658
2017-08-18 | 15:05 | 1.7343 | 0 |  | 1.5
2017-08-18 | 15:10 | 1.7803 | 0 |  | 1.5
2017-08-18 | 15:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 86.918
2017-08-18 | 15:20 | 1.7655 | 0 |  | 1.5
2017-08-18 | 15:25 | 1.7491 | 0 |  | 1.5
2017-08-18 | 15:30 | 1.7772 | 0 | 0 | 1.5 | 0 | 86.6485
2017-08-18 | 15:35 | 1.7514 | 0 |  | 1.5
2017-08-18 | 15:40 | 1.7756 | 0 |  | 1.5
2017-08-18 | 15:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 86.1453
2017-08-18 | 15:50 | 1.7522 | 0 |  | 1.5
2017-08-18 | 15:55 | 1.7499 | 0 |  | 1.5
2017-08-18 | 16:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 85.9565
2017-08-18 | 16:05 | 1.7585 | 0 |  | 1.5
2017-08-18 | 16:10 | 1.7678 | 0 |  | 1.5
2017-08-18 | 16:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 85.7913
2017-08-18 | 16:20 | 1.7429 | 0 |  | 1.5
2017-08-18 | 16:25 | 1.7725 | 0 |  | 1.5
2017-08-18 | 16:30 | 1.7436 | 0 | 0 | 1.5 | 0 | 85.6082
2017-08-18 | 16:35 | 1.7865 | 0 |  | 1.5
2017-08-18 | 16:40 | 1.753 | 0 |  | 1.5
2017-08-18 | 16:45 | 1.7561 | 0 | 0 | 1.5 | 0 | 85.4168
2017-08-18 | 16:50 | 1.7483 | 0 |  | 1.5
2017-08-18 | 16:55 | 1.76 | 0 |  | 1.5
2017-08-18 | 17:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 85.4834
2017-08-18 | 17:05 | 1.7561 | 0 |  | 1.5
2017-08-18 | 17:10 | 1.7694 | 0 |  | 1.5
2017-08-18 | 17:15 | 1.778 | 0 | 0 | 1.5 | 0 | 85.0583
2017-08-18 | 17:20 | 1.7897 | 0 |  | 1.5
2017-08-18 | 17:25 | 1.7959 | 0 |  | 1.5
2017-08-18 | 17:30 | 1.7756 | 0 | 0 | 1.5 | 0 | 84.2671
2017-08-18 | 17:35 | 1.7803 | 0 |  | 1.5
2017-08-18 | 17:40 | 1.7647 | 0 |  | 1.5
2017-08-18 | 17:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 83.6485
2017-08-18 | 17:50 | 1.7655 | 0 |  | 1.5
2017-08-18 | 17:55 | 1.7421 | 0 |  | 1.5
2017-08-18 | 18:00 | 1.7475 | 0 | 0 | 1.5 | 0 | 83.1814
2017-08-18 | 18:05 | 1.7663 | 0 |  | 1.5
2017-08-18 | 18:10 | 1.7608 | 0 |  | 1.5
2017-08-18 | 18:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 82.8967
2017-08-18 | 18:20 | 1.7499 | 0 |  | 1.5
2017-08-18 | 18:25 | 1.7561 | 0 |  | 1.5
2017-08-18 | 18:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.5628
2017-08-18 | 18:35 | 1.7592 | 0 |  | 1.5
2017-08-18 | 18:40 | 1.7452 | 0 |  | 1.5
2017-08-18 | 18:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 82.1449
2017-08-18 | 18:50 | 1.7585 | 0 |  | 1.5
2017-08-18 | 18:55 | 1.7678 | 0 |  | 1.5
2017-08-18 | 19:00 | 1.7811 | 0 | 0 | 1.5 | 0 | 81.8985
2017-08-18 | 19:05 | 1.778 | 0 |  | 1.5
2017-08-18 | 19:10 | 1.767 | 0 |  | 1.5
2017-08-18 | 19:15 | 1.7592 | 0 | 0 | 1.5 | 0 | 81.4494
2017-08-18 | 19:20 | 1.7772 | 0 |  | 1.5
2017-08-18 | 19:25 | 1.7631 | 0 |  | 1.5
2017-08-18 | 19:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 81.0352
2017-08-18 | 19:35 | 1.7522 | 0 |  | 1.5
2017-08-18 | 19:40 | 1.7686 | 0 |  | 1.5
2017-08-18 | 19:45 | 1.7733 | 0 | 0 | 1.5 | 0 | 80.5777
2017-08-18 | 19:50 | 1.7514 | 0 |  | 1.5
2017-08-18 | 19:55 | 1.7811 | 0 |  | 1.5
2017-08-18 | 20:00 | 1.753 | 0 | 0 | 1.5 | 0 | 80.117
2017-08-18 | 20:05 | 1.7694 | 0 |  | 1.5
2017-08-18 | 20:10 | 1.7709 | 0 |  | 1.5
2017-08-18 | 20:15 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.5815
2017-08-18 | 20:20 | 1.7616 | 0 |  | 1.5
2017-08-18 | 20:25 | 1.7616 | 0 |  | 1.5
2017-08-18 | 20:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.6966
2017-08-18 | 20:35 | 1.7249 | 0 |  | 1.5
2017-08-18 | 20:40 | 1.7546 | 0 |  | 1.5
2017-08-18 | 20:45 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.8118
2017-08-18 | 20:50 | 1.746 | 0 |  | 1.5
2017-08-18 | 20:55 | 1.7592 | 0 |  | 1.5
2017-08-18 | 21:00 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.8215
2017-08-18 | 21:05 | -0.10574 | 0 |  | 1.5
2017-08-18 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-18 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 21:20 | -0.10574 | 0 |  | 1.5
2017-08-18 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-18 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-18 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-18 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-18 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-18 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-18 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-18 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-18 | 22:25 | -0.10574 | 0 |  | 1.5
2017-08-18 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 22:35 | -0.10574 | 0 |  | 1.5
2017-08-18 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-18 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-18 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-18 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 23:05 | -0.10574 | 0 |  | 1.5
2017-08-18 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-18 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-18 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-18 | 23:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-18 | 23:40 | -0.10418 | 0 |  | 1.5
2017-08-18 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-18 | 23:50 | -0.10574 | 0 |  | 1.5
2017-08-18 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 0:20 | -0.10574 | 0 |  | 1.5
2017-08-19 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 0:50 | -0.10496 | 0 |  | 1.5
2017-08-19 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-19 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-19 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-19 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 1:20 | -0.10886 | 0 |  | 1.5
2017-08-19 | 1:25 | -0.10808 | 0 |  | 1.5
2017-08-19 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-19 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-19 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 1:50 | -0.10886 | 0 |  | 1.5
2017-08-19 | 1:55 | -0.10886 | 0 |  | 1.5
2017-08-19 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-19 | 2:10 | -0.10808 | 0 |  | 1.5
2017-08-19 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-19 | 2:25 | -0.10808 | 0 |  | 1.5
2017-08-19 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 2:35 | -0.10808 | 0 |  | 1.5
2017-08-19 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-19 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 2:50 | -0.10886 | 0 |  | 1.5
2017-08-19 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-19 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-19 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-19 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-19 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-19 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-19 | 3:40 | -0.10886 | 0 |  | 1.5
2017-08-19 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-19 | 3:55 | -0.10886 | 0 |  | 1.5
2017-08-19 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-19 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-19 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 5:05 | 1.9293 | 0 |  | 1.5
2017-08-19 | 5:10 | 2.1461 | 0 |  | 1.5
2017-08-19 | 5:15 | 1.9823 | 0 | 0 | 1.5 | 0 | 92.5872
2017-08-19 | 5:20 | 1.9168 | 0 |  | 1.5
2017-08-19 | 5:25 | 1.9628 | 0 |  | 1.5
2017-08-19 | 5:30 | 1.9581 | 0 | 0 | 1.5 | 0 | 87.4389
2017-08-19 | 5:35 | 1.8996 | 0 |  | 1.5
2017-08-19 | 5:40 | 1.9035 | 0 |  | 1.5
2017-08-19 | 5:45 | 1.863 | 0 | 0 | 1.5 | 0 | 83.4942
2017-08-19 | 5:50 | 1.8419 | 0 |  | 1.5
2017-08-19 | 5:55 | 1.8279 | 0 |  | 1.5
2017-08-19 | 6:00 | 1.7943 | 0 | 0 | 1.5 | 0 | 81.3201
2017-08-19 | 6:05 | 1.8099 | 0 |  | 1.5
2017-08-19 | 6:10 | 1.8037 | 0 |  | 1.5
2017-08-19 | 6:15 | 1.8162 | 0 | 0 | 1.5 | 0 | 79.9001
2017-08-19 | 6:20 | 1.7725 | 0 |  | 1.5
2017-08-19 | 6:25 | 1.7468 | 0 |  | 1.5
2017-08-19 | 6:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 79.2696
2017-08-19 | 6:35 | 1.7343 | 0 |  | 1.5
2017-08-19 | 6:40 | 1.7561 | 0 |  | 1.5
2017-08-19 | 6:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 78.9988
2017-08-19 | 6:50 | 1.7592 | 0 |  | 1.5
2017-08-19 | 6:55 | 1.7694 | 0 |  | 1.5
2017-08-19 | 7:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 78.728
2017-08-19 | 7:05 | 1.7772 | 0 |  | 1.5
2017-08-19 | 7:10 | 1.7553 | 0 |  | 1.5
2017-08-19 | 7:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 78.425
2017-08-19 | 7:20 | 1.7826 | 0 |  | 1.5
2017-08-19 | 7:25 | 1.7741 | 0 |  | 1.5
2017-08-19 | 7:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 78.2978
2017-08-19 | 7:35 | 1.7304 | 0 |  | 1.5
2017-08-19 | 7:40 | 1.7514 | 0 |  | 1.5
2017-08-19 | 7:45 | 1.7733 | 0 | 0 | 1.5 | 0 | 78.0318
2017-08-19 | 7:50 | 1.7444 | 0 |  | 1.5
2017-08-19 | 7:55 | 1.7561 | 0 |  | 1.5
2017-08-19 | 8:00 | 1.7405 | 0 | 0 | 1.5 | 0 | 77.7785
2017-08-19 | 8:05 | 1.7499 | 0 |  | 1.5
2017-08-19 | 8:10 | 1.7405 | 0 |  | 1.5
2017-08-19 | 8:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 77.8879
2017-08-19 | 8:20 | 1.7655 | 0 |  | 1.5
2017-08-19 | 8:25 | 1.7468 | 0 |  | 1.5
2017-08-19 | 8:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 77.8002
2017-08-19 | 8:35 | 1.746 | 0 |  | 1.5
2017-08-19 | 8:40 | 1.7452 | 0 |  | 1.5
2017-08-19 | 8:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 77.769
2017-08-19 | 8:50 | 1.7491 | 0 |  | 1.5
2017-08-19 | 8:55 | 1.7546 | 0 |  | 1.5
2017-08-19 | 9:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 78.0116
2017-08-19 | 9:05 | 1.7374 | 0 |  | 1.5
2017-08-19 | 9:10 | 1.7577 | 0 |  | 1.5
2017-08-19 | 9:15 | 1.7101 | 0 | 0 | 1.5 | 0 | 78.34
2017-08-19 | 9:20 | 1.7546 | 0 |  | 1.5
2017-08-19 | 9:25 | 1.7624 | 0 |  | 1.5
2017-08-19 | 9:30 | 1.739 | 0 | 0 | 1.5 | 0 | 78.5497
2017-08-19 | 9:35 | 1.7686 | 0 |  | 1.5
2017-08-19 | 9:40 | 1.7421 | 0 |  | 1.5
2017-08-19 | 9:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 78.5763
2017-08-19 | 9:50 | 1.7335 | 0 |  | 1.5
2017-08-19 | 9:55 | 1.7499 | 0 |  | 1.5
2017-08-19 | 10:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 78.6854
2017-08-19 | 10:05 | 1.7374 | 0 |  | 1.5
2017-08-19 | 10:10 | 1.7195 | 0 |  | 1.5
2017-08-19 | 10:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 78.7893
2017-08-19 | 10:20 | 1.753 | 0 |  | 1.5
2017-08-19 | 10:25 | 1.7561 | 0 |  | 1.5
2017-08-19 | 10:30 | 1.7187 | 0 | 0 | 1.5 | 0 | 78.9489
2017-08-19 | 10:35 | 1.7553 | 0 |  | 1.5
2017-08-19 | 10:40 | 1.7327 | 0 |  | 1.5
2017-08-19 | 10:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 79.0757
2017-08-19 | 10:50 | 1.7374 | 0 |  | 1.5
2017-08-19 | 10:55 | 1.7405 | 0 |  | 1.5
2017-08-19 | 11:00 | 1.7343 | 0 | 0 | 1.5 | 0 | 79.4574
2017-08-19 | 11:05 | 1.7475 | 0 |  | 1.5
2017-08-19 | 11:10 | 1.7226 | 0 |  | 1.5
2017-08-19 | 11:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.7628
2017-08-19 | 11:20 | 1.7483 | 0 |  | 1.5
2017-08-19 | 11:25 | 1.7725 | 0 |  | 1.5
2017-08-19 | 11:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 80.0718
2017-08-19 | 11:35 | 1.7546 | 0 |  | 1.5
2017-08-19 | 11:40 | 1.7413 | 0 |  | 1.5
2017-08-19 | 11:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 80.3295
2017-08-19 | 11:50 | 1.7218 | 0 |  | 1.5
2017-08-19 | 11:55 | 1.728 | 0 |  | 1.5
2017-08-19 | 12:00 | 1.7421 | 0 | 0 | 1.5 | 0 | 80.6182
2017-08-19 | 12:05 | 1.7374 | 0 |  | 1.5
2017-08-19 | 12:10 | 1.7195 | 0 |  | 1.5
2017-08-19 | 12:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 80.8427
2017-08-19 | 12:20 | 1.7475 | 0 |  | 1.5
2017-08-19 | 12:25 | 1.7483 | 0 |  | 1.5
2017-08-19 | 12:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 81.1959
2017-08-19 | 12:35 | 1.7296 | 0 |  | 1.5
2017-08-19 | 12:40 | 1.739 | 0 |  | 1.5
2017-08-19 | 12:45 | 1.7366 | 0 | 0 | 1.5 | 0 | 81.6215
2017-08-19 | 12:50 | 1.7616 | 0 |  | 1.5
2017-08-19 | 12:55 | 1.7343 | 0 |  | 1.5
2017-08-19 | 13:00 | 1.7156 | 0 | 0 | 1.5 | 0 | 82.0233
2017-08-19 | 13:05 | 1.7491 | 0 |  | 1.5
2017-08-19 | 13:10 | 1.7522 | 0 |  | 1.5
2017-08-19 | 13:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 82.3057
2017-08-19 | 13:20 | 1.7522 | 0 |  | 1.5
2017-08-19 | 13:25 | 1.7382 | 0 |  | 1.5
2017-08-19 | 13:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 82.6019
2017-08-19 | 13:35 | 1.7358 | 0 |  | 1.5
2017-08-19 | 13:40 | 1.76 | 0 |  | 1.5
2017-08-19 | 13:45 | 1.7327 | 0 | 0 | 1.5 | 0 | 82.7481
2017-08-19 | 13:50 | 1.7366 | 0 |  | 1.5
2017-08-19 | 13:55 | 1.7475 | 0 |  | 1.5
2017-08-19 | 14:00 | 1.7241 | 0 | 0 | 1.5 | 0 | 82.9138
2017-08-19 | 14:05 | 1.7319 | 0 |  | 1.5
2017-08-19 | 14:10 | 1.7421 | 0 |  | 1.5
2017-08-19 | 14:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 83.1356
2017-08-19 | 14:20 | 1.7663 | 0 |  | 1.5
2017-08-19 | 14:25 | 1.7569 | 0 |  | 1.5
2017-08-19 | 14:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 83.2481
2017-08-19 | 14:35 | 1.7436 | 0 |  | 1.5
2017-08-19 | 14:40 | 1.7397 | 0 |  | 1.5
2017-08-19 | 14:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 83.2792
2017-08-19 | 14:50 | 1.7483 | 0 |  | 1.5
2017-08-19 | 14:55 | 1.7296 | 0 |  | 1.5
2017-08-19 | 15:00 | 1.7553 | 0 | 0 | 1.5 | 0 | 83.2719
2017-08-19 | 15:05 | 1.7561 | 0 |  | 1.5
2017-08-19 | 15:10 | 1.7631 | 0 |  | 1.5
2017-08-19 | 15:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 83.2813
2017-08-19 | 15:20 | 1.7585 | 0 |  | 1.5
2017-08-19 | 15:25 | 1.767 | 0 |  | 1.5
2017-08-19 | 15:30 | 1.7803 | 0 | 0 | 1.5 | 0 | 83.0958
2017-08-19 | 15:35 | 1.753 | 0 |  | 1.5
2017-08-19 | 15:40 | 1.7452 | 0 |  | 1.5
2017-08-19 | 15:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 83.0207
2017-08-19 | 15:50 | 1.7663 | 0 |  | 1.5
2017-08-19 | 15:55 | 1.7374 | 0 |  | 1.5
2017-08-19 | 16:00 | 1.7561 | 0 | 0 | 1.5 | 0 | 82.9671
2017-08-19 | 16:05 | 1.7452 | 0 |  | 1.5
2017-08-19 | 16:10 | 1.7452 | 0 |  | 1.5
2017-08-19 | 16:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 82.9645
2017-08-19 | 16:20 | 1.7382 | 0 |  | 1.5
2017-08-19 | 16:25 | 1.739 | 0 |  | 1.5
2017-08-19 | 16:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 82.9162
2017-08-19 | 16:35 | 1.7717 | 0 |  | 1.5
2017-08-19 | 16:40 | 1.7522 | 0 |  | 1.5
2017-08-19 | 16:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 82.7921
2017-08-19 | 16:50 | 1.7631 | 0 |  | 1.5
2017-08-19 | 16:55 | 1.7694 | 0 |  | 1.5
2017-08-19 | 17:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.6671
2017-08-19 | 17:05 | 1.767 | 0 |  | 1.5
2017-08-19 | 17:10 | 1.7561 | 0 |  | 1.5
2017-08-19 | 17:15 | 1.7733 | 0 | 0 | 1.5 | 0 | 82.4791
2017-08-19 | 17:20 | 1.7803 | 0 |  | 1.5
2017-08-19 | 17:25 | 1.7491 | 0 |  | 1.5
2017-08-19 | 17:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.211
2017-08-19 | 17:35 | 1.7522 | 0 |  | 1.5
2017-08-19 | 17:40 | 1.7522 | 0 |  | 1.5
2017-08-19 | 17:45 | 1.7366 | 0 | 0 | 1.5 | 0 | 82.1285
2017-08-19 | 17:50 | 1.7733 | 0 |  | 1.5
2017-08-19 | 17:55 | 1.7327 | 0 |  | 1.5
2017-08-19 | 18:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.8145
2017-08-19 | 18:05 | 1.7039 | 0 |  | 1.5
2017-08-19 | 18:10 | 1.7631 | 0 |  | 1.5
2017-08-19 | 18:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 81.5525
2017-08-19 | 18:20 | 1.7561 | 0 |  | 1.5
2017-08-19 | 18:25 | 1.739 | 0 |  | 1.5
2017-08-19 | 18:30 | 1.7507 | 0 | 0 | 1.5 | 0 | 81.3135
2017-08-19 | 18:35 | 1.7608 | 0 |  | 1.5
2017-08-19 | 18:40 | 1.7819 | 0 |  | 1.5
2017-08-19 | 18:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.1537
2017-08-19 | 18:50 | 1.7553 | 0 |  | 1.5
2017-08-19 | 18:55 | 1.7444 | 0 |  | 1.5
2017-08-19 | 19:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 80.8626
2017-08-19 | 19:05 | 1.7514 | 0 |  | 1.5
2017-08-19 | 19:10 | 1.7499 | 0 |  | 1.5
2017-08-19 | 19:15 | 1.7725 | 0 | 0 | 1.5 | 0 | 80.7577
2017-08-19 | 19:20 | 1.7553 | 0 |  | 1.5
2017-08-19 | 19:25 | 1.7436 | 0 |  | 1.5
2017-08-19 | 19:30 | 1.7709 | 0 | 0 | 1.5 | 0 | 80.5258
2017-08-19 | 19:35 | 1.7561 | 0 |  | 1.5
2017-08-19 | 19:40 | 1.7585 | 0 |  | 1.5
2017-08-19 | 19:45 | 1.7834 | 0 | 0 | 1.5 | 0 | 80.4011
2017-08-19 | 19:50 | 1.7803 | 0 |  | 1.5
2017-08-19 | 19:55 | 1.7834 | 0 |  | 1.5
2017-08-19 | 20:00 | 1.7631 | 0 | 0 | 1.5 | 0 | 80.0521
2017-08-19 | 20:05 | 1.7538 | 0 |  | 1.5
2017-08-19 | 20:10 | 1.767 | 0 |  | 1.5
2017-08-19 | 20:15 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.5439
2017-08-19 | 20:20 | 1.7304 | 0 |  | 1.5
2017-08-19 | 20:25 | 1.767 | 0 |  | 1.5
2017-08-19 | 20:30 | 1.739 | 0 | 0 | 1.5 | 0 | 79.4431
2017-08-19 | 20:35 | 1.7452 | 0 |  | 1.5
2017-08-19 | 20:40 | 1.7709 | 0 |  | 1.5
2017-08-19 | 20:45 | 1.7717 | 0 | 0 | 1.5 | 0 | 79.2279
2017-08-19 | 20:50 | 1.746 | 0 |  | 1.5
2017-08-19 | 20:55 | 1.792 | 0 |  | 1.5
2017-08-19 | 21:00 | 1.7483 | 0 | 0 | 1.5 | 0 | 78.7746
2017-08-19 | 21:05 | -0.10262 | 0 |  | 1.5
2017-08-19 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-19 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-19 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-19 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-19 | 21:40 | -0.10418 | 0 |  | 1.5
2017-08-19 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-19 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-19 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-19 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-19 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 0:20 | -0.10574 | 0 |  | 1.5
2017-08-20 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 0:50 | -0.10496 | 0 |  | 1.5
2017-08-20 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-20 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-20 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-20 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 1:20 | -0.10886 | 0 |  | 1.5
2017-08-20 | 1:25 | -0.10886 | 0 |  | 1.5
2017-08-20 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-20 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-20 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-20 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-20 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-20 | 2:10 | -0.1073 | 0 |  | 1.5
2017-08-20 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-20 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-20 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 2:35 | -0.10808 | 0 |  | 1.5
2017-08-20 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-20 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-20 | 2:55 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 3:05 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:25 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 3:35 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:40 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-20 | 3:55 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 4:05 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 4:20 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:25 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 4:35 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 4:50 | -0.10886 | 0 |  | 1.5
2017-08-20 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-20 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 5:05 | 2.3598 | 0 |  | 1.5
2017-08-20 | 5:10 | 2.384 | 0 |  | 1.5
2017-08-20 | 5:15 | 2.1336 | 0 | 0 | 1.5 | 0 | 87.2051
2017-08-20 | 5:20 | 1.962 | 0 |  | 1.5
2017-08-20 | 5:25 | 1.8809 | 0 |  | 1.5
2017-08-20 | 5:30 | 1.817 | 0 | 0 | 1.5 | 0 | 82.7576
2017-08-20 | 5:35 | 1.792 | 0 |  | 1.5
2017-08-20 | 5:40 | 1.7577 | 0 |  | 1.5
2017-08-20 | 5:45 | 1.767 | 0 | 0 | 1.5 | 0 | 81.7973
2017-08-20 | 5:50 | 1.7608 | 0 |  | 1.5
2017-08-20 | 5:55 | 1.7647 | 0 |  | 1.5
2017-08-20 | 6:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.6514
2017-08-20 | 6:05 | 1.7569 | 0 |  | 1.5
2017-08-20 | 6:10 | 1.7592 | 0 |  | 1.5
2017-08-20 | 6:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 81.7057
2017-08-20 | 6:20 | 1.767 | 0 |  | 1.5
2017-08-20 | 6:25 | 1.7421 | 0 |  | 1.5
2017-08-20 | 6:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 81.6627
2017-08-20 | 6:35 | 1.7639 | 0 |  | 1.5
2017-08-20 | 6:40 | 1.7405 | 0 |  | 1.5
2017-08-20 | 6:45 | 1.739 | 0 | 0 | 1.5 | 0 | 81.6809
2017-08-20 | 6:50 | 1.7343 | 0 |  | 1.5
2017-08-20 | 6:55 | 1.7787 | 0 |  | 1.5
2017-08-20 | 7:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 81.8066
2017-08-20 | 7:05 | 1.7499 | 0 |  | 1.5
2017-08-20 | 7:10 | 1.7499 | 0 |  | 1.5
2017-08-20 | 7:15 | 1.753 | 0 | 0 | 1.5 | 0 | 81.9403
2017-08-20 | 7:20 | 1.7468 | 0 |  | 1.5
2017-08-20 | 7:25 | 1.7234 | 0 |  | 1.5
2017-08-20 | 7:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 82.079
2017-08-20 | 7:35 | 1.7561 | 0 |  | 1.5
2017-08-20 | 7:40 | 1.7499 | 0 |  | 1.5
2017-08-20 | 7:45 | 1.728 | 0 | 0 | 1.5 | 0 | 82.2277
2017-08-20 | 7:50 | 1.7366 | 0 |  | 1.5
2017-08-20 | 7:55 | 1.7335 | 0 |  | 1.5
2017-08-20 | 8:00 | 1.7756 | 0 | 0 | 1.5 | 0 | 82.3972
2017-08-20 | 8:05 | 1.7873 | 0 |  | 1.5
2017-08-20 | 8:10 | 1.8053 | 0 |  | 1.5
2017-08-20 | 8:15 | 1.7787 | 0 | 0 | 1.5 | 0 | 81.0052
2017-08-20 | 8:20 | 1.8021 | 0 |  | 1.5
2017-08-20 | 8:25 | 1.8014 | 0 |  | 1.5
2017-08-20 | 8:30 | 1.8107 | 0 | 0 | 1.5 | 0 | 79.9521
2017-08-20 | 8:35 | 1.7429 | 0 |  | 1.5
2017-08-20 | 8:40 | 1.7491 | 0 |  | 1.5
2017-08-20 | 8:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 79.5538
2017-08-20 | 8:50 | 1.7312 | 0 |  | 1.5
2017-08-20 | 8:55 | 1.7351 | 0 |  | 1.5
2017-08-20 | 9:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 79.3225
2017-08-20 | 9:05 | 1.7616 | 0 |  | 1.5
2017-08-20 | 9:10 | 1.7468 | 0 |  | 1.5
2017-08-20 | 9:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 79.2842
2017-08-20 | 9:20 | 1.7538 | 0 |  | 1.5
2017-08-20 | 9:25 | 1.7592 | 0 |  | 1.5
2017-08-20 | 9:30 | 1.7335 | 0 | 0 | 1.5 | 0 | 79.1385
2017-08-20 | 9:35 | 1.7366 | 0 |  | 1.5
2017-08-20 | 9:40 | 1.7343 | 0 |  | 1.5
2017-08-20 | 9:45 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.2569
2017-08-20 | 9:50 | 1.7413 | 0 |  | 1.5
2017-08-20 | 9:55 | 1.7429 | 0 |  | 1.5
2017-08-20 | 10:00 | 1.76 | 0 | 0 | 1.5 | 0 | 79.274
2017-08-20 | 10:05 | 1.799 | 0 |  | 1.5
2017-08-20 | 10:10 | 1.7452 | 0 |  | 1.5
2017-08-20 | 10:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 79.2297
2017-08-20 | 10:20 | 1.7312 | 0 |  | 1.5
2017-08-20 | 10:25 | 1.7553 | 0 |  | 1.5
2017-08-20 | 10:30 | 1.7491 | 0 | 0 | 1.5 | 0 | 79.4688
2017-08-20 | 10:35 | 1.7374 | 0 |  | 1.5
2017-08-20 | 10:40 | 1.7678 | 0 |  | 1.5
2017-08-20 | 10:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.5164
2017-08-20 | 10:50 | 1.746 | 0 |  | 1.5
2017-08-20 | 10:55 | 1.778 | 0 |  | 1.5
2017-08-20 | 11:00 | 1.746 | 0 | 0 | 1.5 | 0 | 79.4611
2017-08-20 | 11:05 | 1.739 | 0 |  | 1.5
2017-08-20 | 11:10 | 1.7561 | 0 |  | 1.5
2017-08-20 | 11:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.4333
2017-08-20 | 11:20 | 1.7561 | 0 |  | 1.5
2017-08-20 | 11:25 | 1.7585 | 0 |  | 1.5
2017-08-20 | 11:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.459
2017-08-20 | 11:35 | 1.7265 | 0 |  | 1.5
2017-08-20 | 11:40 | 1.7507 | 0 |  | 1.5
2017-08-20 | 11:45 | 1.7304 | 0 | 0 | 1.5 | 0 | 79.8171
2017-08-20 | 11:50 | 1.753 | 0 |  | 1.5
2017-08-20 | 11:55 | 1.7327 | 0 |  | 1.5
2017-08-20 | 12:00 | 1.753 | 0 | 0 | 1.5 | 0 | 80.084
2017-08-20 | 12:05 | 1.7327 | 0 |  | 1.5
2017-08-20 | 12:10 | 1.7436 | 0 |  | 1.5
2017-08-20 | 12:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 80.4277
2017-08-20 | 12:20 | 1.7226 | 0 |  | 1.5
2017-08-20 | 12:25 | 1.7397 | 0 |  | 1.5
2017-08-20 | 12:30 | 1.6953 | 0 | 0 | 1.5 | 0 | 81.0379
2017-08-20 | 12:35 | 1.714 | 0 |  | 1.5
2017-08-20 | 12:40 | 1.7483 | 0 |  | 1.5
2017-08-20 | 12:45 | 1.7312 | 0 | 0 | 1.5 | 0 | 81.5575
2017-08-20 | 12:50 | 1.7109 | 0 |  | 1.5
2017-08-20 | 12:55 | 1.7491 | 0 |  | 1.5
2017-08-20 | 13:00 | 1.7054 | 0 | 0 | 1.5 | 0 | 82.001
2017-08-20 | 13:05 | 1.7444 | 0 |  | 1.5
2017-08-20 | 13:10 | 1.7522 | 0 |  | 1.5
2017-08-20 | 13:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 82.0511
2017-08-20 | 13:20 | 1.7382 | 0 |  | 1.5
2017-08-20 | 13:25 | 1.7475 | 0 |  | 1.5
2017-08-20 | 13:30 | 1.7787 | 0 | 0 | 1.5 | 0 | 82.2137
2017-08-20 | 13:35 | 1.7577 | 0 |  | 1.5
2017-08-20 | 13:40 | 1.7257 | 0 |  | 1.5
2017-08-20 | 13:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 82.35
2017-08-20 | 13:50 | 1.7319 | 0 |  | 1.5
2017-08-20 | 13:55 | 1.7288 | 0 |  | 1.5
2017-08-20 | 14:00 | 1.7967 | 0 | 0 | 1.5 | 0 | 82.3821
2017-08-20 | 14:05 | 1.7413 | 0 |  | 1.5
2017-08-20 | 14:10 | 1.7475 | 0 |  | 1.5
2017-08-20 | 14:15 | 1.7741 | 0 | 0 | 1.5 | 0 | 82.4193
2017-08-20 | 14:20 | 1.7374 | 0 |  | 1.5
2017-08-20 | 14:25 | 1.7452 | 0 |  | 1.5
2017-08-20 | 14:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 82.3914
2017-08-20 | 14:35 | 1.7702 | 0 |  | 1.5
2017-08-20 | 14:40 | 1.7592 | 0 |  | 1.5
2017-08-20 | 14:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 82.2934
2017-08-20 | 14:50 | 1.7358 | 0 |  | 1.5
2017-08-20 | 14:55 | 1.7491 | 0 |  | 1.5
2017-08-20 | 15:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 82.2582
2017-08-20 | 15:05 | 1.7202 | 0 |  | 1.5
2017-08-20 | 15:10 | 1.7709 | 0 |  | 1.5
2017-08-20 | 15:15 | 1.739 | 0 | 0 | 1.5 | 0 | 82.2831
2017-08-20 | 15:20 | 1.7725 | 0 |  | 1.5
2017-08-20 | 15:25 | 1.7195 | 0 |  | 1.5
2017-08-20 | 15:30 | 1.7702 | 0 | 0 | 1.5 | 0 | 82.223
2017-08-20 | 15:35 | 1.7561 | 0 |  | 1.5
2017-08-20 | 15:40 | 1.7873 | 0 |  | 1.5
2017-08-20 | 15:45 | 1.7624 | 0 | 0 | 1.5 | 0 | 81.9217
2017-08-20 | 15:50 | 1.7468 | 0 |  | 1.5
2017-08-20 | 15:55 | 1.7483 | 0 |  | 1.5
2017-08-20 | 16:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.7669
2017-08-20 | 16:05 | 1.7561 | 0 |  | 1.5
2017-08-20 | 16:10 | 1.7452 | 0 |  | 1.5
2017-08-20 | 16:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 81.6488
2017-08-20 | 16:20 | 1.721 | 0 |  | 1.5
2017-08-20 | 16:25 | 1.7475 | 0 |  | 1.5
2017-08-20 | 16:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 81.8136
2017-08-20 | 16:35 | 1.7741 | 0 |  | 1.5
2017-08-20 | 16:40 | 1.7273 | 0 |  | 1.5
2017-08-20 | 16:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 82.0713
2017-08-20 | 16:50 | 1.7514 | 0 |  | 1.5
2017-08-20 | 16:55 | 1.7507 | 0 |  | 1.5
2017-08-20 | 17:00 | 1.7382 | 0 | 0 | 1.5 | 0 | 82.1435
2017-08-20 | 17:05 | 1.7319 | 0 |  | 1.5
2017-08-20 | 17:10 | 1.7319 | 0 |  | 1.5
2017-08-20 | 17:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 82.1294
2017-08-20 | 17:20 | 1.8076 | 0 |  | 1.5
2017-08-20 | 17:25 | 1.7663 | 0 |  | 1.5
2017-08-20 | 17:30 | 1.7507 | 0 | 0 | 1.5 | 0 | 81.8362
2017-08-20 | 17:35 | 1.7522 | 0 |  | 1.5
2017-08-20 | 17:40 | 1.7327 | 0 |  | 1.5
2017-08-20 | 17:45 | 1.753 | 0 | 0 | 1.5 | 0 | 81.7594
2017-08-20 | 17:50 | 1.7678 | 0 |  | 1.5
2017-08-20 | 17:55 | 1.7483 | 0 |  | 1.5
2017-08-20 | 18:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.6751
2017-08-20 | 18:05 | 1.7452 | 0 |  | 1.5
2017-08-20 | 18:10 | 1.7592 | 0 |  | 1.5
2017-08-20 | 18:15 | 1.7343 | 0 | 0 | 1.5 | 0 | 81.4132
2017-08-20 | 18:20 | 1.7748 | 0 |  | 1.5
2017-08-20 | 18:25 | 1.7491 | 0 |  | 1.5
2017-08-20 | 18:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 81.3513
2017-08-20 | 18:35 | 1.7772 | 0 |  | 1.5
2017-08-20 | 18:40 | 1.7725 | 0 |  | 1.5
2017-08-20 | 18:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 81.2001
2017-08-20 | 18:50 | 1.7499 | 0 |  | 1.5
2017-08-20 | 18:55 | 1.7507 | 0 |  | 1.5
2017-08-20 | 19:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 80.8459
2017-08-20 | 19:05 | 1.7561 | 0 |  | 1.5
2017-08-20 | 19:10 | 1.7546 | 0 |  | 1.5
2017-08-20 | 19:15 | 1.7335 | 0 | 0 | 1.5 | 0 | 80.6504
2017-08-20 | 19:20 | 1.7553 | 0 |  | 1.5
2017-08-20 | 19:25 | 1.7475 | 0 |  | 1.5
2017-08-20 | 19:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 80.637
2017-08-20 | 19:35 | 1.7452 | 0 |  | 1.5
2017-08-20 | 19:40 | 1.753 | 0 |  | 1.5
2017-08-20 | 19:45 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.3216
2017-08-20 | 19:50 | 1.7819 | 0 |  | 1.5
2017-08-20 | 19:55 | 1.7499 | 0 |  | 1.5
2017-08-20 | 20:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 80.0206
2017-08-20 | 20:05 | 1.7787 | 0 |  | 1.5
2017-08-20 | 20:10 | 1.746 | 0 |  | 1.5
2017-08-20 | 20:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 79.8507
2017-08-20 | 20:20 | 1.7577 | 0 |  | 1.5
2017-08-20 | 20:25 | 1.753 | 0 |  | 1.5
2017-08-20 | 20:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 79.7531
2017-08-20 | 20:35 | 1.778 | 0 |  | 1.5
2017-08-20 | 20:40 | 1.76 | 0 |  | 1.5
2017-08-20 | 20:45 | 1.753 | 0 | 0 | 1.5 | 0 | 79.313
2017-08-20 | 20:50 | 1.7826 | 0 |  | 1.5
2017-08-20 | 20:55 | 1.753 | 0 |  | 1.5
2017-08-20 | 21:00 | 1.739 | 0 | 0 | 1.5 | 0 | 79.0218
2017-08-20 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-20 | 21:10 | -0.10262 | 0 |  | 1.5
2017-08-20 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-20 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-20 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 21:35 | -0.10496 | 0 |  | 1.5
2017-08-20 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-20 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-20 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-20 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-20 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-20 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-20 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 0:15 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:20 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 0:30 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 0:45 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:50 | -0.10496 | 0 |  | 1.5
2017-08-21 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-21 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 1:00 | -0.10496 | 0 |  | 1.5
2017-08-21 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-21 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-21 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 1:15 | -0.10496 | 0 |  | 1.5
2017-08-21 | 1:20 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:25 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 1:30 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:35 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:40 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 1:45 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:50 | -0.10886 | 0 |  | 1.5
2017-08-21 | 1:55 | -0.11198 | 0 |  | 1.5
2017-08-21 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 2:00 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:05 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:10 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 2:15 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:20 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:25 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 2:30 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:35 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:40 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 2:45 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:50 | -0.10886 | 0 |  | 1.5
2017-08-21 | 2:55 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 3:00 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-21 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 3:15 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-21 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 3:30 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:35 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-21 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 3:45 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-21 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-21 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 4:00 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:05 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 4:15 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:20 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:25 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 4:30 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:35 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 4:45 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:50 | -0.10886 | 0 |  | 1.5
2017-08-21 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-21 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 5:00 | -0.10886 | 0 |  | 1.5
2017-08-21 | 5:05 | 2.2717 | 0 |  | 1.5
2017-08-21 | 5:10 | 2.2803 | 0 |  | 1.5
2017-08-21 | 5:15 | 2.111 | 0 | 0 | 1.5 | 0 | 88.5042
2017-08-21 | 5:15 | 2.111 | 0
2017-08-21 | 5:20 | 1.9519 | 0 |  | 1.5
2017-08-21 | 5:25 | 1.9581 | 0 |  | 1.5
2017-08-21 | 5:30 | 1.8973 | 0 | 0 | 1.5 | 0 | 83.313
2017-08-21 | 5:30 | 1.8973 | 0
2017-08-21 | 5:35 | 1.8903 | 0 |  | 1.5
2017-08-21 | 5:40 | 1.8131 | 0 |  | 1.5
2017-08-21 | 5:45 | 1.8193 | 0 | 0 | 1.5 | 0 | 80.9423
2017-08-21 | 5:45 | 1.8193 | 0
2017-08-21 | 5:50 | 1.7772 | 0 |  | 1.5
2017-08-21 | 5:55 | 1.767 | 0 |  | 1.5
2017-08-21 | 6:00 | 1.7912 | 0 | 0 | 1.5 | 0 | 79.8545
2017-08-21 | 6:00 | 1.7912 | 0
2017-08-21 | 6:05 | 1.7694 | 0 |  | 1.5
2017-08-21 | 6:10 | 1.7733 | 0 |  | 1.5
2017-08-21 | 6:15 |  |  |  | 1.5
2017-08-21 | 6:15 | 1.7834 | 0 | 0 | 1.5 | 0 | 79.342
2017-08-21 | 6:15 | 1.7834 | 0
2017-08-21 | 6:20 | 1.7249 | 0 |  | 1.5
2017-08-21 | 6:25 | 1.7124 | 0 |  | 1.5
2017-08-21 | 6:30 |  |  |  | 1.5
2017-08-21 | 6:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 79.3266
2017-08-21 | 6:30 | 1.7514 | 0
2017-08-21 | 6:35 |  | 0
2017-08-21 | 6:35 | 1.753 |  |  | 1.5
2017-08-21 | 6:40 | 1.7873 | 0 |  | 1.5
2017-08-21 | 6:45 | 1.7507 |  |  | 1.5
2017-08-21 | 6:45 | 1.7507 | 0 | 0 | 1.5 | 0 | 79.1424
2017-08-21 | 6:50 | 1.7608 | 0 |  | 1.5
2017-08-21 | 6:55 | 1.767 | 0 |  | 1.5
2017-08-21 | 7:00 | 1.7748 | 0 | 0 | 1.5 | 0 | 78.7844
2017-08-21 | 7:05 | 1.7538 | 0 |  | 1.5
2017-08-21 | 7:10 | 1.7561 | 0 |  | 1.5
2017-08-21 | 7:15 | 1.7436
2017-08-21 | 7:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 78.5171
2017-08-21 | 7:20 | 1.7631 | 0 |  | 1.5
2017-08-21 | 7:25 | 1.7553 | 0 |  | 1.5
2017-08-21 | 7:30 |  | 0
2017-08-21 | 7:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 78.4476
2017-08-21 | 7:30 | 1.7569
2017-08-21 | 7:35 | 1.7694 | 0 |  | 1.5
2017-08-21 | 7:40 | 1.7491 | 0 |  | 1.5
2017-08-21 | 7:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 78.2059
2017-08-21 | 7:45 | 1.7702 | 0
2017-08-21 | 7:50 | 1.7585 | 0 |  | 1.5
2017-08-21 | 7:55 | 1.7936 | 0 |  | 1.5
2017-08-21 | 8:00 | 1.767 | 0 | 0 | 1.5 | 0 | 78.0474
2017-08-21 | 8:00 | 1.767 | 0
2017-08-21 | 8:05 | 1.7468 | 0 |  | 1.5
2017-08-21 | 8:10 | 1.7499 | 0 |  | 1.5
2017-08-21 | 8:15 | 1.7585 | 0 | 0 | 1.5 | 0 | 78.1916
2017-08-21 | 8:15 | 1.7585 | 0
2017-08-21 | 8:20 | 1.7241 | 0 |  | 1.5
2017-08-21 | 8:25 | 1.7491 | 0 |  | 1.5
2017-08-21 | 8:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.4967
2017-08-21 | 8:30 | 1.7538 | 0
2017-08-21 | 8:35 | 1.7436 | 0 |  | 1.5
2017-08-21 | 8:40 | 1.7335 | 0 |  | 1.5
2017-08-21 | 8:45 | 1.7249 | 0 | 0 | 1.5 | 0 | 78.5625
2017-08-21 | 8:45 | 1.7249 | 0
2017-08-21 | 8:50 | 1.7444 | 0 |  | 1.5
2017-08-21 | 8:55 | 1.7405 | 0 |  | 1.5
2017-08-21 | 9:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 78.6381
2017-08-21 | 9:00 | 1.7436 | 0
2017-08-21 | 9:05 | 1.7702 | 0 |  | 1.5
2017-08-21 | 9:10 | 1.7538 | 0 |  | 1.5
2017-08-21 | 9:15 | 1.739 | 0 | 0 | 1.5 | 0 | 78.7333
2017-08-21 | 9:15 | 1.739 | 0
2017-08-21 | 9:20 | 1.7163 | 0 |  | 1.5
2017-08-21 | 9:25 | 1.7132 | 0 |  | 1.5
2017-08-21 | 9:30 | 1.7218 | 0 | 0 | 1.5 | 0 | 79.1812
2017-08-21 | 9:30 | 1.7218 | 0
2017-08-21 | 9:35 | 1.7452 | 0 |  | 1.5
2017-08-21 | 9:40 | 1.7288 | 0 |  | 1.5
2017-08-21 | 9:45 | 1.7343 | 0 | 0 | 1.5 | 0 | 79.7483
2017-08-21 | 9:45 | 1.7343 | 0
2017-08-21 | 9:50 | 1.7436 | 0 |  | 1.5
2017-08-21 | 9:55 | 1.7764 | 0 |  | 1.5
2017-08-21 | 10:00 | 1.7202 | 0 | 0 | 1.5 | 0 | 79.9656
2017-08-21 | 10:00 | 1.7202 | 0
2017-08-21 | 10:05 | 1.7429 | 0 |  | 1.5
2017-08-21 | 10:10 | 1.7655 | 0 |  | 1.5
2017-08-21 | 10:15 |  |  |  | 1.5 |  | 79.731
2017-08-21 | 10:15 | 1.753 | 0 | 0 | 1.5 | 0
2017-08-21 | 10:20 | 1.7795 | 0 |  | 1.5
2017-08-21 | 10:25 | 1.7709 | 0 |  | 1.5
2017-08-21 | 10:30 | 1.7608 | 0 | 0 | 1.5 | 0 | 79.0972
2017-08-21 | 10:30 | 1.7608 | 0
2017-08-21 | 10:35 | 1.7366 | 0 |  | 1.5
2017-08-21 | 10:40 | 1.7709 | 0 |  | 1.5
2017-08-21 | 10:45 | 1.7772 | 0 | 0 | 1.5 | 0 | 79.1228
2017-08-21 | 10:45 | 1.7772 | 0
2017-08-21 | 10:50 | 1.746 | 0 |  | 1.5
2017-08-21 | 10:55 | 1.76 | 0 |  | 1.5
2017-08-21 | 11:00 | 1.7335 | 0 | 0 | 1.5 | 0 | 79.1751
2017-08-21 | 11:00 | 1.7335 | 0
2017-08-21 | 11:05 | 1.7756 | 0 |  | 1.5
2017-08-21 | 11:10 | 1.7436 | 0 |  | 1.5
2017-08-21 | 11:15 | 1.7234 | 0 | 0 | 1.5 | 0 | 79.4768
2017-08-21 | 11:15 | 1.7234 | 0
2017-08-21 | 11:20 | 1.6836 | 0 |  | 1.5
2017-08-21 | 11:25 | 1.6672 | 0 |  | 1.5
2017-08-21 | 11:30 | 1.7124 | 0 | 0 | 1.5 | 0 | 80.6002
2017-08-21 | 11:30 | 1.7124 | 0
2017-08-21 | 11:35 | 1.7 | 0 |  | 1.5
2017-08-21 | 11:40 | 1.6789 | 0 |  | 1.5
2017-08-21 | 11:45 | 1.682 | 0 | 0 | 1.5 | 0 | 82.1626
2017-08-21 | 11:45 | 1.682 | 0
2017-08-21 | 11:50 | 1.728 | 0 |  | 1.5
2017-08-21 | 11:55 | 1.707 | 0 |  | 1.5
2017-08-21 | 12:00 | 1.7967 | 0 | 0 | 1.5 | 0 | 82.9807
2017-08-21 | 12:00 | 1.7967 | 0
2017-08-21 | 12:05 | 1.7709 | 0 |  | 1.5
2017-08-21 | 12:10 | 1.7522 | 0 |  | 1.5
2017-08-21 | 12:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 82.6512
2017-08-21 | 12:15 | 1.7452 | 0
2017-08-21 | 12:20 | 1.7273 | 0 |  | 1.5
2017-08-21 | 12:25 | 1.7202 | 0 |  | 1.5
2017-08-21 | 12:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 82.815
2017-08-21 | 12:30 | 1.7413 | 0
2017-08-21 | 12:35 | 1.7109 | 0 |  | 1.5
2017-08-21 | 12:40 | 1.7257 | 0 |  | 1.5
2017-08-21 | 12:45 | 1.6961 | 0 | 0 | 1.5 | 0 | 83.3558
2017-08-21 | 12:45 | 1.6961 | 0
2017-08-21 | 12:50 | 1.7218 | 0 |  | 1.5
2017-08-21 | 12:55 | 1.7078 | 0 |  | 1.5
2017-08-21 | 13:00 |  |  |  | 1.5
2017-08-21 | 13:00 | 1.6953 | 0 | 0 | 1.5 | 0 | 84.1339
2017-08-21 | 13:00 | 1.6953 | 0
2017-08-21 | 13:05 | 1.7031 | 0 |  | 1.5
2017-08-21 | 13:10 | 1.707 | 0 |  | 1.5
2017-08-21 | 13:15 | 1.7241 | 0 | 0 | 1.5 | 0 | 85.2569
2017-08-21 | 13:15 | 1.7241 | 0
2017-08-21 | 13:20 | 1.6719 | 0 |  | 1.5
2017-08-21 | 13:25 | 1.7117 | 0 |  | 1.5
2017-08-21 | 13:30 |  |  |  | 1.5
2017-08-21 | 13:30 | 1.6875 | 0 | 0 | 1.5 | 0 | 86.5651
2017-08-21 | 13:30 | 1.6875 | 0
2017-08-21 | 13:35 | 1.7288 | 0 |  | 1.5
2017-08-21 | 13:40 | 1.7694 | 0 |  | 1.5
2017-08-21 | 13:45 |  |  |  | 1.5
2017-08-21 | 13:45 | 1.7881 | 0 | 0 | 1.5 | 0 | 86.5894
2017-08-21 | 13:45 | 1.7881 | 0
2017-08-21 | 13:50 | 1.7733 | 0 |  | 1.5
2017-08-21 | 13:55 | 1.7577 | 0 |  | 1.5
2017-08-21 | 14:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 86.1655
2017-08-21 | 14:00 | 1.7397 | 0 |  | 1.5
2017-08-21 | 14:05 | 1.7873 | 0 |  | 1.5
2017-08-21 | 14:10 | 1.7702 | 0 |  | 1.5
2017-08-21 | 14:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 85.5776
2017-08-21 | 14:15 | 1.7374 | 0 |  | 1.5
2017-08-21 | 14:20 | 1.7631 | 0 |  | 1.5
2017-08-21 | 14:25 | 1.76 | 0 |  | 1.5
2017-08-21 | 14:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 85.4589
2017-08-21 | 14:30 | 1.7273 | 0 |  | 1.5
2017-08-21 | 14:35 | 1.7569 | 0 |  | 1.5
2017-08-21 | 14:40 | 1.7358 | 0 |  | 1.5
2017-08-21 | 14:45 | 1.6968 | 0 | 0 | 1.5 | 0 | 85.8156
2017-08-21 | 14:45 | 1.6968 | 0 |  | 1.5
2017-08-21 | 14:50 | 1.7397 | 0 |  | 1.5
2017-08-21 | 14:55 | 1.7421 | 0 |  | 1.5
2017-08-21 | 15:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 86.3464
2017-08-21 | 15:00 | 1.7429 | 0 |  | 1.5
2017-08-21 | 15:05 | 1.746 | 0 |  | 1.5
2017-08-21 | 15:10 | 1.7561 | 0 |  | 1.5
2017-08-21 | 15:15 | 1.7218 | 0 | 0 | 1.5 | 0 | 86.1092
2017-08-21 | 15:15 | 1.7218 |  |  | 1.5
2017-08-21 | 15:20 | 1.7491 | 0 |  | 1.5
2017-08-21 | 15:25 | 1.7358 | 0 |  | 1.5
2017-08-21 | 15:30 |  | 0
2017-08-21 | 15:30 | 1.7397 | 0 | 0 | 1.5 | 0 | 86.6549
2017-08-21 | 15:30 | 1.7397
2017-08-21 | 15:35 | 1.7413 | 0 |  | 1.5
2017-08-21 | 15:40 | 1.7421 | 0 |  | 1.5
2017-08-21 | 15:45 | 1.7733 | 0 | 0 | 1.5 | 0 | 86.6278
2017-08-21 | 15:45 | 1.7733 | 0
2017-08-21 | 15:50 | 1.7717 | 0 |  | 1.5
2017-08-21 | 15:55 | 1.7733 | 0 |  | 1.5
2017-08-21 | 16:00 | 1.767 | 0 | 0 | 1.5 | 0 | 85.8066
2017-08-21 | 16:00 | 1.767 | 0
2017-08-21 | 16:05 | 1.7538 | 0 |  | 1.5
2017-08-21 | 16:10 | 1.7702 | 0 |  | 1.5
2017-08-21 | 16:15 | 1.767 | 0 | 0 | 1.5 | 0 | 85.0296
2017-08-21 | 16:15 | 1.767 | 0
2017-08-21 | 16:20 | 1.7483 | 0 |  | 1.5
2017-08-21 | 16:25 | 1.7561 | 0 |  | 1.5
2017-08-21 | 16:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 84.606
2017-08-21 | 16:30 | 1.7655 | 0
2017-08-21 | 16:35 | 1.7686 | 0 |  | 1.5
2017-08-21 | 16:40 | 1.7507 | 0 |  | 1.5
2017-08-21 | 16:45 | 1.767 | 0 | 0 | 1.5 | 0 | 84.3523
2017-08-21 | 16:45 | 1.767 | 0
2017-08-21 | 16:50 | 1.7842 | 0 |  | 1.5
2017-08-21 | 16:55 | 1.7483 | 0 |  | 1.5
2017-08-21 | 17:00 | 1.7709 | 0 | 0 | 1.5 | 0 | 83.9318
2017-08-21 | 17:00 | 1.7709 | 0
2017-08-21 | 17:05 |  | 0
2017-08-21 | 17:05 | 1.7717 |  |  | 1.5
2017-08-21 | 17:10 | 1.7717 | 0 |  | 1.5
2017-08-21 | 17:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 83.5335
2017-08-21 | 17:15 | 1.7647 | 0
2017-08-21 | 17:20 | 1.7592 | 0 |  | 1.5
2017-08-21 | 17:25 | 1.8029 | 0 |  | 1.5
2017-08-21 | 17:30 | 1.7702 | 0 | 0 | 1.5 | 0 | 82.8379
2017-08-21 | 17:30 | 1.7702 | 0
2017-08-21 | 17:35 | 1.7772 | 0 |  | 1.5
2017-08-21 | 17:40 | 1.7624 | 0 |  | 1.5
2017-08-21 | 17:45 | 1.7748 | 0 | 0 | 1.5 | 0 | 82.5074
2017-08-21 | 17:45 | 1.7748 | 0
2017-08-21 | 17:50 | 1.7811 | 0 |  | 1.5
2017-08-21 | 17:55 | 1.7592 | 0 |  | 1.5
2017-08-21 | 18:00 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.3043
2017-08-21 | 18:00 | 1.7631 | 0
2017-08-21 | 18:05 | 1.7764 | 0 |  | 1.5
2017-08-21 | 18:10 | 1.7429 | 0 |  | 1.5
2017-08-21 | 18:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 82.1312
2017-08-21 | 18:15 | 1.7616 | 0
2017-08-21 | 18:20 | 1.7803 | 0 |  | 1.5
2017-08-21 | 18:25 | 1.7928 | 0 |  | 1.5
2017-08-21 | 18:30 | 1.7553 | 0 | 0 | 1.5 | 0 | 81.7254
2017-08-21 | 18:30 | 1.7553 | 0
2017-08-21 | 18:35 | 1.7764 | 0 |  | 1.5
2017-08-21 | 18:40 | 1.7491 | 0 |  | 1.5
2017-08-21 | 18:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 81.3811
2017-08-21 | 18:45 | 1.7475 | 0
2017-08-21 | 18:50 | 1.7507 | 0 |  | 1.5
2017-08-21 | 18:55 | 1.7663 | 0 |  | 1.5
2017-08-21 | 19:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 80.9568
2017-08-21 | 19:00 | 1.7686 | 0
2017-08-21 | 19:05 | 1.7624 | 0 |  | 1.5
2017-08-21 | 19:10 | 1.7592 | 0 |  | 1.5
2017-08-21 | 19:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 80.5267
2017-08-21 | 19:15 | 1.7546
2017-08-21 | 19:20 | 1.7639 | 0 |  | 1.5
2017-08-21 | 19:25 | 1.7663 | 0 |  | 1.5
2017-08-21 | 19:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 80.267
2017-08-21 | 19:35 | 1.7522 | 0 |  | 1.5
2017-08-21 | 19:40 | 1.7631 | 0 |  | 1.5
2017-08-21 | 19:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 79.7477
2017-08-21 | 19:50 | 1.767 | 0 |  | 1.5
2017-08-21 | 19:55 | 1.7382 | 0 |  | 1.5
2017-08-21 | 20:00 | 1.7608
2017-08-21 | 20:00 | 1.76 | 0 | 0 | 1.5 | 0 | 79.5411
2017-08-21 | 20:05 | 1.7491 | 0 |  | 1.5
2017-08-21 | 20:10 | 1.7624 | 0 |  | 1.5
2017-08-21 | 20:15 |  | 0
2017-08-21 | 20:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.1288
2017-08-21 | 20:15 | 1.7546
2017-08-21 | 20:20 | 1.7608 | 0 |  | 1.5
2017-08-21 | 20:25 | 1.7569 | 0 |  | 1.5
2017-08-21 | 20:30 | 1.7889 | 0 | 0 | 1.5 | 0 | 78.8165
2017-08-21 | 20:30 | 1.7889 | 0
2017-08-21 | 20:35 | 1.7538 | 0 |  | 1.5
2017-08-21 | 20:40 | 1.7678 | 0 |  | 1.5
2017-08-21 | 20:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 78.4746
2017-08-21 | 20:45 | 1.7429 | 0
2017-08-21 | 20:50 | 1.7327 | 0 |  | 1.5
2017-08-21 | 20:55 | 1.7553 | 0 |  | 1.5
2017-08-21 | 21:00 | 1.7358 | 0 | 0 | 1.5 | 0 | 78.5491
2017-08-21 | 21:00 | 1.7358 | 0
2017-08-21 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-21 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-21 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 21:15 | -0.10496 | 0
2017-08-21 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-21 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-21 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 21:30 | -0.10418 | 0
2017-08-21 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-21 | 21:40 | -0.10418 | 0 |  | 1.5
2017-08-21 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 21:45 | -0.10418 | 0
2017-08-21 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-21 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 22:00 | -0.10496 | 0
2017-08-21 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 22:15 | -0.10496 | 0
2017-08-21 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 22:30 | -0.10496 | 0
2017-08-21 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 22:45 | -0.10496 | 0
2017-08-21 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-21 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-21 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 23:00 | -0.10418 | 0
2017-08-21 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-21 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-21 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 23:15 | -0.10496 | 0
2017-08-21 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-21 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-21 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 23:30 | -0.10418 | 0
2017-08-21 | 23:35 | -0.10418 | 0 |  | 1.5
2017-08-21 | 23:40 | -0.10418 | 0 |  | 1.5
2017-08-21 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-21 | 23:45 | -0.10418 | 0
2017-08-21 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-21 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-21 | 24:00 |  |  |  | 1.5
2017-08-22 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 0:00 | -0.10418 | 0
2017-08-22 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-22 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-22 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-22 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-22 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-22 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-22 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 0:50 | -0.1034 | 0 |  | 1.5
2017-08-22 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-22 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-22 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-22 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 1:20 | -0.1073 | 0 |  | 1.5
2017-08-22 | 1:25 | -0.11042 | 0 |  | 1.5
2017-08-22 | 1:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 1:35 | -0.1073 | 0 |  | 1.5
2017-08-22 | 1:40 | -0.1073 | 0 |  | 1.5
2017-08-22 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 1:50 | -0.1073 | 0 |  | 1.5
2017-08-22 | 1:55 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:10 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 2:20 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:25 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:40 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 2:50 | -0.1073 | 0 |  | 1.5
2017-08-22 | 2:55 | -0.1073 | 0 |  | 1.5
2017-08-22 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 3:05 | -0.1073 | 0 |  | 1.5
2017-08-22 | 3:10 | -0.1073 | 0 |  | 1.5
2017-08-22 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-22 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-22 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-22 | 3:40 | -0.1073 | 0 |  | 1.5
2017-08-22 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-22 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-22 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-22 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-22 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 4:20 | -0.1151 | 0 |  | 1.5
2017-08-22 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-22 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 4:35 | -0.1073 | 0 |  | 1.5
2017-08-22 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-22 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-22 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-22 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 5:05 | 1.9371 | 0 |  | 1.5
2017-08-22 | 5:10 | 2.1469 | 0 |  | 1.5
2017-08-22 | 5:15 | 1.9971 | 0 | 0 | 1.5 | 0 | 92.7528
2017-08-22 | 5:20 | 1.9207 | 0 |  | 1.5
2017-08-22 | 5:25 | 1.9168 | 0 |  | 1.5
2017-08-22 | 5:30 | 1.9558 | 0 | 0 | 1.5 | 0 | 88.1462
2017-08-22 | 5:35 | 1.9145 | 0 |  | 1.5
2017-08-22 | 5:40 | 1.9059 | 0 |  | 1.5
2017-08-22 | 5:45 | 1.8731 | 0 | 0 | 1.5 | 0 | 84.1529
2017-08-22 | 5:50 | 1.8396 | 0 |  | 1.5
2017-08-22 | 5:55 | 1.838 | 0 |  | 1.5
2017-08-22 | 6:00 | 1.8255 | 0 | 0 | 1.5 | 0 | 81.5442
2017-08-22 | 6:05 | 1.8185 | 0 |  | 1.5
2017-08-22 | 6:10 | 1.8349 | 0 |  | 1.5
2017-08-22 | 6:15 | 1.7928 | 0 | 0 | 1.5 | 0 | 79.9242
2017-08-22 | 6:20 | 1.7585 | 0 |  | 1.5
2017-08-22 | 6:25 | 1.7904 | 0 |  | 1.5
2017-08-22 | 6:30 | 1.7889 | 0 | 0 | 1.5 | 0 | 79.0877
2017-08-22 | 6:35 | 1.7592 | 0 |  | 1.5
2017-08-22 | 6:40 | 1.7592 | 0 |  | 1.5
2017-08-22 | 6:45 | 1.7904 | 0 | 0 | 1.5 | 0 | 78.4292
2017-08-22 | 6:50 | 1.767 | 0 |  | 1.5
2017-08-22 | 6:55 | 1.7639 | 0 |  | 1.5
2017-08-22 | 7:00 | 1.739 | 0 | 0 | 1.5 | 0 | 78.1411
2017-08-22 | 7:05 | 1.7702 | 0 |  | 1.5
2017-08-22 | 7:10 | 1.7616 | 0 |  | 1.5
2017-08-22 | 7:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 77.8126
2017-08-22 | 7:20 | 1.7702 | 0 |  | 1.5
2017-08-22 | 7:25 | 1.7265 | 0 |  | 1.5
2017-08-22 | 7:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 77.7008
2017-08-22 | 7:35 | 1.7475 | 0 |  | 1.5
2017-08-22 | 7:40 | 1.7507 | 0 |  | 1.5
2017-08-22 | 7:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 77.5383
2017-08-22 | 7:50 | 1.7202 | 0 |  | 1.5
2017-08-22 | 7:55 | 1.7319 | 0 |  | 1.5
2017-08-22 | 8:00 | 1.7304 | 0 | 0 | 1.5 | 0 | 77.5496
2017-08-22 | 8:05 | 1.7296 | 0 |  | 1.5
2017-08-22 | 8:10 | 1.7187 | 0 |  | 1.5
2017-08-22 | 8:15 | 1.7592 | 0 | 0 | 1.5 | 0 | 77.9098
2017-08-22 | 8:20 | 1.7522 | 0 |  | 1.5
2017-08-22 | 8:25 | 1.7101 | 0 |  | 1.5
2017-08-22 | 8:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 78.1423
2017-08-22 | 8:35 | 1.7608 | 0 |  | 1.5
2017-08-22 | 8:40 | 1.76 | 0 |  | 1.5
2017-08-22 | 8:45 | 1.753 | 0 | 0 | 1.5 | 0 | 78.011
2017-08-22 | 8:50 | 1.7218 | 0 |  | 1.5
2017-08-22 | 8:55 | 1.7273 | 0 |  | 1.5
2017-08-22 | 9:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 78.1069
2017-08-22 | 9:05 | 1.7421 | 0 |  | 1.5
2017-08-22 | 9:10 | 1.753 | 0 |  | 1.5
2017-08-22 | 9:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 78.5633
2017-08-22 | 9:20 | 1.7273 | 0 |  | 1.5
2017-08-22 | 9:25 | 1.7241 | 0 |  | 1.5
2017-08-22 | 9:30 | 1.7288 | 0 | 0 | 1.5 | 0 | 79.1811
2017-08-22 | 9:35 | 1.7148 | 0 |  | 1.5
2017-08-22 | 9:40 | 1.7343 | 0 |  | 1.5
2017-08-22 | 9:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 79.514
2017-08-22 | 9:50 | 1.7452 | 0 |  | 1.5
2017-08-22 | 9:55 | 1.7475 | 0 |  | 1.5
2017-08-22 | 10:00 | 1.7296 | 0 | 0 | 1.5 | 0 | 79.4189
2017-08-22 | 10:05 | 1.7444 | 0 |  | 1.5
2017-08-22 | 10:10 | 1.7421 | 0 |  | 1.5
2017-08-22 | 10:15 | 1.7007 | 0 | 0 | 1.5 | 0 | 79.9814
2017-08-22 | 10:20 | 1.6898 | 0 |  | 1.5
2017-08-22 | 10:25 | 1.7 | 0 |  | 1.5
2017-08-22 | 10:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 81.0427
2017-08-22 | 10:35 | 1.714 | 0 |  | 1.5
2017-08-22 | 10:40 | 1.746 | 0 |  | 1.5
2017-08-22 | 10:45 | 1.7265 | 0 | 0 | 1.5 | 0 | 81.8298
2017-08-22 | 10:50 | 1.7343 | 0 |  | 1.5
2017-08-22 | 10:55 | 1.7686 | 0 |  | 1.5
2017-08-22 | 11:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.9896
2017-08-22 | 11:05 | 1.7514 | 0 |  | 1.5
2017-08-22 | 11:10 | 1.7187 | 0 |  | 1.5
2017-08-22 | 11:15 | 1.7304 | 0 | 0 | 1.5 | 0 | 82.213
2017-08-22 | 11:20 | 1.7078 | 0 |  | 1.5
2017-08-22 | 11:25 | 1.7234 | 0 |  | 1.5
2017-08-22 | 11:30 | 1.7421 | 0 | 0 | 1.5 | 0 | 82.7837
2017-08-22 | 11:35 | 1.6937 | 0 |  | 1.5
2017-08-22 | 11:40 | 1.7296 | 0 |  | 1.5
2017-08-22 | 11:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 83.3522
2017-08-22 | 11:50 | 1.7273 | 0 |  | 1.5
2017-08-22 | 11:55 | 1.7405 | 0 |  | 1.5
2017-08-22 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 0 | 83.8145
2017-08-22 | 12:05 | 1.7163 | 0 |  | 1.5
2017-08-22 | 12:10 | 1.7015 | 0 |  | 1.5
2017-08-22 | 12:15 | 1.76 | 0 | 0 | 1.5 | 0 | 84.3231
2017-08-22 | 12:20 | 1.7436 | 0 |  | 1.5
2017-08-22 | 12:25 | 1.7343 | 0 |  | 1.5
2017-08-22 | 12:30 | 1.7156 | 0 | 0 | 1.5 | 0 | 84.683
2017-08-22 | 12:35 | 1.7678 | 0 |  | 1.5
2017-08-22 | 12:40 | 1.806 | 0 |  | 1.5
2017-08-22 | 12:45 | 1.785 | 0 | 0 | 1.5 | 0 | 84.0141
2017-08-22 | 12:50 | 1.8053 | 0 |  | 1.5
2017-08-22 | 12:55 | 1.7959 | 0 |  | 1.5
2017-08-22 | 13:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 83.5379
2017-08-22 | 13:05 | 1.7444 | 0 |  | 1.5
2017-08-22 | 13:10 | 1.7631 | 0 |  | 1.5
2017-08-22 | 13:15 | 1.7304 | 0 | 0 | 1.5 | 0 | 83.2998
2017-08-22 | 13:20 | 1.7343 | 0 |  | 1.5
2017-08-22 | 13:25 | 1.7312 | 0 |  | 1.5
2017-08-22 | 13:30 | 1.728 | 0 | 0 | 1.5 | 0 | 83.5897
2017-08-22 | 13:35 | 1.7546 | 0 |  | 1.5
2017-08-22 | 13:40 | 1.7327 | 0 |  | 1.5
2017-08-22 | 13:45 | 1.7039 | 0 | 0 | 1.5 | 0 | 84.1988
2017-08-22 | 13:50 | 1.7413 | 0 |  | 1.5
2017-08-22 | 13:55 | 1.7023 | 0 |  | 1.5
2017-08-22 | 14:00 | 1.753 | 0 | 0 | 1.5 | 0 | 84.4273
2017-08-22 | 14:05 | 1.7538 | 0 |  | 1.5
2017-08-22 | 14:10 | 1.785 | 0 |  | 1.5
2017-08-22 | 14:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 84.2345
2017-08-22 | 14:20 | 1.7585 | 0 |  | 1.5
2017-08-22 | 14:25 | 1.7819 | 0 |  | 1.5
2017-08-22 | 14:30 | 1.7249 | 0 | 0 | 1.5 | 0 | 84.0949
2017-08-22 | 14:35 | 1.7374 | 0 |  | 1.5
2017-08-22 | 14:40 | 1.7397 | 0 |  | 1.5
2017-08-22 | 14:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 84.1487
2017-08-22 | 14:50 | 1.7351 | 0 |  | 1.5
2017-08-22 | 14:55 | 1.7546 | 0 |  | 1.5
2017-08-22 | 15:00 | 1.753 | 0 | 0 | 1.5 | 0 | 84.4981
2017-08-22 | 15:05 | 1.7241 | 0 |  | 1.5
2017-08-22 | 15:10 | 1.7226 | 0 |  | 1.5
2017-08-22 | 15:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 84.7925
2017-08-22 | 15:20 | 1.792 | 0 |  | 1.5
2017-08-22 | 15:25 | 1.785 | 0 |  | 1.5
2017-08-22 | 15:30 | 1.6953 | 0 | 0 | 1.5 | 0 | 84.6925
2017-08-22 | 15:35 | 1.7124 | 0 |  | 1.5
2017-08-22 | 15:40 | 1.7241 | 0 |  | 1.5
2017-08-22 | 15:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 85.2982
2017-08-22 | 15:50 | 1.7343 | 0 |  | 1.5
2017-08-22 | 15:55 | 1.753 | 0 |  | 1.5
2017-08-22 | 16:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 85.3516
2017-08-22 | 16:05 | 1.7327 | 0 |  | 1.5
2017-08-22 | 16:10 | 1.7304 | 0 |  | 1.5
2017-08-22 | 16:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 85.7686
2017-08-22 | 16:20 | 1.7686 | 0 |  | 1.5
2017-08-22 | 16:25 | 1.7577 | 0 |  | 1.5
2017-08-22 | 16:30 | 1.753 | 0 | 0 | 1.5 | 0 | 85.7306
2017-08-22 | 16:35 | 1.7663 | 0 |  | 1.5
2017-08-22 | 16:40 | 1.7819 | 0 |  | 1.5
2017-08-22 | 16:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 85.1858
2017-08-22 | 16:50 | 1.8411 | 0 |  | 1.5
2017-08-22 | 16:55 | 1.7951 | 0 |  | 1.5
2017-08-22 | 17:00 | 1.7787 | 0 | 0 | 1.5 | 0 | 83.5101
2017-08-22 | 17:05 | 1.7694 | 0 |  | 1.5
2017-08-22 | 17:10 | 1.778 | 0 |  | 1.5
2017-08-22 | 17:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.7386
2017-08-22 | 17:20 | 1.7873 | 0 |  | 1.5
2017-08-22 | 17:25 | 1.7904 | 0 |  | 1.5
2017-08-22 | 17:30 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.9469
2017-08-22 | 17:35 | 1.7772 | 0 |  | 1.5
2017-08-22 | 17:40 | 1.767 | 0 |  | 1.5
2017-08-22 | 17:45 | 1.7709 | 0 | 0 | 1.5 | 0 | 81.1465
2017-08-22 | 17:50 | 1.7982 | 0 |  | 1.5
2017-08-22 | 17:55 | 1.7889 | 0 |  | 1.5
2017-08-22 | 18:00 | 1.778 | 0 | 0 | 1.5 | 0 | 80.5074
2017-08-22 | 18:05 | 1.7444 | 0 |  | 1.5
2017-08-22 | 18:10 | 1.753 | 0 |  | 1.5
2017-08-22 | 18:15 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.4489
2017-08-22 | 18:20 | 1.7826 | 0 |  | 1.5
2017-08-22 | 18:25 | 1.7514 | 0 |  | 1.5
2017-08-22 | 18:30 | 1.7709 | 0 | 0 | 1.5 | 0 | 80.3561
2017-08-22 | 18:35 | 1.7756 | 0 |  | 1.5
2017-08-22 | 18:40 | 1.7546 | 0 |  | 1.5
2017-08-22 | 18:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 80.129
2017-08-22 | 18:50 | 1.7585 | 0 |  | 1.5
2017-08-22 | 18:55 | 1.7741 | 0 |  | 1.5
2017-08-22 | 19:00 | 1.7748 | 0 | 0 | 1.5 | 0 | 79.7875
2017-08-22 | 19:05 | 1.7678 | 0 |  | 1.5
2017-08-22 | 19:10 | 1.7624 | 0 |  | 1.5
2017-08-22 | 19:15 | 1.7717 | 0 | 0 | 1.5 | 0 | 79.5346
2017-08-22 | 19:20 | 1.7444 | 0 |  | 1.5
2017-08-22 | 19:25 | 1.7514 | 0 |  | 1.5
2017-08-22 | 19:30 | 1.7608 | 0 | 0 | 1.5 | 0 | 79.2395
2017-08-22 | 19:35 | 1.7694 | 0 |  | 1.5
2017-08-22 | 19:40 | 1.7475 | 0 |  | 1.5
2017-08-22 | 19:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 79.0514
2017-08-22 | 19:50 | 1.7546 | 0 |  | 1.5
2017-08-22 | 19:55 | 1.7865 | 0 |  | 1.5
2017-08-22 | 20:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 78.7238
2017-08-22 | 20:05 | 1.767 | 0 |  | 1.5
2017-08-22 | 20:10 | 1.7585 | 0 |  | 1.5
2017-08-22 | 20:15 | 1.7819 | 0 | 0 | 1.5 | 0 | 78.4626
2017-08-22 | 20:20 | 1.7819 | 0 |  | 1.5
2017-08-22 | 20:25 | 1.7647 | 0 |  | 1.5
2017-08-22 | 20:30 | 1.7819 | 0 | 0 | 1.5 | 0 | 78.0231
2017-08-22 | 20:35 | 1.7936 | 0 |  | 1.5
2017-08-22 | 20:40 | 1.7514 | 0 |  | 1.5
2017-08-22 | 20:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 77.7259
2017-08-22 | 20:50 | 1.7429 | 0 |  | 1.5
2017-08-22 | 20:55 | 1.7811 | 0 |  | 1.5
2017-08-22 | 21:00 | 1.7444 | 0 | 0 | 1.5 | 0 | 77.6386
2017-08-22 | 21:05 | -0.10496 | 0 |  | 1.5
2017-08-22 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-22 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-22 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-22 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-22 | 21:40 | -0.10418 | 0 |  | 1.5
2017-08-22 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 21:50 | -0.10418 | 0 |  | 1.5
2017-08-22 | 21:55 | -0.10418 | 0 |  | 1.5
2017-08-22 | 22:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-22 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-22 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-22 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-22 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-22 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-22 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 22:50 | -0.10574 | 0 |  | 1.5
2017-08-22 | 22:55 | -0.10574 | 0 |  | 1.5
2017-08-22 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-22 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-22 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-22 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-22 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-22 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-22 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-22 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-22 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-23 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-23 | 0:10 | -0.10496 | 0 |  | 1.5
2017-08-23 | 0:15 | -0.12524 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 0:20 | -0.11042 | 0 |  | 1.5
2017-08-23 | 0:25 | -0.11042 | 0 |  | 1.5
2017-08-23 | 0:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 0:35 | -0.11042 | 0 |  | 1.5
2017-08-23 | 0:40 | -0.10964 | 0 |  | 1.5
2017-08-23 | 0:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 0:50 | -0.11042 | 0 |  | 1.5
2017-08-23 | 0:55 | -0.11042 | 0 |  | 1.5
2017-08-23 | 1:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 1:05 | -0.10964 | 0 |  | 1.5
2017-08-23 | 1:10 | -0.10964 | 0 |  | 1.5
2017-08-23 | 1:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 1:20 | -0.11354 | 0 |  | 1.5
2017-08-23 | 1:25 | -0.11354 | 0 |  | 1.5
2017-08-23 | 1:30 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 1:35 | -0.11432 | 0 |  | 1.5
2017-08-23 | 1:40 | -0.11432 | 0 |  | 1.5
2017-08-23 | 1:45 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 1:50 | -0.11432 | 0 |  | 1.5
2017-08-23 | 1:55 | -0.11432 | 0 |  | 1.5
2017-08-23 | 2:00 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 2:05 | -0.11354 | 0 |  | 1.5
2017-08-23 | 2:10 | -0.11432 | 0 |  | 1.5
2017-08-23 | 2:15 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 2:20 | -0.11432 | 0 |  | 1.5
2017-08-23 | 2:25 | -0.11432 | 0 |  | 1.5
2017-08-23 | 2:30 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 2:35 | -0.11432 | 0 |  | 1.5
2017-08-23 | 2:40 | -0.11354 | 0 |  | 1.5
2017-08-23 | 2:45 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 2:50 | -0.11354 | 0 |  | 1.5
2017-08-23 | 2:55 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:00 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 3:05 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:10 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:15 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 3:20 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:25 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:30 | -0.11354 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 3:35 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:40 | -0.11432 | 0 |  | 1.5
2017-08-23 | 3:45 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 3:50 | -0.11354 | 0 |  | 1.5
2017-08-23 | 3:55 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:00 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 4:05 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:10 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:15 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 4:20 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:25 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:30 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 4:35 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:40 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:45 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 4:50 | -0.11432 | 0 |  | 1.5
2017-08-23 | 4:55 | -0.11432 | 0 |  | 1.5
2017-08-23 | 5:00 | -0.11432 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 5:05 | 1.8965 | 0 |  | 1.5
2017-08-23 | 5:10 | 2.051 | 0 |  | 1.5
2017-08-23 | 5:15 | 1.9293 | 0 | 0 | 1.5 | 0 | 94.3891
2017-08-23 | 5:20 | 1.902 | 0 |  | 1.5
2017-08-23 | 5:25 | 1.9269 | 0 |  | 1.5
2017-08-23 | 5:30 | 1.9917 | 0 | 0 | 1.5 | 0 | 89.4437
2017-08-23 | 5:35 | 2.0104 | 0 |  | 1.5
2017-08-23 | 5:40 | 1.955 | 0 |  | 1.5
2017-08-23 | 5:45 | 1.8887 | 0 | 0 | 1.5 | 0 | 83.767
2017-08-23 | 5:50 | 1.856 | 0 |  | 1.5
2017-08-23 | 5:55 | 1.8692 | 0 |  | 1.5
2017-08-23 | 6:00 | 1.8287 | 0 | 0 | 1.5 | 0 | 80.8312
2017-08-23 | 6:05 | 1.8076 | 0 |  | 1.5
2017-08-23 | 6:10 | 1.8076 | 0 |  | 1.5
2017-08-23 | 6:15 | 1.785 | 0 | 0 | 1.5 | 0 | 79.4327
2017-08-23 | 6:20 | 1.7865 | 0 |  | 1.5
2017-08-23 | 6:25 | 1.7647 | 0 |  | 1.5
2017-08-23 | 6:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 78.641
2017-08-23 | 6:35 | 1.7569 | 0 |  | 1.5
2017-08-23 | 6:40 | 1.7741 | 0 |  | 1.5
2017-08-23 | 6:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 78.2603
2017-08-23 | 6:50 | 1.767 | 0 |  | 1.5
2017-08-23 | 6:55 | 1.7865 | 0 |  | 1.5
2017-08-23 | 7:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 77.8518
2017-08-23 | 7:05 | 1.7608 | 0 |  | 1.5
2017-08-23 | 7:10 | 1.7507 | 0 |  | 1.5
2017-08-23 | 7:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 77.6092
2017-08-23 | 7:20 | 1.7663 | 0 |  | 1.5
2017-08-23 | 7:25 | 1.7561 | 0 |  | 1.5
2017-08-23 | 7:30 | 1.746 | 0 | 0 | 1.5 | 0 | 77.473
2017-08-23 | 7:35 | 1.7834 | 0 |  | 1.5
2017-08-23 | 7:40 | 1.7655 | 0 |  | 1.5
2017-08-23 | 7:45 | 1.753 | 0 | 0 | 1.5 | 0 | 77.2573
2017-08-23 | 7:50 | 1.778 | 0 |  | 1.5
2017-08-23 | 7:55 | 1.7787 | 0 |  | 1.5
2017-08-23 | 8:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 77.1133
2017-08-23 | 8:05 | 1.7507 | 0 |  | 1.5
2017-08-23 | 8:10 | 1.7335 | 0 |  | 1.5
2017-08-23 | 8:15 | 1.7163 | 0 | 0 | 1.5 | 0 | 77.5876
2017-08-23 | 8:20 | 1.7288 | 0 |  | 1.5
2017-08-23 | 8:25 | 1.7733 | 0 |  | 1.5
2017-08-23 | 8:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 77.7682
2017-08-23 | 8:35 | 1.7709 | 0 |  | 1.5
2017-08-23 | 8:40 | 1.7319 | 0 |  | 1.5
2017-08-23 | 8:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 78.0067
2017-08-23 | 8:50 | 1.7522 | 0 |  | 1.5
2017-08-23 | 8:55 | 1.7717 | 0 |  | 1.5
2017-08-23 | 9:00 | 1.7694 | 0 | 0 | 1.5 | 0 | 78.1385
2017-08-23 | 9:05 | 1.7741 | 0 |  | 1.5
2017-08-23 | 9:10 | 1.7452 | 0 |  | 1.5
2017-08-23 | 9:15 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.4572
2017-08-23 | 9:20 | 1.7296 | 0 |  | 1.5
2017-08-23 | 9:25 | 1.7132 | 0 |  | 1.5
2017-08-23 | 9:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 78.9337
2017-08-23 | 9:35 | 1.7335 | 0 |  | 1.5
2017-08-23 | 9:40 | 1.7358 | 0 |  | 1.5
2017-08-23 | 9:45 | 1.6945 | 0 | 0 | 1.5 | 0 | 79.568
2017-08-23 | 9:50 | 1.7335 | 0 |  | 1.5
2017-08-23 | 9:55 | 1.7195 | 0 |  | 1.5
2017-08-23 | 10:00 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.9567
2017-08-23 | 10:05 | 1.7756 | 0 |  | 1.5
2017-08-23 | 10:10 | 1.7569 | 0 |  | 1.5
2017-08-23 | 10:15 | 1.7374 | 0 | 0 | 1.5 | 0 | 79.5974
2017-08-23 | 10:20 | 1.7343 | 0 |  | 1.5
2017-08-23 | 10:25 | 1.6961 | 0 |  | 1.5
2017-08-23 | 10:30 | 1.7319 | 0 | 0 | 1.5 | 0 | 79.8677
2017-08-23 | 10:35 | 1.7335 | 0 |  | 1.5
2017-08-23 | 10:40 | 1.7413 | 0 |  | 1.5
2017-08-23 | 10:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 80.2785
2017-08-23 | 10:50 | 1.778 | 0 |  | 1.5
2017-08-23 | 10:55 | 1.7491 | 0 |  | 1.5
2017-08-23 | 11:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 80.455
2017-08-23 | 11:05 | 1.7226 | 0 |  | 1.5
2017-08-23 | 11:10 | 1.7202 | 0 |  | 1.5
2017-08-23 | 11:15 | 1.7382 | 0 | 0 | 1.5 | 0 | 80.9828
2017-08-23 | 11:20 | 1.753 | 0 |  | 1.5
2017-08-23 | 11:25 | 1.7171 | 0 |  | 1.5
2017-08-23 | 11:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 81.4739
2017-08-23 | 11:35 | 1.7491 | 0 |  | 1.5
2017-08-23 | 11:40 | 1.7234 | 0 |  | 1.5
2017-08-23 | 11:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 81.7674
2017-08-23 | 11:50 | 1.7608 | 0 |  | 1.5
2017-08-23 | 11:55 | 1.7413 | 0 |  | 1.5
2017-08-23 | 12:00 | 1.6984 | 0 | 0 | 1.5 | 0 | 82.1299
2017-08-23 | 12:05 | 1.7226 | 0 |  | 1.5
2017-08-23 | 12:10 | 1.7187 | 0 |  | 1.5
2017-08-23 | 12:15 | 1.7382 | 0 | 0 | 1.5 | 0 | 82.7039
2017-08-23 | 12:20 | 1.7468 | 0 |  | 1.5
2017-08-23 | 12:25 | 1.785 | 0 |  | 1.5
2017-08-23 | 12:30 | 1.7772 | 0 | 0 | 1.5 | 0 | 82.5493
2017-08-23 | 12:35 | 1.7819 | 0 |  | 1.5
2017-08-23 | 12:40 | 1.76 | 0 |  | 1.5
2017-08-23 | 12:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 82.3414
2017-08-23 | 12:50 | 1.7585 | 0 |  | 1.5
2017-08-23 | 12:55 | 1.7405 | 0 |  | 1.5
2017-08-23 | 13:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 82.6825
2017-08-23 | 13:05 | 1.7101 | 0 |  | 1.5
2017-08-23 | 13:10 | 1.7507 | 0 |  | 1.5
2017-08-23 | 13:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 83.2909
2017-08-23 | 13:20 | 1.6929 | 0 |  | 1.5
2017-08-23 | 13:25 | 1.7288 | 0 |  | 1.5
2017-08-23 | 13:30 | 1.7374 | 0 | 0 | 1.5 | 0 | 83.8963
2017-08-23 | 13:35 | 1.7741 | 0 |  | 1.5
2017-08-23 | 13:40 | 1.7889 | 0 |  | 1.5
2017-08-23 | 13:45 | 1.7904 | 0 | 0 | 1.5 | 0 | 83.2234
2017-08-23 | 13:50 | 1.7366 | 0 |  | 1.5
2017-08-23 | 13:55 | 1.7819 | 0 |  | 1.5
2017-08-23 | 14:00 | 1.7764 | 0 | 0 | 1.5 | 0 | 82.6321
2017-08-23 | 14:05 | 1.792 | 0 |  | 1.5
2017-08-23 | 14:10 | 1.7811 | 0 |  | 1.5
2017-08-23 | 14:15 | 1.7702 | 0 | 0 | 1.5 | 0 | 82.0151
2017-08-23 | 14:20 | 1.7117 | 0 |  | 1.5
2017-08-23 | 14:25 | 1.6953 | 0 |  | 1.5
2017-08-23 | 14:30 | 1.7156 | 0 | 0 | 1.5 | 0 | 82.8533
2017-08-23 | 14:35 | 1.76 | 0 |  | 1.5
2017-08-23 | 14:40 | 1.7444 | 0 |  | 1.5
2017-08-23 | 14:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 83.0154
2017-08-23 | 14:50 | 1.7561 | 0 |  | 1.5
2017-08-23 | 14:55 | 1.7631 | 0 |  | 1.5
2017-08-23 | 15:00 | 1.746 | 0 | 0 | 1.5 | 0 | 82.8519
2017-08-23 | 15:05 | 1.7257 | 0 |  | 1.5
2017-08-23 | 15:10 | 1.7382 | 0 |  | 1.5
2017-08-23 | 15:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 82.9348
2017-08-23 | 15:20 | 1.7577 | 0 |  | 1.5
2017-08-23 | 15:25 | 1.7312 | 0 |  | 1.5
2017-08-23 | 15:30 | 1.7592 | 0 | 0 | 1.5 | 0 | 82.7864
2017-08-23 | 15:35 | 1.7507 | 0 |  | 1.5
2017-08-23 | 15:40 | 1.7639 | 0 |  | 1.5
2017-08-23 | 15:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 82.6665
2017-08-23 | 15:50 | 1.7468 | 0 |  | 1.5
2017-08-23 | 15:55 | 1.739 | 0 |  | 1.5
2017-08-23 | 16:00 | 1.767 | 0 | 0 | 1.5 | 0 | 82.5153
2017-08-23 | 16:05 | 1.7592 | 0 |  | 1.5
2017-08-23 | 16:10 | 1.7577 | 0 |  | 1.5
2017-08-23 | 16:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 82.3416
2017-08-23 | 16:20 | 1.7967 | 0 |  | 1.5
2017-08-23 | 16:25 | 1.7748 | 0 |  | 1.5
2017-08-23 | 16:30 | 1.778 | 0 | 0 | 1.5 | 0 | 81.9753
2017-08-23 | 16:35 | 1.746 | 0 |  | 1.5
2017-08-23 | 16:40 | 1.7881 | 0 |  | 1.5
2017-08-23 | 16:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.8228
2017-08-23 | 16:50 | 1.7468 | 0 |  | 1.5
2017-08-23 | 16:55 | 1.7507 | 0 |  | 1.5
2017-08-23 | 17:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 81.8401
2017-08-23 | 17:05 | 1.7491 | 0 |  | 1.5
2017-08-23 | 17:10 | 1.7694 | 0 |  | 1.5
2017-08-23 | 17:15 | 1.7756 | 0 | 0 | 1.5 | 0 | 81.6303
2017-08-23 | 17:20 | 1.7709 | 0 |  | 1.5
2017-08-23 | 17:25 | 1.7709 | 0 |  | 1.5
2017-08-23 | 17:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 81.1042
2017-08-23 | 17:35 | 1.7873 | 0 |  | 1.5
2017-08-23 | 17:40 | 1.7764 | 0 |  | 1.5
2017-08-23 | 17:45 | 1.7319 | 0 | 0 | 1.5 | 0 | 80.5376
2017-08-23 | 17:50 | 1.7756 | 0 |  | 1.5
2017-08-23 | 17:55 | 1.76 | 0 |  | 1.5
2017-08-23 | 18:00 | 1.7795 | 0 | 0 | 1.5 | 0 | 80.1093
2017-08-23 | 18:05 | 1.792 | 0 |  | 1.5
2017-08-23 | 18:10 | 1.7538 | 0 |  | 1.5
2017-08-23 | 18:15 | 1.7296 | 0 | 0 | 1.5 | 0 | 79.7056
2017-08-23 | 18:20 | 1.7709 | 0 |  | 1.5
2017-08-23 | 18:25 | 1.7273 | 0 |  | 1.5
2017-08-23 | 18:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.4785
2017-08-23 | 18:35 | 1.7499 | 0 |  | 1.5
2017-08-23 | 18:40 | 1.7366 | 0 |  | 1.5
2017-08-23 | 18:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 79.2994
2017-08-23 | 18:50 | 1.76 | 0 |  | 1.5
2017-08-23 | 18:55 | 1.7756 | 0 |  | 1.5
2017-08-23 | 19:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 78.9635
2017-08-23 | 19:05 | 1.7702 | 0 |  | 1.5
2017-08-23 | 19:10 | 1.7624 | 0 |  | 1.5
2017-08-23 | 19:15 | 1.7694 | 0 | 0 | 1.5 | 0 | 78.7302
2017-08-23 | 19:20 | 1.7725 | 0 |  | 1.5
2017-08-23 | 19:25 | 1.7608 | 0 |  | 1.5
2017-08-23 | 19:30 | 1.7811 | 0 | 0 | 1.5 | 0 | 78.2213
2017-08-23 | 19:35 | 1.7702 | 0 |  | 1.5
2017-08-23 | 19:40 | 1.7936 | 0 |  | 1.5
2017-08-23 | 19:45 | 1.7709 | 0 | 0 | 1.5 | 0 | 77.5435
2017-08-23 | 19:50 | 1.7647 | 0 |  | 1.5
2017-08-23 | 19:55 | 1.7335 | 0 |  | 1.5
2017-08-23 | 20:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 77.4425
2017-08-23 | 20:05 | 1.7507 | 0 |  | 1.5
2017-08-23 | 20:10 | 1.7624 | 0 |  | 1.5
2017-08-23 | 20:15 | 1.7787 | 0 | 0 | 1.5 | 0 | 77.2017
2017-08-23 | 20:20 | 1.7569 | 0 |  | 1.5
2017-08-23 | 20:25 | 1.7444 | 0 |  | 1.5
2017-08-23 | 20:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 77.2694
2017-08-23 | 20:35 | 1.7616 | 0 |  | 1.5
2017-08-23 | 20:40 | 1.7507 | 0 |  | 1.5
2017-08-23 | 20:45 | 1.7452 | 0 | 0 | 1.5 | 0 | 77.3915
2017-08-23 | 20:50 | 1.7358 | 0 |  | 1.5
2017-08-23 | 20:55 | 1.7343 | 0 |  | 1.5
2017-08-23 | 21:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 77.5866
2017-08-23 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-23 | 21:10 | -0.10574 | 0 |  | 1.5
2017-08-23 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-23 | 21:25 | -0.10574 | 0 |  | 1.5
2017-08-23 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-23 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-23 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 21:50 | -0.10652 | 0 |  | 1.5
2017-08-23 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-23 | 22:10 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 22:20 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:25 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 22:35 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:40 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 22:50 | -0.10652 | 0 |  | 1.5
2017-08-23 | 22:55 | -0.1073 | 0 |  | 1.5
2017-08-23 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 23:05 | -0.10652 | 0 |  | 1.5
2017-08-23 | 23:10 | -0.10652 | 0 |  | 1.5
2017-08-23 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 23:20 | -0.10652 | 0 |  | 1.5
2017-08-23 | 23:25 | -0.10574 | 0 |  | 1.5
2017-08-23 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-23 | 23:40 | -0.10652 | 0 |  | 1.5
2017-08-23 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-23 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-23 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-24 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 0:05 | -0.10574 | 0 |  | 1.5
2017-08-24 | 0:10 | -0.10574 | 0 |  | 1.5
2017-08-24 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 0:20 | -0.10496 | 0 |  | 1.5
2017-08-24 | 0:25 | -0.10496 | 0 |  | 1.5
2017-08-24 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-24 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-24 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 0:50 | -0.10496 | 0 |  | 1.5
2017-08-24 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-24 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-24 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-24 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 1:20 | -0.10808 | 0 |  | 1.5
2017-08-24 | 1:25 | -0.10808 | 0 |  | 1.5
2017-08-24 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 1:35 | -0.10964 | 0 |  | 1.5
2017-08-24 | 1:40 | -0.10886 | 0 |  | 1.5
2017-08-24 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 1:50 | -0.10886 | 0 |  | 1.5
2017-08-24 | 1:55 | -0.10886 | 0 |  | 1.5
2017-08-24 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 2:05 | -0.10886 | 0 |  | 1.5
2017-08-24 | 2:10 | -0.10886 | 0 |  | 1.5
2017-08-24 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-24 | 2:25 | -0.10808 | 0 |  | 1.5
2017-08-24 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 2:35 | -0.1073 | 0 |  | 1.5
2017-08-24 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-24 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 2:50 | -0.10808 | 0 |  | 1.5
2017-08-24 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-24 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-24 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-24 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 3:20 | -0.1073 | 0 |  | 1.5
2017-08-24 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-24 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-24 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-24 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 3:50 | -0.1073 | 0 |  | 1.5
2017-08-24 | 3:55 | -0.10964 | 0 |  | 1.5
2017-08-24 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 4:05 | -0.10964 | 0 |  | 1.5
2017-08-24 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-24 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 4:20 | -0.10964 | 0 |  | 1.5
2017-08-24 | 4:25 | -0.10964 | 0 |  | 1.5
2017-08-24 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 4:35 | -0.10886 | 0 |  | 1.5
2017-08-24 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-24 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 4:50 | -0.10886 | 0 |  | 1.5
2017-08-24 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-24 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 25
2017-08-24 | 5:05 | 1.7514 | 0 |  | 1.5
2017-08-24 | 5:10 | 1.9769 | 0 |  | 1.5
2017-08-24 | 5:15 | 1.8567 | 0 | 0 | 1.5 | 0 | 95.9527
2017-08-24 | 5:20 | 1.8638 | 0 |  | 1.5
2017-08-24 | 5:25 | 1.9285 | 0 |  | 1.5
2017-08-24 | 5:30 | 2.019 | 0 | 0 | 1.5 | 0 | 91.3322
2017-08-24 | 5:35 | 2.0369 | 0 |  | 1.5
2017-08-24 | 5:40 | 1.9784 | 0 |  | 1.5
2017-08-24 | 5:45 | 1.9379 | 0 | 0 | 1.5 | 0 | 84.6115
2017-08-24 | 5:50 | 1.909 | 0 |  | 1.5
2017-08-24 | 5:55 | 1.845 | 0 |  | 1.5
2017-08-24 | 6:00 | 1.8521 | 0 | 0 | 1.5 | 0 | 81.0049
2017-08-24 | 6:05 | 1.8357 | 0 |  | 1.5
2017-08-24 | 6:10 | 1.8138 | 0 |  | 1.5
2017-08-24 | 6:15 | 1.7959 | 0 | 0 | 1.5 | 0 | 79.3988
2017-08-24 | 6:20 | 1.7538 | 0 |  | 1.5
2017-08-24 | 6:25 | 1.7725 | 0 |  | 1.5
2017-08-24 | 6:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 78.8851
2017-08-24 | 6:35 | 1.753 | 0 |  | 1.5
2017-08-24 | 6:40 | 1.7858 | 0 |  | 1.5
2017-08-24 | 6:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 78.5623
2017-08-24 | 6:50 | 1.7717 | 0 |  | 1.5
2017-08-24 | 6:55 | 1.7764 | 0 |  | 1.5
2017-08-24 | 7:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 78.2075
2017-08-24 | 7:05 | 1.7522 | 0 |  | 1.5
2017-08-24 | 7:10 | 1.778 | 0 |  | 1.5
2017-08-24 | 7:15 | 1.7787 | 0 | 0 | 1.5 | 0 | 77.6954
2017-08-24 | 7:20 | 1.7756 | 0 |  | 1.5
2017-08-24 | 7:25 | 1.7507 | 0 |  | 1.5
2017-08-24 | 7:30 | 1.7678 | 0 | 0 | 1.5 | 0
2017-08-24 | 7:30 | [5 empty] | 77.3527
2017-08-24 | 7:35 | 1.7553 | 0 |  | 1.5
2017-08-24 | 7:40 | 1.746 | 0 |  | 1.5
2017-08-24 | 7:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 77.2043
2017-08-24 | 7:50 | 1.7241 | 0 |  | 1.5
2017-08-24 | 7:55 | 1.7195 | 0 |  | 1.5
2017-08-24 | 8:00 | 1.753 | 0 | 0 | 1.5 | 0 | 77.7986
2017-08-24 | 8:05 | 1.7436 | 0 |  | 1.5
2017-08-24 | 8:10 | 1.721 | 0 |  | 1.5
2017-08-24 | 8:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 78.2489
2017-08-24 | 8:20 | 1.7351 | 0 |  | 1.5
2017-08-24 | 8:25 | 1.7702 | 0 |  | 1.5
2017-08-24 | 8:30 | 1.7491 | 0 | 0 | 1.5 | 0 | 78.6448
2017-08-24 | 8:35 | 1.6516 | 0 |  | 1.5
2017-08-24 | 8:40 | 1.6664 | 0 |  | 1.5
2017-08-24 | 8:45 | 1.6812 | 0 | 0 | 1.5 | 0 | 80.4646
2017-08-24 | 8:50 | 1.7366 | 0 |  | 1.5
2017-08-24 | 8:55 | 1.7873 | 0 |  | 1.5
2017-08-24 | 9:00 | 1.7725 | 0 | 0 | 1.5 | 0 | 80.1898
2017-08-24 | 9:05 | 1.7436 | 0 |  | 1.5
2017-08-24 | 9:10 | 1.785 | 0 |  | 1.5
2017-08-24 | 9:15 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.9107
2017-08-24 | 9:20 | 1.7826 | 0 |  | 1.5
2017-08-24 | 9:25 | 1.7514 | 0 |  | 1.5
2017-08-24 | 9:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 79.738
2017-08-24 | 9:35 | 1.7327 | 0 |  | 1.5
2017-08-24 | 9:40 | 1.7405 | 0 |  | 1.5
2017-08-24 | 9:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 79.9997
2017-08-24 | 9:50 | 1.7639 | 0 |  | 1.5
2017-08-24 | 9:55 | 1.7241 | 0 |  | 1.5
2017-08-24 | 10:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 80.1529
2017-08-24 | 10:05 | 1.7148 | 0 |  | 1.5
2017-08-24 | 10:10 | 1.7468 | 0 |  | 1.5
2017-08-24 | 10:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 80.4086
2017-08-24 | 10:20 | 1.7538 | 0 |  | 1.5
2017-08-24 | 10:25 | 1.7717 | 0 |  | 1.5
2017-08-24 | 10:30 | 1.7694 | 0 | 0 | 1.5 | 0 | 80.2652
2017-08-24 | 10:35 | 1.7288 | 0 |  | 1.5
2017-08-24 | 10:40 | 1.7616 | 0 |  | 1.5
2017-08-24 | 10:45 | 1.7062 | 0 | 0 | 1.5 | 0 | 80.3126
2017-08-24 | 10:50 | 1.7522 | 0 |  | 1.5
2017-08-24 | 10:55 | 1.6992 | 0 |  | 1.5
2017-08-24 | 11:00 | 1.6984 | 0 | 0 | 1.5 | 0 | 80.5081
2017-08-24 | 11:05 | 1.7413 | 0 |  | 1.5
2017-08-24 | 11:10 | 1.7226 | 0 |  | 1.5
2017-08-24 | 11:15 | 1.7132 | 0 | 0 | 1.5 | 0 | 81.1221
2017-08-24 | 11:20 | 1.7124 | 0 |  | 1.5
2017-08-24 | 11:25 | 1.6875 | 0 |  | 1.5
2017-08-24 | 11:30 | 1.728 | 0 | 0 | 1.5 | 0 | 81.9672
2017-08-24 | 11:35 | 1.7429 | 0 |  | 1.5
2017-08-24 | 11:40 | 1.7226 | 0 |  | 1.5
2017-08-24 | 11:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 82.4458
2017-08-24 | 11:50 | 1.7039 | 0 |  | 1.5
2017-08-24 | 11:55 | 1.6922 | 0 |  | 1.5
2017-08-24 | 12:00 | 1.6898 | 0 | 0 | 1.5 | 0
2017-08-24 | 12:00 | [5 empty] | 83.6207
2017-08-24 | 12:05 | 1.6898 | 0 |  | 1.5
2017-08-24 | 12:10 | 1.7015 | 0 |  | 1.5
2017-08-24 | 12:15 | 1.6719 | 0 | 0 | 1.5 | 0 | 85.3024
2017-08-24 | 12:20 | 1.6922 | 0 |  | 1.5
2017-08-24 | 12:25 | 1.7273 | 0 |  | 1.5
2017-08-24 | 12:30 | 1.6758 | 0 | 0 | 1.5 | 0
2017-08-24 | 12:30 | [5 empty] | 87.049
2017-08-24 | 12:35 | 1.6976 | 0 |  | 1.5
2017-08-24 | 12:40 | -0.11276 | 0 |  | 1.5
2017-08-24 | 12:45 | -0.11666 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 12:50 | -0.1151 | 0 |  | 1.5
2017-08-24 | 12:55 | -0.12056 | 0 |  | 1.5
2017-08-24 | 13:00 | 1.1766 | 0 | 0 | 1.5 | 0
2017-08-24 | 13:00 |  |  |  | 1.5 |  | 99.9624
2017-08-24 | 13:05 | 1.7772 | 0 |  | 1.5
2017-08-24 | 13:10 | 1.7031 | 0 |  | 1.5
2017-08-24 | 13:15 | 1.6493 | 0 | 0 | 1.5 | 0 | 100
2017-08-24 | 13:20 | 1.6851 | 0 |  | 1.5
2017-08-24 | 13:25 | 1.7577 | 0 |  | 1.5
2017-08-24 | 13:30 | 1.8544 | 0 | 0 | 1.5 | 0 | 99.0711
2017-08-24 | 13:35 | 1.8614 | 0 |  | 1.5
2017-08-24 | 13:40 | 1.8552 | 0 |  | 1.5
2017-08-24 | 13:45 | 1.8302 | 0 | 0 | 1.5 | 0 | 96.113
2017-08-24 | 13:50 | 1.8053 | 0 |  | 1.5
2017-08-24 | 13:55 | 1.8131 | 0 |  | 1.5
2017-08-24 | 14:00 | 1.8099 | 0 | 0 | 1.5 | 0 | 94.5121
2017-08-24 | 14:05 | 1.8053 | 0 |  | 1.5
2017-08-24 | 14:10 | 1.856 | 0 |  | 1.5
2017-08-24 | 14:15 | 1.8224 | 0 | 0 | 1.5 | 0 | 92.6342
2017-08-24 | 14:20 | 1.8614 | 0 |  | 1.5
2017-08-24 | 14:25 | 1.8092 | 0 |  | 1.5
2017-08-24 | 14:30 | 1.8123 | 0 | 0 | 1.5 | 0 | 90.3307
2017-08-24 | 14:35 | 1.8606 | 0 |  | 1.5
2017-08-24 | 14:40 | 1.8021 | 0 |  | 1.5
2017-08-24 | 14:45 | 1.8146 | 0 | 0 | 1.5 | 0 | 88.3168
2017-08-24 | 14:50 | 1.8279 | 0 |  | 1.5
2017-08-24 | 14:55 | 1.7811 | 0 |  | 1.5
2017-08-24 | 15:00 | 1.7842 | 0 | 0 | 1.5 | 0 | 86.7943
2017-08-24 | 15:05 | 1.7803 | 0 |  | 1.5
2017-08-24 | 15:10 | 1.8349 | 0 |  | 1.5
2017-08-24 | 15:15 | 1.7951 | 0 | 0 | 1.5 | 0 | 85.6958
2017-08-24 | 15:20 | 1.7803 | 0 |  | 1.5
2017-08-24 | 15:25 | 1.7975 | 0 |  | 1.5
2017-08-24 | 15:30 | 1.7577 | 0 | 0 | 1.5 | 0 | 84.6094
2017-08-24 | 15:35 | 1.7842 | 0 |  | 1.5
2017-08-24 | 15:40 | 1.7561 | 0 |  | 1.5
2017-08-24 | 15:45 | 1.8037 | 0 | 0 | 1.5 | 0 | 83.7429
2017-08-24 | 15:50 | 1.8333 | 0 |  | 1.5
2017-08-24 | 15:55 | 1.7296 | 0 |  | 1.5
2017-08-24 | 16:00 | 1.7475 | 0 | 0 | 1.5 | 0 | 82.8662
2017-08-24 | 16:05 | 1.7577 | 0 |  | 1.5
2017-08-24 | 16:10 | 1.7811 | 0 |  | 1.5
2017-08-24 | 16:15 | 1.7592 | 0 | 0 | 1.5 | 0 | 82.4839
2017-08-24 | 16:20 | 1.8076 | 0 |  | 1.5
2017-08-24 | 16:25 | 1.7928 | 0 |  | 1.5
2017-08-24 | 16:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 81.7802
2017-08-24 | 16:35 | 1.7819 | 0 |  | 1.5
2017-08-24 | 16:40 | 1.7343 | 0 |  | 1.5
2017-08-24 | 16:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 81.2782
2017-08-24 | 16:50 | 1.7881 | 0 |  | 1.5
2017-08-24 | 16:55 | 1.7397 | 0 |  | 1.5
2017-08-24 | 17:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.1576
2017-08-24 | 17:05 | 1.746 | 0 |  | 1.5
2017-08-24 | 17:10 | 1.7054 | 0 |  | 1.5
2017-08-24 | 17:15 | 1.721 | 0 | 0 | 1.5 | 0 | 81.6105
2017-08-24 | 17:20 | 1.7936 | 0 |  | 1.5
2017-08-24 | 17:25 | 1.7429 | 0 |  | 1.5
2017-08-24 | 17:30 | 1.7436 | 0 | 0 | 1.5 | 0 | 81.3165
2017-08-24 | 17:35 | 1.7405 | 0 |  | 1.5
2017-08-24 | 17:40 | 1.7522 | 0 |  | 1.5
2017-08-24 | 17:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 81.2227
2017-08-24 | 17:50 | 1.7312 | 0 |  | 1.5
2017-08-24 | 17:55 | 1.7616 | 0 |  | 1.5
2017-08-24 | 18:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 81.0148
2017-08-24 | 18:05 | 1.7663 | 0 |  | 1.5
2017-08-24 | 18:10 | 1.7569 | 0 |  | 1.5
2017-08-24 | 18:15 | 1.7826 | 0 | 0 | 1.5 | 0 | 80.4733
2017-08-24 | 18:20 | 1.7483 | 0 |  | 1.5
2017-08-24 | 18:25 | 1.76 | 0 |  | 1.5
2017-08-24 | 18:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 80.271
2017-08-24 | 18:35 | 1.7296 | 0 |  | 1.5
2017-08-24 | 18:40 | 1.7717 | 0 |  | 1.5
2017-08-24 | 18:45 | 1.746 | 0 | 0 | 1.5 | 0 | 80.1087
2017-08-24 | 18:50 | 1.7468 | 0 |  | 1.5
2017-08-24 | 18:55 | 1.7507 | 0 |  | 1.5
2017-08-24 | 19:00 | 1.7569 | 0 | 0 | 1.5 | 0 | 79.948
2017-08-24 | 19:05 | 1.7585 | 0 |  | 1.5
2017-08-24 | 19:10 | 1.7171 | 0 |  | 1.5
2017-08-24 | 19:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 79.6293
2017-08-24 | 19:20 | 1.7561 | 0 |  | 1.5
2017-08-24 | 19:25 | 1.7647 | 0 |  | 1.5
2017-08-24 | 19:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 79.4674
2017-08-24 | 19:35 | 1.7686 | 0 |  | 1.5
2017-08-24 | 19:40 | 1.7865 | 0 |  | 1.5
2017-08-24 | 19:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.2253
2017-08-24 | 19:50 | 1.7764 | 0 |  | 1.5
2017-08-24 | 19:55 | 1.7655 | 0 |  | 1.5
2017-08-24 | 20:00 | 1.778 | 0 | 0 | 1.5 | 0 | 78.9956
2017-08-24 | 20:05 | 1.746 | 0 |  | 1.5
2017-08-24 | 20:10 | 1.7569 | 0 |  | 1.5
2017-08-24 | 20:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 78.7619
2017-08-24 | 20:20 | 1.7218 | 0 |  | 1.5
2017-08-24 | 20:25 | 1.7795 | 0 |  | 1.5
2017-08-24 | 20:30 | 1.7608 | 0 | 0 | 1.5 | 0 | 78.4281
2017-08-24 | 20:35 | 1.753 | 0 |  | 1.5
2017-08-24 | 20:40 | 1.7639 | 0 |  | 1.5
2017-08-24 | 20:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 78.1187
2017-08-24 | 20:50 | 1.7538 | 0 |  | 1.5
2017-08-24 | 20:55 | 1.7405 | 0 |  | 1.5
2017-08-24 | 21:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 21:05 | -0.1034 | 0 |  | 1.5
2017-08-24 | 21:10 | -0.10652 | 0 |  | 1.5
2017-08-24 | 21:15 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 21:20 | -0.11198 | 0 |  | 1.5
2017-08-24 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-24 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 21:35 | -0.10652 | 0 |  | 1.5
2017-08-24 | 21:40 | -0.10652 | 0 |  | 1.5
2017-08-24 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 21:50 | -0.10652 | 0 |  | 1.5
2017-08-24 | 21:55 | -0.1073 | 0 |  | 1.5
2017-08-24 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 22:05 | -0.10808 | 0 |  | 1.5
2017-08-24 | 22:10 | -0.10808 | 0 |  | 1.5
2017-08-24 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 22:20 | -0.1073 | 0 |  | 1.5
2017-08-24 | 22:25 | -0.1073 | 0 |  | 1.5
2017-08-24 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 22:35 | -0.1073 | 0 |  | 1.5
2017-08-24 | 22:40 | -0.10808 | 0 |  | 1.5
2017-08-24 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 22:50 | -0.10652 | 0 |  | 1.5
2017-08-24 | 22:55 | -0.10652 | 0 |  | 1.5
2017-08-24 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 23:05 | -0.10652 | 0 |  | 1.5
2017-08-24 | 23:10 | -0.10574 | 0 |  | 1.5
2017-08-24 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 23:20 | -0.10574 | 0 |  | 1.5
2017-08-24 | 23:25 | -0.10574 | 0 |  | 1.5
2017-08-24 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 23:35 | -0.10574 | 0 |  | 1.5
2017-08-24 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-24 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-24 | 23:50 | -0.10574 | 0 |  | 1.5
2017-08-24 | 23:55 | -0.10574 | 0 |  | 1.5
2017-08-25 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 0:05 | -0.10496 | 0 |  | 1.5
2017-08-25 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-25 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 0:20 | -0.10418 | 0 |  | 1.5
2017-08-25 | 0:25 | -0.10808 | 0 |  | 1.5
2017-08-25 | 0:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 0:35 | -0.1034 | 0 |  | 1.5
2017-08-25 | 0:40 | -0.10418 | 0 |  | 1.5
2017-08-25 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-25 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-25 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-25 | 1:10 | -0.10496 | 0 |  | 1.5
2017-08-25 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 1:20 | -0.10808 | 0 |  | 1.5
2017-08-25 | 1:25 | -0.10808 | 0 |  | 1.5
2017-08-25 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-25 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-25 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 1:50 | -0.10886 | 0 |  | 1.5
2017-08-25 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-25 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-25 | 2:10 | -0.10886 | 0 |  | 1.5
2017-08-25 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-25 | 2:25 | -0.10886 | 0 |  | 1.5
2017-08-25 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 2:35 | -0.10886 | 0 |  | 1.5
2017-08-25 | 2:40 | -0.10886 | 0 |  | 1.5
2017-08-25 | 2:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 2:50 | -0.10964 | 0 |  | 1.5
2017-08-25 | 2:55 | -0.10886 | 0 |  | 1.5
2017-08-25 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 3:05 | -0.10964 | 0 |  | 1.5
2017-08-25 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-25 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-25 | 3:25 | -0.10886 | 0 |  | 1.5
2017-08-25 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 3:35 | -0.10886 | 0 |  | 1.5
2017-08-25 | 3:40 | -0.10964 | 0 |  | 1.5
2017-08-25 | 3:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 3:50 | -0.11042 | 0 |  | 1.5
2017-08-25 | 3:55 | -0.10964 | 0 |  | 1.5
2017-08-25 | 4:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 4:05 | -0.11042 | 0 |  | 1.5
2017-08-25 | 4:10 | -0.11042 | 0 |  | 1.5
2017-08-25 | 4:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 4:20 | -0.11042 | 0 |  | 1.5
2017-08-25 | 4:25 | -0.11042 | 0 |  | 1.5
2017-08-25 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 4:35 | -0.10964 | 0 |  | 1.5
2017-08-25 | 4:40 | -0.10964 | 0 |  | 1.5
2017-08-25 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 4:50 | -0.11042 | 0 |  | 1.5
2017-08-25 | 4:55 | -0.11042 | 0 |  | 1.5
2017-08-25 | 5:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 5:05 | 2.3154 | 0 |  | 1.5
2017-08-25 | 5:10 | 2.3208 | 0 |  | 1.5
2017-08-25 | 5:15 | 2.0642 | 0 | 0 | 1.5 | 0 | 88.3189
2017-08-25 | 5:20 | 1.9457 | 0 |  | 1.5
2017-08-25 | 5:25 | 1.8536 | 0 |  | 1.5
2017-08-25 | 5:30 | 1.8014 | 0 | 0 | 1.5 | 0 | 84.5569
2017-08-25 | 5:35 | 1.7577 | 0 |  | 1.5
2017-08-25 | 5:40 | 1.7522 | 0 |  | 1.5
2017-08-25 | 5:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 84.0147
2017-08-25 | 5:50 | 1.7507 | 0 |  | 1.5
2017-08-25 | 5:55 | 1.7491 | 0 |  | 1.5
2017-08-25 | 6:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 84.1048
2017-08-25 | 6:05 | 1.7491 | 0 |  | 1.5
2017-08-25 | 6:10 | 1.7304 | 0 |  | 1.5
2017-08-25 | 6:15 | 1.7202 | 0 | 0 | 1.5 | 0 | 84.1321
2017-08-25 | 6:20 | 1.7335 | 0 |  | 1.5
2017-08-25 | 6:25 | 1.7514 | 0 |  | 1.5
2017-08-25 | 6:30 | 1.7592 | 0 | 0 | 1.5 | 0 | 84.2379
2017-08-25 | 6:35 | 1.7522 | 0 |  | 1.5
2017-08-25 | 6:40 | 1.7647 | 0 |  | 1.5
2017-08-25 | 6:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 84.3149
2017-08-25 | 6:50 | 1.7569 | 0 |  | 1.5
2017-08-25 | 6:55 | 1.7452 | 0 |  | 1.5
2017-08-25 | 7:00 | 1.7553 | 0 | 0 | 1.5 | 0 | 84.4557
2017-08-25 | 7:05 | 1.7327 | 0 |  | 1.5
2017-08-25 | 7:10 | 1.7296 | 0 |  | 1.5
2017-08-25 | 7:15 | 1.7265 | 0 | 0 | 1.5 | 0 | 84.6289
2017-08-25 | 7:20 | 1.7452 | 0 |  | 1.5
2017-08-25 | 7:25 | 1.7452 | 0 |  | 1.5
2017-08-25 | 7:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 84.7634
2017-08-25 | 7:35 | 1.7507 | 0.043362 |  | 1.5
2017-08-25 | 7:40 | 1.7397 | 0 |  | 1.5
2017-08-25 | 7:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 85.061
2017-08-25 | 7:50 | 1.7312 | 0 |  | 1.5
2017-08-25 | 7:55 | 1.7491 | 0 |  | 1.5
2017-08-25 | 8:00 | 1.7413 | 0 | 0 | 1.5 | 0 | 85.3693
2017-08-25 | 8:05 | 1.7265 | 0 |  | 1.5
2017-08-25 | 8:10 | 1.7405 | 0 |  | 1.5
2017-08-25 | 8:15 | 1.7592 | 0 | 0 | 1.5 | 0 | 85.7894
2017-08-25 | 8:20 | 1.7967 | 0 |  | 1.5
2017-08-25 | 8:25 | 1.8622 | 0 |  | 1.5
2017-08-25 | 8:30 | 1.8326 | 0 | 0 | 1.5 | 0 | 83.4522
2017-08-25 | 8:35 | 1.8427 | 0 |  | 1.5
2017-08-25 | 8:40 | 1.8014 | 0 |  | 1.5
2017-08-25 | 8:45 | 1.8146 | 0 | 0 | 1.5 | 0 | 81.7552
2017-08-25 | 8:50 | 1.7491 | 0 |  | 1.5
2017-08-25 | 8:55 | 1.7936 | 0 |  | 1.5
2017-08-25 | 9:00 | 1.7405 | 0 | 0 | 1.5 | 0 | 81.27
2017-08-25 | 9:05 | 1.7764 | 0 |  | 1.5
2017-08-25 | 9:10 | 1.7366 | 0 |  | 1.5
2017-08-25 | 9:15 | 1.7382 | 0 | 0 | 1.5 | 0 | 81.1166
2017-08-25 | 9:20 | 1.7514 | 0 |  | 1.5
2017-08-25 | 9:25 | 1.7397 | 0 |  | 1.5
2017-08-25 | 9:30 | 1.7507 | 0 | 0 | 1.5 | 0 | 80.98
2017-08-25 | 9:35 | 1.7429 | 0 |  | 1.5
2017-08-25 | 9:40 | 1.7405 | 0 |  | 1.5
2017-08-25 | 9:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 80.9599
2017-08-25 | 9:50 | 1.753 | 0 |  | 1.5
2017-08-25 | 9:55 | 1.7156 | 0 |  | 1.5
2017-08-25 | 10:00 | 1.7265 | 0 | 0 | 1.5 | 0 | 81.1993
2017-08-25 | 10:05 | 1.7468 | 0 |  | 1.5
2017-08-25 | 10:10 | 1.7507 | 0 |  | 1.5
2017-08-25 | 10:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 81.2389
2017-08-25 | 10:20 | 1.7312 | 0 |  | 1.5
2017-08-25 | 10:25 | 1.7811 | 0 |  | 1.5
2017-08-25 | 10:30 | 1.7296 | 0 | 0 | 1.5 | 0 | 81.3538
2017-08-25 | 10:35 | 1.7858 | 0 |  | 1.5
2017-08-25 | 10:40 | 1.7811 | 0 |  | 1.5
2017-08-25 | 10:45 | 1.7304 | 0 | 0 | 1.5 | 0 | 81.4297
2017-08-25 | 10:50 | 1.7226 | 0 |  | 1.5
2017-08-25 | 10:55 | 1.7366 | 0 |  | 1.5
2017-08-25 | 11:00 | 1.746 | 0 | 0 | 1.5 | 0 | 81.1599
2017-08-25 | 11:05 | 1.7764 | 0 |  | 1.5
2017-08-25 | 11:10 | 1.7296 | 0 |  | 1.5
2017-08-25 | 11:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 81.1988
2017-08-25 | 11:20 | 1.7397 | 0 |  | 1.5
2017-08-25 | 11:25 | 1.7195 | 0 |  | 1.5
2017-08-25 | 11:30 | 1.7335 | 0 | 0 | 1.5 | 0 | 81.6803
2017-08-25 | 11:35 | 1.7312 | 0 |  | 1.5
2017-08-25 | 11:40 | 1.6836 | 0 |  | 1.5
2017-08-25 | 11:45 | 1.7117 | 0 | 0 | 1.5 | 0 | 82.9797
2017-08-25 | 11:50 | 1.7117 | 0 |  | 1.5
2017-08-25 | 11:55 | 1.7202 | 0 |  | 1.5
2017-08-25 | 12:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 83.8413
2017-08-25 | 12:05 | 1.6867 | 0 |  | 1.5
2017-08-25 | 12:10 | 1.7226 | 0 |  | 1.5
2017-08-25 | 12:15 | 1.6867 | 0 | 0 | 1.5 | 0 | 85.0138
2017-08-25 | 12:20 | 1.714 | 0 |  | 1.5
2017-08-25 | 12:25 | 1.7 | 0 |  | 1.5
2017-08-25 | 12:30 | 1.7156 | 0 | 0 | 1.5 | 0 | 86.2601
2017-08-25 | 12:35 | 1.7124 | 0 |  | 1.5
2017-08-25 | 12:40 | 1.721 | 0 |  | 1.5
2017-08-25 | 12:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 87.1106
2017-08-25 | 12:50 | 1.7468 | 0 |  | 1.5
2017-08-25 | 12:55 | 1.7343 | 0 |  | 1.5
2017-08-25 | 13:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 87.4841
2017-08-25 | 13:05 | 1.7709 | 0 |  | 1.5
2017-08-25 | 13:10 | 1.7631 | 0 |  | 1.5
2017-08-25 | 13:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 87.1516
2017-08-25 | 13:20 | 1.7507 | 0 |  | 1.5
2017-08-25 | 13:25 | 1.7452 | 0 |  | 1.5
2017-08-25 | 13:30 | 1.7163 | 0 | 0 | 1.5 | 0 | 87.4493
2017-08-25 | 13:35 | 1.7312 | 0 |  | 1.5
2017-08-25 | 13:40 | 1.7156 | 0 |  | 1.5
2017-08-25 | 13:45 | 1.7358 | 0 | 0 | 1.5 | 0 | 87.8895
2017-08-25 | 13:50 | 1.7304 | 0 |  | 1.5
2017-08-25 | 13:55 | 1.7717 | 0 |  | 1.5
2017-08-25 | 14:00 | 1.7975 | 0 | 0 | 1.5 | 0 | 87.7676
2017-08-25 | 14:05 | 1.7764 | 0 |  | 1.5
2017-08-25 | 14:10 | 1.7764 | 0 |  | 1.5
2017-08-25 | 14:15 | 1.7982 | 0 | 0 | 1.5 | 0 | 86.7557
2017-08-25 | 14:20 | 1.7772 | 0 |  | 1.5
2017-08-25 | 14:25 | 1.7569 | 0 |  | 1.5
2017-08-25 | 14:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 86.0657
2017-08-25 | 14:35 | 1.6922 | 0 |  | 1.5
2017-08-25 | 14:40 | 1.7811 | 0 |  | 1.5
2017-08-25 | 14:45 | 1.7561 | 0 | 0 | 1.5 | 0 | 86.2275
2017-08-25 | 14:50 | 1.7413 | 0 |  | 1.5
2017-08-25 | 14:55 | 1.799 | 0 |  | 1.5
2017-08-25 | 15:00 | 1.7733 | 0 | 0 | 1.5 | 0 | 85.5833
2017-08-25 | 15:05 | 1.7561 | 0 |  | 1.5
2017-08-25 | 15:10 | 1.7499 | 0 |  | 1.5
2017-08-25 | 15:15 | 1.7865 | 0 | 0 | 1.5 | 0 | 85.0508
2017-08-25 | 15:20 | 1.7546 | 0 |  | 1.5
2017-08-25 | 15:25 | 1.7819 | 0 |  | 1.5
2017-08-25 | 15:30 | 1.7436 | 0 | 0 | 1.5 | 0 | 84.7178
2017-08-25 | 15:35 | 1.7452 | 0 |  | 1.5
2017-08-25 | 15:40 | 1.7569 | 0 |  | 1.5
2017-08-25 | 15:45 | 1.7491 | 0 | 0 | 1.5 | 0 | 84.7377
2017-08-25 | 15:50 | 1.7764 | 0 |  | 1.5
2017-08-25 | 15:55 | 1.7631 | 0 |  | 1.5
2017-08-25 | 16:00 | 1.7865 | 0 | 0 | 1.5 | 0 | 84.2201
2017-08-25 | 16:05 | 1.7702 | 0 |  | 1.5
2017-08-25 | 16:10 | 1.7655 | 0 |  | 1.5
2017-08-25 | 16:15 | 1.7756 | 0 | 0 | 1.5 | 0 | 83.4447
2017-08-25 | 16:20 | 1.7546 | 0 |  | 1.5
2017-08-25 | 16:25 | 1.7733 | 0 |  | 1.5
2017-08-25 | 16:30 | 1.7725 | 0 | 0 | 1.5 | 0 | 82.8335
2017-08-25 | 16:35 | 1.7592 | 0 |  | 1.5
2017-08-25 | 16:40 | 1.7561 | 0 |  | 1.5
2017-08-25 | 16:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 82.4944
2017-08-25 | 16:50 | 1.7834 | 0 |  | 1.5
2017-08-25 | 16:55 | 1.7795 | 0 |  | 1.5
2017-08-25 | 17:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 81.8217
2017-08-25 | 17:05 | 1.7803 | 0 |  | 1.5
2017-08-25 | 17:10 | 1.7873 | 0 |  | 1.5
2017-08-25 | 17:15 | 1.7686 | 0 | 0 | 1.5 | 0 | 81.2664
2017-08-25 | 17:20 | 1.7741 | 0 |  | 1.5
2017-08-25 | 17:25 | 1.7741 | 0 |  | 1.5
2017-08-25 | 17:30 | 1.778 | 0 | 0 | 1.5 | 0 | 80.304
2017-08-25 | 17:35 | 1.7717 | 0 |  | 1.5
2017-08-25 | 17:40 | 1.7772 | 0 |  | 1.5
2017-08-25 | 17:45 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.5011
2017-08-25 | 17:50 | 1.7647 | 0 |  | 1.5
2017-08-25 | 17:55 | 1.7663 | 0 |  | 1.5
2017-08-25 | 18:00 | 1.767 | 0 | 0 | 1.5 | 0 | 79.1688
2017-08-25 | 18:05 | 1.7483 | 0 |  | 1.5
2017-08-25 | 18:10 | 1.7132 | 0 |  | 1.5
2017-08-25 | 18:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 79.4123
2017-08-25 | 18:20 | 1.7702 | 0 |  | 1.5
2017-08-25 | 18:25 | 1.7787 | 0 |  | 1.5
2017-08-25 | 18:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 79.2903
2017-08-25 | 18:35 | 1.7429 | 0 |  | 1.5
2017-08-25 | 18:40 | 1.7569 | 0 |  | 1.5
2017-08-25 | 18:45 | 1.7717 | 0 | 0 | 1.5 | 0 | 79.147
2017-08-25 | 18:50 | 1.778 | 0 |  | 1.5
2017-08-25 | 18:55 | 1.7491 | 0 |  | 1.5
2017-08-25 | 19:00 | 1.7319 | 0 | 0 | 1.5 | 0 | 79.1409
2017-08-25 | 19:05 | 1.7655 | 0 |  | 1.5
2017-08-25 | 19:10 | 1.7304 | 0 |  | 1.5
2017-08-25 | 19:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 79.0907
2017-08-25 | 19:20 | 1.7561 | 0 |  | 1.5
2017-08-25 | 19:25 | 1.7405 | 0 |  | 1.5
2017-08-25 | 19:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 78.7999
2017-08-25 | 19:35 | 1.7249 | 0 |  | 1.5
2017-08-25 | 19:40 | 1.7577 | 0 |  | 1.5
2017-08-25 | 19:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 78.8706
2017-08-25 | 19:50 | 1.746 | 0 |  | 1.5
2017-08-25 | 19:55 | 1.7312 | 0 |  | 1.5
2017-08-25 | 20:00 | 1.7741 | 0 | 0 | 1.5 | 0 | 78.5852
2017-08-25 | 20:05 | 1.7624 | 0 |  | 1.5
2017-08-25 | 20:10 | 1.7475 | 0 |  | 1.5
2017-08-25 | 20:15 | 1.7249 | 0 | 0 | 1.5 | 0 | 78.3038
2017-08-25 | 20:20 | 1.7561 | 0 |  | 1.5
2017-08-25 | 20:25 | 1.7452 | 0 |  | 1.5
2017-08-25 | 20:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 78.2384
2017-08-25 | 20:35 | 1.7507 | 0 |  | 1.5
2017-08-25 | 20:40 | 1.7468 | 0 |  | 1.5
2017-08-25 | 20:45 | 1.7834 | 0 | 0 | 1.5 | 0 | 78.075
2017-08-25 | 20:50 | 1.7507 | 0 |  | 1.5
2017-08-25 | 20:55 | 1.785 | 0 |  | 1.5
2017-08-25 | 21:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 77.8619
2017-08-25 | 21:05 | -0.10262 | 0 |  | 1.5
2017-08-25 | 21:10 | -0.1034 | 0 |  | 1.5
2017-08-25 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-25 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-25 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-25 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-25 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 21:50 | -0.10418 | 0 |  | 1.5
2017-08-25 | 21:55 | -0.10574 | 0 |  | 1.5
2017-08-25 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-25 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-25 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-25 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-25 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-25 | 22:40 | -0.10496 | 0 |  | 1.5
2017-08-25 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 22:50 | -0.10418 | 0 |  | 1.5
2017-08-25 | 22:55 | -0.10262 | 0 |  | 1.5
2017-08-25 | 23:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 23:05 | -0.10262 | 0 |  | 1.5
2017-08-25 | 23:10 | -0.10262 | 0 |  | 1.5
2017-08-25 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 23:20 | -0.1034 | 0 |  | 1.5
2017-08-25 | 23:25 | -0.1034 | 0 |  | 1.5
2017-08-25 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 23:35 | -0.10262 | 0 |  | 1.5
2017-08-25 | 23:40 | -0.1034 | 0 |  | 1.5
2017-08-25 | 23:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-25 | 23:50 | -0.1034 | 0 |  | 1.5
2017-08-25 | 23:55 | -0.1034 | 0 |  | 1.5
2017-08-26 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-26 | 0:05 | -0.1034 | 0 |  | 1.5
2017-08-26 | 0:10 | -0.10574 | 0 |  | 1.5
2017-08-26 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-26 | 0:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 0:20 | -0.1034 | 0 |  | 1.5
2017-08-26 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-26 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-26 | 0:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 0:35 | -0.10496 | 0 |  | 1.5
2017-08-26 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-26 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-26 | 0:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 0:50 | -0.10496 | 0 |  | 1.5
2017-08-26 | 0:55 | -0.10496 | 0 |  | 1.5
2017-08-26 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-26 | 1:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-26 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-26 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-26 | 1:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 1:20 | -0.1073 | 0 |  | 1.5
2017-08-26 | 1:25 | -0.1073 | 0 |  | 1.5
2017-08-26 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 1:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 1:35 | -0.1073 | 0 |  | 1.5
2017-08-26 | 1:40 | -0.1073 | 0 |  | 1.5
2017-08-26 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-26 | 1:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-26 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-26 | 2:00 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-26 | 2:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 2:05 | -0.1073 | 0 |  | 1.5
2017-08-26 | 2:10 | -0.1073 | 0 |  | 1.5
2017-08-26 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 2:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-26 | 2:25 | -0.10808 | 0 |  | 1.5
2017-08-26 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-08-26 | 2:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 2:35 | -0.10808 | 0 |  | 1.5
2017-08-26 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-26 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 2:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 2:50 | -0.10808 | 0 |  | 1.5
2017-08-26 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 3:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 3:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 3:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-08-26 | 3:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-26 | 3:55 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-08-26 | 4:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 4:05 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-08-26 | 4:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 4:20 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:25 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-08-26 | 4:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 4:35 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-08-26 | 4:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 4:50 | -0.10886 | 0 |  | 1.5
2017-08-26 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-26 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-08-26 | 5:00 |  |  |  | 1.5 |  | 25
2017-08-26 | 5:05 | 2.1422 | 0 |  | 1.5
2017-08-26 | 5:10 | 2.1789 | 0 |  | 1.5
2017-08-26 | 5:15 | 1.9823 | 0 | 0 | 1.5 | 0
2017-08-26 | 5:15 |  |  |  | 1.5 |  | 90.8778
2017-08-26 | 5:20 | 1.8903 | 0 |  | 1.5
2017-08-26 | 5:25 | 1.8294 | 0 |  | 1.5
2017-08-26 | 5:30 | 1.8045 | 0 | 0 | 1.5 | 0
2017-08-26 | 5:30 |  |  |  | 1.5 |  | 87.7615
2017-08-26 | 5:35 | 1.7819 | 0 |  | 1.5
2017-08-26 | 5:40 | 1.7624 | 0 |  | 1.5
2017-08-26 | 5:45 | 1.7741 | 0 | 0 | 1.5 | 0
2017-08-26 | 5:45 |  |  |  | 1.5 |  | 87.2555
2017-08-26 | 5:50 | 1.7647 | 0 |  | 1.5
2017-08-26 | 5:55 | 1.7585 | 0 |  | 1.5
2017-08-26 | 6:00 | 1.7655 | 0 | 0 | 1.5 | 0
2017-08-26 | 6:00 |  |  |  | 1.5 |  | 87.2784
2017-08-26 | 6:05 | 1.7522 | 0 |  | 1.5
2017-08-26 | 6:10 | 1.7592 | 0 |  | 1.5
2017-08-26 | 6:15 | 1.7304 | 0 | 0 | 1.5 | 0
2017-08-26 | 6:15 |  |  |  | 1.5 |  | 87.5679
2017-08-26 | 6:20 | 1.7319 | 0 |  | 1.5
2017-08-26 | 6:25 | 1.7234 | 0 |  | 1.5
2017-08-26 | 6:30 | 1.7725 | 0 | 0 | 1.5 | 0
2017-08-26 | 6:30 |  |  |  | 1.5 |  | 87.9297
2017-08-26 | 6:35 | 1.7483 | 0 |  | 1.5
2017-08-26 | 6:40 | 1.7507 | 0 |  | 1.5
2017-08-26 | 6:45 | 1.7405 | 0 | 0 | 1.5 | 0
2017-08-26 | 6:45 |  |  |  | 1.5 |  | 88.1986
2017-08-26 | 6:50 | 1.753 | 0 |  | 1.5
2017-08-26 | 6:55 | 1.7538 | 0 |  | 1.5
2017-08-26 | 7:00 | 1.7499 | 0 | 0 | 1.5 | 0
2017-08-26 | 7:00 |  |  |  | 1.5 |  | 88.1839
2017-08-26 | 7:05 | 1.7585 | 0 |  | 1.5
2017-08-26 | 7:10 | 1.7343 | 0 |  | 1.5
2017-08-26 | 7:15 | 1.7288 | 0 | 0 | 1.5 | 0
2017-08-26 | 7:15 | [5 empty] | 88.3815
2017-08-26 | 7:20 | 1.7397 | 0 |  | 1.5
2017-08-26 | 7:25 | 1.7234 | 0 |  | 1.5
2017-08-26 | 7:30 | 1.7296 | 0 | 0 | 1.5 | 0
2017-08-26 | 7:30 |  |  |  | 1.5 |  | 88.7145
2017-08-26 | 7:35 | 1.8053 | 0 |  | 1.5
2017-08-26 | 7:40 | 1.8825 | 0 |  | 1.5
2017-08-26 | 7:45 | 1.9566 | 0 | 0 | 1.5 | 0
2017-08-26 | 7:45 |  |  |  | 1.5 |  | 85.9964
2017-08-26 | 7:50 | 1.9519 | 0 |  | 1.5
2017-08-26 | 7:55 | 1.8723 | 0 |  | 1.5
2017-08-26 | 8:00 | 1.845 | 0 | 0 | 1.5 | 0
2017-08-26 | 8:00 |  |  |  | 1.5 |  | 81.8149
2017-08-26 | 8:05 | 1.8255 | 0 |  | 1.5
2017-08-26 | 8:10 | 1.8029 | 0 |  | 1.5
2017-08-26 | 8:15 | 1.7982 | 0 | 0 | 1.5 | 0
2017-08-26 | 8:15 |  |  |  | 1.5 |  | 80.1765
2017-08-26 | 8:20 | 1.7889 | 0 |  | 1.5
2017-08-26 | 8:25 | 1.7709 | 0 |  | 1.5
2017-08-26 | 8:30 | 1.7694 | 0 | 0 | 1.5 | 0
2017-08-26 | 8:30 |  |  |  | 1.5 |  | 79.3267
2017-08-26 | 8:35 | 1.7826 | 0 |  | 1.5
2017-08-26 | 8:40 | 1.7429 | 0 |  | 1.5
2017-08-26 | 8:45 | 1.7429 | 0 | 0 | 1.5 | 0
2017-08-26 | 8:45 |  |  |  | 1.5 |  | 79.0524
2017-08-26 | 8:50 | 1.7647 | 0 |  | 1.5
2017-08-26 | 8:55 | 1.785 | 0 |  | 1.5
2017-08-26 | 9:00 | 1.7717 | 0 | 0 | 1.5 | 0
2017-08-26 | 9:00 |  |  |  | 1.5 |  | 78.7246
2017-08-26 | 9:05 | 1.7663 | 0 |  | 1.5
2017-08-26 | 9:10 | 1.7639 | 0 |  | 1.5
2017-08-26 | 9:15 | 1.7733 | 0 | 0 | 1.5 | 0
2017-08-26 | 9:15 |  |  |  | 1.5 |  | 78.4551
2017-08-26 | 9:20 | 1.7663 | 0 |  | 1.5
2017-08-26 | 9:25 | 1.7358 | 0 |  | 1.5
2017-08-26 | 9:30 | 1.7663 | 0 | 0 | 1.5 | 0
2017-08-26 | 9:30 |  |  |  | 1.5 |  | 78.2314
2017-08-26 | 9:35 | 1.7296 | 0 |  | 1.5
2017-08-26 | 9:40 | 1.746 | 0 |  | 1.5
2017-08-26 | 9:45 | 1.7335 | 0 | 0 | 1.5 | 0
2017-08-26 | 9:45 |  |  |  | 1.5 |  | 78.0315
2017-08-26 | 9:50 | 1.7405 | 0 |  | 1.5
2017-08-26 | 9:55 | 1.7319 | 0 |  | 1.5
2017-08-26 | 10:00 | 1.7483 | 0 | 0 | 1.5 | 0
2017-08-26 | 10:00 |  |  |  | 1.5 |  | 78.2079
2017-08-26 | 10:05 | 1.7733 | 0 |  | 1.5
2017-08-26 | 10:10 | 1.767 | 0 |  | 1.5
2017-08-26 | 10:15 | 1.7226 | 0 | 0 | 1.5 | 0
2017-08-26 | 10:15 |  |  |  | 1.5 |  | 78.093
2017-08-26 | 10:20 | 1.7538 | 0 |  | 1.5
2017-08-26 | 10:25 | 1.7273 | 0 |  | 1.5
2017-08-26 | 10:30 | 1.7553 | 0 | 0 | 1.5 | 0
2017-08-26 | 10:30 |  |  |  | 1.5 |  | 78.1043
2017-08-26 | 10:35 | 1.7304 | 0 |  | 1.5
2017-08-26 | 10:40 | 1.7436 | 0 |  | 1.5
2017-08-26 | 10:45 | 1.7327 | 0 | 0 | 1.5 | 0
2017-08-26 | 10:45 | [5 empty] | 78.0577
2017-08-26 | 10:50 | 1.7319 | 0 |  | 1.5
2017-08-26 | 10:55 | 1.7421 | 0 |  | 1.5
2017-08-26 | 11:00 | 1.7608 | 0 | 0 | 1.5 | 0
2017-08-26 | 11:00 |  |  |  | 1.5 |  | 78.2803
2017-08-26 | 11:05 | 1.7889 | 0 |  | 1.5
2017-08-26 | 11:10 | 1.7538 | 0 |  | 1.5
2017-08-26 | 11:15 | 1.7405 | 0 | 0 | 1.5 | 0
2017-08-26 | 11:15 |  |  |  | 1.5 |  | 78.329
2017-08-26 | 11:20 | 1.7499 | 0 |  | 1.5
2017-08-26 | 11:25 | 1.7335 | 0 |  | 1.5
2017-08-26 | 11:30 | 1.7273 | 0 | 0 | 1.5 | 0
2017-08-26 | 11:30 |  |  |  | 1.5 |  | 78.4841
2017-08-26 | 11:35 | 1.7241 | 0 |  | 1.5
2017-08-26 | 11:40 | 1.6906 | 0 |  | 1.5
2017-08-26 | 11:45 | 1.7444 | 0 | 0 | 1.5 | 0
2017-08-26 | 11:45 |  |  |  | 1.5 |  | 79.1828
2017-08-26 | 11:50 | 1.714 | 0 |  | 1.5
2017-08-26 | 11:55 | 1.7023 | 0 |  | 1.5
2017-08-26 | 12:00 | 1.7046 | 0 | 0 | 1.5 | 0
2017-08-26 | 12:00 |  |  |  | 1.5 |  | 80.1807
2017-08-26 | 12:05 | 1.6898 | 0 |  | 1.5
2017-08-26 | 12:10 | 1.7031 | 0 |  | 1.5
2017-08-26 | 12:15 | 1.7163 | 0 | 0 | 1.5 | 0
2017-08-26 | 12:15 |  |  |  | 1.5 |  | 81.1942
2017-08-26 | 12:20 | 1.7218 | 0 |  | 1.5
2017-08-26 | 12:25 | 1.6992 | 0 |  | 1.5
2017-08-26 | 12:30 | 1.7093 | 0 | 0 | 1.5 | 0
2017-08-26 | 12:30 |  |  |  | 1.5 |  | 82.2228
2017-08-26 | 12:35 | 1.6945 | 0 |  | 1.5
2017-08-26 | 12:40 | 1.707 | 0 |  | 1.5
2017-08-26 | 12:45 | 1.6883 | 0 | 0 | 1.5 | 0
2017-08-26 | 12:45 |  |  |  | 1.5 |  | 83.3822
2017-08-26 | 12:50 | 1.7358 | 0 |  | 1.5
2017-08-26 | 12:55 | 1.7351 | 0 |  | 1.5
2017-08-26 | 13:00 | 1.7499 | 0 | 0 | 1.5 | 0
2017-08-26 | 13:00 |  |  |  | 1.5 |  | 83.827
2017-08-26 | 13:05 | 1.7452 | 0 |  | 1.5
2017-08-26 | 13:10 | 1.7288 | 0 |  | 1.5
2017-08-26 | 13:15 | 1.7265 | 0 | 0 | 1.5 | 0
2017-08-26 | 13:15 |  |  |  | 1.5 |  | 84.3588
2017-08-26 | 13:20 | 1.7296 | 0 |  | 1.5
2017-08-26 | 13:25 | 1.7382 | 0 |  | 1.5
2017-08-26 | 13:30 | 1.7249 | 0 | 0 | 1.5 | 0
2017-08-26 | 13:30 |  |  |  | 1.5 |  | 84.7617
2017-08-26 | 13:35 | 1.7156 | 0 |  | 1.5
2017-08-26 | 13:40 | 1.7179 | 0 |  | 1.5
2017-08-26 | 13:45 | 1.7366 | 0 | 0 | 1.5 | 0
2017-08-26 | 13:45 |  |  |  | 1.5 |  | 85.237
2017-08-26 | 13:50 | 1.7725 | 0 |  | 1.5
2017-08-26 | 13:55 | 1.7741 | 0 |  | 1.5
2017-08-26 | 14:00 | 1.7998 | 0 | 0 | 1.5 | 0
2017-08-26 | 14:00 |  |  |  | 1.5 |  | 84.8507
2017-08-26 | 14:05 | 1.7616 | 0 |  | 1.5
2017-08-26 | 14:10 | 1.7663 | 0 |  | 1.5
2017-08-26 | 14:15 | 1.7655 | 0 | 0 | 1.5 | 0
2017-08-26 | 14:15 |  |  |  | 1.5 |  | 84.56
2017-08-26 | 14:20 | 1.7366 | 0 |  | 1.5
2017-08-26 | 14:25 | 1.7647 | 0 |  | 1.5
2017-08-26 | 14:30 | 1.76 | 0 | 0 | 1.5 | 0
2017-08-26 | 14:30 | 1.76 | 0 |  | 1.5 |  | 84.1381
2017-08-26 | 14:35 | 1.7764 | 0 |  | 1.5
2017-08-26 | 14:40 | 1.7507 | 0 |  | 1.5
2017-08-26 | 14:45 | 1.7273 | 0 | 0 | 1.5 | 0
2017-08-26 | 14:45 |  |  |  | 1.5 |  | 83.9162
2017-08-26 | 14:50 | 1.7382 | 0 |  | 1.5
2017-08-26 | 14:55 | 1.7413 | 0 |  | 1.5
2017-08-26 | 15:00 | 1.7639 | 0 | 0 | 1.5 | 0
2017-08-26 | 15:00 |  |  |  | 1.5 |  | 83.8192
2017-08-26 | 15:05 | 1.7561 | 0 |  | 1.5
2017-08-26 | 15:10 | 1.7577 | 0 |  | 1.5
2017-08-26 | 15:15 | 1.7553 | 0 | 0 | 1.5 | 0
2017-08-26 | 15:15 |  |  |  | 1.5 |  | 83.7021
2017-08-26 | 15:20 | 1.7382 | 0 |  | 1.5
2017-08-26 | 15:25 | 1.7624 | 0 |  | 1.5
2017-08-26 | 15:30 | 1.7834 | 0 | 0 | 1.5 | 0
2017-08-26 | 15:30 |  |  |  | 1.5 |  | 83.315
2017-08-26 | 15:35 | 1.7444 | 0 |  | 1.5
2017-08-26 | 15:40 | 1.7538 | 0 |  | 1.5
2017-08-26 | 15:45 | 1.7702 | 0 | 0 | 1.5 | 0
2017-08-26 | 15:45 |  |  |  | 1.5 |  | 82.8667
2017-08-26 | 15:50 | 1.7639 | 0 |  | 1.5
2017-08-26 | 15:55 | 1.778 | 0 |  | 1.5
2017-08-26 | 16:00 | 1.7616 | 0 | 0 | 1.5 | 0
2017-08-26 | 16:00 |  |  |  | 1.5 |  | 82.3877
2017-08-26 | 16:05 | 1.7678 | 0 |  | 1.5
2017-08-26 | 16:10 | 1.7803 | 0 |  | 1.5
2017-08-26 | 16:15 | 1.7452 | 0 | 0 | 1.5 | 0
2017-08-26 | 16:15 |  |  |  | 1.5 |  | 81.8524
2017-08-26 | 16:20 | 1.7694 | 0 |  | 1.5
2017-08-26 | 16:25 | 1.7647 | 0 |  | 1.5
2017-08-26 | 16:30 | 1.7546 | 0 | 0 | 1.5 | 0
2017-08-26 | 16:30 |  |  |  | 1.5 |  | 81.3744
2017-08-26 | 16:35 | 1.7873 | 0 |  | 1.5
2017-08-26 | 16:40 | 1.7873 | 0 |  | 1.5
2017-08-26 | 16:45 | 1.7733 | 0 | 0 | 1.5 | 0
2017-08-26 | 16:45 |  |  |  | 1.5 |  | 80.9111
2017-08-26 | 16:50 | 1.7702 | 0 |  | 1.5
2017-08-26 | 16:55 | 1.7663 | 0 |  | 1.5
2017-08-26 | 17:00 | 1.7655 | 0 | 0 | 1.5 | 0
2017-08-26 | 17:00 |  |  |  | 1.5 |  | 80.5345
2017-08-26 | 17:05 | 1.7421 | 0 |  | 1.5
2017-08-26 | 17:10 | 1.7647 | 0 |  | 1.5
2017-08-26 | 17:15 | 1.7811 | 0 | 0 | 1.5 | 0
2017-08-26 | 17:15 | [5 empty] | 80.1821
2017-08-26 | 17:20 | 1.7928 | 0 |  | 1.5
2017-08-26 | 17:25 | 1.76 | 0 |  | 1.5
2017-08-26 | 17:30 | 1.7725 | 0 | 0 | 1.5 | 0
2017-08-26 | 17:30 |  |  |  | 1.5 |  | 79.651
2017-08-26 | 17:35 | 1.7842 | 0 |  | 1.5
2017-08-26 | 17:40 | 1.7678 | 0 |  | 1.5
2017-08-26 | 17:45 | 1.767 | 0 | 0 | 1.5 | 0
2017-08-26 | 17:45 |  |  |  | 1.5 |  | 79.0252
2017-08-26 | 17:50 | 1.7631 | 0 |  | 1.5
2017-08-26 | 17:55 | 1.7546 | 0 |  | 1.5
2017-08-26 | 18:00 | 1.7639 | 0 | 0 | 1.5 | 0
2017-08-26 | 18:00 |  |  |  | 1.5 |  | 78.709
2017-08-26 | 18:05 | 1.8045 | 0 |  | 1.5
2017-08-26 | 18:10 | 1.7826 | 0 |  | 1.5
2017-08-26 | 18:15 | 1.7592 | 0 | 0 | 1.5 | 0
2017-08-26 | 18:15 |  |  |  | 1.5 |  | 78.5056
2017-08-26 | 18:20 | 1.7569 | 0 |  | 1.5
2017-08-26 | 18:25 | 1.7608 | 0 |  | 1.5
2017-08-26 | 18:30 | 1.7631 | 0 | 0 | 1.5 | 0
2017-08-26 | 18:30 |  |  |  | 1.5 |  | 78.4737
2017-08-26 | 18:35 | 1.7819 | 0 |  | 1.5
2017-08-26 | 18:40 | 1.767 | 0 |  | 1.5
2017-08-26 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 0
2017-08-26 | 18:45 |  |  |  | 1.5 |  | 78.1351
2017-08-26 | 18:50 | 1.7366 | 0 |  | 1.5
2017-08-26 | 18:55 | 1.7468 | 0 |  | 1.5
2017-08-26 | 19:00 | 1.7507 | 0 | 0 | 1.5 | 0
2017-08-26 | 19:00 |  |  |  | 1.5 |  | 78.1317
2017-08-26 | 19:05 | 1.7577 | 0 |  | 1.5
2017-08-26 | 19:10 | 1.7553 | 0 |  | 1.5
2017-08-26 | 19:15 | 1.7491 | 0 | 0 | 1.5 | 0
2017-08-26 | 19:15 |  |  |  | 1.5 |  | 78.1005
2017-08-26 | 19:20 | 1.7655 | 0 |  | 1.5
2017-08-26 | 19:25 | 1.7444 | 0 |  | 1.5
2017-08-26 | 19:30 | 1.7491 | 0 | 0 | 1.5 | 0
2017-08-26 | 19:30 |  |  |  | 1.5 |  | 77.9642
2017-08-26 | 19:35 | 1.7592 | 0 |  | 1.5
2017-08-26 | 19:40 | 1.7561 | 0 |  | 1.5
2017-08-26 | 19:45 | 1.7585 | 0 | 0 | 1.5 | 0
2017-08-26 | 19:45 |  |  |  | 1.5 |  | 78.1279
2017-08-26 | 19:50 | 1.7569 | 0 |  | 1.5
2017-08-26 | 19:55 | 1.7304 | 0 |  | 1.5
2017-08-26 | 20:00 | 1.7351 | 0 | 0 | 1.5 | 0
2017-08-26 | 20:00 |  |  |  | 1.5 |  | 78.1721
2017-08-26 | 20:05 | 1.7616 | 0 |  | 1.5
2017-08-26 | 20:10 | 1.7546 | 0 |  | 1.5
2017-08-26 | 20:15 | 1.7514 | 0 | 0 | 1.5 | 0
2017-08-26 | 20:15 |  |  |  | 1.5 |  | 78.1615
2017-08-26 | 20:20 | 1.7616 | 0 |  | 1.5
2017-08-26 | 20:25 | 1.7335 | 0 |  | 1.5
2017-08-26 | 20:30 | 1.7421 | 0 | 0 | 1.5 | 0
2017-08-26 | 20:30 |  |  |  | 1.5 |  | 78.0787
2017-08-26 | 20:35 | 1.76 | 0 |  | 1.5
2017-08-26 | 20:40 | 1.7468 | 0 |  | 1.5
2017-08-26 | 20:45 | 1.7475 | 0 | 0 | 1.5 | 0
2017-08-26 | 20:45 |  |  |  | 1.5 |  | 78.1765
2017-08-26 | 20:50 | 1.7686 | 0 |  | 1.5
2017-08-26 | 20:55 | 1.7382 | 0 |  | 1.5
2017-08-26 | 21:00 | 1.7468 | 0 | 0 | 1.5 | 0
2017-08-26 | 21:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-26 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-26 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-26 | 21:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-26 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-26 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-26 | 21:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-26 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-26 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0
2017-08-26 | 21:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 21:50 | -0.10652 | 0 |  | 1.5
2017-08-26 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-26 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-26 | 22:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-26 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-26 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-08-26 | 22:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-26 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-26 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-08-26 | 22:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-26 | 22:40 | -0.10418 | 0 |  | 1.5
2017-08-26 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-26 | 22:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 22:50 | -0.10418 | 0 |  | 1.5
2017-08-26 | 22:55 | -0.10418 | 0 |  | 1.5
2017-08-26 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0
2017-08-26 | 23:00 |  |  |  | 1.5 |  | 0
2017-08-26 | 23:05 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:10 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:15 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-26 | 23:15 |  |  |  | 1.5 |  | 0
2017-08-26 | 23:20 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:25 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:30 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-26 | 23:30 |  |  |  | 1.5 |  | 0
2017-08-26 | 23:35 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:40 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:45 | -0.1034 | 0 | 0 | 1.5 | 0
2017-08-26 | 23:45 |  |  |  | 1.5 |  | 0
2017-08-26 | 23:50 | -0.1034 | 0 |  | 1.5
2017-08-26 | 23:55 | -0.1034 | 0 |  | 1.5
2017-08-27 | 0:00 | -0.10262 | 0 | 0 | 1.5 | 0
2017-08-27 | 0:00 |  |  |  | 1.5 |  | 0
2017-08-27 | 0:05 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:10 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 0:20 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:25 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 0:35 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:40 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 0:50 | -0.10262 | 0 |  | 1.5
2017-08-27 | 0:55 | -0.10262 | 0 |  | 1.5
2017-08-27 | 1:00 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 1:05 | -0.10262 | 0 |  | 1.5
2017-08-27 | 1:10 | -0.10262 | 0 |  | 1.5
2017-08-27 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 1:20 | -0.10652 | 0 |  | 1.5
2017-08-27 | 1:25 | -0.10574 | 0 |  | 1.5
2017-08-27 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 1:35 | -0.10574 | 0 |  | 1.5
2017-08-27 | 1:40 | -0.10574 | 0 |  | 1.5
2017-08-27 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 1:50 | -0.10652 | 0 |  | 1.5
2017-08-27 | 1:55 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 2:05 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:10 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 2:20 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:25 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 2:35 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:40 | -0.10652 | 0 |  | 1.5
2017-08-27 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 2:50 | -0.10808 | 0 |  | 1.5
2017-08-27 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:10 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 3:20 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-27 | 3:55 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 4:20 | -0.1073 | 0 |  | 1.5
2017-08-27 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-27 | 4:55 | -0.10808 | 0 |  | 1.5
2017-08-27 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 5:05 | 2.1898 | 0 |  | 1.5
2017-08-27 | 5:10 | 2.2179 | 0 |  | 1.5
2017-08-27 | 5:15 | 2.0673 | 0 | 0 | 1.5 | 0 | 90.1506
2017-08-27 | 5:20 | 2.0221 | 0 |  | 1.5
2017-08-27 | 5:25 | 1.9823 | 0 |  | 1.5
2017-08-27 | 5:30 | 1.9488 | 0 | 0 | 1.5 | 0 | 83.6593
2017-08-27 | 5:35 | 1.8903 | 0 |  | 1.5
2017-08-27 | 5:40 | 1.8614 | 0 |  | 1.5
2017-08-27 | 5:45 | 1.806 | 0 | 0 | 1.5 | 0 | 80.5293
2017-08-27 | 5:50 | 1.8138 | 0 |  | 1.5
2017-08-27 | 5:55 | 1.7733 | 0 |  | 1.5
2017-08-27 | 6:00 | 1.7803 | 0 | 0 | 1.5 | 0 | 79.2764
2017-08-27 | 6:05 | 1.76 | 0 |  | 1.5
2017-08-27 | 6:10 | 1.7546 | 0 |  | 1.5
2017-08-27 | 6:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 78.5996
2017-08-27 | 6:20 | 1.7397 | 0 |  | 1.5
2017-08-27 | 6:25 | 1.7413 | 0 |  | 1.5
2017-08-27 | 6:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 78.2194
2017-08-27 | 6:35 | 1.7928 | 0 |  | 1.5
2017-08-27 | 6:40 | 1.7444 | 0 |  | 1.5
2017-08-27 | 6:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 77.8907
2017-08-27 | 6:50 | 1.7756 | 0 |  | 1.5
2017-08-27 | 6:55 | 1.7748 | 0 |  | 1.5
2017-08-27 | 7:00 | 1.753 | 0 | 0 | 1.5 | 0 | 77.3791
2017-08-27 | 7:05 | 1.7631 | 0 |  | 1.5
2017-08-27 | 7:10 | 1.785 | 0 |  | 1.5
2017-08-27 | 7:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 76.8433
2017-08-27 | 7:20 | 1.7616 | 0 |  | 1.5
2017-08-27 | 7:25 | 1.7639 | 0 |  | 1.5
2017-08-27 | 7:30 | 1.7592 | 0 | 0 | 1.5 | 0 | 76.7225
2017-08-27 | 7:35 | 1.76 | 0 |  | 1.5
2017-08-27 | 7:40 | 1.7514 | 0 |  | 1.5
2017-08-27 | 7:45 | 1.746 | 0 | 0 | 1.5 | 0 | 76.6678
2017-08-27 | 7:50 | 1.7491 | 0 |  | 1.5
2017-08-27 | 7:55 | 1.7234 | 0 |  | 1.5
2017-08-27 | 8:00 | 1.7569 | 0 | 0 | 1.5 | 0 | 76.5527
2017-08-27 | 8:05 | 1.7296 | 0 |  | 1.5
2017-08-27 | 8:10 | 1.7163 | 0 |  | 1.5
2017-08-27 | 8:15 | 1.7585 | 0 | 0 | 1.5 | 0 | 76.5477
2017-08-27 | 8:20 | 1.7717 | 0 |  | 1.5
2017-08-27 | 8:25 | 1.739 | 0 |  | 1.5
2017-08-27 | 8:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 76.6269
2017-08-27 | 8:35 | 1.7608 | 0 |  | 1.5
2017-08-27 | 8:40 | 1.7561 | 0 |  | 1.5
2017-08-27 | 8:45 | 1.7358 | 0 | 0 | 1.5 | 0 | 76.5704
2017-08-27 | 8:50 | 1.7694 | 0 |  | 1.5
2017-08-27 | 8:55 | 1.7702 | 0 |  | 1.5
2017-08-27 | 9:00 | 1.7631 | 0 | 0 | 1.5 | 0 | 76.8284
2017-08-27 | 9:05 | 1.7413 | 0 |  | 1.5
2017-08-27 | 9:10 | 1.7678 | 0 |  | 1.5
2017-08-27 | 9:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 76.9159
2017-08-27 | 9:20 | 1.7241 | 0 |  | 1.5
2017-08-27 | 9:25 | 1.7288 | 0 |  | 1.5
2017-08-27 | 9:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 77.117
2017-08-27 | 9:35 | 1.746 | 0 |  | 1.5
2017-08-27 | 9:40 | 1.7577 | 0 |  | 1.5
2017-08-27 | 9:45 | 1.7218 | 0 | 0 | 1.5 | 0 | 77.2948
2017-08-27 | 9:50 | 1.7538 | 0 |  | 1.5
2017-08-27 | 9:55 | 1.7358 | 0 |  | 1.5
2017-08-27 | 10:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 77.5184
2017-08-27 | 10:05 | 1.7561 | 0 |  | 1.5
2017-08-27 | 10:10 | 1.7195 | 0 |  | 1.5
2017-08-27 | 10:15 | 1.7538 | 0 | 0 | 1.5 | 0 | 77.6177
2017-08-27 | 10:20 | 1.7163 | 0 |  | 1.5
2017-08-27 | 10:25 | 1.7327 | 0 |  | 1.5
2017-08-27 | 10:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 77.8991
2017-08-27 | 10:35 | 1.7483 | 0 |  | 1.5
2017-08-27 | 10:40 | 1.7709 | 0 |  | 1.5
2017-08-27 | 10:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 77.8586
2017-08-27 | 10:50 | 1.7436 | 0 |  | 1.5
2017-08-27 | 10:55 | 1.739 | 0 |  | 1.5
2017-08-27 | 11:00 | 1.7234 | 0 | 0 | 1.5 | 0 | 77.9956
2017-08-27 | 11:05 | 1.7483 | 0 |  | 1.5
2017-08-27 | 11:10 | 1.7179 | 0 |  | 1.5
2017-08-27 | 11:15 | 1.7179 | 0 | 0 | 1.5 | 0 | 78.2925
2017-08-27 | 11:20 | 1.7499 | 0 |  | 1.5
2017-08-27 | 11:25 | 1.7405 | 0 |  | 1.5
2017-08-27 | 11:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 78.5469
2017-08-27 | 11:35 | 1.7335 | 0 |  | 1.5
2017-08-27 | 11:40 | 1.7452 | 0 |  | 1.5
2017-08-27 | 11:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 78.9122
2017-08-27 | 11:50 | 1.753 | 0 |  | 1.5
2017-08-27 | 11:55 | 1.7366 | 0 |  | 1.5
2017-08-27 | 12:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.1781
2017-08-27 | 12:05 | 1.7475 | 0 |  | 1.5
2017-08-27 | 12:10 | 1.7312 | 0 |  | 1.5
2017-08-27 | 12:15 | 1.7163 | 0 | 0 | 1.5 | 0 | 79.6656
2017-08-27 | 12:20 | 1.721 | 0 |  | 1.5
2017-08-27 | 12:25 | 1.7436 | 0 |  | 1.5
2017-08-27 | 12:30 | 1.7296 | 0 | 0 | 1.5 | 0 | 80.6038
2017-08-27 | 12:35 | 1.7226 | 0 |  | 1.5
2017-08-27 | 12:40 | 1.7296 | 0 |  | 1.5
2017-08-27 | 12:45 | 1.7078 | 0 | 0 | 1.5 | 0 | 81.2304
2017-08-27 | 12:50 | 1.7397 | 0 |  | 1.5
2017-08-27 | 12:55 | 1.7265 | 0 |  | 1.5
2017-08-27 | 13:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 81.7968
2017-08-27 | 13:05 | 1.6906 | 0 |  | 1.5
2017-08-27 | 13:10 | 1.7257 | 0 |  | 1.5
2017-08-27 | 13:15 | 1.7148 | 0 | 0 | 1.5 | 0 | 82.7714
2017-08-27 | 13:20 | 1.6945 | 0 |  | 1.5
2017-08-27 | 13:25 | 1.7046 | 0 |  | 1.5
2017-08-27 | 13:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 83.7296
2017-08-27 | 13:35 | 1.7062 | 0 |  | 1.5
2017-08-27 | 13:40 | 1.7327 | 0 |  | 1.5
2017-08-27 | 13:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 84.2832
2017-08-27 | 13:50 | 1.8099 | 0 |  | 1.5
2017-08-27 | 13:55 | 1.7764 | 0 |  | 1.5
2017-08-27 | 14:00 | 1.778 | 0 | 0 | 1.5 | 0 | 83.3769
2017-08-27 | 14:05 | 1.7686 | 0 |  | 1.5
2017-08-27 | 14:10 | 1.7702 | 0 |  | 1.5
2017-08-27 | 14:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.6947
2017-08-27 | 14:20 | 1.7709 | 0 |  | 1.5
2017-08-27 | 14:25 | 1.7195 | 0 |  | 1.5
2017-08-27 | 14:30 | 1.7319 | 0 | 0 | 1.5 | 0 | 82.5122
2017-08-27 | 14:35 | 1.728 | 0 |  | 1.5
2017-08-27 | 14:40 | 1.7538 | 0 |  | 1.5
2017-08-27 | 14:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 82.5244
2017-08-27 | 14:50 | 1.7561 | 0 |  | 1.5
2017-08-27 | 14:55 | 1.7319 | 0 |  | 1.5
2017-08-27 | 15:00 | 1.7795 | 0 | 0 | 1.5 | 0 | 82.607
2017-08-27 | 15:05 | 1.7468 | 0 |  | 1.5
2017-08-27 | 15:10 | 1.7514 | 0 |  | 1.5
2017-08-27 | 15:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 82.669
2017-08-27 | 15:20 | 1.739 | 0 |  | 1.5
2017-08-27 | 15:25 | 1.7546 | 0 |  | 1.5
2017-08-27 | 15:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 82.7018
2017-08-27 | 15:35 | 1.7475 | 0 |  | 1.5
2017-08-27 | 15:40 | 1.7936 | 0 |  | 1.5
2017-08-27 | 15:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 82.2073
2017-08-27 | 15:50 | 1.7717 | 0 |  | 1.5
2017-08-27 | 15:55 | 1.7663 | 0 |  | 1.5
2017-08-27 | 16:00 | 1.753 | 0 | 0 | 1.5 | 0 | 81.8186
2017-08-27 | 16:05 | 1.7842 | 0 |  | 1.5
2017-08-27 | 16:10 | 1.7569 | 0 |  | 1.5
2017-08-27 | 16:15 | 1.7764 | 0 | 0 | 1.5 | 0 | 81.4258
2017-08-27 | 16:20 | 1.7936 | 0 |  | 1.5
2017-08-27 | 16:25 | 1.7561 | 0 |  | 1.5
2017-08-27 | 16:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 81.1119
2017-08-27 | 16:35 | 1.7842 | 0 |  | 1.5
2017-08-27 | 16:40 | 1.7702 | 0 |  | 1.5
2017-08-27 | 16:45 | 1.7655 | 0 | 0 | 1.5 | 0 | 80.7416
2017-08-27 | 16:50 | 1.7366 | 0 |  | 1.5
2017-08-27 | 16:55 | 1.7561 | 0 |  | 1.5
2017-08-27 | 17:00 | 1.7663 | 0 | 0 | 1.5 | 0 | 80.5941
2017-08-27 | 17:05 | 1.7553 | 0 |  | 1.5
2017-08-27 | 17:10 | 1.7514 | 0 |  | 1.5
2017-08-27 | 17:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 80.4298
2017-08-27 | 17:20 | 1.8146 | 0 |  | 1.5
2017-08-27 | 17:25 | 1.7608 | 0 |  | 1.5
2017-08-27 | 17:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 79.7154
2017-08-27 | 17:35 | 1.7967 | 0 |  | 1.5
2017-08-27 | 17:40 | 1.785 | 0 |  | 1.5
2017-08-27 | 17:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 79.3201
2017-08-27 | 17:50 | 1.7335 | 0 |  | 1.5
2017-08-27 | 17:55 | 1.7343 | 0 |  | 1.5
2017-08-27 | 18:00 | 1.746 | 0 | 0 | 1.5 | 0 | 79.0051
2017-08-27 | 18:05 | 1.7538 | 0 |  | 1.5
2017-08-27 | 18:10 | 1.76 | 0 |  | 1.5
2017-08-27 | 18:15 | 1.7366 | 0 | 0 | 1.5 | 0 | 78.8591
2017-08-27 | 18:20 | 1.746 | 0 |  | 1.5
2017-08-27 | 18:25 | 1.767 | 0 |  | 1.5
2017-08-27 | 18:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 78.7227
2017-08-27 | 18:35 | 1.7429 | 0 |  | 1.5
2017-08-27 | 18:40 | 1.7522 | 0 |  | 1.5
2017-08-27 | 18:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.6919
2017-08-27 | 18:50 | 1.7717 | 0 |  | 1.5
2017-08-27 | 18:55 | 1.7514 | 0 |  | 1.5
2017-08-27 | 19:00 | 1.7663 | 0 | 0 | 1.5 | 0 | 78.6108
2017-08-27 | 19:05 | 1.7702 | 0 |  | 1.5
2017-08-27 | 19:10 | 1.7756 | 0 |  | 1.5
2017-08-27 | 19:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 78.5378
2017-08-27 | 19:20 | 1.7663 | 0 |  | 1.5
2017-08-27 | 19:25 | 1.7452 | 0 |  | 1.5
2017-08-27 | 19:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 78.2257
2017-08-27 | 19:35 | 1.7553 | 0 |  | 1.5
2017-08-27 | 19:40 | 1.7709 | 0 |  | 1.5
2017-08-27 | 19:45 | 1.7655 | 0 | 0 | 1.5 | 0 | 77.9266
2017-08-27 | 19:50 | 1.7436 | 0 |  | 1.5
2017-08-27 | 19:55 | 1.7296 | 0 |  | 1.5
2017-08-27 | 20:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.2235
2017-08-27 | 20:05 | 1.7405 | 0 |  | 1.5
2017-08-27 | 20:10 | 1.753 | 0 |  | 1.5
2017-08-27 | 20:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 78.2428
2017-08-27 | 20:20 | 1.7366 | 0 |  | 1.5
2017-08-27 | 20:25 | 1.7709 | 0 |  | 1.5
2017-08-27 | 20:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 78.2382
2017-08-27 | 20:35 | 1.7694 | 0 |  | 1.5
2017-08-27 | 20:40 | 1.7421 | 0 |  | 1.5
2017-08-27 | 20:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 78.3044
2017-08-27 | 20:50 | 1.7475 | 0 |  | 1.5
2017-08-27 | 20:55 | 1.7514 | 0 |  | 1.5
2017-08-27 | 21:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.1576
2017-08-27 | 21:05 | -0.10262 | 0 |  | 1.5
2017-08-27 | 21:10 | -0.1034 | 0 |  | 1.5
2017-08-27 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-27 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-27 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-27 | 21:40 | -0.10652 | 0 |  | 1.5
2017-08-27 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-27 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-27 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 22:05 | -0.10574 | 0 |  | 1.5
2017-08-27 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-27 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 22:20 | -0.10574 | 0 |  | 1.5
2017-08-27 | 22:25 | -0.10574 | 0 |  | 1.5
2017-08-27 | 22:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 22:35 | -0.10418 | 0 |  | 1.5
2017-08-27 | 22:40 | -0.10418 | 0 |  | 1.5
2017-08-27 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 22:50 | -0.10418 | 0 |  | 1.5
2017-08-27 | 22:55 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 23:05 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:10 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 23:20 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:25 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 23:35 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:40 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-27 | 23:50 | -0.10418 | 0 |  | 1.5
2017-08-27 | 23:55 | -0.10418 | 0 |  | 1.5
2017-08-28 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-28 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-28 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 0:20 | -0.1034 | 0 |  | 1.5
2017-08-28 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-28 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 0:35 | -0.1034 | 0 |  | 1.5
2017-08-28 | 0:40 | -0.1034 | 0 |  | 1.5
2017-08-28 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 0:50 | -0.1034 | 0 |  | 1.5
2017-08-28 | 0:55 | -0.1034 | 0 |  | 1.5
2017-08-28 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 1:05 | -0.1034 | 0 |  | 1.5
2017-08-28 | 1:10 | -0.1034 | 0 |  | 1.5
2017-08-28 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 1:20 | -0.10652 | 0 |  | 1.5
2017-08-28 | 1:25 | -0.10574 | 0 |  | 1.5
2017-08-28 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 1:35 | -0.10652 | 0 |  | 1.5
2017-08-28 | 1:40 | -0.10652 | 0 |  | 1.5
2017-08-28 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-28 | 1:55 | -0.10808 | 0 |  | 1.5
2017-08-28 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-28 | 2:10 | -0.10808 | 0 |  | 1.5
2017-08-28 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-28 | 2:25 | -0.10808 | 0 |  | 1.5
2017-08-28 | 2:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 2:35 | -0.10652 | 0 |  | 1.5
2017-08-28 | 2:40 | -0.10652 | 0 |  | 1.5
2017-08-28 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 2:50 | -0.10652 | 0 |  | 1.5
2017-08-28 | 2:55 | -0.10652 | 0 |  | 1.5
2017-08-28 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 3:05 | -0.10652 | 0 |  | 1.5
2017-08-28 | 3:10 | -0.10652 | 0 |  | 1.5
2017-08-28 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 3:20 | -0.10652 | 0 |  | 1.5
2017-08-28 | 3:25 | -0.10652 | 0 |  | 1.5
2017-08-28 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 3:35 | -0.10886 | 0 |  | 1.5
2017-08-28 | 3:40 | -0.10886 | 0 |  | 1.5
2017-08-28 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-28 | 3:55 | -0.10886 | 0 |  | 1.5
2017-08-28 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 4:05 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:10 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 4:20 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:25 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 4:35 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:40 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 4:50 | -0.10808 | 0 |  | 1.5
2017-08-28 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-28 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 5:05 | 2.0034 | 0 |  | 1.5
2017-08-28 | 5:10 | 2.1368 | 0 |  | 1.5
2017-08-28 | 5:15 | 2.0276 | 0 | 0 | 1.5 | 0 | 91.6727
2017-08-28 | 5:20 | 1.9691 | 0 |  | 1.5
2017-08-28 | 5:25 | 1.9628 | 0 |  | 1.5
2017-08-28 | 5:30 | 1.9496 | 0 | 0 | 1.5 | 0 | 85.5654
2017-08-28 | 5:35 | 1.8731 | 0 |  | 1.5
2017-08-28 | 5:40 | 1.87 | 0 |  | 1.5
2017-08-28 | 5:45 | 1.8224 | 0 | 0 | 1.5 | 0 | 82.1182
2017-08-28 | 5:50 | 1.8154 | 0 |  | 1.5
2017-08-28 | 5:55 | 1.8068 | 0 |  | 1.5
2017-08-28 | 6:00 | 1.778 | 0 | 0 | 1.5 | 0 | 80.583
2017-08-28 | 6:05 | 1.7725 | 0 |  | 1.5
2017-08-28 | 6:10 | 1.7343 | 0 |  | 1.5
2017-08-28 | 6:15 | 1.7873 | 0 | 0 | 1.5 | 0 | 79.9232
2017-08-28 | 6:20 | 1.7795 | 0 |  | 1.5
2017-08-28 | 6:25 | 1.7686 | 0 |  | 1.5
2017-08-28 | 6:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 79.3037
2017-08-28 | 6:35 | 1.7507 | 0 |  | 1.5
2017-08-28 | 6:40 | 1.7585 | 0 |  | 1.5
2017-08-28 | 6:45 | 1.7748 | 0 | 0 | 1.5 | 0 | 78.9913
2017-08-28 | 6:50 | 1.7733 | 0 |  | 1.5
2017-08-28 | 6:55 | 1.7546 | 0 |  | 1.5
2017-08-28 | 7:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 78.6829
2017-08-28 | 7:05 | 1.7748 | 0 |  | 1.5
2017-08-28 | 7:10 | 1.7733 | 0 |  | 1.5
2017-08-28 | 7:15 | 1.7741 | 0 | 0 | 1.5 | 0 | 78.1606
2017-08-28 | 7:20 | 1.7257 | 0 |  | 1.5
2017-08-28 | 7:25 | 1.7748 | 0 |  | 1.5
2017-08-28 | 7:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 77.9506
2017-08-28 | 7:35 | 1.728 | 0 |  | 1.5
2017-08-28 | 7:40 | 1.7577 | 0 |  | 1.5
2017-08-28 | 7:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 77.8884
2017-08-28 | 7:50 | 1.7413 | 0 |  | 1.5
2017-08-28 | 7:55 | 1.7343 | 0 |  | 1.5
2017-08-28 | 8:00 | 1.7343 | 0 | 0 | 1.5 | 0 | 78.0531
2017-08-28 | 8:05 | 1.7546 | 0 |  | 1.5
2017-08-28 | 8:10 | 1.7577 | 0 |  | 1.5
2017-08-28 | 8:15 | 1.7366 | 0 | 0 | 1.5 | 0 | 78.2379
2017-08-28 | 8:20 | 1.7397 | 0 |  | 1.5
2017-08-28 | 8:25 | 1.7288 | 0 |  | 1.5
2017-08-28 | 8:30 | 1.7491 | 0 | 0 | 1.5 | 0 | 78.7322
2017-08-28 | 8:35 | 1.7819 | 0 |  | 1.5
2017-08-28 | 8:40 | 1.7265 | 0 |  | 1.5
2017-08-28 | 8:45 | 1.7031 | 0 | 0 | 1.5 | 0 | 78.6084
2017-08-28 | 8:50 | 1.7514 | 0 |  | 1.5
2017-08-28 | 8:55 | 1.7288 | 0 |  | 1.5
2017-08-28 | 9:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.6272
2017-08-28 | 9:05 | 1.7054 | 0 |  | 1.5
2017-08-28 | 9:10 | 1.7156 | 0 |  | 1.5
2017-08-28 | 9:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 79.3405
2017-08-28 | 9:20 | 1.739 | 0 |  | 1.5
2017-08-28 | 9:25 | 1.7374 | 0 |  | 1.5
2017-08-28 | 9:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.7542
2017-08-28 | 9:35 | 1.7351 | 0 |  | 1.5
2017-08-28 | 9:40 | 1.7054 | 0 |  | 1.5
2017-08-28 | 9:45 | 1.7046 | 0 | 0 | 1.5 | 0 | 80.3434
2017-08-28 | 9:50 | 1.7249 | 0 |  | 1.5
2017-08-28 | 9:55 | 1.7202 | 0 |  | 1.5
2017-08-28 | 10:00 | 1.7085 | 0 | 0 | 1.5 | 0 | 81.2139
2017-08-28 | 10:05 | 1.721 | 0 |  | 1.5
2017-08-28 | 10:10 | 1.7187 | 0 |  | 1.5
2017-08-28 | 10:15 | 1.7655 | 0 | 0 | 1.5 | 0 | 81.9089
2017-08-28 | 10:20 | 1.739 | 0 |  | 1.5
2017-08-28 | 10:25 | 1.7039 | 0 |  | 1.5
2017-08-28 | 10:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 82.5532
2017-08-28 | 10:35 | 1.7319 | 0 |  | 1.5
2017-08-28 | 10:40 | 1.7413 | 0 |  | 1.5
2017-08-28 | 10:45 | 1.7085 | 0 | 0 | 1.5 | 0 | 83.071
2017-08-28 | 10:50 | 1.7928 | 0 |  | 1.5
2017-08-28 | 10:55 | 1.767 | 0 |  | 1.5
2017-08-28 | 11:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 82.6966
2017-08-28 | 11:05 | 1.7608 | 0 |  | 1.5
2017-08-28 | 11:10 | 1.7577 | 0 |  | 1.5
2017-08-28 | 11:15 | 1.7491 | 0 | 0 | 1.5 | 0 | 82.3455
2017-08-28 | 11:20 | 1.7366 | 0 |  | 1.5
2017-08-28 | 11:25 | 1.6851 | 0 |  | 1.5
2017-08-28 | 11:30 | 1.7187 | 0 | 0 | 1.5 | 0 | 83.2097
2017-08-28 | 11:35 | 1.7054 | 0 |  | 1.5
2017-08-28 | 11:40 | 1.682 | 0 |  | 1.5
2017-08-28 | 11:45 | 1.6734 | 0 | 0 | 1.5 | 0 | 84.4702
2017-08-28 | 11:50 | 1.7156 | 0 |  | 1.5
2017-08-28 | 11:55 | 1.7046 | 0 |  | 1.5
2017-08-28 | 12:00 | 1.6906 | 0 | 0 | 1.5 | 0 | 85.6392
2017-08-28 | 12:05 | 1.7202 | 0 |  | 1.5
2017-08-28 | 12:10 | 1.7202 | 0 |  | 1.5
2017-08-28 | 12:15 | 1.7171 | 0 | 0 | 1.5 | 0 | 86.6553
2017-08-28 | 12:20 | 1.7007 | 0 |  | 1.5
2017-08-28 | 12:25 | 1.7093 | 0 |  | 1.5
2017-08-28 | 12:30 | 1.721 | 0 | 0 | 1.5 | 0 | 87.611
2017-08-28 | 12:35 | 1.7577 | 0 |  | 1.5
2017-08-28 | 12:40 | 1.7195 | 0 |  | 1.5
2017-08-28 | 12:45 | 1.7249 | 0 | 0 | 1.5 | 0 | 88.0848
2017-08-28 | 12:50 | 1.6961 | 0 |  | 1.5
2017-08-28 | 12:55 | 1.7163 | 0 |  | 1.5
2017-08-28 | 13:00 | 1.7023 | 0 | 0 | 1.5 | 0 | 89.1634
2017-08-28 | 13:05 | 1.6992 | 0 |  | 1.5
2017-08-28 | 13:10 | 1.7436 | 0 |  | 1.5
2017-08-28 | 13:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 90.1146
2017-08-28 | 13:20 | 1.7397 | 0 |  | 1.5
2017-08-28 | 13:25 | 1.7405 | 0 |  | 1.5
2017-08-28 | 13:30 | 1.6976 | 0 | 0 | 1.5 | 0 | 90.6756
2017-08-28 | 13:35 | 1.7366 | 0 |  | 1.5
2017-08-28 | 13:40 | 1.7241 | 0 |  | 1.5
2017-08-28 | 13:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 91.3877
2017-08-28 | 13:50 | 1.7405 | 0 |  | 1.5
2017-08-28 | 13:55 | 1.7343 | 0 |  | 1.5
2017-08-28 | 14:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 91.7511
2017-08-28 | 14:05 | 1.7647 | 0 |  | 1.5
2017-08-28 | 14:10 | 1.7319 | 0 |  | 1.5
2017-08-28 | 14:15 | 1.7296 | 0 | 0 | 1.5 | 0 | 92.1596
2017-08-28 | 14:20 | 1.7522 | 0 |  | 1.5
2017-08-28 | 14:25 | 1.721 | 0 |  | 1.5
2017-08-28 | 14:30 | 1.7202 | 0 | 0 | 1.5 | 0 | 92.8706
2017-08-28 | 14:35 | 1.739 | 0 |  | 1.5
2017-08-28 | 14:40 | 1.7405 | 0 |  | 1.5
2017-08-28 | 14:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 92.9262
2017-08-28 | 14:50 | 1.7538 | 0 |  | 1.5
2017-08-28 | 14:55 | 1.7717 | 0 |  | 1.5
2017-08-28 | 15:00 | 1.746 | 0 | 0 | 1.5 | 0 | 92.7843
2017-08-28 | 15:05 | 1.767 | 0 |  | 1.5
2017-08-28 | 15:10 | 1.7382 | 0 |  | 1.5
2017-08-28 | 15:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 92.6719
2017-08-28 | 15:20 | 1.7491 | 0 |  | 1.5
2017-08-28 | 15:25 | 1.7288 | 0 |  | 1.5
2017-08-28 | 15:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 92.4439
2017-08-28 | 15:35 | 1.7608 | 0 |  | 1.5
2017-08-28 | 15:40 | 1.7772 | 0 |  | 1.5
2017-08-28 | 15:45 | 1.7889 | 0 | 0 | 1.5 | 0 | 91.8974
2017-08-28 | 15:50 | 1.7772 | 0 |  | 1.5
2017-08-28 | 15:55 | 1.7608 | 0 |  | 1.5
2017-08-28 | 16:00 | 1.7756 | 0 | 0 | 1.5 | 0 | 91.3485
2017-08-28 | 16:05 | 1.7639 | 0 |  | 1.5
2017-08-28 | 16:10 | 1.7756 | 0 |  | 1.5
2017-08-28 | 16:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 90.8318
2017-08-28 | 16:20 | 1.7951 | 0 |  | 1.5
2017-08-28 | 16:25 | 1.7585 | 0 |  | 1.5
2017-08-28 | 16:30 | 1.767 | 0 | 0 | 1.5 | 0 | 90.112
2017-08-28 | 16:35 | 1.7725 | 0 |  | 1.5
2017-08-28 | 16:40 | 1.7943 | 0 |  | 1.5
2017-08-28 | 16:45 | 1.7858 | 0 | 0 | 1.5 | 0 | 89.1405
2017-08-28 | 16:50 | 1.7982 | 0 |  | 1.5
2017-08-28 | 16:55 | 1.8092 | 0 |  | 1.5
2017-08-28 | 17:00 | 1.7694 | 0 | 0 | 1.5 | 0 | 88.3028
2017-08-28 | 17:05 | 1.8092 | 0 |  | 1.5
2017-08-28 | 17:10 | 1.7897 | 0 |  | 1.5
2017-08-28 | 17:15 | 1.778 | 0 | 0 | 1.5 | 0 | 87.2228
2017-08-28 | 17:20 | 1.8232 | 0 |  | 1.5
2017-08-28 | 17:25 | 1.7764 | 0 |  | 1.5
2017-08-28 | 17:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 86.0528
2017-08-28 | 17:35 | 1.7772 | 0 |  | 1.5
2017-08-28 | 17:40 | 1.7811 | 0 |  | 1.5
2017-08-28 | 17:45 | 1.7787 | 0 | 0 | 1.5 | 0 | 85.4336
2017-08-28 | 17:50 | 1.8076 | 0 |  | 1.5
2017-08-28 | 17:55 | 1.7787 | 0 |  | 1.5
2017-08-28 | 18:00 | 1.8053 | 0 | 0 | 1.5 | 0 | 84.3886
2017-08-28 | 18:05 | 1.785 | 0 |  | 1.5
2017-08-28 | 18:10 | 1.7881 | 0 |  | 1.5
2017-08-28 | 18:15 | 1.7795 | 0 | 0 | 1.5 | 0 | 83.2476
2017-08-28 | 18:20 | 1.7881 | 0 |  | 1.5
2017-08-28 | 18:25 | 1.785 | 0 |  | 1.5
2017-08-28 | 18:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 82.6237
2017-08-28 | 18:35 | 1.7624 | 0 |  | 1.5
2017-08-28 | 18:40 | 1.7686 | 0 |  | 1.5
2017-08-28 | 18:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 82.2813
2017-08-28 | 18:50 | 1.7592 | 0 |  | 1.5
2017-08-28 | 18:55 | 1.7756 | 0 |  | 1.5
2017-08-28 | 19:00 | 1.7912 | 0 | 0 | 1.5 | 0 | 81.9004
2017-08-28 | 19:05 | 1.7647 | 0 |  | 1.5
2017-08-28 | 19:10 | 1.7592 | 0 |  | 1.5
2017-08-28 | 19:15 | 1.767 | 0 | 0 | 1.5 | 0 | 81.6136
2017-08-28 | 19:20 | 1.7639 | 0 |  | 1.5
2017-08-28 | 19:25 | 1.7686 | 0 |  | 1.5
2017-08-28 | 19:30 | 1.7795 | 0 | 0 | 1.5 | 0 | 81.3054
2017-08-28 | 19:35 | 1.7741 | 0 |  | 1.5
2017-08-28 | 19:40 | 1.7795 | 0 |  | 1.5
2017-08-28 | 19:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 80.8303
2017-08-28 | 19:50 | 1.7624 | 0 |  | 1.5
2017-08-28 | 19:55 | 1.7709 | 0 |  | 1.5
2017-08-28 | 20:00 | 1.753 | 0 | 0 | 1.5 | 0 | 80.4674
2017-08-28 | 20:05 | 1.7608 | 0 |  | 1.5
2017-08-28 | 20:10 | 1.7912 | 0 |  | 1.5
2017-08-28 | 20:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 80.148
2017-08-28 | 20:20 | 1.7163 | 0 |  | 1.5
2017-08-28 | 20:25 | 1.7709 | 0 |  | 1.5
2017-08-28 | 20:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 79.987
2017-08-28 | 20:35 | 1.7795 | 0 |  | 1.5
2017-08-28 | 20:40 | 1.7312 | 0 |  | 1.5
2017-08-28 | 20:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 79.7898
2017-08-28 | 20:50 | 1.7413 | 0 |  | 1.5
2017-08-28 | 20:55 | 1.7709 | 0 |  | 1.5
2017-08-28 | 21:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.5428
2017-08-28 | 21:05 | -0.10262 | 0 |  | 1.5
2017-08-28 | 21:10 | -0.10418 | 0 |  | 1.5
2017-08-28 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-28 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-28 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 21:35 | -0.10496 | 0 |  | 1.5
2017-08-28 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-28 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 21:50 | -0.1034 | 0 |  | 1.5
2017-08-28 | 21:55 | -0.10574 | 0 |  | 1.5
2017-08-28 | 22:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 22:05 | -0.10418 | 0 |  | 1.5
2017-08-28 | 22:10 | -0.10574 | 0 |  | 1.5
2017-08-28 | 22:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 22:20 | -0.10418 | 0 |  | 1.5
2017-08-28 | 22:25 | -0.10418 | 0 |  | 1.5
2017-08-28 | 22:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 22:35 | -0.10418 | 0 |  | 1.5
2017-08-28 | 22:40 | -0.10418 | 0 |  | 1.5
2017-08-28 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 22:50 | -0.10418 | 0 |  | 1.5
2017-08-28 | 22:55 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 23:05 | -0.10418 | 0 |  | 1.5
2017-08-28 | 23:10 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 23:20 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:25 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 23:35 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:40 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-28 | 23:50 | -0.1034 | 0 |  | 1.5
2017-08-28 | 23:55 | -0.1034 | 0 |  | 1.5
2017-08-29 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 0:05 | -0.1034 | 0 |  | 1.5
2017-08-29 | 0:10 | -0.1034 | 0 |  | 1.5
2017-08-29 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 0:20 | -0.1034 | 0 |  | 1.5
2017-08-29 | 0:25 | -0.1034 | 0 |  | 1.5
2017-08-29 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 0:35 | -0.10262 | 0 |  | 1.5
2017-08-29 | 0:40 | -0.10262 | 0 |  | 1.5
2017-08-29 | 0:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 0:50 | -0.10262 | 0 |  | 1.5
2017-08-29 | 0:55 | -0.10262 | 0 |  | 1.5
2017-08-29 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 1:05 | -0.10262 | 0 |  | 1.5
2017-08-29 | 1:10 | -0.10262 | 0 |  | 1.5
2017-08-29 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 1:20 | -0.10574 | 0 |  | 1.5
2017-08-29 | 1:25 | -0.10574 | 0 |  | 1.5
2017-08-29 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-29 | 1:40 | -0.10574 | 0 |  | 1.5
2017-08-29 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 1:50 | -0.10574 | 0 |  | 1.5
2017-08-29 | 1:55 | -0.10574 | 0 |  | 1.5
2017-08-29 | 2:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 2:05 | -0.10652 | 0 |  | 1.5
2017-08-29 | 2:10 | -0.10652 | 0 |  | 1.5
2017-08-29 | 2:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 2:20 | -0.10652 | 0 |  | 1.5
2017-08-29 | 2:25 | -0.10652 | 0 |  | 1.5
2017-08-29 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 2:35 | -0.10574 | 0 |  | 1.5
2017-08-29 | 2:40 | -0.10574 | 0 |  | 1.5
2017-08-29 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 2:50 | -0.10652 | 0 |  | 1.5
2017-08-29 | 2:55 | -0.10652 | 0 |  | 1.5
2017-08-29 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 3:05 | -0.10574 | 0 |  | 1.5
2017-08-29 | 3:10 | -0.10574 | 0 |  | 1.5
2017-08-29 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 3:20 | -0.10652 | 0 |  | 1.5
2017-08-29 | 3:25 | -0.10652 | 0 |  | 1.5
2017-08-29 | 3:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 3:35 | -0.10652 | 0 |  | 1.5
2017-08-29 | 3:40 | -0.10652 | 0 |  | 1.5
2017-08-29 | 3:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 3:50 | -0.10652 | 0 |  | 1.5
2017-08-29 | 3:55 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 4:05 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:10 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 4:20 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:25 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 4:35 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:40 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 4:50 | -0.10652 | 0 |  | 1.5
2017-08-29 | 4:55 | -0.1073 | 0 |  | 1.5
2017-08-29 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 5:05 | 1.4706 | 0 |  | 1.5
2017-08-29 | 5:10 | 1.8489 | 0 |  | 1.5
2017-08-29 | 5:15 | 1.806 | 0 | 0 | 1.5 | 0 | 98.1655
2017-08-29 | 5:20 | 1.8458 | 0 |  | 1.5
2017-08-29 | 5:25 | 1.9371 | 0 |  | 1.5
2017-08-29 | 5:30 | 2.0018 | 0 | 0 | 1.5 | 0 | 93.9179
2017-08-29 | 5:35 | 2.0806 | 0 |  | 1.5
2017-08-29 | 5:40 | 2.0205 | 0 |  | 1.5
2017-08-29 | 5:45 | 1.9613 | 0 | 0 | 1.5 | 0 | 86.6508
2017-08-29 | 5:50 | 1.9106 | 0 |  | 1.5
2017-08-29 | 5:55 | 1.8872 | 0 |  | 1.5
2017-08-29 | 6:00 | 1.8731 | 0 | 0 | 1.5 | 0 | 82.6999
2017-08-29 | 6:05 | 1.8638 | 0 |  | 1.5
2017-08-29 | 6:10 | 1.8341 | 0 |  | 1.5
2017-08-29 | 6:15 | 1.8388 | 0 | 0 | 1.5 | 0 | 80.3264
2017-08-29 | 6:20 | 1.8021 | 0 |  | 1.5
2017-08-29 | 6:25 | 1.7967 | 0 |  | 1.5
2017-08-29 | 6:30 | 1.76 | 0 | 0 | 1.5 | 0 | 79.4651
2017-08-29 | 6:35 | 1.7834 | 0 |  | 1.5
2017-08-29 | 6:40 | 1.7507 | 0 |  | 1.5
2017-08-29 | 6:45 | 1.7241 | 0 | 0 | 1.5 | 0 | 79.1599
2017-08-29 | 6:50 | 1.7187 | 0 |  | 1.5
2017-08-29 | 6:55 | 1.7475 | 0 |  | 1.5
2017-08-29 | 7:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 79.3498
2017-08-29 | 7:05 | 1.7429 | 0 |  | 1.5
2017-08-29 | 7:10 | 1.7553 | 0 |  | 1.5
2017-08-29 | 7:15 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.1182
2017-08-29 | 7:20 | 1.7592 | 0 |  | 1.5
2017-08-29 | 7:25 | 1.7296 | 0 |  | 1.5
2017-08-29 | 7:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 79.2833
2017-08-29 | 7:35 | 1.7491 | 0 |  | 1.5
2017-08-29 | 7:40 | 1.7335 | 0 |  | 1.5
2017-08-29 | 7:45 | 1.7234 | 0 | 0 | 1.5 | 0 | 79.4512
2017-08-29 | 7:50 | 1.7639 | 0 |  | 1.5
2017-08-29 | 7:55 | 1.7514 | 0 |  | 1.5
2017-08-29 | 8:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 79.397
2017-08-29 | 8:05 | 1.767 | 0 |  | 1.5
2017-08-29 | 8:10 | 1.753 | 0 |  | 1.5
2017-08-29 | 8:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 79.4744
2017-08-29 | 8:20 | 1.7429 | 0 |  | 1.5
2017-08-29 | 8:25 | 1.746 | 0 |  | 1.5
2017-08-29 | 8:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 79.617
2017-08-29 | 8:35 | 1.7491 | 0 |  | 1.5
2017-08-29 | 8:40 | 1.7218 | 0 |  | 1.5
2017-08-29 | 8:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 79.877
2017-08-29 | 8:50 | 1.7694 | 0 |  | 1.5
2017-08-29 | 8:55 | 1.7265 | 0 |  | 1.5
2017-08-29 | 9:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 80.06
2017-08-29 | 9:05 | 1.7171 | 0 |  | 1.5
2017-08-29 | 9:10 | 1.7444 | 0 |  | 1.5
2017-08-29 | 9:15 | 1.7179 | 0 | 0 | 1.5 | 0 | 80.3346
2017-08-29 | 9:20 | 1.7522 | 0 |  | 1.5
2017-08-29 | 9:25 | 1.7491 | 0 |  | 1.5
2017-08-29 | 9:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 80.5969
2017-08-29 | 9:35 | 1.7273 | 0 |  | 1.5
2017-08-29 | 9:40 | 1.7468 | 0 |  | 1.5
2017-08-29 | 9:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 80.795
2017-08-29 | 9:50 | 1.7452 | 0 |  | 1.5
2017-08-29 | 9:55 | 1.7288 | 0 |  | 1.5
2017-08-29 | 10:00 | 1.728 | 0 | 0 | 1.5 | 0 | 81.0124
2017-08-29 | 10:05 | 1.7499 | 0 |  | 1.5
2017-08-29 | 10:10 | 1.7616 | 0 |  | 1.5
2017-08-29 | 10:15 | 1.7358 | 0 | 0 | 1.5 | 0 | 81.1129
2017-08-29 | 10:20 | 1.7429 | 0 |  | 1.5
2017-08-29 | 10:25 | 1.728 | 0 |  | 1.5
2017-08-29 | 10:30 | 1.7296 | 0 | 0 | 1.5 | 0 | 81.3359
2017-08-29 | 10:35 | 1.7468 | 0 |  | 1.5
2017-08-29 | 10:40 | 1.6625 | 0 |  | 1.5
2017-08-29 | 10:45 | 1.707 | 0 | 0 | 1.5 | 0 | 82.4692
2017-08-29 | 10:50 | 1.6836 | 0 |  | 1.5
2017-08-29 | 10:55 | 1.7117 | 0 |  | 1.5
2017-08-29 | 11:00 | 1.721 | 0 | 0 | 1.5 | 0 | 83.8461
2017-08-29 | 11:05 | 1.7218 | 0 |  | 1.5
2017-08-29 | 11:10 | 1.739 | 0 |  | 1.5
2017-08-29 | 11:15 | 1.7265 | 0 | 0 | 1.5 | 0 | 84.3338
2017-08-29 | 11:20 | 1.7171 | 0 |  | 1.5
2017-08-29 | 11:25 | 1.6547 | 0 |  | 1.5
2017-08-29 | 11:30 | 1.689 | 0 | 0 | 1.5 | 0 | 86.0435
2017-08-29 | 11:35 | 1.7312 | 0 |  | 1.5
2017-08-29 | 11:40 | 1.721 | 0 |  | 1.5
2017-08-29 | 11:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 86.7287
2017-08-29 | 11:50 | 1.7421 | 0 |  | 1.5
2017-08-29 | 11:55 | 1.7374 | 0 |  | 1.5
2017-08-29 | 12:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 86.852
2017-08-29 | 12:05 | 1.7265 | 0 |  | 1.5
2017-08-29 | 12:10 | 1.7241 | 0 |  | 1.5
2017-08-29 | 12:15 | 1.7592 | 0 | 0 | 1.5 | 0 | 87.1869
2017-08-29 | 12:20 | 1.7405 | 0 |  | 1.5
2017-08-29 | 12:25 | 1.7179 | 0 |  | 1.5
2017-08-29 | 12:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 87.5532
2017-08-29 | 12:35 | 1.7358 | 0 |  | 1.5
2017-08-29 | 12:40 | 1.7546 | 0 |  | 1.5
2017-08-29 | 12:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 87.6107
2017-08-29 | 12:50 | 1.7507 | 0 |  | 1.5
2017-08-29 | 12:55 | 1.7327 | 0 |  | 1.5
2017-08-29 | 13:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 87.7914
2017-08-29 | 13:05 | 1.7429 | 0 |  | 1.5
2017-08-29 | 13:10 | 1.7405 | 0 |  | 1.5
2017-08-29 | 13:15 | 1.7748 | 0 | 0 | 1.5 | 0 | 87.8298
2017-08-29 | 13:20 | 1.8068 | 0 |  | 1.5
2017-08-29 | 13:25 | 1.7507 | 0 |  | 1.5
2017-08-29 | 13:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 87.1325
2017-08-29 | 13:35 | 1.7522 | 0 |  | 1.5
2017-08-29 | 13:40 | 1.7413 | 0 |  | 1.5
2017-08-29 | 13:45 | 1.7148 | 0 | 0 | 1.5 | 0 | 87.2892
2017-08-29 | 13:50 | 1.7748 | 0 |  | 1.5
2017-08-29 | 13:55 | 1.7491 | 0 |  | 1.5
2017-08-29 | 14:00 | 1.7351 | 0 | 0 | 1.5 | 0 | 87.4856
2017-08-29 | 14:05 | 1.7436 | 0 |  | 1.5
2017-08-29 | 14:10 | 1.7374 | 0 |  | 1.5
2017-08-29 | 14:15 | 1.721 | 0 | 0 | 1.5 | 0 | 87.6863
2017-08-29 | 14:20 | 1.7234 | 0 |  | 1.5
2017-08-29 | 14:25 | 1.7327 | 0 |  | 1.5
2017-08-29 | 14:30 | 1.7304 | 0 | 0 | 1.5 | 0 | 88.0258
2017-08-29 | 14:35 | 1.739 | 0 |  | 1.5
2017-08-29 | 14:40 | 1.7522 | 0 |  | 1.5
2017-08-29 | 14:45 | 1.7273 | 0 | 0 | 1.5 | 0 | 88.3938
2017-08-29 | 14:50 | 1.7592 | 0 |  | 1.5
2017-08-29 | 14:55 | 1.7569 | 0 |  | 1.5
2017-08-29 | 15:00 | 1.7343 | 0 | 0 | 1.5 | 0 | 88.5386
2017-08-29 | 15:05 | 1.7507 | 0 |  | 1.5
2017-08-29 | 15:10 | 1.7592 | 0 |  | 1.5
2017-08-29 | 15:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 88.4495
2017-08-29 | 15:20 | 1.7663 | 0 |  | 1.5
2017-08-29 | 15:25 | 1.7452 | 0 |  | 1.5
2017-08-29 | 15:30 | 1.76 | 0 | 0 | 1.5 | 0 | 88.41
2017-08-29 | 15:35 | 1.7569 | 0 |  | 1.5
2017-08-29 | 15:40 | 1.7678 | 0 |  | 1.5
2017-08-29 | 15:45 | 1.7358 | 0 | 0 | 1.5 | 0 | 88.3862
2017-08-29 | 15:50 | 1.7522 | 0 |  | 1.5
2017-08-29 | 15:55 | 1.7491 | 0 |  | 1.5
2017-08-29 | 16:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 88.255
2017-08-29 | 16:05 | 1.753 | 0 |  | 1.5
2017-08-29 | 16:10 | 1.7725 | 0 |  | 1.5
2017-08-29 | 16:15 | 1.7897 | 0 | 0 | 1.5 | 0 | 87.9237
2017-08-29 | 16:20 | 1.7756 | 0 |  | 1.5
2017-08-29 | 16:25 | 1.7616 | 0 |  | 1.5
2017-08-29 | 16:30 | 1.7717 | 0 | 0 | 1.5 | 0 | 87.1771
2017-08-29 | 16:35 | 1.7585 | 0 |  | 1.5
2017-08-29 | 16:40 | 1.7655 | 0 |  | 1.5
2017-08-29 | 16:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 86.7296
2017-08-29 | 16:50 | 1.7686 | 0 |  | 1.5
2017-08-29 | 16:55 | 1.7569 | 0 |  | 1.5
2017-08-29 | 17:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 86.2804
2017-08-29 | 17:05 | 1.7772 | 0 |  | 1.5
2017-08-29 | 17:10 | 1.7967 | 0 |  | 1.5
2017-08-29 | 17:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 85.7425
2017-08-29 | 17:20 | 1.7936 | 0 |  | 1.5
2017-08-29 | 17:25 | 1.7717 | 0 |  | 1.5
2017-08-29 | 17:30 | 1.7795 | 0 | 0 | 1.5 | 0 | 84.9657
2017-08-29 | 17:35 | 1.778 | 0 |  | 1.5
2017-08-29 | 17:40 | 1.7405 | 0 |  | 1.5
2017-08-29 | 17:45 | 1.7803 | 0 | 0 | 1.5 | 0 | 84.2037
2017-08-29 | 17:50 | 1.7717 | 0 |  | 1.5
2017-08-29 | 17:55 | 1.7764 | 0 |  | 1.5
2017-08-29 | 18:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 83.6024
2017-08-29 | 18:05 | 1.7655 | 0 |  | 1.5
2017-08-29 | 18:10 | 1.7616 | 0 |  | 1.5
2017-08-29 | 18:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 83.1331
2017-08-29 | 18:20 | 1.7647 | 0 |  | 1.5
2017-08-29 | 18:25 | 1.7421 | 0 |  | 1.5
2017-08-29 | 18:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.8632
2017-08-29 | 18:35 | 1.7608 | 0 |  | 1.5
2017-08-29 | 18:40 | 1.7803 | 0 |  | 1.5
2017-08-29 | 18:45 | 1.7358 | 0 | 0 | 1.5 | 0 | 82.5788
2017-08-29 | 18:50 | 1.7842 | 0 |  | 1.5
2017-08-29 | 18:55 | 1.76 | 0 |  | 1.5
2017-08-29 | 19:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 82.2037
2017-08-29 | 19:05 | 1.7819 | 0 |  | 1.5
2017-08-29 | 19:10 | 1.7312 | 0 |  | 1.5
2017-08-29 | 19:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 81.9864
2017-08-29 | 19:20 | 1.7748 | 0 |  | 1.5
2017-08-29 | 19:25 | 1.7382 | 0 |  | 1.5
2017-08-29 | 19:30 | 1.7717 | 0 | 0 | 1.5 | 0 | 81.7338
2017-08-29 | 19:35 | 1.7538 | 0 |  | 1.5
2017-08-29 | 19:40 | 1.7624 | 0 |  | 1.5
2017-08-29 | 19:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 81.1838
2017-08-29 | 19:50 | 1.767 | 0 |  | 1.5
2017-08-29 | 19:55 | 1.7951 | 0 |  | 1.5
2017-08-29 | 20:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 80.625
2017-08-29 | 20:05 | 1.7725 | 0 |  | 1.5
2017-08-29 | 20:10 | 1.7795 | 0 |  | 1.5
2017-08-29 | 20:15 | 1.7585 | 0 | 0 | 1.5 | 0 | 80.1261
2017-08-29 | 20:20 | 1.7717 | 0 |  | 1.5
2017-08-29 | 20:25 | 1.7624 | 0 |  | 1.5
2017-08-29 | 20:30 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.5951
2017-08-29 | 20:35 | 1.7436 | 0 |  | 1.5
2017-08-29 | 20:40 | 1.7234 | 0 |  | 1.5
2017-08-29 | 20:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 79.9182
2017-08-29 | 20:50 | 1.7546 | 0 |  | 1.5
2017-08-29 | 20:55 | 1.7483 | 0 |  | 1.5
2017-08-29 | 21:00 | 1.7475 | 0 | 0 | 1.5 | 0 | 80.0357
2017-08-29 | 21:05 | -0.10262 | 0 |  | 1.5
2017-08-29 | 21:10 | -0.1034 | 0 |  | 1.5
2017-08-29 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 21:20 | -0.10418 | 0 |  | 1.5
2017-08-29 | 21:25 | -0.10418 | 0 |  | 1.5
2017-08-29 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 21:35 | -0.1034 | 0 |  | 1.5
2017-08-29 | 21:40 | -0.10496 | 0 |  | 1.5
2017-08-29 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 21:50 | -0.10496 | 0 |  | 1.5
2017-08-29 | 21:55 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 22:05 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:10 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 22:20 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:25 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 22:35 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:40 | -0.10574 | 0 |  | 1.5
2017-08-29 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 22:50 | -0.10496 | 0 |  | 1.5
2017-08-29 | 22:55 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 23:05 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:10 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 23:20 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:25 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 23:35 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:40 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-29 | 23:50 | -0.10496 | 0 |  | 1.5
2017-08-29 | 23:55 | -0.10496 | 0 |  | 1.5
2017-08-30 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 0:05 | -0.10418 | 0 |  | 1.5
2017-08-30 | 0:10 | -0.10418 | 0 |  | 1.5
2017-08-30 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 0:20 | -0.10496 | 0 |  | 1.5
2017-08-30 | 0:25 | -0.10418 | 0 |  | 1.5
2017-08-30 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-30 | 0:40 | -0.10496 | 0 |  | 1.5
2017-08-30 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 0:50 | -0.10418 | 0 |  | 1.5
2017-08-30 | 0:55 | -0.10418 | 0 |  | 1.5
2017-08-30 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 1:05 | -0.10418 | 0 |  | 1.5
2017-08-30 | 1:10 | -0.10418 | 0 |  | 1.5
2017-08-30 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 1:20 | -0.10808 | 0 |  | 1.5
2017-08-30 | 1:25 | -0.10808 | 0 |  | 1.5
2017-08-30 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 1:35 | -0.10808 | 0 |  | 1.5
2017-08-30 | 1:40 | -0.10808 | 0 |  | 1.5
2017-08-30 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 1:50 | -0.10808 | 0 |  | 1.5
2017-08-30 | 1:55 | -0.10886 | 0 |  | 1.5
2017-08-30 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 2:05 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:10 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 2:20 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:25 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 2:35 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:40 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 2:50 | -0.10808 | 0 |  | 1.5
2017-08-30 | 2:55 | -0.10808 | 0 |  | 1.5
2017-08-30 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 3:05 | -0.10808 | 0 |  | 1.5
2017-08-30 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-30 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-30 | 3:25 | -0.10808 | 0 |  | 1.5
2017-08-30 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 3:35 | -0.10808 | 0 |  | 1.5
2017-08-30 | 3:40 | -0.10808 | 0 |  | 1.5
2017-08-30 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 3:50 | -0.10808 | 0 |  | 1.5
2017-08-30 | 3:55 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 4:05 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 4:20 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:25 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 4:35 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:40 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 4:50 | -0.10886 | 0 |  | 1.5
2017-08-30 | 4:55 | -0.10886 | 0 |  | 1.5
2017-08-30 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 5:05 | 1.9886 | 0 |  | 1.5
2017-08-30 | 5:10 | 2.0705 | 0 |  | 1.5
2017-08-30 | 5:15 | 1.9893 | 0 | 0 | 1.5 | 0 | 93.024
2017-08-30 | 5:20 | 1.9449 | 0 |  | 1.5
2017-08-30 | 5:25 | 2.0088 | 0 |  | 1.5
2017-08-30 | 5:30 | 1.9566 | 0 | 0 | 1.5 | 0 | 86.7245
2017-08-30 | 5:35 | 1.9425 | 0 |  | 1.5
2017-08-30 | 5:40 | 1.8708 | 0 |  | 1.5
2017-08-30 | 5:45 | 1.8497 | 0 | 0 | 1.5 | 0 | 82.7186
2017-08-30 | 5:50 | 1.8341 | 0 |  | 1.5
2017-08-30 | 5:55 | 1.8014 | 0 |  | 1.5
2017-08-30 | 6:00 | 1.8123 | 0 | 0 | 1.5 | 0 | 80.7776
2017-08-30 | 6:05 | 1.8014 | 0 |  | 1.5
2017-08-30 | 6:10 | 1.7702 | 0 |  | 1.5
2017-08-30 | 6:15 | 1.7717 | 0 | 0 | 1.5 | 0 | 79.8046
2017-08-30 | 6:20 | 1.7405 | 0 |  | 1.5
2017-08-30 | 6:25 | 1.7624 | 0 |  | 1.5
2017-08-30 | 6:30 | 1.778 | 0 | 0 | 1.5 | 0 | 79.425
2017-08-30 | 6:35 | 1.7741 | 0 |  | 1.5
2017-08-30 | 6:40 | 1.7561 | 0 |  | 1.5
2017-08-30 | 6:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 79.053
2017-08-30 | 6:50 | 1.7702 | 0 |  | 1.5
2017-08-30 | 6:55 | 1.7639 | 0 |  | 1.5
2017-08-30 | 7:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 78.8363
2017-08-30 | 7:05 | 1.7655 | 0 |  | 1.5
2017-08-30 | 7:10 | 1.7694 | 0 |  | 1.5
2017-08-30 | 7:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 78.578
2017-08-30 | 7:20 | 1.7702 | 0 |  | 1.5
2017-08-30 | 7:25 | 1.7343 | 0 |  | 1.5
2017-08-30 | 7:30 | 1.7343 | 0 | 0 | 1.5 | 0 | 78.501
2017-08-30 | 7:35 | 1.7553 | 0 |  | 1.5
2017-08-30 | 7:40 | 1.7366 | 0 |  | 1.5
2017-08-30 | 7:45 | 1.753 | 0 | 0 | 1.5 | 0 | 78.5212
2017-08-30 | 7:50 | 1.7546 | 0 |  | 1.5
2017-08-30 | 7:55 | 1.7421 | 0 |  | 1.5
2017-08-30 | 8:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 78.475
2017-08-30 | 8:05 | 1.7007 | 0 |  | 1.5
2017-08-30 | 8:10 | 1.7195 | 0 |  | 1.5
2017-08-30 | 8:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 78.691
2017-08-30 | 8:20 | 1.7117 | 0 |  | 1.5
2017-08-30 | 8:25 | 1.7273 | 0 |  | 1.5
2017-08-30 | 8:30 | 1.7296 | 0 | 0 | 1.5 | 0 | 79.2354
2017-08-30 | 8:35 | 1.7327 | 0 |  | 1.5
2017-08-30 | 8:40 | 1.7452 | 0 |  | 1.5
2017-08-30 | 8:45 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.4071
2017-08-30 | 8:50 | 1.7538 | 0 |  | 1.5
2017-08-30 | 8:55 | 1.7663 | 0 |  | 1.5
2017-08-30 | 9:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 79.5469
2017-08-30 | 9:05 | 1.7483 | 0 |  | 1.5
2017-08-30 | 9:10 | 1.7218 | 0 |  | 1.5
2017-08-30 | 9:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 79.9867
2017-08-30 | 9:20 | 1.739 | 0 |  | 1.5
2017-08-30 | 9:25 | 1.76 | 0 |  | 1.5
2017-08-30 | 9:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 80.1389
2017-08-30 | 9:35 | 1.7538 | 0 |  | 1.5
2017-08-30 | 9:40 | 1.7608 | 0 |  | 1.5
2017-08-30 | 9:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 79.9808
2017-08-30 | 9:50 | 1.7553 | 0 |  | 1.5
2017-08-30 | 9:55 | 1.7374 | 0 |  | 1.5
2017-08-30 | 10:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 79.8345
2017-08-30 | 10:05 | 1.7296 | 0 |  | 1.5
2017-08-30 | 10:10 | 1.7413 | 0 |  | 1.5
2017-08-30 | 10:15 | 1.714 | 0 | 0 | 1.5 | 0 | 79.9273
2017-08-30 | 10:20 | 1.7429 | 0 |  | 1.5
2017-08-30 | 10:25 | 1.7304 | 0 |  | 1.5
2017-08-30 | 10:30 | 1.7296 | 0 | 0 | 1.5 | 0 | 80.1096
2017-08-30 | 10:35 | 1.7234 | 0 |  | 1.5
2017-08-30 | 10:40 | 1.7811 | 0 |  | 1.5
2017-08-30 | 10:45 | 1.7296 | 0 | 0 | 1.5 | 0 | 80.2354
2017-08-30 | 10:50 | 1.7163 | 0 |  | 1.5
2017-08-30 | 10:55 | 1.739 | 0 |  | 1.5
2017-08-30 | 11:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 80.6557
2017-08-30 | 11:05 | 1.7054 | 0 |  | 1.5
2017-08-30 | 11:10 | 1.7078 | 0 |  | 1.5
2017-08-30 | 11:15 | 1.7202 | 0 | 0 | 1.5 | 0 | 81.3801
2017-08-30 | 11:20 | 1.7475 | 0 |  | 1.5
2017-08-30 | 11:25 | 1.7374 | 0 |  | 1.5
2017-08-30 | 11:30 | 1.7062 | 0 | 0 | 1.5 | 0 | 82.0864
2017-08-30 | 11:35 | 1.7078 | 0 |  | 1.5
2017-08-30 | 11:40 | 1.6828 | 0 |  | 1.5
2017-08-30 | 11:45 | 1.6773 | 0 | 0 | 1.5 | 0 | 83.5646
2017-08-30 | 11:50 | 1.7015 | 0 |  | 1.5
2017-08-30 | 11:55 | 1.6953 | 0 |  | 1.5
2017-08-30 | 12:00 | 1.7288 | 0 | 0 | 1.5 | 0 | 84.9754
2017-08-30 | 12:05 | 1.739 | 0 |  | 1.5
2017-08-30 | 12:10 | 1.6945 | 0 |  | 1.5
2017-08-30 | 12:15 | 1.7039 | 0 | 0 | 1.5 | 0 | 85.8369
2017-08-30 | 12:20 | 1.7085 | 0 |  | 1.5
2017-08-30 | 12:25 | 1.7031 | 0 |  | 1.5
2017-08-30 | 12:30 | 1.7078 | 0 | 0 | 1.5 | 0 | 87.0721
2017-08-30 | 12:35 | 1.6851 | 0 |  | 1.5
2017-08-30 | 12:40 | 1.7031 | 0 |  | 1.5
2017-08-30 | 12:45 | 1.6968 | 0 | 0 | 1.5 | 0 | 88.2903
2017-08-30 | 12:50 | 1.7343 | 0 |  | 1.5
2017-08-30 | 12:55 | 1.7772 | 0 |  | 1.5
2017-08-30 | 13:00 | 1.7725 | 0 | 0 | 1.5 | 0 | 88.43
2017-08-30 | 13:05 | 1.7585 | 0 |  | 1.5
2017-08-30 | 13:10 | 1.7538 | 0 |  | 1.5
2017-08-30 | 13:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 88.0083
2017-08-30 | 13:20 | 1.714 | 0 |  | 1.5
2017-08-30 | 13:25 | 1.7507 | 0 |  | 1.5
2017-08-30 | 13:30 | 1.7507 | 0 | 0 | 1.5 | 0 | 88.2737
2017-08-30 | 13:35 | 1.7288 | 0 |  | 1.5
2017-08-30 | 13:40 | 1.7522 | 0 |  | 1.5
2017-08-30 | 13:45 | 1.753 | 0 | 0 | 1.5 | 0 | 88.2962
2017-08-30 | 13:50 | 1.7522 | 0 |  | 1.5
2017-08-30 | 13:55 | 1.7655 | 0 |  | 1.5
2017-08-30 | 14:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 88.1316
2017-08-30 | 14:05 | 1.7421 | 0 |  | 1.5
2017-08-30 | 14:10 | 1.7561 | 0 |  | 1.5
2017-08-30 | 14:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 87.711
2017-08-30 | 14:20 | 1.7452 | 0 |  | 1.5
2017-08-30 | 14:25 | 1.7507 | 0 |  | 1.5
2017-08-30 | 14:30 | 1.8045 | 0 | 0 | 1.5 | 0 | 87.3982
2017-08-30 | 14:35 | 1.7265 | 0 |  | 1.5
2017-08-30 | 14:40 | 1.7444 | 0 |  | 1.5
2017-08-30 | 14:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 87.6246
2017-08-30 | 14:50 | 1.7249 | 0 |  | 1.5
2017-08-30 | 14:55 | 1.746 | 0 |  | 1.5
2017-08-30 | 15:00 | 1.7265 | 0 | 0 | 1.5 | 0 | 87.8415
2017-08-30 | 15:05 | 1.721 | 0 |  | 1.5
2017-08-30 | 15:10 | 1.7514 | 0 |  | 1.5
2017-08-30 | 15:15 | 1.7366 | 0 | 0 | 1.5 | 0 | 88.3632
2017-08-30 | 15:20 | 1.7546 | 0 |  | 1.5
2017-08-30 | 15:25 | 1.76 | 0 |  | 1.5
2017-08-30 | 15:30 | 1.7507 | 0 | 0 | 1.5 | 0 | 88.334
2017-08-30 | 15:35 | 1.7499 | 0 |  | 1.5
2017-08-30 | 15:40 | 1.7741 | 0 |  | 1.5
2017-08-30 | 15:45 | 1.7912 | 0 | 0 | 1.5 | 0 | 87.6507
2017-08-30 | 15:50 | 1.7865 | 0 |  | 1.5
2017-08-30 | 15:55 | 1.7881 | 0 |  | 1.5
2017-08-30 | 16:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 86.8641
2017-08-30 | 16:05 | 1.7616 | 0 |  | 1.5
2017-08-30 | 16:10 | 1.7358 | 0 |  | 1.5
2017-08-30 | 16:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 86.3919
2017-08-30 | 16:20 | 1.7491 | 0 |  | 1.5
2017-08-30 | 16:25 | 1.7608 | 0 |  | 1.5
2017-08-30 | 16:30 | 1.7873 | 0 | 0 | 1.5 | 0 | 85.9006
2017-08-30 | 16:35 | 1.7904 | 0 |  | 1.5
2017-08-30 | 16:40 | 1.7678 | 0 |  | 1.5
2017-08-30 | 16:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 85.136
2017-08-30 | 16:50 | 1.7608 | 0 |  | 1.5
2017-08-30 | 16:55 | 1.7873 | 0 |  | 1.5
2017-08-30 | 17:00 | 1.7764 | 0 | 0 | 1.5 | 0 | 84.4555
2017-08-30 | 17:05 | 1.7514 | 0 |  | 1.5
2017-08-30 | 17:10 | 1.7936 | 0 |  | 1.5
2017-08-30 | 17:15 | 1.792 | 0 | 0 | 1.5 | 0 | 83.935
2017-08-30 | 17:20 | 1.7678 | 0 |  | 1.5
2017-08-30 | 17:25 | 1.7772 | 0 |  | 1.5
2017-08-30 | 17:30 | 1.7881 | 0 | 0 | 1.5 | 0 | 83.0668
2017-08-30 | 17:35 | 1.8029 | 0 |  | 1.5
2017-08-30 | 17:40 | 1.7873 | 0 |  | 1.5
2017-08-30 | 17:45 | 1.7795 | 0 | 0 | 1.5 | 0 | 81.9638
2017-08-30 | 17:50 | 1.7819 | 0 |  | 1.5
2017-08-30 | 17:55 | 1.7522 | 0 |  | 1.5
2017-08-30 | 18:00 | 1.76 | 0 | 0 | 1.5 | 0 | 81.1607
2017-08-30 | 18:05 | 1.8006 | 0 |  | 1.5
2017-08-30 | 18:10 | 1.7639 | 0 |  | 1.5
2017-08-30 | 18:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 80.5821
2017-08-30 | 18:20 | 1.7631 | 0 |  | 1.5
2017-08-30 | 18:25 | 1.7725 | 0 |  | 1.5
2017-08-30 | 18:30 | 1.7491 | 0 | 0 | 1.5 | 0 | 80.2565
2017-08-30 | 18:35 | 1.7772 | 0 |  | 1.5
2017-08-30 | 18:40 | 1.7733 | 0 |  | 1.5
2017-08-30 | 18:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 79.8646
2017-08-30 | 18:50 | 1.7631 | 0 |  | 1.5
2017-08-30 | 18:55 | 1.7561 | 0 |  | 1.5
2017-08-30 | 19:00 | 1.7553 | 0 | 0 | 1.5 | 0 | 79.5171
2017-08-30 | 19:05 | 1.7678 | 0 |  | 1.5
2017-08-30 | 19:10 | 1.7475 | 0 |  | 1.5
2017-08-30 | 19:15 | 1.746 | 0 | 0 | 1.5 | 0 | 79.2961
2017-08-30 | 19:20 | 1.7764 | 0 |  | 1.5
2017-08-30 | 19:25 | 1.7553 | 0 |  | 1.5
2017-08-30 | 19:30 | 1.7756 | 0 | 0 | 1.5 | 0 | 78.9077
2017-08-30 | 19:35 | 1.746 | 0 |  | 1.5
2017-08-30 | 19:40 | 1.7936 | 0 |  | 1.5
2017-08-30 | 19:45 | 1.7803 | 0 | 0 | 1.5 | 0 | 78.5524
2017-08-30 | 19:50 | 1.7507 | 0 |  | 1.5
2017-08-30 | 19:55 | 1.7366 | 0 |  | 1.5
2017-08-30 | 20:00 | 1.7015 | 0 | 0 | 1.5 | 0 | 78.9873
2017-08-30 | 20:05 | 1.728 | 0 |  | 1.5
2017-08-30 | 20:10 | 1.7327 | 0 |  | 1.5
2017-08-30 | 20:15 | 1.746 | 0 | 0 | 1.5 | 0 | 79.5387
2017-08-30 | 20:20 | 1.7078 | 0 |  | 1.5
2017-08-30 | 20:25 | 1.7335 | 0 |  | 1.5
2017-08-30 | 20:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.926
2017-08-30 | 20:35 | 1.7624 | 0 |  | 1.5
2017-08-30 | 20:40 | 1.7491 | 0 |  | 1.5
2017-08-30 | 20:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 79.7146
2017-08-30 | 20:50 | 1.753 | 0 |  | 1.5
2017-08-30 | 20:55 | 1.7803 | 0 |  | 1.5
2017-08-30 | 21:00 | 1.7553 | 0 | 0 | 1.5 | 0 | 79.6068
2017-08-30 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-30 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-30 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-30 | 21:25 | -0.10574 | 0 |  | 1.5
2017-08-30 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 21:35 | -0.10574 | 0 |  | 1.5
2017-08-30 | 21:40 | -0.10574 | 0 |  | 1.5
2017-08-30 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 21:50 | -0.10574 | 0 |  | 1.5
2017-08-30 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 22:05 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:10 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 22:20 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:25 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 22:35 | -0.1073 | 0 |  | 1.5
2017-08-30 | 22:40 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 22:50 | -0.10652 | 0 |  | 1.5
2017-08-30 | 22:55 | -0.10652 | 0 |  | 1.5
2017-08-30 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 23:05 | -0.10652 | 0 |  | 1.5
2017-08-30 | 23:10 | -0.10652 | 0 |  | 1.5
2017-08-30 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 23:20 | -0.10652 | 0 |  | 1.5
2017-08-30 | 23:25 | -0.10652 | 0 |  | 1.5
2017-08-30 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 23:35 | -0.10652 | 0 |  | 1.5
2017-08-30 | 23:40 | -0.10574 | 0 |  | 1.5
2017-08-30 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-30 | 23:50 | -0.10574 | 0 |  | 1.5
2017-08-30 | 23:55 | -0.10652 | 0 |  | 1.5
2017-08-31 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 0:05 | -0.10574 | 0 |  | 1.5
2017-08-31 | 0:10 | -0.10574 | 0 |  | 1.5
2017-08-31 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 0:20 | -0.10574 | 0 |  | 1.5
2017-08-31 | 0:25 | -0.10574 | 0 |  | 1.5
2017-08-31 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 0:35 | -0.10418 | 0 |  | 1.5
2017-08-31 | 0:40 | -0.10574 | 0 |  | 1.5
2017-08-31 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 0:50 | -0.10574 | 0 |  | 1.5
2017-08-31 | 0:55 | -0.10574 | 0 |  | 1.5
2017-08-31 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 1:05 | -0.10496 | 0 |  | 1.5
2017-08-31 | 1:10 | -0.10574 | 0 |  | 1.5
2017-08-31 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 1:20 | -0.10886 | 0 |  | 1.5
2017-08-31 | 1:25 | -0.10652 | 0 |  | 1.5
2017-08-31 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 1:35 | -0.10886 | 0 |  | 1.5
2017-08-31 | 1:40 | -0.10886 | 0 |  | 1.5
2017-08-31 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 1:50 | -0.10886 | 0 |  | 1.5
2017-08-31 | 1:55 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 2:05 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:10 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 2:20 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:25 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 2:35 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:40 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 2:50 | -0.10886 | 0 |  | 1.5
2017-08-31 | 2:55 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 3:05 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:10 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 3:20 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:25 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 3:35 | -0.11042 | 0 |  | 1.5
2017-08-31 | 3:40 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 3:50 | -0.10886 | 0 |  | 1.5
2017-08-31 | 3:55 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 4:05 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:10 | -0.10886 | 0 |  | 1.5
2017-08-31 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 4:20 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:25 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:30 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 4:35 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:40 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:45 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 4:50 | -0.10964 | 0 |  | 1.5
2017-08-31 | 4:55 | -0.10964 | 0 |  | 1.5
2017-08-31 | 5:00 | -0.10964 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 5:05 | 1.9262 | 0 |  | 1.5
2017-08-31 | 5:10 | 2.0868 | 0 |  | 1.5
2017-08-31 | 5:15 | 1.9324 | 0 | 0 | 1.5 | 0 | 93.8526
2017-08-31 | 5:20 | 1.8708 | 0 |  | 1.5
2017-08-31 | 5:25 | 1.8755 | 0 |  | 1.5
2017-08-31 | 5:30 | 1.9636 | 0 | 0 | 1.5 | 0 | 89.8923
2017-08-31 | 5:35 | 1.9535 | 0 |  | 1.5
2017-08-31 | 5:40 | 1.9324 | 0 |  | 1.5
2017-08-31 | 5:45 | 1.8778 | 0 | 0 | 1.5 | 0 | 85.0404
2017-08-31 | 5:50 | 1.8669 | 0 |  | 1.5
2017-08-31 | 5:55 | 1.8864 | 0 |  | 1.5
2017-08-31 | 6:00 | 1.8388 | 0 | 0 | 1.5 | 0 | 82.0024
2017-08-31 | 6:05 | 1.8232 | 0 |  | 1.5
2017-08-31 | 6:10 | 1.806 | 0 |  | 1.5
2017-08-31 | 6:15 | 1.8021 | 0 | 0 | 1.5 | 0 | 80.2699
2017-08-31 | 6:20 | 1.8045 | 0 |  | 1.5
2017-08-31 | 6:25 | 1.7795 | 0 |  | 1.5
2017-08-31 | 6:30 | 1.7709 | 0 | 0 | 1.5 | 0 | 79.4409
2017-08-31 | 6:35 | 1.7608 | 0 |  | 1.5
2017-08-31 | 6:40 | 1.7592 | 0 |  | 1.5
2017-08-31 | 6:45 | 1.7733 | 0 | 0 | 1.5 | 0 | 79.0011
2017-08-31 | 6:50 | 1.7491 | 0 |  | 1.5
2017-08-31 | 6:55 | 1.7499 | 0 |  | 1.5
2017-08-31 | 7:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 78.8229
2017-08-31 | 7:05 | 1.7366 | 0 |  | 1.5
2017-08-31 | 7:10 | 1.7499 | 0 |  | 1.5
2017-08-31 | 7:15 | 1.7436 | 0 | 0 | 1.5 | 0 | 78.8445
2017-08-31 | 7:20 | 1.7499 | 0 |  | 1.5
2017-08-31 | 7:25 | 1.7694 | 0 |  | 1.5
2017-08-31 | 7:30 | 1.7335 | 0 | 0 | 1.5 | 0 | 78.7178
2017-08-31 | 7:35 | 1.7483 | 0 |  | 1.5
2017-08-31 | 7:40 | 1.7468 | 0 |  | 1.5
2017-08-31 | 7:45 | 1.7491 | 0 | 0 | 1.5 | 0 | 78.799
2017-08-31 | 7:50 | 1.7834 | 0 |  | 1.5
2017-08-31 | 7:55 | 1.7405 | 0 |  | 1.5
2017-08-31 | 8:00 | 1.7382 | 0 | 0 | 1.5 | 0 | 78.9687
2017-08-31 | 8:05 | 1.7343 | 0 |  | 1.5
2017-08-31 | 8:10 | 1.714 | 0 |  | 1.5
2017-08-31 | 8:15 | 1.7218 | 0 | 0 | 1.5 | 0 | 79.8232
2017-08-31 | 8:20 | 1.7007 | 0 |  | 1.5
2017-08-31 | 8:25 | 1.7265 | 0 |  | 1.5
2017-08-31 | 8:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 80.3335
2017-08-31 | 8:35 | 1.7343 | 0 |  | 1.5
2017-08-31 | 8:40 | 1.6602 | 0 |  | 1.5
2017-08-31 | 8:45 | 1.739 | 0 | 0 | 1.5 | 0 | 81.4125
2017-08-31 | 8:50 | 1.7569 | 0 |  | 1.5
2017-08-31 | 8:55 | 1.7624 | 0 |  | 1.5
2017-08-31 | 9:00 | 1.767 | 0 | 0 | 1.5 | 0 | 81.2286
2017-08-31 | 9:05 | 1.7678 | 0 |  | 1.5
2017-08-31 | 9:10 | 1.7748 | 0 |  | 1.5
2017-08-31 | 9:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 80.8766
2017-08-31 | 9:20 | 1.7546 | 0 |  | 1.5
2017-08-31 | 9:25 | 1.7429 | 0 |  | 1.5
2017-08-31 | 9:30 | 1.7366 | 0 | 0 | 1.5 | 0 | 80.886
2017-08-31 | 9:35 | 1.7366 | 0 |  | 1.5
2017-08-31 | 9:40 | 2.1524 | 0 |  | 1.5
2017-08-31 | 9:45 | 1.9995 | 0 | 0 | 1.5 | 0 | 76.7471
2017-08-31 | 9:50 | 1.4449 | 0 |  | 1.5
2017-08-31 | 9:55 | 1.5369 | 0 |  | 1.5
2017-08-31 | 10:00 | 1.6539 | 0 | 0 | 1.5 | 0 | 79.9726
2017-08-31 | 10:05 | 1.6695 | 0 |  | 1.5
2017-08-31 | 10:10 | 1.7031 | 0 |  | 1.5
2017-08-31 | 10:15 | 1.6961 | 0 | 0 | 1.5 | 0 | 81.3747
2017-08-31 | 10:20 | 1.7202 | 0 |  | 1.5
2017-08-31 | 10:25 | 1.7054 | 0 |  | 1.5
2017-08-31 | 10:30 | 1.7249 | 0 | 0 | 1.5 | 0 | 81.9748
2017-08-31 | 10:35 | 1.7343 | 0 |  | 1.5
2017-08-31 | 10:40 | 1.739 | 0 |  | 1.5
2017-08-31 | 10:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.0349
2017-08-31 | 10:50 | 1.7358 | 0 |  | 1.5
2017-08-31 | 10:55 | 1.7514 | 0 |  | 1.5
2017-08-31 | 11:00 | 1.7468 | 0 | 0 | 1.5 | 0 | 82.3191
2017-08-31 | 11:05 | 1.7491 | 0 |  | 1.5
2017-08-31 | 11:10 | 1.7156 | 0 |  | 1.5
2017-08-31 | 11:15 | 1.6742 | 0 | 0 | 1.5 | 0 | 83.1431
2017-08-31 | 11:20 | 1.7078 | 0 |  | 1.5
2017-08-31 | 11:25 | 1.668 | 0 |  | 1.5
2017-08-31 | 11:30 | 1.6415 | 0 | 0 | 1.5 | 0 | 85.2516
2017-08-31 | 11:35 | 1.6859 | 0 |  | 1.5
2017-08-31 | 11:40 | 1.689 | 0 |  | 1.5
2017-08-31 | 11:45 | 1.7 | 0 | 0 | 1.5 | 0 | 86.8229
2017-08-31 | 11:50 | 1.7085 | 0 |  | 1.5
2017-08-31 | 11:55 | 1.7148 | 0 |  | 1.5
2017-08-31 | 12:00 | 1.7241 | 0 | 0 | 1.5 | 0 | 87.6081
2017-08-31 | 12:05 | 1.7491 | 0 |  | 1.5
2017-08-31 | 12:10 | 1.7631 | 0 |  | 1.5
2017-08-31 | 12:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 87.3295
2017-08-31 | 12:20 | 1.7741 | 0 |  | 1.5
2017-08-31 | 12:25 | 1.7257 | 0 |  | 1.5
2017-08-31 | 12:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 87.604
2017-08-31 | 12:35 | 1.7475 | 0 |  | 1.5
2017-08-31 | 12:40 | 1.7756 | 0 |  | 1.5
2017-08-31 | 12:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 87.5477
2017-08-31 | 12:50 | 1.7187 | 0 |  | 1.5
2017-08-31 | 12:55 | 1.7468 | 0 |  | 1.5
2017-08-31 | 13:00 | 1.7241 | 0 | 0 | 1.5 | 0 | 87.9272
2017-08-31 | 13:05 | 1.7366 | 0 |  | 1.5
2017-08-31 | 13:10 | 1.7546 | 0 |  | 1.5
2017-08-31 | 13:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 88.2669
2017-08-31 | 13:20 | 1.7226 | 0 |  | 1.5
2017-08-31 | 13:25 | 1.6929 | 0 |  | 1.5
2017-08-31 | 13:30 | 1.7218 | 0 | 0 | 1.5 | 0 | 89.05
2017-08-31 | 13:35 | 1.7062 | 0 |  | 1.5
2017-08-31 | 13:40 | 1.7249 | 0 |  | 1.5
2017-08-31 | 13:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 89.5107
2017-08-31 | 13:50 | 1.7397 | 0 |  | 1.5
2017-08-31 | 13:55 | 1.7109 | 0 |  | 1.5
2017-08-31 | 14:00 | 1.6805 | 0 | 0 | 1.5 | 0 | 90.2512
2017-08-31 | 14:05 | 1.7663 | 0 |  | 1.5
2017-08-31 | 14:10 | 1.7366 | 0 |  | 1.5
2017-08-31 | 14:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 90.5491
2017-08-31 | 14:20 | 1.7179 | 0 |  | 1.5
2017-08-31 | 14:25 | 1.721 | 0 |  | 1.5
2017-08-31 | 14:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 91.0997
2017-08-31 | 14:35 | 1.746 | 0 |  | 1.5
2017-08-31 | 14:40 | 1.7218 | 0 |  | 1.5
2017-08-31 | 14:45 | 1.7187 | 0 | 0 | 1.5 | 0 | 91.6077
2017-08-31 | 14:50 | 1.753 | 0 |  | 1.5
2017-08-31 | 14:55 | 1.7592 | 0 |  | 1.5
2017-08-31 | 15:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 91.6729
2017-08-31 | 15:05 | 1.7663 | 0 |  | 1.5
2017-08-31 | 15:10 | 1.7156 | 0 |  | 1.5
2017-08-31 | 15:15 | 1.7514 | 0 | 0 | 1.5 | 0 | 91.8933
2017-08-31 | 15:20 | 1.739 | 0 |  | 1.5
2017-08-31 | 15:25 | 1.7538 | 0 |  | 1.5
2017-08-31 | 15:30 | 1.7694 | 0 | 0 | 1.5 | 0 | 91.9615
2017-08-31 | 15:35 | 1.753 | 0 |  | 1.5
2017-08-31 | 15:40 | 1.7335 | 0 |  | 1.5
2017-08-31 | 15:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 92.0294
2017-08-31 | 15:50 | 1.7795 | 0 |  | 1.5
2017-08-31 | 15:55 | 1.7624 | 0 |  | 1.5
2017-08-31 | 16:00 | 1.7819 | 0 | 0 | 1.5 | 0 | 91.3834
2017-08-31 | 16:05 | 1.7881 | 0 |  | 1.5
2017-08-31 | 16:10 | 1.7491 | 0 |  | 1.5
2017-08-31 | 16:15 | 1.7085 | 0 | 0 | 1.5 | 0 | 91.0132
2017-08-31 | 16:20 | 1.767 | 0 |  | 1.5
2017-08-31 | 16:25 | 1.7951 | 0 |  | 1.5
2017-08-31 | 16:30 | 1.7819 | 0 | 0 | 1.5 | 0 | 90.4928
2017-08-31 | 16:35 | 1.7967 | 0 |  | 1.5
2017-08-31 | 16:40 | 1.8396 | 0 |  | 1.5
2017-08-31 | 16:45 | 1.8193 | 0 | 0 | 1.5 | 0 | 88.9554
2017-08-31 | 16:50 | 1.8248 | 0 |  | 1.5
2017-08-31 | 16:55 | 1.8162 | 0 |  | 1.5
2017-08-31 | 17:00 | 1.8123 | 0 | 0 | 1.5 | 0 | 87.2374
2017-08-31 | 17:05 | 1.8138 | 0 |  | 1.5
2017-08-31 | 17:10 | 1.8006 | 0 |  | 1.5
2017-08-31 | 17:15 | 1.8021 | 0 | 0 | 1.5 | 0 | 85.6869
2017-08-31 | 17:20 | 1.8084 | 0 |  | 1.5
2017-08-31 | 17:25 | 1.7959 | 0 |  | 1.5
2017-08-31 | 17:30 | 1.8092 | 0 | 0 | 1.5 | 0 | 84.1411
2017-08-31 | 17:35 | 1.8115 | 0 |  | 1.5
2017-08-31 | 17:40 | 1.8248 | 0 |  | 1.5
2017-08-31 | 17:45 | 1.8123 | 0 | 0 | 1.5 | 0 | 82.7626
2017-08-31 | 17:50 | 1.7421 | 0 |  | 1.5
2017-08-31 | 17:55 | 1.7647 | 0 |  | 1.5
2017-08-31 | 18:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 82.0156
2017-08-31 | 18:05 | 1.7826 | 0 |  | 1.5
2017-08-31 | 18:10 | 1.7764 | 0 |  | 1.5
2017-08-31 | 18:15 | 1.7538 | 0 | 0 | 1.5 | 0 | 81.3309
2017-08-31 | 18:20 | 1.7616 | 0 |  | 1.5
2017-08-31 | 18:25 | 1.7343 | 0 |  | 1.5
2017-08-31 | 18:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 81.014
2017-08-31 | 18:35 | 1.7741 | 0 |  | 1.5
2017-08-31 | 18:40 | 1.7561 | 0 |  | 1.5
2017-08-31 | 18:45 | 1.753 | 0 | 0 | 1.5 | 0 | 80.6797
2017-08-31 | 18:50 | 1.7569 | 0 |  | 1.5
2017-08-31 | 18:55 | 1.7725 | 0 |  | 1.5
2017-08-31 | 19:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 80.3514
2017-08-31 | 19:05 | 1.7647 | 0 |  | 1.5
2017-08-31 | 19:10 | 1.7725 | 0 |  | 1.5
2017-08-31 | 19:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 80.0549
2017-08-31 | 19:20 | 1.7639 | 0 |  | 1.5
2017-08-31 | 19:25 | 1.7717 | 0 |  | 1.5
2017-08-31 | 19:30 | 1.7881 | 0 | 0 | 1.5 | 0 | 79.4127
2017-08-31 | 19:35 | 1.7865 | 0 |  | 1.5
2017-08-31 | 19:40 | 1.7741 | 0 |  | 1.5
2017-08-31 | 19:45 | 1.7748 | 0 | 0 | 1.5 | 0 | 78.6424
2017-08-31 | 19:50 | 1.7678 | 0 |  | 1.5
2017-08-31 | 19:55 | 1.7514 | 0 |  | 1.5
2017-08-31 | 20:00 | 1.7218 | 0 | 0 | 1.5 | 0 | 78.4592
2017-08-31 | 20:05 | 1.7335 | 0 |  | 1.5
2017-08-31 | 20:10 | 1.7452 | 0 |  | 1.5
2017-08-31 | 20:15 | 1.7686 | 0 | 0 | 1.5 | 0 | 78.5011
2017-08-31 | 20:20 | 1.7397 | 0 |  | 1.5
2017-08-31 | 20:25 | 1.7327 | 0 |  | 1.5
2017-08-31 | 20:30 | 1.7522 | 0 | 0 | 1.5 | 0 | 78.6894
2017-08-31 | 20:35 | 1.7397 | 0 |  | 1.5
2017-08-31 | 20:40 | 1.728 | 0 |  | 1.5
2017-08-31 | 20:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 78.802
2017-08-31 | 20:50 | 1.7241 | 0 |  | 1.5
2017-08-31 | 20:55 | 1.7725 | 0 |  | 1.5
2017-08-31 | 21:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 78.8661
2017-08-31 | 21:05 | -0.10418 | 0 |  | 1.5
2017-08-31 | 21:10 | -0.10496 | 0 |  | 1.5
2017-08-31 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 21:20 | -0.10496 | 0 |  | 1.5
2017-08-31 | 21:25 | -0.10496 | 0 |  | 1.5
2017-08-31 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 21:35 | -0.10418 | 0 |  | 1.5
2017-08-31 | 21:40 | -0.10652 | 0 |  | 1.5
2017-08-31 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 21:50 | -0.10652 | 0 |  | 1.5
2017-08-31 | 21:55 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 22:05 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:10 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 22:20 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:25 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 22:35 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:40 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 22:50 | -0.10652 | 0 |  | 1.5
2017-08-31 | 22:55 | -0.10652 | 0 |  | 1.5
2017-08-31 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 23:05 | -0.10652 | 0 |  | 1.5
2017-08-31 | 23:10 | -0.10652 | 0 |  | 1.5
2017-08-31 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 23:20 | -0.10652 | 0 |  | 1.5
2017-08-31 | 23:25 | -0.10574 | 0 |  | 1.5
2017-08-31 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 23:35 | -0.10574 | 0 |  | 1.5
2017-08-31 | 23:40 | -0.10574 | 0 |  | 1.5
2017-08-31 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-08-31 | 23:50 | -0.10574 | 0 |  | 1.5
2017-08-31 | 23:55 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 0:05 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:10 | -0.10652 | 0 |  | 1.5
2017-09-01 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 0:20 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:25 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 0:35 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:40 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 0:50 | -0.10574 | 0 |  | 1.5
2017-09-01 | 0:55 | -0.10496 | 0 |  | 1.5
2017-09-01 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 1:05 | -0.10496 | 0 |  | 1.5
2017-09-01 | 1:10 | -0.10496 | 0 |  | 1.5
2017-09-01 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 1:20 | -0.10886 | 0 |  | 1.5
2017-09-01 | 1:25 | -0.10886 | 0 |  | 1.5
2017-09-01 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 1:35 | -0.10886 | 0 |  | 1.5
2017-09-01 | 1:40 | -0.10886 | 0 |  | 1.5
2017-09-01 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 1:50 | -0.10808 | 0 |  | 1.5
2017-09-01 | 1:55 | -0.10808 | 0 |  | 1.5
2017-09-01 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 2:05 | -0.10808 | 0 |  | 1.5
2017-09-01 | 2:10 | -0.10886 | 0 |  | 1.5
2017-09-01 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 2:20 | -0.10886 | 0 |  | 1.5
2017-09-01 | 2:25 | -0.10886 | 0 |  | 1.5
2017-09-01 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 2:35 | -0.10886 | 0 |  | 1.5
2017-09-01 | 2:40 | -0.10886 | 0 |  | 1.5
2017-09-01 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 2:50 | -0.10886 | 0 |  | 1.5
2017-09-01 | 2:55 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 3:05 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:10 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 3:20 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:25 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 3:35 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:40 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 3:50 | -0.10886 | 0 |  | 1.5
2017-09-01 | 3:55 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 4:05 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:10 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 4:20 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:25 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 4:35 | -0.11198 | 0 |  | 1.5
2017-09-01 | 4:40 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 4:50 | -0.10886 | 0 |  | 1.5
2017-09-01 | 4:55 | -0.10886 | 0 |  | 1.5
2017-09-01 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 5:05 | 2.0455 | 0 |  | 1.5
2017-09-01 | 5:10 | 2.1352 | 0 |  | 1.5
2017-09-01 | 5:15 | 2.0096 | 0 | 0 | 1.5 | 0 | 91.6766
2017-09-01 | 5:20 | 1.973 | 0 |  | 1.5
2017-09-01 | 5:25 | 1.98 | 0 |  | 1.5
2017-09-01 | 5:30 | 1.9262 | 0 | 0 | 1.5 | 0 | 85.7558
2017-09-01 | 5:35 | 1.8794 | 0 |  | 1.5
2017-09-01 | 5:40 | 1.8848 | 0 |  | 1.5
2017-09-01 | 5:45 | 1.8645 | 0 | 0 | 1.5 | 0 | 82.2401
2017-09-01 | 5:50 | 1.8014 | 0 |  | 1.5
2017-09-01 | 5:55 | 1.7912 | 0 |  | 1.5
2017-09-01 | 6:00 | 1.8232 | 0 | 0 | 1.5 | 0 | 80.5363
2017-09-01 | 6:05 | 1.7897 | 0 |  | 1.5
2017-09-01 | 6:10 | 1.7975 | 0 |  | 1.5
2017-09-01 | 6:15 | 1.7889 | 0 | 0 | 1.5 | 0 | 79.5101
2017-09-01 | 6:20 | 1.76 | 0 |  | 1.5
2017-09-01 | 6:25 | 1.7624 | 0 |  | 1.5
2017-09-01 | 6:30 | 1.7826 | 0 | 0 | 1.5 | 0 | 78.9795
2017-09-01 | 6:35 | 1.792 | 0 |  | 1.5
2017-09-01 | 6:40 | 1.7834 | 0 |  | 1.5
2017-09-01 | 6:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 78.4435
2017-09-01 | 6:50 | 1.7561 | 0 |  | 1.5
2017-09-01 | 6:55 | 1.7538 | 0 |  | 1.5
2017-09-01 | 7:00 | 1.7608 | 0 | 0 | 1.5 | 0 | 78.0953
2017-09-01 | 7:05 | 1.7803 | 0 |  | 1.5
2017-09-01 | 7:10 | 1.7624 | 0 |  | 1.5
2017-09-01 | 7:15 | 1.7249 | 0 | 0 | 1.5 | 0 | 77.9614
2017-09-01 | 7:20 | 1.714 | 0 |  | 1.5
2017-09-01 | 7:25 | 1.7413 | 0 |  | 1.5
2017-09-01 | 7:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.29
2017-09-01 | 7:35 | 1.7335 | 0 |  | 1.5
2017-09-01 | 7:40 | 1.7382 | 0 |  | 1.5
2017-09-01 | 7:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 78.645
2017-09-01 | 7:50 | 1.7725 | 0 |  | 1.5
2017-09-01 | 7:55 | 1.7499 | 0 |  | 1.5
2017-09-01 | 8:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.7285
2017-09-01 | 8:05 | 1.7226 | 0 |  | 1.5
2017-09-01 | 8:10 | 1.7241 | 0 |  | 1.5
2017-09-01 | 8:15 | 1.7405 | 0 | 0 | 1.5 | 0 | 79.1133
2017-09-01 | 8:20 | 1.7405 | 0 |  | 1.5
2017-09-01 | 8:25 | 1.7397 | 0 |  | 1.5
2017-09-01 | 8:30 | 1.7288 | 0 | 0 | 1.5 | 0 | 79.2809
2017-09-01 | 8:35 | 1.7335 | 0 |  | 1.5
2017-09-01 | 8:40 | 1.7335 | 0 |  | 1.5
2017-09-01 | 8:45 | 1.7452 | 0 | 0 | 1.5 | 0 | 79.3384
2017-09-01 | 8:50 | 1.7319 | 0 |  | 1.5
2017-09-01 | 8:55 | 1.7507 | 0 |  | 1.5
2017-09-01 | 9:00 | 1.7483 | 0 | 0 | 1.5 | 0 | 79.6001
2017-09-01 | 9:05 | 1.7616 | 0 |  | 1.5
2017-09-01 | 9:10 | 1.7491 | 0 |  | 1.5
2017-09-01 | 9:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 79.6472
2017-09-01 | 9:20 | 1.728 | 0 |  | 1.5
2017-09-01 | 9:25 | 1.746 | 0 |  | 1.5
2017-09-01 | 9:30 | 1.7171 | 0 | 0 | 1.5 | 0 | 80.1869
2017-09-01 | 9:35 | 1.7421 | 0 |  | 1.5
2017-09-01 | 9:40 | 1.7709 | 0 |  | 1.5
2017-09-01 | 9:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 80.3998
2017-09-01 | 9:50 | 1.7179 | 0 |  | 1.5
2017-09-01 | 9:55 | 1.7577 | 0 |  | 1.5
2017-09-01 | 10:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 80.6976
2017-09-01 | 10:05 | 1.7288 | 0 |  | 1.5
2017-09-01 | 10:10 | 1.7257 | 0 |  | 1.5
2017-09-01 | 10:15 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.0252
2017-09-01 | 10:20 | 1.7538 | 0 |  | 1.5
2017-09-01 | 10:25 | 1.7608 | 0 |  | 1.5
2017-09-01 | 10:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 81.3109
2017-09-01 | 10:35 | 1.7226 | 0 |  | 1.5
2017-09-01 | 10:40 | 1.7351 | 0 |  | 1.5
2017-09-01 | 10:45 | 1.6844 | 0 | 0 | 1.5 | 0 | 81.9972
2017-09-01 | 10:50 | 1.7499 | 0 |  | 1.5
2017-09-01 | 10:55 | 1.7304 | 0 |  | 1.5
2017-09-01 | 11:00 | 1.6929 | 0 | 0 | 1.5 | 0 | 82.9987
2017-09-01 | 11:05 | 1.7187 | 0 |  | 1.5
2017-09-01 | 11:10 | 1.7109 | 0 |  | 1.5
2017-09-01 | 11:15 | 1.6984 | 0 | 0 | 1.5 | 0 | 84.1187
2017-09-01 | 11:20 | 1.7046 | 0 |  | 1.5
2017-09-01 | 11:25 | 1.6859 | 0 |  | 1.5
2017-09-01 | 11:30 | 1.707 | 0 | 0 | 1.5 | 0 | 85.5998
2017-09-01 | 11:35 | 1.7163 | 0 |  | 1.5
2017-09-01 | 11:40 | 1.7304 | 0 |  | 1.5
2017-09-01 | 11:45 | 1.7234 | 0 | 0 | 1.5 | 0 | 86.373
2017-09-01 | 11:50 | 1.739 | 0 |  | 1.5
2017-09-01 | 11:55 | 1.7296 | 0 |  | 1.5
2017-09-01 | 12:00 | 1.7234 | 0 | 0 | 1.5 | 0 | 86.7986
2017-09-01 | 12:05 | 1.7046 | 0 |  | 1.5
2017-09-01 | 12:10 | 1.7039 | 0 |  | 1.5
2017-09-01 | 12:15 | 1.7241 | 0 | 0 | 1.5 | 0 | 87.6345
2017-09-01 | 12:20 | 1.7226 | 0 |  | 1.5
2017-09-01 | 12:25 | 1.728 | 0 |  | 1.5
2017-09-01 | 12:30 | 1.7366 | 0 | 0 | 1.5 | 0 | 88.3559
2017-09-01 | 12:35 | 1.7265 | 0 |  | 1.5
2017-09-01 | 12:40 | 1.746 | 0 |  | 1.5
2017-09-01 | 12:45 | 1.7452 | 0 | 0 | 1.5 | 0 | 88.5914
2017-09-01 | 12:50 | 1.7608 | 0 |  | 1.5
2017-09-01 | 12:55 | 1.7546 | 0 |  | 1.5
2017-09-01 | 13:00 | 1.7709 | 0 | 0 | 1.5 | 0 | 88.816
2017-09-01 | 13:05 | 1.7405 | 0 |  | 1.5
2017-09-01 | 13:10 | 1.7257 | 0 |  | 1.5
2017-09-01 | 13:15 | 1.7405 | 0 | 0 | 1.5 | 0 | 89.1485
2017-09-01 | 13:20 | 1.7257 | 0 |  | 1.5
2017-09-01 | 13:25 | 1.746 | 0 |  | 1.5
2017-09-01 | 13:30 | 1.714 | 0 | 0 | 1.5 | 0 | 89.6406
2017-09-01 | 13:35 | 1.7351 | 0 |  | 1.5
2017-09-01 | 13:40 | 1.7156 | 0 |  | 1.5
2017-09-01 | 13:45 | 1.7343 | 0 | 0 | 1.5 | 0 | 90.1632
2017-09-01 | 13:50 | 1.7436 | 0 |  | 1.5
2017-09-01 | 13:55 | 1.7366 | 0 |  | 1.5
2017-09-01 | 14:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 90.2618
2017-09-01 | 14:05 | 1.7577 | 0 |  | 1.5
2017-09-01 | 14:10 | 1.7452 | 0 |  | 1.5
2017-09-01 | 14:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 90.3962
2017-09-01 | 14:20 | 1.7647 | 0 |  | 1.5
2017-09-01 | 14:25 | 1.7663 | 0 |  | 1.5
2017-09-01 | 14:30 | 1.7421 | 0 | 0 | 1.5 | 0 | 90.5742
2017-09-01 | 14:35 | 1.7218 | 0 |  | 1.5
2017-09-01 | 14:40 | 1.6929 | 0 |  | 1.5
2017-09-01 | 14:45 | 1.7085 | 0 | 0 | 1.5 | 0 | 91.7814
2017-09-01 | 14:50 | 1.7023 | 0 |  | 1.5
2017-09-01 | 14:55 | 1.7023 | 0 |  | 1.5
2017-09-01 | 15:00 | 1.7148 | 0 | 0 | 1.5 | 0 | 92.7944
2017-09-01 | 15:05 | 1.7514 | 0 |  | 1.5
2017-09-01 | 15:10 | 1.7764 | 0 |  | 1.5
2017-09-01 | 15:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 92.8781
2017-09-01 | 15:20 | 1.7717 | 0 |  | 1.5
2017-09-01 | 15:25 | 1.7546 | 0 |  | 1.5
2017-09-01 | 15:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 92.4268
2017-09-01 | 15:35 | 1.7717 | 0 |  | 1.5
2017-09-01 | 15:40 | 1.7928 | 0 |  | 1.5
2017-09-01 | 15:45 | 1.7881 | 0 | 0 | 1.5 | 0 | 91.6128
2017-09-01 | 15:50 | 1.7811 | 0 |  | 1.5
2017-09-01 | 15:55 | 1.7975 | 0 |  | 1.5
2017-09-01 | 16:00 | 1.7967 | 0 | 0 | 1.5 | 0 | 90.4337
2017-09-01 | 16:05 | 1.8138 | 0 |  | 1.5
2017-09-01 | 16:10 | 1.8084 | 0 |  | 1.5
2017-09-01 | 16:15 | 1.8107 | 0 | 0 | 1.5 | 0 | 88.804
2017-09-01 | 16:20 | 1.8123 | 0 |  | 1.5
2017-09-01 | 16:25 | 1.8045 | 0 |  | 1.5
2017-09-01 | 16:30 | 1.7975 | 0 | 0 | 1.5 | 0 | 87.3791
2017-09-01 | 16:35 | 1.7858 | 0 |  | 1.5
2017-09-01 | 16:40 | 1.76 | 0 |  | 1.5
2017-09-01 | 16:45 | 1.8092 | 0 | 0 | 1.5 | 0 | 86.4513
2017-09-01 | 16:50 | 1.7834 | 0 |  | 1.5
2017-09-01 | 16:55 | 1.7756 | 0 |  | 1.5
2017-09-01 | 17:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 85.515
2017-09-01 | 17:05 | 1.7795 | 0 |  | 1.5
2017-09-01 | 17:10 | 1.76 | 0 |  | 1.5
2017-09-01 | 17:15 | 1.7803 | 0 | 0 | 1.5 | 0 | 84.8499
2017-09-01 | 17:20 | 1.7858 | 0 |  | 1.5
2017-09-01 | 17:25 | 1.8123 | 0 |  | 1.5
2017-09-01 | 17:30 | 1.8014 | 0 | 0 | 1.5 | 0 | 83.606
2017-09-01 | 17:35 | 1.7842 | 0 |  | 1.5
2017-09-01 | 17:40 | 1.7865 | 0 |  | 1.5
2017-09-01 | 17:45 | 1.8006 | 0 | 0 | 1.5 | 0 | 82.7467
2017-09-01 | 17:50 | 1.7733 | 0 |  | 1.5
2017-09-01 | 17:55 | 1.7772 | 0 |  | 1.5
2017-09-01 | 18:00 | 1.7873 | 0 | 0 | 1.5 | 0 | 82.1058
2017-09-01 | 18:05 | 1.7702 | 0 |  | 1.5
2017-09-01 | 18:10 | 1.767 | 0 |  | 1.5
2017-09-01 | 18:15 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.6395
2017-09-01 | 18:20 | 1.7436 | 0 |  | 1.5
2017-09-01 | 18:25 | 1.7678 | 0 |  | 1.5
2017-09-01 | 18:30 | 1.7858 | 0 | 0 | 1.5 | 0 | 81.1387
2017-09-01 | 18:35 | 1.7631 | 0 |  | 1.5
2017-09-01 | 18:40 | 1.7616 | 0 |  | 1.5
2017-09-01 | 18:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 80.682
2017-09-01 | 18:50 | 1.7483 | 0 |  | 1.5
2017-09-01 | 18:55 | 1.7702 | 0 |  | 1.5
2017-09-01 | 19:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 80.5666
2017-09-01 | 19:05 | 1.739 | 0 |  | 1.5
2017-09-01 | 19:10 | 1.7522 | 0 |  | 1.5
2017-09-01 | 19:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 80.4498
2017-09-01 | 19:20 | 1.7514 | 0 |  | 1.5
2017-09-01 | 19:25 | 1.7631 | 0 |  | 1.5
2017-09-01 | 19:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 80.3321
2017-09-01 | 19:35 | 1.7522 | 0 |  | 1.5
2017-09-01 | 19:40 | 1.7553 | 0 |  | 1.5
2017-09-01 | 19:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 80.0811
2017-09-01 | 19:50 | 1.7772 | 0 |  | 1.5
2017-09-01 | 19:55 | 1.7678 | 0 |  | 1.5
2017-09-01 | 20:00 | 1.7733 | 0 | 0 | 1.5 | 0 | 79.6187
2017-09-01 | 20:05 | 1.7748 | 0 |  | 1.5
2017-09-01 | 20:10 | 1.7826 | 0 |  | 1.5
2017-09-01 | 20:15 | 1.7881 | 0 | 0 | 1.5 | 0 | 79.184
2017-09-01 | 20:20 | 1.7585 | 0 |  | 1.5
2017-09-01 | 20:25 | 1.7436 | 0 |  | 1.5
2017-09-01 | 20:30 | 1.7148 | 0 | 0 | 1.5 | 0 | 79.2104
2017-09-01 | 20:35 | 1.746 | 0 |  | 1.5
2017-09-01 | 20:40 | 1.7304 | 0 |  | 1.5
2017-09-01 | 20:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 79.3622
2017-09-01 | 20:50 | 1.7382 | 0 |  | 1.5
2017-09-01 | 20:55 | 1.7405 | 0 |  | 1.5
2017-09-01 | 21:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 79.5973
2017-09-01 | 21:05 | -0.1034 | 0 |  | 1.5
2017-09-01 | 21:10 | -0.1034 | 0 |  | 1.5
2017-09-01 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 21:20 | -0.10574 | 0 |  | 1.5
2017-09-01 | 21:25 | -0.10496 | 0 |  | 1.5
2017-09-01 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-01 | 21:40 | -0.10496 | 0 |  | 1.5
2017-09-01 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 21:50 | -0.10574 | 0 |  | 1.5
2017-09-01 | 21:55 | -0.10574 | 0 |  | 1.5
2017-09-01 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 22:05 | -0.1073 | 0 |  | 1.5
2017-09-01 | 22:10 | -0.10574 | 0 |  | 1.5
2017-09-01 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 22:20 | -0.10574 | 0 |  | 1.5
2017-09-01 | 22:25 | -0.10574 | 0 |  | 1.5
2017-09-01 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 22:35 | -0.10496 | 0 |  | 1.5
2017-09-01 | 22:40 | -0.10496 | 0 |  | 1.5
2017-09-01 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 22:50 | -0.10496 | 0 |  | 1.5
2017-09-01 | 22:55 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 23:05 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:10 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 23:20 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:25 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 23:35 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:40 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-01 | 23:50 | -0.10496 | 0 |  | 1.5
2017-09-01 | 23:55 | -0.10496 | 0 |  | 1.5
2017-09-02 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-02 | 0:05 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:10 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-09-02 | 0:15 | -0.10418 | 0 |  | 1.5 |  | 0
2017-09-02 | 0:20 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:25 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0
2017-09-02 | 0:30 | -0.10418 | 0 |  | 1.5 |  | 0
2017-09-02 | 0:35 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:40 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0
2017-09-02 | 0:45 | -0.10418 | 0 |  | 1.5 |  | 0
2017-09-02 | 0:50 | -0.10418 | 0 |  | 1.5
2017-09-02 | 0:55 | -0.10418 | 0 |  | 1.5
2017-09-02 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0
2017-09-02 | 1:00 | -0.10418 | 0 |  | 1.5 |  | 0
2017-09-02 | 1:05 | -0.1034 | 0 |  | 1.5
2017-09-02 | 1:10 | -0.10418 | 0 |  | 1.5
2017-09-02 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-09-02 | 1:15 | -0.10418 | 0 |  | 1.5 |  | 0
2017-09-02 | 1:20 | -0.1073 | 0 |  | 1.5
2017-09-02 | 1:25 | -0.1073 | 0 |  | 1.5
2017-09-02 | 1:30 | -0.1073 | 0 | 0 | 1.5 | 0
2017-09-02 | 1:30 | -0.1073 | 0 |  | 1.5 |  | 0
2017-09-02 | 1:35 | -0.1073 | 0 |  | 1.5
2017-09-02 | 1:40 | -0.1073 | 0 |  | 1.5
2017-09-02 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0
2017-09-02 | 1:45 | -0.1073 | 0 |  | 1.5 |  | 0
2017-09-02 | 1:50 | -0.1073 | 0 |  | 1.5
2017-09-02 | 1:55 | -0.1073 | 0 |  | 1.5
2017-09-02 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 2:00 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 2:05 | -0.1073 | 0 |  | 1.5
2017-09-02 | 2:10 | -0.1073 | 0 |  | 1.5
2017-09-02 | 2:15 | -0.1073 | 0 | 0 | 1.5 | 0
2017-09-02 | 2:15 | -0.1073 | 0 |  | 1.5 |  | 0
2017-09-02 | 2:20 | -0.10808 | 0 |  | 1.5
2017-09-02 | 2:25 | -0.10808 | 0 |  | 1.5
2017-09-02 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 2:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 2:35 | -0.10808 | 0 |  | 1.5
2017-09-02 | 2:40 | -0.10808 | 0 |  | 1.5
2017-09-02 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 2:45 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-02 | 2:55 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 3:00 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 3:05 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:10 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 3:15 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 3:20 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:25 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 3:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 3:35 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:40 | -0.10886 | 0 |  | 1.5
2017-09-02 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 3:45 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 3:50 | -0.10808 | 0 |  | 1.5
2017-09-02 | 3:55 | -0.10808 | 0 |  | 1.5
2017-09-02 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 4:00 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 4:05 | -0.10808 | 0 |  | 1.5
2017-09-02 | 4:10 | -0.10808 | 0 |  | 1.5
2017-09-02 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 4:15 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 4:20 | -0.10808 | 0 |  | 1.5
2017-09-02 | 4:25 | -0.11276 | 0 |  | 1.5
2017-09-02 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 4:30 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 4:35 | -0.10886 | 0 |  | 1.5
2017-09-02 | 4:40 | -0.10808 | 0 |  | 1.5
2017-09-02 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 4:45 | -0.10808 | 0 |  | 1.5 |  | 0
2017-09-02 | 4:50 | -0.10808 | 0 |  | 1.5
2017-09-02 | 4:55 | -0.10808 | 0 |  | 1.5
2017-09-02 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0
2017-09-02 | 5:00 | -0.10808 | 0 |  | 1.5 |  | 25
2017-09-02 | 5:05 | 1.9839 | 0 |  | 1.5
2017-09-02 | 5:10 | 2.1149 | 0 |  | 1.5
2017-09-02 | 5:15 | 1.9542 | 0 | 0 | 1.5 | 0
2017-09-02 | 5:15 | 1.9542 | 0 |  | 1.5 |  | 93.009
2017-09-02 | 5:20 | 1.8591 | 0 |  | 1.5
2017-09-02 | 5:25 | 1.8817 | 0 |  | 1.5
2017-09-02 | 5:30 | 1.8825 | 0 | 0 | 1.5 | 0
2017-09-02 | 5:30 | 1.8825 | 0 |  | 1.5 |  | 89.0392
2017-09-02 | 5:35 | 1.9035 | 0 |  | 1.5
2017-09-02 | 5:40 | 1.8622 | 0 |  | 1.5
2017-09-02 | 5:45 | 1.8645 | 0 | 0 | 1.5 | 0
2017-09-02 | 5:45 | 1.8645 | 0 |  | 1.5 |  | 85.3862
2017-09-02 | 5:50 | 1.8021 | 0 |  | 1.5
2017-09-02 | 5:55 | 1.817 | 0 |  | 1.5
2017-09-02 | 6:00 | 1.7975 | 0 | 0 | 1.5 | 0
2017-09-02 | 6:00 | 1.7975 | 0 |  | 1.5 |  | 83.5447
2017-09-02 | 6:05 | 1.7717 | 0 |  | 1.5
2017-09-02 | 6:10 | 1.806 | 0 |  | 1.5
2017-09-02 | 6:15 | 1.7561 | 0 | 0 | 1.5 | 0
2017-09-02 | 6:15 | 1.7561 | 0 |  | 1.5 |  | 82.2516
2017-09-02 | 6:20 | 1.7943 | 0 |  | 1.5
2017-09-02 | 6:25 | 1.7678 | 0 |  | 1.5
2017-09-02 | 6:30 | 1.7795 | 0 | 0 | 1.5 | 0
2017-09-02 | 6:30 | 1.7795 | 0 |  | 1.5 |  | 81.3589
2017-09-02 | 6:35 | 1.778 | 0 |  | 1.5
2017-09-02 | 6:40 | 1.7452 | 0 |  | 1.5
2017-09-02 | 6:45 | 1.7522 | 0 | 0 | 1.5 | 0
2017-09-02 | 6:45 | 1.7522 | 0 |  | 1.5 |  | 80.8283
2017-09-02 | 6:50 | 1.7663 | 0 |  | 1.5
2017-09-02 | 6:55 | 1.7663 | 0 |  | 1.5
2017-09-02 | 7:00 | 1.7865 | 0 | 0 | 1.5 | 0
2017-09-02 | 7:00 | 1.7865 | 0 |  | 1.5 |  | 80.0146
2017-09-02 | 7:05 | 1.7639 | 0 |  | 1.5
2017-09-02 | 7:10 | 1.7655 | 0 |  | 1.5
2017-09-02 | 7:15 | 1.7585 | 0 | 0 | 1.5 | 0
2017-09-02 | 7:15 | 1.7585 | 0 |  | 1.5 |  | 79.4456
2017-09-02 | 7:20 | 1.7569 | 0 |  | 1.5
2017-09-02 | 7:25 | 1.7577 | 0 |  | 1.5
2017-09-02 | 7:30 | 1.7514 | 0 | 0 | 1.5 | 0
2017-09-02 | 7:30 | 1.7514 | 0 |  | 1.5 |  | 79.1522
2017-09-02 | 7:35 | 1.7452 | 0 |  | 1.5
2017-09-02 | 7:40 | 1.7694 | 0 |  | 1.5
2017-09-02 | 7:45 | 1.7382 | 0 | 0 | 1.5 | 0
2017-09-02 | 7:45 | 1.7382 | 0 |  | 1.5 |  | 78.9539
2017-09-02 | 7:50 | 1.7631 | 0 |  | 1.5
2017-09-02 | 7:55 | 1.7733 | 0 |  | 1.5
2017-09-02 | 8:00 | 1.7358 | 0 | 0 | 1.5 | 0
2017-09-02 | 8:00 | 1.7358 | 0 |  | 1.5 |  | 78.6279
2017-09-02 | 8:05 | 1.7795 | 0 |  | 1.5
2017-09-02 | 8:10 | 1.7288 | 0 |  | 1.5
2017-09-02 | 8:15 | 1.7694 | 0 | 0 | 1.5 | 0
2017-09-02 | 8:15 | 1.7694 | 0 |  | 1.5 |  | 78.3504
2017-09-02 | 8:20 | 1.7569 | 0 |  | 1.5
2017-09-02 | 8:25 | 1.7514 | 0 |  | 1.5
2017-09-02 | 8:30 | 1.7655 | 0 | 0 | 1.5 | 0
2017-09-02 | 8:30 | 1.7655 | 0 |  | 1.5 |  | 78.2447
2017-09-02 | 8:35 | 1.721 | 0 |  | 1.5
2017-09-02 | 8:40 | 1.7616 | 0 |  | 1.5
2017-09-02 | 8:45 | 1.7499 | 0 | 0 | 1.5 | 0
2017-09-02 | 8:45 | 1.7499 | 0 |  | 1.5 |  | 78.3024
2017-09-02 | 8:50 | 1.76 | 0 |  | 1.5
2017-09-02 | 8:55 | 1.7897 | 0 |  | 1.5
2017-09-02 | 9:00 | 1.76 | 0 | 0 | 1.5 | 0
2017-09-02 | 9:00 | 1.76 | 0 |  | 1.5 |  | 78.2577
2017-09-02 | 9:05 | 1.7304 | 0 |  | 1.5
2017-09-02 | 9:10 | 1.7444 | 0 |  | 1.5
2017-09-02 | 9:15 | 1.7553 | 0 | 0 | 1.5 | 0
2017-09-02 | 9:15 | 1.7553 | 0 |  | 1.5 |  | 78.241
2017-09-02 | 9:20 | 1.7366 | 0 |  | 1.5
2017-09-02 | 9:25 | 1.7257 | 0 |  | 1.5
2017-09-02 | 9:30 | 1.7717 | 0 | 0 | 1.5 | 0
2017-09-02 | 9:30 | 1.7717 | 0 |  | 1.5 |  | 78.222
2017-09-02 | 9:35 | 1.7382 | 0 |  | 1.5
2017-09-02 | 9:40 | 1.7585 | 0 |  | 1.5
2017-09-02 | 9:45 | 1.7312 | 0 | 0 | 1.5 | 0
2017-09-02 | 9:45 | 1.7312 | 0 |  | 1.5 |  | 78.4111
2017-09-02 | 9:50 | 1.7639 | 0 |  | 1.5
2017-09-02 | 9:55 | 1.7429 | 0 |  | 1.5
2017-09-02 | 10:00 | 1.7468 | 0 | 0 | 1.5 | 0
2017-09-02 | 10:00 | 1.7468 | 0 |  | 1.5 |  | 78.5309
2017-09-02 | 10:05 | 1.753 | 0 |  | 1.5
2017-09-02 | 10:10 | 1.7382 | 0 |  | 1.5
2017-09-02 | 10:15 | 1.7304 | 0 | 0 | 1.5 | 0
2017-09-02 | 10:15 | 1.7304 | 0 |  | 1.5 |  | 78.7468
2017-09-02 | 10:20 | 1.7561 | 0 |  | 1.5
2017-09-02 | 10:25 | 1.7436 | 0 |  | 1.5
2017-09-02 | 10:30 | 1.7343 | 0 | 0 | 1.5 | 0
2017-09-02 | 10:30 | 1.7343 | 0 |  | 1.5 |  | 78.9741
2017-09-02 | 10:35 | 1.7351 | 0 |  | 1.5
2017-09-02 | 10:40 | 1.7491 | 0 |  | 1.5
2017-09-02 | 10:45 | 1.7343 | 0 | 0 | 1.5 | 0
2017-09-02 | 10:45 | 1.7343 | 0 |  | 1.5 |  | 79.2704
2017-09-02 | 10:50 | 1.7475 | 0 |  | 1.5
2017-09-02 | 10:55 | 1.6968 | 0 |  | 1.5
2017-09-02 | 11:00 | 1.7015 | 0 | 0 | 1.5 | 0
2017-09-02 | 11:00 | 1.7015 | 0 |  | 1.5 |  | 80.09
2017-09-02 | 11:05 | 1.7101 | 0 |  | 1.5
2017-09-02 | 11:10 | 1.7101 | 0 |  | 1.5
2017-09-02 | 11:15 | 1.6828 | 0 | 0 | 1.5 | 0
2017-09-02 | 11:15 | 1.6828 | 0 |  | 1.5 |  | 81.1944
2017-09-02 | 11:20 | 1.6976 | 0 |  | 1.5
2017-09-02 | 11:25 | 1.739 | 0 |  | 1.5
2017-09-02 | 11:30 | 1.7195 | 0 | 0 | 1.5 | 0
2017-09-02 | 11:30 | 1.7195 | 0 |  | 1.5 |  | 82.0075
2017-09-02 | 11:35 | 1.739 | 0 |  | 1.5
2017-09-02 | 11:40 | 1.7093 | 0 |  | 1.5
2017-09-02 | 11:45 | 1.7241 | 0 | 0 | 1.5 | 0
2017-09-02 | 11:45 | 1.7241 | 0 |  | 1.5 |  | 82.9588
2017-09-02 | 11:50 | 1.7085 | 0 |  | 1.5
2017-09-02 | 11:55 | 1.739 | 0 |  | 1.5
2017-09-02 | 12:00 | 1.6883 | 0 | 0 | 1.5 | 0
2017-09-02 | 12:00 | 1.6883 | 0 |  | 1.5 |  | 84.051
2017-09-02 | 12:05 | 1.7171 | 0 |  | 1.5
2017-09-02 | 12:10 | 1.7327 | 0 |  | 1.5
2017-09-02 | 12:15 | 1.7429 | 0 | 0 | 1.5 | 0
2017-09-02 | 12:15 | 1.7429 | 0 |  | 1.5 |  | 84.8092
2017-09-02 | 12:20 | 1.7491 | 0 |  | 1.5
2017-09-02 | 12:25 | 1.7522 | 0 |  | 1.5
2017-09-02 | 12:30 | 1.7436 | 0 | 0 | 1.5 | 0
2017-09-02 | 12:30 | 1.7436 | 0 |  | 1.5 |  | 85.1265
2017-09-02 | 12:35 | 1.7405 | 0 |  | 1.5
2017-09-02 | 12:40 | 1.7639 | 0 |  | 1.5
2017-09-02 | 12:45 | 1.7241 | 0 | 0 | 1.5 | 0
2017-09-02 | 12:45 | 1.7241 | 0 |  | 1.5 |  | 85.4259
2017-09-02 | 12:50 | 1.7468 | 0 |  | 1.5
2017-09-02 | 12:55 | 1.7585 | 0 |  | 1.5
2017-09-02 | 13:00 | 1.7273 | 0 | 0 | 1.5 | 0
2017-09-02 | 13:00 | 1.7273 | 0 |  | 1.5 |  | 85.6458
2017-09-02 | 13:05 | 1.7608 | 0 |  | 1.5
2017-09-02 | 13:10 | 1.7343 | 0 |  | 1.5
2017-09-02 | 13:15 | 1.7413 | 0 | 0 | 1.5 | 0
2017-09-02 | 13:15 | 1.7413 | 0 |  | 1.5 |  | 85.8257
2017-09-02 | 13:20 | 1.7421 | 0 |  | 1.5
2017-09-02 | 13:25 | 1.7257 | 0 |  | 1.5
2017-09-02 | 13:30 | 1.7538 | 0 | 0 | 1.5 | 0
2017-09-02 | 13:30 | 1.7538 | 0 |  | 1.5 |  | 86.0562
2017-09-02 | 13:35 | 1.7592 | 0 |  | 1.5
2017-09-02 | 13:40 | 1.7351 | 0 |  | 1.5
2017-09-02 | 13:45 | 1.7499 | 0 | 0 | 1.5 | 0
2017-09-02 | 13:45 | 1.7499 | 0 |  | 1.5 |  | 86.1496
2017-09-02 | 13:50 | 1.7257 | 0 |  | 1.5
2017-09-02 | 13:55 | 1.7592 | 0 |  | 1.5
2017-09-02 | 14:00 | 1.7577 | 0 | 0 | 1.5 | 0
2017-09-02 | 14:00 | 1.7577 | 0 |  | 1.5 |  | 86.264
2017-09-02 | 14:05 | 1.721 | 0 |  | 1.5
2017-09-02 | 14:10 | 1.7468 | 0 |  | 1.5
2017-09-02 | 14:15 | 1.728 | 0 | 0 | 1.5 | 0
2017-09-02 | 14:15 | 1.728 | 0 |  | 1.5 |  | 86.5874
2017-09-02 | 14:20 | 1.7444 | 0 |  | 1.5
2017-09-02 | 14:25 | 1.7436 | 0 |  | 1.5
2017-09-02 | 14:30 | 1.7241 | 0 | 0 | 1.5 | 0
2017-09-02 | 14:30 | 1.7241 | 0 |  | 1.5 |  | 86.7901
2017-09-02 | 14:35 | 1.7655 | 0 |  | 1.5
2017-09-02 | 14:40 | 1.7335 | 0 |  | 1.5
2017-09-02 | 14:45 | 1.7249 | 0 | 0 | 1.5 | 0
2017-09-02 | 14:45 | 1.7249 | 0 |  | 1.5 |  | 87.2392
2017-09-02 | 14:50 | 1.7023 | 0 |  | 1.5
2017-09-02 | 14:55 | 1.7163 | 0 |  | 1.5
2017-09-02 | 15:00 | 1.7179 | 0 | 0 | 1.5 | 0
2017-09-02 | 15:00 | 1.7179 | 0 |  | 1.5 |  | 88.0281
2017-09-02 | 15:05 | 1.7226 | 0 |  | 1.5
2017-09-02 | 15:10 | 1.7561 | 0 |  | 1.5
2017-09-02 | 15:15 | 1.7374 | 0 | 0 | 1.5 | 0
2017-09-02 | 15:15 | 1.7374 | 0 |  | 1.5 |  | 88.3063
2017-09-02 | 15:20 | 1.7405 | 0 |  | 1.5
2017-09-02 | 15:25 | 1.714 | 0 |  | 1.5
2017-09-02 | 15:30 | 1.7343 | 0 | 0 | 1.5 | 0
2017-09-02 | 15:30 | 1.7343 | 0 |  | 1.5 |  | 88.8323
2017-09-02 | 15:35 | 1.739 | 0 |  | 1.5
2017-09-02 | 15:40 | 1.746 | 0 |  | 1.5
2017-09-02 | 15:45 | 1.7507 | 0 | 0 | 1.5 | 0
2017-09-02 | 15:45 | 1.7507 | 0 |  | 1.5 |  | 89.2594
2017-09-02 | 15:50 | 1.739 | 0 |  | 1.5
2017-09-02 | 15:55 | 1.7421 | 0 |  | 1.5
2017-09-02 | 16:00 | 1.7405 | 0 | 0 | 1.5 | 0
2017-09-02 | 16:00 | 1.7405 | 0 |  | 1.5 |  | 89.5137
2017-09-02 | 16:05 | 1.767 | 0 |  | 1.5
2017-09-02 | 16:10 | 1.753 | 0 |  | 1.5
2017-09-02 | 16:15 | 1.7951 | 0 | 0 | 1.5 | 0
2017-09-02 | 16:15 | 1.7951 | 0 |  | 1.5 |  | 89.2047
2017-09-02 | 16:20 | 1.76 | 0 |  | 1.5
2017-09-02 | 16:25 | 1.7975 | 0 |  | 1.5
2017-09-02 | 16:30 | 1.7787 | 0 | 0 | 1.5 | 0
2017-09-02 | 16:30 | 1.7787 | 0 |  | 1.5 |  | 88.5212
2017-09-02 | 16:35 | 1.7842 | 0 |  | 1.5
2017-09-02 | 16:40 | 1.8084 | 0 |  | 1.5
2017-09-02 | 16:45 | 1.7694 | 0 | 0 | 1.5 | 0
2017-09-02 | 16:45 | 1.7694 | 0 |  | 1.5 |  | 87.3378
2017-09-02 | 16:50 | 1.7795 | 0 |  | 1.5
2017-09-02 | 16:55 | 1.7709 | 0 |  | 1.5
2017-09-02 | 17:00 | 1.7647 | 0 | 0 | 1.5 | 0
2017-09-02 | 17:00 | 1.7647 | 0 |  | 1.5 |  | 86.4983
2017-09-02 | 17:05 | 1.7912 | 0 |  | 1.5
2017-09-02 | 17:10 | 1.7741 | 0 |  | 1.5
2017-09-02 | 17:15 | 1.7741 | 0 | 0 | 1.5 | 0
2017-09-02 | 17:15 | 1.7741 | 0 |  | 1.5 |  | 85.7613
2017-09-02 | 17:20 | 1.7826 | 0 |  | 1.5
2017-09-02 | 17:25 | 1.7717 | 0 |  | 1.5
2017-09-02 | 17:30 | 1.8138 | 0 | 0 | 1.5 | 0
2017-09-02 | 17:30 | 1.8138 | 0 |  | 1.5 |  | 84.8969
2017-09-02 | 17:35 | 1.792 | 0 |  | 1.5
2017-09-02 | 17:40 | 1.7826 | 0 |  | 1.5
2017-09-02 | 17:45 | 1.7624 | 0 | 0 | 1.5 | 0
2017-09-02 | 17:45 | 1.7624 | 0 |  | 1.5 |  | 84.1996
2017-09-02 | 17:50 | 1.7663 | 0 |  | 1.5
2017-09-02 | 17:55 | 1.7592 | 0 |  | 1.5
2017-09-02 | 18:00 | 1.7834 | 0 | 0 | 1.5 | 0
2017-09-02 | 18:00 | 1.7834 | 0 |  | 1.5 |  | 83.6427
2017-09-02 | 18:05 | 1.753 | 0 |  | 1.5
2017-09-02 | 18:10 | 1.7499 | 0 |  | 1.5
2017-09-02 | 18:15 | 1.7733 | 0 | 0 | 1.5 | 0
2017-09-02 | 18:15 | 1.7733 | 0 |  | 1.5 |  | 83.1762
2017-09-02 | 18:20 | 1.7468 | 0 |  | 1.5
2017-09-02 | 18:25 | 1.7616 | 0 |  | 1.5
2017-09-02 | 18:30 | 1.7444 | 0 | 0 | 1.5 | 0
2017-09-02 | 18:30 | 1.7444 | 0 |  | 1.5 |  | 82.9695
2017-09-02 | 18:35 | 1.7733 | 0 |  | 1.5
2017-09-02 | 18:40 | 1.76 | 0 |  | 1.5
2017-09-02 | 18:45 | 1.7546 | 0 | 0 | 1.5 | 0
2017-09-02 | 18:45 | 1.7546 | 0 |  | 1.5 |  | 82.7519
2017-09-02 | 18:50 | 1.7819 | 0 |  | 1.5
2017-09-02 | 18:55 | 1.7429 | 0 |  | 1.5
2017-09-02 | 19:00 | 1.7616 | 0 | 0 | 1.5 | 0
2017-09-02 | 19:00 | 1.7616 | 0 |  | 1.5 |  | 82.3793
2017-09-02 | 19:05 | 1.7507 | 0 |  | 1.5
2017-09-02 | 19:10 | 1.7678 | 0 |  | 1.5
2017-09-02 | 19:15 | 1.7663 | 0 | 0 | 1.5 | 0
2017-09-02 | 19:15 | 1.7663 | 0 |  | 1.5 |  | 82.0363
2017-09-02 | 19:20 | 1.7702 | 0 |  | 1.5
2017-09-02 | 19:25 | 1.7826 | 0 |  | 1.5
2017-09-02 | 19:30 | 1.7491 | 0 | 0 | 1.5 | 0
2017-09-02 | 19:30 | 1.7491 | 0 |  | 1.5 |  | 81.6829
2017-09-02 | 19:35 | 1.7834 | 0 |  | 1.5
2017-09-02 | 19:40 | 1.7686 | 0 |  | 1.5
2017-09-02 | 19:45 | 1.7374 | 0 | 0 | 1.5 | 0
2017-09-02 | 19:45 | 1.7374 | 0 |  | 1.5 |  | 81.4633
2017-09-02 | 19:50 | 1.7585 | 0 |  | 1.5
2017-09-02 | 19:55 | 1.7405 | 0 |  | 1.5
2017-09-02 | 20:00 | 1.7663 | 0 | 0 | 1.5 | 0
2017-09-02 | 20:00 | 1.7663 | 0 |  | 1.5 |  | 81.2953
2017-09-02 | 20:05 | 1.7811 | 0 |  | 1.5
2017-09-02 | 20:10 | 1.7733 | 0 |  | 1.5
2017-09-02 | 20:15 | 1.7553 | 0 | 0 | 1.5 | 0
2017-09-02 | 20:15 | 1.7553 | 0 |  | 1.5 |  | 80.8578
2017-09-02 | 20:20 | 1.7569 | 0 |  | 1.5
2017-09-02 | 20:25 | 1.76 | 0 |  | 1.5
2017-09-02 | 20:30 | 1.746 | 0 | 0 | 1.5 | 0
2017-09-02 | 20:30 | 1.746 | 0 |  | 1.5 |  | 80.5311
2017-09-02 | 20:35 | 1.7631 | 0 |  | 1.5
2017-09-02 | 20:40 | 1.7468 | 0 |  | 1.5
2017-09-02 | 20:45 | 1.7834 | 0 | 0 | 1.5 | 0
2017-09-02 | 20:45 | 1.7834 | 0 |  | 1.5 |  | 80.2929
2017-09-02 | 20:50 | 1.7491 | 0 |  | 1.5
2017-09-02 | 20:55 | 1.7873 | 0 |  | 1.5
2017-09-02 | 21:00 | 1.7663 | 0 | 0 | 1.5 | 0
2017-09-02 | 21:00 | 1.7663 | 0 |  | 1.5 |  | 0
2017-09-02 | 21:05 | -0.10262 | 0 |  | 1.5
2017-09-02 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-02 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0
2017-09-02 | 21:15 | -0.10418 | 0 |  | 1.5 |  | 0
2017-09-02 | 21:20 | -0.10418 | 0 |  | 1.5
2017-09-02 | 21:25 | -0.10496 | 0 |  | 1.5
2017-09-02 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 21:30 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-02 | 21:40 | -0.10496 | 0 |  | 1.5
2017-09-02 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 21:45 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 21:50 | -0.10496 | 0 |  | 1.5
2017-09-02 | 21:55 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 22:00 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 22:05 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:10 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 22:15 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 22:20 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:25 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 22:30 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 22:35 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:40 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 22:45 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 22:50 | -0.10496 | 0 |  | 1.5
2017-09-02 | 22:55 | -0.10496 | 0 |  | 1.5
2017-09-02 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 23:00 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 23:05 | -0.10496 | 0 |  | 1.5
2017-09-02 | 23:10 | -0.10574 | 0 |  | 1.5
2017-09-02 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-02 | 23:15 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-02 | 23:20 | -0.10496 | 0 |  | 1.5
2017-09-02 | 23:25 | -0.10574 | 0 |  | 1.5
2017-09-02 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-02 | 23:30 | -0.10574 | 0 |  | 1.5 |  | 0
2017-09-02 | 23:35 | -0.10574 | 0 |  | 1.5
2017-09-02 | 23:40 | -0.10574 | 0 |  | 1.5
2017-09-02 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-02 | 23:45 | -0.10574 | 0 |  | 1.5 |  | 0
2017-09-02 | 23:50 | -0.10496 | 0 |  | 1.5
2017-09-02 | 23:55 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0
2017-09-03 | 0:00 | -0.10496 | 0 |  | 1.5 |  | 0
2017-09-03 | 0:05 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:10 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 0:20 | -0.10574 | 0 |  | 1.5
2017-09-03 | 0:25 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 0:35 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:40 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 0:50 | -0.10496 | 0 |  | 1.5
2017-09-03 | 0:55 | -0.10496 | 0 |  | 1.5
2017-09-03 | 1:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 1:05 | -0.10418 | 0 |  | 1.5
2017-09-03 | 1:10 | -0.10418 | 0 |  | 1.5
2017-09-03 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 1:20 | -0.10808 | 0 |  | 1.5
2017-09-03 | 1:25 | -0.10808 | 0 |  | 1.5
2017-09-03 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 1:35 | -0.10808 | 0 |  | 1.5
2017-09-03 | 1:40 | -0.10808 | 0 |  | 1.5
2017-09-03 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 1:50 | -0.10808 | 0 |  | 1.5
2017-09-03 | 1:55 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 2:05 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:10 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 2:20 | -0.10886 | 0 |  | 1.5
2017-09-03 | 2:25 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 2:35 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:40 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-03 | 2:55 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 3:05 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:10 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 3:20 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:25 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 3:35 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:40 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 3:50 | -0.10808 | 0 |  | 1.5
2017-09-03 | 3:55 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 4:05 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:10 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 4:20 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:25 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 4:35 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:40 | -0.10886 | 0 |  | 1.5
2017-09-03 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 4:50 | -0.10808 | 0 |  | 1.5
2017-09-03 | 4:55 | -0.10808 | 0 |  | 1.5
2017-09-03 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 5:05 | 1.6048 | 0 |  | 1.5
2017-09-03 | 5:10 | 1.9948 | 0 |  | 1.5
2017-09-03 | 5:15 | 1.8684 | 0 | 0 | 1.5 | 0 | 95.5831
2017-09-03 | 5:20 | 1.8497 | 0 |  | 1.5
2017-09-03 | 5:25 | 1.9683 | 0 |  | 1.5
2017-09-03 | 5:30 | 2.0003 | 0 | 0 | 1.5 | 0 | 90.862
2017-09-03 | 5:35 | 1.9535 | 0 |  | 1.5
2017-09-03 | 5:40 | 1.8965 | 0 |  | 1.5
2017-09-03 | 5:45 | 1.8856 | 0 | 0 | 1.5 | 0 | 86.2227
2017-09-03 | 5:50 | 1.8544 | 0 |  | 1.5
2017-09-03 | 5:55 | 1.8224 | 0 |  | 1.5
2017-09-03 | 6:00 | 1.8263 | 0 | 0 | 1.5 | 0 | 83.9215
2017-09-03 | 6:05 | 1.8458 | 0 |  | 1.5
2017-09-03 | 6:10 | 1.7686 | 0 |  | 1.5
2017-09-03 | 6:15 | 1.7811 | 0 | 0 | 1.5 | 0 | 82.3147
2017-09-03 | 6:20 | 1.7928 | 0 |  | 1.5
2017-09-03 | 6:25 | 1.7912 | 0 |  | 1.5
2017-09-03 | 6:30 | 1.7772 | 0 | 0 | 1.5 | 0 | 81.3909
2017-09-03 | 6:35 | 1.7733 | 0 |  | 1.5
2017-09-03 | 6:40 | 1.7631 | 0 |  | 1.5
2017-09-03 | 6:45 | 1.7897 | 0 | 0 | 1.5 | 0 | 80.4983
2017-09-03 | 6:50 | 1.7982 | 0 |  | 1.5
2017-09-03 | 6:55 | 1.7397 | 0 |  | 1.5
2017-09-03 | 7:00 | 1.753 | 0 | 0 | 1.5 | 0 | 79.9627
2017-09-03 | 7:05 | 1.7468 | 0 |  | 1.5
2017-09-03 | 7:10 | 1.7748 | 0 |  | 1.5
2017-09-03 | 7:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.7686
2017-09-03 | 7:20 | 1.7351 | 0 |  | 1.5
2017-09-03 | 7:25 | 1.767 | 0 |  | 1.5
2017-09-03 | 7:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 79.6034
2017-09-03 | 7:35 | 1.7507 | 0 |  | 1.5
2017-09-03 | 7:40 | 1.7772 | 0 |  | 1.5
2017-09-03 | 7:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.2692
2017-09-03 | 7:50 | 1.7569 | 0 |  | 1.5
2017-09-03 | 7:55 | 1.7507 | 0 |  | 1.5
2017-09-03 | 8:00 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.0519
2017-09-03 | 8:05 | 1.7725 | 0 |  | 1.5
2017-09-03 | 8:10 | 1.7655 | 0 |  | 1.5
2017-09-03 | 8:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 79.0227
2017-09-03 | 8:20 | 1.7592 | 0 |  | 1.5
2017-09-03 | 8:25 | 1.7585 | 0 |  | 1.5
2017-09-03 | 8:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 79.0045
2017-09-03 | 8:35 | 1.7647 | 0 |  | 1.5
2017-09-03 | 8:40 | 1.7405 | 0 |  | 1.5
2017-09-03 | 8:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 79.142
2017-09-03 | 8:50 | 1.7522 | 0 |  | 1.5
2017-09-03 | 8:55 | 1.7873 | 0 |  | 1.5
2017-09-03 | 9:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 78.9155
2017-09-03 | 9:05 | 1.7413 | 0 |  | 1.5
2017-09-03 | 9:10 | 1.7327 | 0 |  | 1.5
2017-09-03 | 9:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 79.0551
2017-09-03 | 9:20 | 1.7616 | 0 |  | 1.5
2017-09-03 | 9:25 | 1.7429 | 0 |  | 1.5
2017-09-03 | 9:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 79.0316
2017-09-03 | 9:35 | 1.7358 | 0 |  | 1.5
2017-09-03 | 9:40 | 1.7686 | 0 |  | 1.5
2017-09-03 | 9:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 79.2153
2017-09-03 | 9:50 | 1.7421 | 0 |  | 1.5
2017-09-03 | 9:55 | 1.7452 | 0 |  | 1.5
2017-09-03 | 10:00 | 1.7187 | 0 | 0 | 1.5 | 0 | 79.3322
2017-09-03 | 10:05 | 1.7351 | 0 |  | 1.5
2017-09-03 | 10:10 | 1.7335 | 0 |  | 1.5
2017-09-03 | 10:15 | 1.7358 | 0 | 0 | 1.5 | 0 | 79.8055
2017-09-03 | 10:20 | 1.7468 | 0 |  | 1.5
2017-09-03 | 10:25 | 1.7546 | 0 |  | 1.5
2017-09-03 | 10:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 80.1099
2017-09-03 | 10:35 | 1.7179 | 0 |  | 1.5
2017-09-03 | 10:40 | 1.7561 | 0 |  | 1.5
2017-09-03 | 10:45 | 1.7319 | 0 | 0 | 1.5 | 0 | 80.4172
2017-09-03 | 10:50 | 1.7195 | 0 |  | 1.5
2017-09-03 | 10:55 | 1.7148 | 0 |  | 1.5
2017-09-03 | 11:00 | 1.6836 | 0 | 0 | 1.5 | 0 | 81.2355
2017-09-03 | 11:05 | 1.7397 | 0 |  | 1.5
2017-09-03 | 11:10 | 1.7405 | 0 |  | 1.5
2017-09-03 | 11:15 | 1.7 | 0 | 0 | 1.5 | 0 | 81.7197
2017-09-03 | 11:20 | 1.7148 | 0 |  | 1.5
2017-09-03 | 11:25 | 1.7327 | 0 |  | 1.5
2017-09-03 | 11:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 82.4401
2017-09-03 | 11:35 | 1.7031 | 0 |  | 1.5
2017-09-03 | 11:40 | 1.707 | 0 |  | 1.5
2017-09-03 | 11:45 | 1.7101 | 0 | 0 | 1.5 | 0 | 83.3633
2017-09-03 | 11:50 | 1.7436 | 0 |  | 1.5
2017-09-03 | 11:55 | 1.7585 | 0 |  | 1.5
2017-09-03 | 12:00 | 1.7202 | 0 | 0 | 1.5 | 0 | 83.9387
2017-09-03 | 12:05 | 1.7234 | 0 |  | 1.5
2017-09-03 | 12:10 | 1.7358 | 0 |  | 1.5
2017-09-03 | 12:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 84.3401
2017-09-03 | 12:20 | 1.7436 | 0 |  | 1.5
2017-09-03 | 12:25 | 1.7132 | 0 |  | 1.5
2017-09-03 | 12:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 84.8623
2017-09-03 | 12:35 | 1.7312 | 0 |  | 1.5
2017-09-03 | 12:40 | 1.7218 | 0 |  | 1.5
2017-09-03 | 12:45 | 1.7288 | 0 | 0 | 1.5 | 0 | 85.3141
2017-09-03 | 12:50 | 1.7234 | 0 |  | 1.5
2017-09-03 | 12:55 | 1.728 | 0 |  | 1.5
2017-09-03 | 13:00 | 1.7351 | 0 | 0 | 1.5 | 0 | 85.814
2017-09-03 | 13:05 | 1.7101 | 0 |  | 1.5
2017-09-03 | 13:10 | 1.7475 | 0 |  | 1.5
2017-09-03 | 13:15 | 1.721 | 0 | 0 | 1.5 | 0 | 86.3304
2017-09-03 | 13:20 | 1.746 | 0 |  | 1.5
2017-09-03 | 13:25 | 1.7397 | 0 |  | 1.5
2017-09-03 | 13:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 86.6955
2017-09-03 | 13:35 | 1.7475 | 0 |  | 1.5
2017-09-03 | 13:40 | 1.7522 | 0 |  | 1.5
2017-09-03 | 13:45 | 1.753 | 0 | 0 | 1.5 | 0 | 86.77
2017-09-03 | 13:50 | 1.7319 | 0 |  | 1.5
2017-09-03 | 13:55 | 1.7468 | 0 |  | 1.5
2017-09-03 | 14:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 86.8807
2017-09-03 | 14:05 | 1.7491 | 0 |  | 1.5
2017-09-03 | 14:10 | 1.7522 | 0 |  | 1.5
2017-09-03 | 14:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 86.8372
2017-09-03 | 14:20 | 1.7522 | 0 |  | 1.5
2017-09-03 | 14:25 | 1.7436 | 0 |  | 1.5
2017-09-03 | 14:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 87.0572
2017-09-03 | 14:35 | 1.7639 | 0 |  | 1.5
2017-09-03 | 14:40 | 1.7304 | 0 |  | 1.5
2017-09-03 | 14:45 | 1.6984 | 0 | 0 | 1.5 | 0 | 87.5477
2017-09-03 | 14:50 | 1.7327 | 0 |  | 1.5
2017-09-03 | 14:55 | 1.7187 | 0 |  | 1.5
2017-09-03 | 15:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 88.0743
2017-09-03 | 15:05 | 1.7257 | 0 |  | 1.5
2017-09-03 | 15:10 | 1.7499 | 0 |  | 1.5
2017-09-03 | 15:15 | 1.767 | 0 | 0 | 1.5 | 0 | 88.4718
2017-09-03 | 15:20 | 1.7335 | 0 |  | 1.5
2017-09-03 | 15:25 | 1.7241 | 0 |  | 1.5
2017-09-03 | 15:30 | 1.7351 | 0 | 0 | 1.5 | 0 | 88.9131
2017-09-03 | 15:35 | 1.7335 | 0 |  | 1.5
2017-09-03 | 15:40 | 1.7694 | 0 |  | 1.5
2017-09-03 | 15:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 88.8404
2017-09-03 | 15:50 | 1.7951 | 0 |  | 1.5
2017-09-03 | 15:55 | 1.7803 | 0 |  | 1.5
2017-09-03 | 16:00 | 1.8154 | 0 | 0 | 1.5 | 0 | 87.7653
2017-09-03 | 16:05 | 1.8092 | 0 |  | 1.5
2017-09-03 | 16:10 | 1.8053 | 0 |  | 1.5
2017-09-03 | 16:15 | 1.7904 | 0 | 0 | 1.5 | 0 | 86.387
2017-09-03 | 16:20 | 1.7865 | 0 |  | 1.5
2017-09-03 | 16:25 | 1.7748 | 0 |  | 1.5
2017-09-03 | 16:30 | 1.7764 | 0 | 0 | 1.5 | 0 | 85.3797
2017-09-03 | 16:30 | 1.7709 |  |  | 1.5
2017-09-03 | 16:35 | 1.7803 | 0 |  | 1.5
2017-09-03 | 16:40 | 1.753 | 0 |  | 1.5
2017-09-03 | 16:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 84.762
2017-09-03 | 16:50 | 1.7702 | 0 |  | 1.5
2017-09-03 | 16:55 | 1.7733 | 0 |  | 1.5
2017-09-03 | 17:00 | 1.7413 | 0 | 0 | 1.5 | 0 | 84.1716
2017-09-03 | 17:05 | 1.76 | 0 |  | 1.5
2017-09-03 | 17:10 | 1.792 | 0 |  | 1.5
2017-09-03 | 17:15 | 1.7772 | 0 | 0 | 1.5 | 0 | 83.5805
2017-09-03 | 17:20 | 1.7897 | 0 |  | 1.5
2017-09-03 | 17:25 | 1.7842 | 0 |  | 1.5
2017-09-03 | 17:30 | 1.7647 | 0 | 0 | 1.5 | 0 | 82.8487
2017-09-03 | 17:35 | 1.7819 | 0 |  | 1.5
2017-09-03 | 17:40 | 1.7717 | 0 |  | 1.5
2017-09-03 | 17:45 | 1.7717 | 0 | 0 | 1.5 | 0 | 82.148
2017-09-03 | 17:50 | 1.7889 | 0 |  | 1.5
2017-09-03 | 17:55 | 1.7639 | 0 |  | 1.5
2017-09-03 | 18:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 81.481
2017-09-03 | 18:05 | 1.7616 | 0 |  | 1.5
2017-09-03 | 18:10 | 1.7787 | 0 |  | 1.5
2017-09-03 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 80.9158
2017-09-03 | 18:20 | 1.7686 | 0 |  | 1.5
2017-09-03 | 18:25 | 1.767 | 0 |  | 1.5
2017-09-03 | 18:30 | 1.7491 | 0 | 0 | 1.5 | 0 | 80.6319
2017-09-03 | 18:35 | 1.7624 | 0 |  | 1.5
2017-09-03 | 18:40 | 1.7647 | 0 |  | 1.5
2017-09-03 | 18:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 80.282
2017-09-03 | 18:50 | 1.7819 | 0 |  | 1.5
2017-09-03 | 18:55 | 1.7397 | 0 |  | 1.5
2017-09-03 | 19:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 80.0197
2017-09-03 | 19:05 | 1.7561 | 0 |  | 1.5
2017-09-03 | 19:10 | 1.7577 | 0 |  | 1.5
2017-09-03 | 19:15 | 1.7709 | 0 | 0 | 1.5 | 0 | 79.8177
2017-09-03 | 19:20 | 1.7795 | 0 |  | 1.5
2017-09-03 | 19:25 | 1.7663 | 0 |  | 1.5
2017-09-03 | 19:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 79.3334
2017-09-03 | 19:35 | 1.7647 | 0 |  | 1.5
2017-09-03 | 19:40 | 1.7811 | 0 |  | 1.5
2017-09-03 | 19:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 78.8466
2017-09-03 | 19:50 | 1.7507 | 0 |  | 1.5
2017-09-03 | 19:55 | 1.7561 | 0 |  | 1.5
2017-09-03 | 20:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.6873
2017-09-03 | 20:05 | 1.7335 | 0 |  | 1.5
2017-09-03 | 20:10 | 1.7382 | 0 |  | 1.5
2017-09-03 | 20:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 78.6224
2017-09-03 | 20:20 | 1.753 | 0 |  | 1.5
2017-09-03 | 20:25 | 1.7491 | 0 |  | 1.5
2017-09-03 | 20:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 78.2878
2017-09-03 | 20:35 | 1.7327 | 0 |  | 1.5
2017-09-03 | 20:40 |  | 0
2017-09-03 | 20:40 | 1.753 |  |  | 1.5
2017-09-03 | 20:45 | 1.7499 | 0 |  | 1.5 |  | 78.0128
2017-09-03 | 20:45 | 1.7436 | 0 | 0 | 1.5 | 0
2017-09-03 | 20:50 | 1.7351 | 0 |  | 1.5
2017-09-03 | 20:55 | 1.7265 | 0 |  | 1.5
2017-09-03 | 21:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 78.2691
2017-09-03 | 21:05 | -0.10496 | 0 |  | 1.5
2017-09-03 | 21:10 | -0.10574 | 0 |  | 1.5
2017-09-03 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 21:20 | -0.10574 | 0 |  | 1.5
2017-09-03 | 21:25 | -0.10574 | 0 |  | 1.5
2017-09-03 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 21:35 | -0.10652 | 0 |  | 1.5
2017-09-03 | 21:40 | -0.10652 | 0 |  | 1.5
2017-09-03 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 21:50 | -0.10652 | 0 |  | 1.5
2017-09-03 | 21:55 | -0.10652 | 0 |  | 1.5
2017-09-03 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 22:05 | -0.10652 | 0 |  | 1.5
2017-09-03 | 22:10 | -0.10652 | 0 |  | 1.5
2017-09-03 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 22:20 | -0.10574 | 0 |  | 1.5
2017-09-03 | 22:25 | -0.10652 | 0 |  | 1.5
2017-09-03 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 22:35 | -0.10652 | 0 |  | 1.5
2017-09-03 | 22:40 | -0.10652 | 0 |  | 1.5
2017-09-03 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 22:50 | -0.10574 | 0 |  | 1.5
2017-09-03 | 22:55 | -0.10574 | 0 |  | 1.5
2017-09-03 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 23:05 | -0.10652 | 0 |  | 1.5
2017-09-03 | 23:10 | -0.10574 | 0 |  | 1.5
2017-09-03 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 23:20 | -0.10574 | 0 |  | 1.5
2017-09-03 | 23:25 | -0.10652 | 0 |  | 1.5
2017-09-03 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 23:35 | -0.10574 | 0 |  | 1.5
2017-09-03 | 23:40 | -0.10574 | 0 |  | 1.5
2017-09-03 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-03 | 23:50 | -0.10574 | 0 |  | 1.5
2017-09-03 | 23:55 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 0:05 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:10 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 0:20 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:25 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 0:35 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:40 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 0:50 | -0.10574 | 0 |  | 1.5
2017-09-04 | 0:55 | -0.10574 | 0 |  | 1.5
2017-09-04 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 1:05 | -0.10574 | 0 |  | 1.5
2017-09-04 | 1:10 | -0.10574 | 0 |  | 1.5
2017-09-04 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 1:20 | -0.10886 | 0 |  | 1.5
2017-09-04 | 1:25 | -0.10886 | 0 |  | 1.5
2017-09-04 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 1:35 | -0.10886 | 0 |  | 1.5
2017-09-04 | 1:40 | -0.10886 | 0 |  | 1.5
2017-09-04 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 1:50 | -0.10886 | 0 |  | 1.5
2017-09-04 | 1:55 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 2:05 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:10 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 2:20 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:25 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 2:35 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:40 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 2:50 | -0.10886 | 0 |  | 1.5
2017-09-04 | 2:55 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 3:05 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:10 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 3:20 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:25 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 3:35 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:40 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 3:50 | -0.10886 | 0 |  | 1.5
2017-09-04 | 3:55 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 4:05 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:10 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 4:20 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:25 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 4:35 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:40 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 4:50 | -0.10886 | 0 |  | 1.5
2017-09-04 | 4:55 | -0.10886 | 0 |  | 1.5
2017-09-04 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 5:05 | 1.7436 | 0 |  | 1.5
2017-09-04 | 5:10 | 1.9784 | 0 |  | 1.5
2017-09-04 | 5:15 | 1.9566 | 0 | 0 | 1.5 | 0 | 95.1258
2017-09-04 | 5:20 | 1.8614 | 0 |  | 1.5
2017-09-04 | 5:25 | 1.9371 | 0 |  | 1.5
2017-09-04 | 5:30 | 1.9761 | 0 | 0 | 1.5 | 0 | 90.7297
2017-09-04 | 5:35 | 1.9667 | 0 |  | 1.5
2017-09-04 | 5:40 | 1.8872 | 0 |  | 1.5
2017-09-04 | 5:45 | 1.8583 | 0 | 0 | 1.5 | 0 | 86.2985
2017-09-04 | 5:50 | 1.838 | 0 |  | 1.5
2017-09-04 | 5:55 | 1.8084 | 0 |  | 1.5
2017-09-04 | 6:00 | 1.831 | 0 | 0 | 1.5 | 0 | 83.7635
2017-09-04 | 6:05 | 1.8146 | 0 |  | 1.5
2017-09-04 | 6:10 | 1.8076 | 0 |  | 1.5
2017-09-04 | 6:15 | 1.8131 | 0 | 0 | 1.5 | 0 | 82.0564
2017-09-04 | 6:20 | 1.8224 | 0 |  | 1.5
2017-09-04 | 6:25 | 1.778 | 0 |  | 1.5
2017-09-04 | 6:30 | 1.7803 | 0 | 0 | 1.5 | 0 | 81.0514
2017-09-04 | 6:35 | 1.7616 | 0 |  | 1.5
2017-09-04 | 6:40 | 1.7686 | 0 |  | 1.5
2017-09-04 | 6:45 | 1.7881 | 0 | 0 | 1.5 | 0 | 80.3735
2017-09-04 | 6:50 | 1.7889 | 0 |  | 1.5
2017-09-04 | 6:55 | 1.7873 | 0 |  | 1.5
2017-09-04 | 7:00 | 1.8084 | 0 | 0 | 1.5 | 0 | 79.4695
2017-09-04 | 7:05 | 1.7897 | 0 |  | 1.5
2017-09-04 | 7:10 | 1.7358 | 0 |  | 1.5
2017-09-04 | 7:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.2277
2017-09-04 | 7:20 | 1.76 | 0 |  | 1.5
2017-09-04 | 7:25 | 1.7561 | 0 |  | 1.5
2017-09-04 | 7:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.1141
2017-09-04 | 7:35 | 1.7546 | 0 |  | 1.5
2017-09-04 | 7:40 | 1.7725 | 0 |  | 1.5
2017-09-04 | 7:45 | 1.7553 | 0 | 0 | 1.5 | 0 | 79.0921
2017-09-04 | 7:50 | 1.7702 | 0 |  | 1.5
2017-09-04 | 7:55 | 1.7678 | 0 |  | 1.5
2017-09-04 | 8:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 78.8848
2017-09-04 | 8:05 | 1.7351 | 0 |  | 1.5
2017-09-04 | 8:10 | 1.7569 | 0 |  | 1.5
2017-09-04 | 8:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 78.978
2017-09-04 | 8:20 | 1.7429 | 0 |  | 1.5
2017-09-04 | 8:25 | 1.7647 | 0 |  | 1.5
2017-09-04 | 8:30 | 1.7374 | 0 | 0 | 1.5 | 0 | 78.8947
2017-09-04 | 8:35 | 1.7585 | 0 |  | 1.5
2017-09-04 | 8:40 | 1.7577 | 0 |  | 1.5
2017-09-04 | 8:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 78.8782
2017-09-04 | 8:50 | 1.7592 | 0 |  | 1.5
2017-09-04 | 8:55 | 1.7522 | 0 |  | 1.5
2017-09-04 | 9:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 78.7574
2017-09-04 | 9:05 | 1.7803 | 0 |  | 1.5
2017-09-04 | 9:10 | 1.7335 | 0 |  | 1.5
2017-09-04 | 9:15 | 1.6961 | 0 | 0 | 1.5 | 0 | 78.9043
2017-09-04 | 9:20 | 1.7546 | 0 |  | 1.5
2017-09-04 | 9:25 | 1.7678 | 0 |  | 1.5
2017-09-04 | 9:30 | 1.7397 | 0 | 0 | 1.5 | 0 | 78.8747
2017-09-04 | 9:35 | 1.7561 | 0 |  | 1.5
2017-09-04 | 9:40 | 1.7475 | 0 |  | 1.5
2017-09-04 | 9:45 | 1.7312 | 0 | 0 | 1.5 | 0 | 78.9952
2017-09-04 | 9:50 | 1.7156 | 0 |  | 1.5
2017-09-04 | 9:55 | 1.7561 | 0 |  | 1.5
2017-09-04 | 10:00 | 1.728 | 0 | 0 | 1.5 | 0 | 79.3444
2017-09-04 | 10:05 | 1.7257 | 0 |  | 1.5
2017-09-04 | 10:10 | 1.7608 | 0 |  | 1.5
2017-09-04 | 10:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 79.4682
2017-09-04 | 10:20 | 1.7429 | 0 |  | 1.5
2017-09-04 | 10:25 | 1.7507 | 0 |  | 1.5
2017-09-04 | 10:30 | 1.7655 | 0 | 0 | 1.5 | 0 | 79.6192
2017-09-04 | 10:35 | 1.7117 | 0 |  | 1.5
2017-09-04 | 10:40 | 1.7265 | 0 |  | 1.5
2017-09-04 | 10:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 79.9192
2017-09-04 | 10:50 | 1.7304 | 0 |  | 1.5
2017-09-04 | 10:55 | 1.7218 | 0 |  | 1.5
2017-09-04 | 11:00 | 1.7405 | 0 | 0 | 1.5 | 0 | 80.3239
2017-09-04 | 11:05 | 1.7569 | 0 |  | 1.5
2017-09-04 | 11:10 | 1.7312 | 0 |  | 1.5
2017-09-04 | 11:15 | 1.7163 | 0 | 0 | 1.5 | 0 | 80.7805
2017-09-04 | 11:20 | 1.7265 | 0 |  | 1.5
2017-09-04 | 11:25 | 1.7304 | 0 |  | 1.5
2017-09-04 | 11:30 | 1.7148 | 0 | 0 | 1.5 | 0 | 81.3334
2017-09-04 | 11:35 | 1.7085 | 0 |  | 1.5
2017-09-04 | 11:40 | 1.7483 | 0 |  | 1.5
2017-09-04 | 11:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 81.6534
2017-09-04 | 11:50 | 1.7046 | 0 |  | 1.5
2017-09-04 | 11:55 | 1.7117 | 0 |  | 1.5
2017-09-04 | 12:00 | 1.739 | 0 | 0 | 1.5 | 0 | 82.0564
2017-09-04 | 12:05 | 1.728 | 0 |  | 1.5
2017-09-04 | 12:10 | 1.7507 | 0 |  | 1.5
2017-09-04 | 12:15 | 1.7296 | 0 | 0 | 1.5 | 0 | 82.3971
2017-09-04 | 12:20 | 1.7452 | 0 |  | 1.5
2017-09-04 | 12:25 | 1.7179 | 0 |  | 1.5
2017-09-04 | 12:30 | 1.7046 | 0 | 0 | 1.5 | 0 | 82.944
2017-09-04 | 12:35 | 1.7109 | 0 |  | 1.5
2017-09-04 | 12:40 | 1.7117 | 0 |  | 1.5
2017-09-04 | 12:45 | 1.7686 | 0 | 0 | 1.5 | 0 | 83.2731
2017-09-04 | 12:50 | 1.7608 | 0 |  | 1.5
2017-09-04 | 12:55 | 1.7577 | 0 |  | 1.5
2017-09-04 | 13:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 83.1871
2017-09-04 | 13:05 | 1.7624 | 0 |  | 1.5
2017-09-04 | 13:10 | 1.753 | 0 |  | 1.5
2017-09-04 | 13:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 82.7068
2017-09-04 | 13:20 | 1.7873 | 0 |  | 1.5
2017-09-04 | 13:25 | 1.7717 | 0 |  | 1.5
2017-09-04 | 13:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 82.5202
2017-09-04 | 13:35 | 1.76 | 0 |  | 1.5
2017-09-04 | 13:40 | 1.753 | 0 |  | 1.5
2017-09-04 | 13:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 82.4152
2017-09-04 | 13:50 | 1.7553 | 0 |  | 1.5
2017-09-04 | 13:55 | 1.7397 | 0 |  | 1.5
2017-09-04 | 14:00 | 1.7366 | 0 | 0 | 1.5 | 0 | 82.6883
2017-09-04 | 14:05 | 1.7553 | 0 |  | 1.5
2017-09-04 | 14:10 | 1.7366 | 0 |  | 1.5
2017-09-04 | 14:15 | 1.7491 | 0 | 0 | 1.5 | 0 | 82.6476
2017-09-04 | 14:20 | 1.7491 | 0 |  | 1.5
2017-09-04 | 14:25 | 1.7631 | 0 |  | 1.5
2017-09-04 | 14:30 | 1.7101 | 0 | 0 | 1.5 | 0 | 82.5785
2017-09-04 | 14:35 | 1.7429 | 0 |  | 1.5
2017-09-04 | 14:40 | 1.7319 | 0 |  | 1.5
2017-09-04 | 14:45 | 1.739 | 0 | 0 | 1.5 | 0 | 82.6883
2017-09-04 | 14:50 | 1.7405 | 0 |  | 1.5
2017-09-04 | 14:55 | 1.7538 | 0 |  | 1.5
2017-09-04 | 15:00 | 1.7787 | 0 | 0 | 1.5 | 0 | 82.732
2017-09-04 | 15:05 | 1.7468 | 0 |  | 1.5
2017-09-04 | 15:10 | 1.7452 | 0 |  | 1.5
2017-09-04 | 15:15 | 1.7514 | 0 | 0 | 1.5 | 0 | 82.9461
2017-09-04 | 15:20 | 1.7382 | 0 |  | 1.5
2017-09-04 | 15:25 | 1.7288 | 0 |  | 1.5
2017-09-04 | 15:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 83.0552
2017-09-04 | 15:35 | 1.7366 | 0 |  | 1.5
2017-09-04 | 15:40 | 1.739 | 0 |  | 1.5
2017-09-04 | 15:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 83.0866
2017-09-04 | 15:50 | 1.7522 | 0 |  | 1.5
2017-09-04 | 15:55 | 1.7444 | 0 |  | 1.5
2017-09-04 | 16:00 | 1.7733 | 0 | 0 | 1.5 | 0 | 83.0569
2017-09-04 | 16:05 | 1.7678 | 0 |  | 1.5
2017-09-04 | 16:10 | 1.7483 | 0 |  | 1.5
2017-09-04 | 16:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 83.0724
2017-09-04 | 16:20 | 1.7686 | 0 |  | 1.5
2017-09-04 | 16:25 | 1.753 | 0 |  | 1.5
2017-09-04 | 16:30 | 1.7592 | 0 | 0 | 1.5 | 0 | 82.9382
2017-09-04 | 16:35 | 1.7608 | 0 |  | 1.5
2017-09-04 | 16:40 | 1.7624 | 0 |  | 1.5
2017-09-04 | 16:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 82.7757
2017-09-04 | 16:50 | 1.7553 | 0 |  | 1.5
2017-09-04 | 16:55 | 1.7429 | 0 |  | 1.5
2017-09-04 | 17:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.4961
2017-09-04 | 17:05 | 1.7686 | 0 |  | 1.5
2017-09-04 | 17:10 | 1.7546 | 0 |  | 1.5
2017-09-04 | 17:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 82.3599
2017-09-04 | 17:20 | 1.7491 | 0 |  | 1.5
2017-09-04 | 17:25 | 1.7678 | 0 |  | 1.5
2017-09-04 | 17:30 | 1.7366 | 0 | 0 | 1.5 | 0 | 81.9744
2017-09-04 | 17:35 | 1.7218 | 0 |  | 1.5
2017-09-04 | 17:40 | 1.7686 | 0 |  | 1.5
2017-09-04 | 17:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 81.7291
2017-09-04 | 17:50 | 1.7842 | 0 |  | 1.5
2017-09-04 | 17:55 | 1.7436 | 0 |  | 1.5
2017-09-04 | 18:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.3662
2017-09-04 | 18:05 | 1.7343 | 0 |  | 1.5
2017-09-04 | 18:10 | 1.753 | 0 |  | 1.5
2017-09-04 | 18:15 | 1.7358 | 0 | 0 | 1.5 | 0 | 81.3251
2017-09-04 | 18:20 | 1.7483 | 0 |  | 1.5
2017-09-04 | 18:25 | 1.7639 | 0 |  | 1.5
2017-09-04 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.114
2017-09-04 | 18:35 | 1.7413 | 0 |  | 1.5
2017-09-04 | 18:40 | 1.7592 | 0 |  | 1.5
2017-09-04 | 18:45 | 1.7655 | 0 | 0 | 1.5 | 0 | 80.9513
2017-09-04 | 18:50 | 1.7312 | 0 |  | 1.5
2017-09-04 | 18:55 | 1.7741 | 0 |  | 1.5
2017-09-04 | 19:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 80.6474
2017-09-04 | 19:05 | 1.7452 | 0 |  | 1.5
2017-09-04 | 19:10 | 1.7585 | 0 |  | 1.5
2017-09-04 | 19:15 | 1.7538 | 0 | 0 | 1.5 | 0 | 80.2897
2017-09-04 | 19:20 | 1.785 | 0 |  | 1.5
2017-09-04 | 19:25 | 1.7702 | 0 |  | 1.5
2017-09-04 | 19:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 79.946
2017-09-04 | 19:35 | 1.7522 | 0 |  | 1.5
2017-09-04 | 19:40 | 1.7624 | 0 |  | 1.5
2017-09-04 | 19:45 | 1.7803 | 0 | 0 | 1.5 | 0 | 79.6052
2017-09-04 | 19:50 | 1.7592 | 0 |  | 1.5
2017-09-04 | 19:55 | 1.7725 | 0 |  | 1.5
2017-09-04 | 20:00 | 1.7639 | 0 | 0 | 1.5 | 0 | 79.1748
2017-09-04 | 20:05 | 1.7546 | 0 |  | 1.5
2017-09-04 | 20:10 | 1.7811 | 0 |  | 1.5
2017-09-04 | 20:15 | 1.7772 | 0 | 0 | 1.5 | 0 | 78.7448
2017-09-04 | 20:20 | 1.7561 | 0 |  | 1.5
2017-09-04 | 20:25 | 1.7663 | 0 |  | 1.5
2017-09-04 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 78.4352
2017-09-04 | 20:35 | 1.7569 | 0 |  | 1.5
2017-09-04 | 20:40 | 1.7538 | 0 |  | 1.5
2017-09-04 | 20:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 78.0524
2017-09-04 | 20:50 | 1.728 | 0 |  | 1.5
2017-09-04 | 20:55 | 1.7725 | 0 |  | 1.5
2017-09-04 | 21:00 | 1.7374 | 0 | 0 | 1.5 | 0 | 77.9437
2017-09-04 | 21:05 | -0.10496 | 0 |  | 1.5
2017-09-04 | 21:10 | -0.10574 | 0 |  | 1.5
2017-09-04 | 21:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 21:20 | -0.10652 | 0 |  | 1.5
2017-09-04 | 21:25 | -0.10652 | 0 |  | 1.5
2017-09-04 | 21:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 21:35 | -0.1073 | 0 |  | 1.5
2017-09-04 | 21:40 | -0.10652 | 0 |  | 1.5
2017-09-04 | 21:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 21:50 | -0.10652 | 0 |  | 1.5
2017-09-04 | 21:55 | -0.10652 | 0 |  | 1.5
2017-09-04 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 22:05 | -0.10652 | 0 |  | 1.5
2017-09-04 | 22:10 | -0.10652 | 0 |  | 1.5
2017-09-04 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 22:20 | -0.10652 | 0 |  | 1.5
2017-09-04 | 22:25 | -0.10652 | 0 |  | 1.5
2017-09-04 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 22:35 | -0.10652 | 0 |  | 1.5
2017-09-04 | 22:40 | -0.10574 | 0 |  | 1.5
2017-09-04 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 22:50 | -0.10574 | 0 |  | 1.5
2017-09-04 | 22:55 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 23:05 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:10 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 23:20 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:25 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 23:35 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:40 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-04 | 23:50 | -0.10574 | 0 |  | 1.5
2017-09-04 | 23:55 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 0:05 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:10 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 0:20 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:25 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 0:35 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:40 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 0:50 | -0.10574 | 0 |  | 1.5
2017-09-05 | 0:55 | -0.10574 | 0 |  | 1.5
2017-09-05 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 1:05 | -0.10574 | 0 |  | 1.5
2017-09-05 | 1:10 | -0.10574 | 0 |  | 1.5
2017-09-05 | 1:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 1:20 | -0.10964 | 0 |  | 1.5
2017-09-05 | 1:25 | -0.10886 | 0 |  | 1.5
2017-09-05 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 1:35 | -0.10886 | 0 |  | 1.5
2017-09-05 | 1:40 | -0.10886 | 0 |  | 1.5
2017-09-05 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 1:50 | -0.10886 | 0 |  | 1.5
2017-09-05 | 1:55 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 2:05 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:10 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 2:20 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:25 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 2:35 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:40 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 2:50 | -0.10886 | 0 |  | 1.5
2017-09-05 | 2:55 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 3:05 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:10 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 3:20 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:25 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 3:35 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:40 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 3:50 | -0.10886 | 0 |  | 1.5
2017-09-05 | 3:55 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 4:05 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:10 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 4:20 | -0.10808 | 0 |  | 1.5
2017-09-05 | 4:25 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 4:35 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:40 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 4:50 | -0.10886 | 0 |  | 1.5
2017-09-05 | 4:55 | -0.10886 | 0 |  | 1.5
2017-09-05 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 5:05 | 1.5939 | 0 |  | 1.5
2017-09-05 | 5:10 | 1.9488 | 0 |  | 1.5
2017-09-05 | 5:15 | 1.9597 | 0 | 0 | 1.5 | 0 | 95.858
2017-09-05 | 5:20 | 1.8326 | 0 |  | 1.5
2017-09-05 | 5:25 | 1.916 | 0 |  | 1.5
2017-09-05 | 5:30 | 1.9519 | 0 | 0 | 1.5 | 0 | 92.2572
2017-09-05 | 5:35 | 1.9691 | 0 |  | 1.5
2017-09-05 | 5:40 | 1.9511 | 0 |  | 1.5
2017-09-05 | 5:45 | 1.8833 | 0 | 0 | 1.5 | 0 | 87.001
2017-09-05 | 5:50 | 1.8388 | 0 |  | 1.5
2017-09-05 | 5:55 | 1.8497 | 0 |  | 1.5
2017-09-05 | 6:00 | 1.8271 | 0 | 0 | 1.5 | 0 | 84.2958
2017-09-05 | 6:05 | 1.8388 | 0 |  | 1.5
2017-09-05 | 6:10 | 1.7959 | 0 |  | 1.5
2017-09-05 | 6:15 | 1.7982 | 0 | 0 | 1.5 | 0 | 82.5163
2017-09-05 | 6:20 | 1.7873 | 0 |  | 1.5
2017-09-05 | 6:25 | 1.7795 | 0 |  | 1.5
2017-09-05 | 6:30 | 1.7725 | 0 | 0 | 1.5 | 0 | 81.3809
2017-09-05 | 6:35 | 1.7756 | 0 |  | 1.5
2017-09-05 | 6:40 | 1.7787 | 0 |  | 1.5
2017-09-05 | 6:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 80.7984
2017-09-05 | 6:50 | 1.7826 | 0 |  | 1.5
2017-09-05 | 6:55 | 1.76 | 0 |  | 1.5
2017-09-05 | 7:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 80.3937
2017-09-05 | 7:05 | 1.7811 | 0 |  | 1.5
2017-09-05 | 7:10 | 1.7717 | 0 |  | 1.5
2017-09-05 | 7:15 | 1.7725 | 0 | 0 | 1.5 | 0 | 79.9515
2017-09-05 | 7:20 | 1.792 | 0 |  | 1.5
2017-09-05 | 7:25 | 1.7522 | 0 |  | 1.5
2017-09-05 | 7:30 | 1.76 | 0 | 0 | 1.5 | 0 | 79.3401
2017-09-05 | 7:35 | 1.7491 | 0 |  | 1.5
2017-09-05 | 7:40 | 1.7483 | 0 |  | 1.5
2017-09-05 | 7:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 79.3342
2017-09-05 | 7:50 | 1.739 | 0 |  | 1.5
2017-09-05 | 7:55 | 1.7382 | 0 |  | 1.5
2017-09-05 | 8:00 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.7537
2017-09-05 | 8:05 | 1.7273 | 0 |  | 1.5
2017-09-05 | 8:10 | 1.728 | 0 |  | 1.5
2017-09-05 | 8:15 | 1.6664 | 0 | 0 | 1.5 | 0 | 80.6681
2017-09-05 | 8:20 | 1.7039 | 0 |  | 1.5
2017-09-05 | 8:25 | 1.7132 | 0 |  | 1.5
2017-09-05 | 8:30 | 1.7288 | 0 | 0 | 1.5 | 0 | 81.9222
2017-09-05 | 8:35 | 1.7007 | 0 |  | 1.5
2017-09-05 | 8:40 | 1.7397 | 0 |  | 1.5
2017-09-05 | 8:45 | 1.728 | 0 | 0 | 1.5 | 0 | 82.4173
2017-09-05 | 8:50 | 1.7421 | 0 |  | 1.5
2017-09-05 | 8:55 | 1.7366 | 0 |  | 1.5
2017-09-05 | 9:00 | 1.7304 | 0 | 0 | 1.5 | 0 | 82.7631
2017-09-05 | 9:05 | 1.7468 | 0 |  | 1.5
2017-09-05 | 9:10 | 1.7351 | 0 |  | 1.5
2017-09-05 | 9:15 | 1.707 | 0 | 0 | 1.5 | 0 | 83.2204
2017-09-05 | 9:20 | 1.6929 | 0 |  | 1.5
2017-09-05 | 9:25 | 1.6968 | 0 |  | 1.5
2017-09-05 | 9:30 | 1.7351 | 0 | 0 | 1.5 | 0 | 84.596
2017-09-05 | 9:35 | 1.7039 | 0 |  | 1.5
2017-09-05 | 9:40 | 1.7241 | 0 |  | 1.5
2017-09-05 | 9:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 85.1117
2017-09-05 | 9:50 | 1.7663 | 0 |  | 1.5
2017-09-05 | 9:55 | 1.7249 | 0 |  | 1.5
2017-09-05 | 10:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 85.2798
2017-09-05 | 10:05 | 1.7382 | 0 |  | 1.5
2017-09-05 | 10:10 | 1.7296 | 0 |  | 1.5
2017-09-05 | 10:15 | 1.7343 | 0 | 0 | 1.5 | 0 | 85.3767
2017-09-05 | 10:20 | 1.7803 | 0 |  | 1.5
2017-09-05 | 10:25 | 1.728 | 0 |  | 1.5
2017-09-05 | 10:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 85.7104
2017-09-05 | 10:35 | 1.7608 | 0 |  | 1.5
2017-09-05 | 10:40 | 1.7639 | 0 |  | 1.5
2017-09-05 | 10:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 85.4181
2017-09-05 | 10:50 | 1.8162 | 0 |  | 1.5
2017-09-05 | 10:55 | 1.746 | 0 |  | 1.5
2017-09-05 | 11:00 | 1.7694 | 0 | 0 | 1.5 | 0 | 84.6193
2017-09-05 | 11:05 | 1.7553 | 0 |  | 1.5
2017-09-05 | 11:10 | 1.7655 | 0 |  | 1.5
2017-09-05 | 11:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 84.242
2017-09-05 | 11:20 | 1.7538 | 0 |  | 1.5
2017-09-05 | 11:25 | 1.7655 | 0 |  | 1.5
2017-09-05 | 11:30 | 1.7234 | 0 | 0 | 1.5 | 0 | 84.4282
2017-09-05 | 11:35 | 1.7647 | 0 |  | 1.5
2017-09-05 | 11:40 | 1.7499 | 0 |  | 1.5
2017-09-05 | 11:45 | 1.7366 | 0 | 0 | 1.5 | 0 | 84.5429
2017-09-05 | 11:50 | 1.7483 | 0 |  | 1.5
2017-09-05 | 11:55 | 1.7351 | 0 |  | 1.5
2017-09-05 | 12:00 | 1.7475 | 0 | 0 | 1.5 | 0 | 84.5782
2017-09-05 | 12:05 | 1.7296 | 0 |  | 1.5
2017-09-05 | 12:10 | 1.7046 | 0 |  | 1.5
2017-09-05 | 12:15 | 1.7366 | 0 | 0 | 1.5 | 0 | 85.068
2017-09-05 | 12:20 | 1.7358 | 0 |  | 1.5
2017-09-05 | 12:25 | 1.7319 | 0 |  | 1.5
2017-09-05 | 12:30 | 1.7265 | 0 | 0 | 1.5 | 0 | 85.6534
2017-09-05 | 12:35 | 1.7257 | 0 |  | 1.5
2017-09-05 | 12:40 | 1.7117 | 0 |  | 1.5
2017-09-05 | 12:45 | 1.7124 | 0 | 0 | 1.5 | 0 | 86.6052
2017-09-05 | 12:50 | 1.8107 | 0 |  | 1.5
2017-09-05 | 12:55 | 1.7561 | 0 |  | 1.5
2017-09-05 | 13:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 86.5031
2017-09-05 | 13:05 | 1.7218 | 0 |  | 1.5
2017-09-05 | 13:10 | 1.7312 | 0 |  | 1.5
2017-09-05 | 13:15 | 1.714 | 0 | 0 | 1.5 | 0 | 87.1553
2017-09-05 | 13:20 | 1.7335 | 0 |  | 1.5
2017-09-05 | 13:25 | 1.7226 | 0 |  | 1.5
2017-09-05 | 13:30 | 1.6968 | 0 | 0 | 1.5 | 0 | 87.945
2017-09-05 | 13:35 | 1.6953 | 0 |  | 1.5
2017-09-05 | 13:40 | 1.6703 | 0 |  | 1.5
2017-09-05 | 13:45 | 1.7234 | 0 | 0 | 1.5 | 0 | 89.3372
2017-09-05 | 13:50 | 1.7195 | 0 |  | 1.5
2017-09-05 | 13:55 | 1.7312 | 0 |  | 1.5
2017-09-05 | 14:00 | 1.7148 | 0 | 0 | 1.5 | 0 | 89.9435
2017-09-05 | 14:05 | 1.7795 | 0 |  | 1.5
2017-09-05 | 14:10 | 1.7881 | 0 |  | 1.5
2017-09-05 | 14:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 89.4662
2017-09-05 | 14:20 | 1.7787 | 0 |  | 1.5
2017-09-05 | 14:25 | 1.7475 | 0 |  | 1.5
2017-09-05 | 14:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 89.0639
2017-09-05 | 14:35 | 1.753 | 0 |  | 1.5
2017-09-05 | 14:40 | 1.7483 | 0 |  | 1.5
2017-09-05 | 14:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 88.7391
2017-09-05 | 14:50 | 1.7858 | 0 |  | 1.5
2017-09-05 | 14:55 | 1.7787 | 0 |  | 1.5
2017-09-05 | 15:00 | 1.7608 | 0 | 0 | 1.5 | 0 | 88.2658
2017-09-05 | 15:05 | 1.7577 | 0 |  | 1.5
2017-09-05 | 15:10 | 1.746 | 0 |  | 1.5
2017-09-05 | 15:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 87.966
2017-09-05 | 15:20 | 1.7312 | 0 |  | 1.5
2017-09-05 | 15:25 | 1.7429 | 0 |  | 1.5
2017-09-05 | 15:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 88.326
2017-09-05 | 15:35 | 1.7304 | 0 |  | 1.5
2017-09-05 | 15:40 | 1.7592 | 0 |  | 1.5
2017-09-05 | 15:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 88.3834
2017-09-05 | 15:50 | 1.7772 | 0 |  | 1.5
2017-09-05 | 15:55 | 1.7826 | 0 |  | 1.5
2017-09-05 | 16:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 87.7501
2017-09-05 | 16:05 | 1.7826 | 0 |  | 1.5
2017-09-05 | 16:10 | 1.7577 | 0 |  | 1.5
2017-09-05 | 16:15 | 1.7865 | 0 | 0 | 1.5 | 0 | 87.281
2017-09-05 | 16:20 | 1.7436 | 0 |  | 1.5
2017-09-05 | 16:25 | 1.7296 | 0 |  | 1.5
2017-09-05 | 16:30 | 1.7772 | 0 | 0 | 1.5 | 0 | 87.316
2017-09-05 | 16:35 | 1.7639 | 0 |  | 1.5
2017-09-05 | 16:40 | 1.7569 | 0 |  | 1.5
2017-09-05 | 16:45 | 1.7912 | 0 | 0 | 1.5 | 0 | 86.7967
2017-09-05 | 16:50 | 1.7741 | 0 |  | 1.5
2017-09-05 | 16:55 | 1.7904 | 0 |  | 1.5
2017-09-05 | 17:00 | 1.7834 | 0 | 0 | 1.5 | 0 | 85.8599
2017-09-05 | 17:05 | 1.7936 | 0 |  | 1.5
2017-09-05 | 17:10 | 1.7764 | 0 |  | 1.5
2017-09-05 | 17:15 | 1.8045 | 0 | 0 | 1.5 | 0 | 84.8902
2017-09-05 | 17:20 | 1.7616 | 0 |  | 1.5
2017-09-05 | 17:25 | 1.7928 | 0 |  | 1.5
2017-09-05 | 17:30 | 1.7959 | 0 | 0 | 1.5 | 0 | 84.0715
2017-09-05 | 17:35 | 1.7764 | 0 |  | 1.5
2017-09-05 | 17:40 | 1.8053 | 0 |  | 1.5
2017-09-05 | 17:45 | 1.8092 | 0 | 0 | 1.5 | 0 | 83.2234
2017-09-05 | 17:50 | 1.7881 | 0 |  | 1.5
2017-09-05 | 17:55 | 1.7639 | 0 |  | 1.5
2017-09-05 | 18:00 | 1.778 | 0 | 0 | 1.5 | 0 | 82.5277
2017-09-05 | 18:05 | 1.7655 | 0 |  | 1.5
2017-09-05 | 18:10 | 1.7803 | 0 |  | 1.5
2017-09-05 | 18:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 82.075
2017-09-05 | 18:20 | 1.7585 | 0 |  | 1.5
2017-09-05 | 18:25 | 1.753 | 0 |  | 1.5
2017-09-05 | 18:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 81.9606
2017-09-05 | 18:35 | 1.7374 | 0 |  | 1.5
2017-09-05 | 18:40 | 1.7834 | 0 |  | 1.5
2017-09-05 | 18:45 | 1.7709 | 0 | 0 | 1.5 | 0 | 81.8815
2017-09-05 | 18:50 | 1.7795 | 0 |  | 1.5
2017-09-05 | 18:55 | 1.799 | 0 |  | 1.5
2017-09-05 | 19:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 81.5099
2017-09-05 | 19:05 | 1.799 | 0 |  | 1.5
2017-09-05 | 19:10 | 1.767 | 0 |  | 1.5
2017-09-05 | 19:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 81.0062
2017-09-05 | 19:20 | 1.7577 | 0 |  | 1.5
2017-09-05 | 19:25 | 1.7834 | 0 |  | 1.5
2017-09-05 | 19:30 | 1.7811 | 0 | 0 | 1.5 | 0 | 80.5891
2017-09-05 | 19:35 | 1.7507 | 0 |  | 1.5
2017-09-05 | 19:40 | 1.7436 | 0 |  | 1.5
2017-09-05 | 19:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 80.1792
2017-09-05 | 19:50 | 1.7725 | 0 |  | 1.5
2017-09-05 | 19:55 | 1.778 | 0 |  | 1.5
2017-09-05 | 20:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.6098
2017-09-05 | 20:05 | 1.7522 | 0 |  | 1.5
2017-09-05 | 20:10 | 1.7507 | 0 |  | 1.5
2017-09-05 | 20:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 79.406
2017-09-05 | 20:20 | 1.7499 | 0 |  | 1.5
2017-09-05 | 20:25 | 1.7561 | 0 |  | 1.5
2017-09-05 | 20:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 79.4453
2017-09-05 | 20:35 | 1.7616 | 0 |  | 1.5
2017-09-05 | 20:40 | 1.7358 | 0 |  | 1.5
2017-09-05 | 20:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 79.5037
2017-09-05 | 20:50 | 1.7889 | 0 |  | 1.5
2017-09-05 | 20:55 | 1.7717 | 0 |  | 1.5
2017-09-05 | 21:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 79.1443
2017-09-05 | 21:05 | -0.1034 | 0 |  | 1.5
2017-09-05 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-05 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 21:20 | -0.10496 | 0 |  | 1.5
2017-09-05 | 21:25 | -0.10496 | 0 |  | 1.5
2017-09-05 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-05 | 21:40 | -0.10496 | 0 |  | 1.5
2017-09-05 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 21:50 | -0.10496 | 0 |  | 1.5
2017-09-05 | 21:55 | -0.10808 | 0 |  | 1.5
2017-09-05 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 22:05 | -0.10574 | 0 |  | 1.5
2017-09-05 | 22:10 | -0.10574 | 0 |  | 1.5
2017-09-05 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 22:20 | -0.10574 | 0 |  | 1.5
2017-09-05 | 22:25 | -0.10574 | 0 |  | 1.5
2017-09-05 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 22:35 | -0.10496 | 0 |  | 1.5
2017-09-05 | 22:40 | -0.10574 | 0 |  | 1.5
2017-09-05 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 22:50 | -0.10496 | 0 |  | 1.5
2017-09-05 | 22:55 | -0.10496 | 0 |  | 1.5
2017-09-05 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 23:05 | -0.10496 | 0 |  | 1.5
2017-09-05 | 23:10 | -0.10496 | 0 |  | 1.5
2017-09-05 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 23:20 | -0.10418 | 0 |  | 1.5
2017-09-05 | 23:25 | -0.10418 | 0 |  | 1.5
2017-09-05 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 23:35 | -0.10418 | 0 |  | 1.5
2017-09-05 | 23:40 | -0.10418 | 0 |  | 1.5
2017-09-05 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-05 | 23:50 | -0.10418 | 0 |  | 1.5
2017-09-05 | 23:55 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 0:05 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:10 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 0:20 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:25 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 0:35 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:40 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 0:50 | -0.1034 | 0 |  | 1.5
2017-09-06 | 0:55 | -0.1034 | 0 |  | 1.5
2017-09-06 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 1:05 | -0.1034 | 0 |  | 1.5
2017-09-06 | 1:10 | -0.1034 | 0 |  | 1.5
2017-09-06 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 1:20 | -0.10574 | 0 |  | 1.5
2017-09-06 | 1:25 | -0.10652 | 0 |  | 1.5
2017-09-06 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 1:35 | -0.10574 | 0 |  | 1.5
2017-09-06 | 1:40 | -0.10574 | 0 |  | 1.5
2017-09-06 | 1:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 1:50 | -0.10574 | 0 |  | 1.5
2017-09-06 | 1:55 | -0.10574 | 0 |  | 1.5
2017-09-06 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 2:05 | -0.10652 | 0 |  | 1.5
2017-09-06 | 2:10 | -0.10652 | 0 |  | 1.5
2017-09-06 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 2:20 | -0.10652 | 0 |  | 1.5
2017-09-06 | 2:25 | -0.10652 | 0 |  | 1.5
2017-09-06 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 2:35 | -0.10652 | 0 |  | 1.5
2017-09-06 | 2:40 | -0.10652 | 0 |  | 1.5
2017-09-06 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-06 | 2:55 | -0.1073 | 0 |  | 1.5
2017-09-06 | 3:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 3:05 | -0.12134 | 0 |  | 1.5
2017-09-06 | 3:10 | -0.12134 | 0 |  | 1.5
2017-09-06 | 3:15 | -0.1229 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 3:20 | -0.12134 | 0 |  | 1.5
2017-09-06 | 3:25 | -0.12134 | 0 |  | 1.5
2017-09-06 | 3:30 | -0.12134 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 3:35 | -0.12212 | 0 |  | 1.5
2017-09-06 | 3:40 | -0.12212 | 0 |  | 1.5
2017-09-06 | 3:45 | -0.12056 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 3:50 | -0.12056 | 0 |  | 1.5
2017-09-06 | 3:55 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:00 | -0.12056 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 4:05 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:10 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:15 | -0.12056 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 4:20 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:25 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:30 | -0.12134 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 4:35 | -0.12134 | 0 |  | 1.5
2017-09-06 | 4:40 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:45 | -0.12134 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 4:50 | -0.12056 | 0 |  | 1.5
2017-09-06 | 4:55 | -0.12056 | 0 |  | 1.5
2017-09-06 | 5:00 | -0.12056 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 5:05 | 1.4847 | 0.60931 |  | 1.5
2017-09-06 | 5:10 | 1.9238 | 0 |  | 1.5
2017-09-06 | 5:15 | 1.9051 | 0 | 0 | 1.5 | 0 | 96.9524
2017-09-06 | 5:20 | 1.8599 | 0 |  | 1.5
2017-09-06 | 5:25 | 1.9332 | 0 |  | 1.5
2017-09-06 | 5:30 | 1.955 | 0 | 0 | 1.5 | 0 | 92.6069
2017-09-06 | 5:35 | 1.9784 | 0 |  | 1.5
2017-09-06 | 5:40 | 1.9691 | 0 |  | 1.5
2017-09-06 | 5:45 | 1.923 | 0 | 0 | 1.5 | 0 | 87.3755
2017-09-06 | 5:50 | 1.8638 | 0 |  | 1.5
2017-09-06 | 5:55 | 1.8567 | 0 |  | 1.5
2017-09-06 | 6:00 | 1.8497 | 0 | 0 | 1.5 | 0 | 84.2979
2017-09-06 | 6:05 | 1.8294 | 0 |  | 1.5
2017-09-06 | 6:10 | 1.8084 | 0 |  | 1.5
2017-09-06 | 6:15 | 1.7951 | 0 | 0 | 1.5 | 0 | 82.3595
2017-09-06 | 6:20 | 1.799 | 0 |  | 1.5
2017-09-06 | 6:25 | 1.8185 | 0 |  | 1.5
2017-09-06 | 6:30 | 1.7819 | 0 | 0 | 1.5 | 0 | 80.9741
2017-09-06 | 6:35 | 1.7756 | 0 |  | 1.5
2017-09-06 | 6:40 | 1.7819 | 0 |  | 1.5
2017-09-06 | 6:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 80.1708
2017-09-06 | 6:50 | 1.7436 | 0 |  | 1.5
2017-09-06 | 6:55 | 1.8021 | 0 |  | 1.5
2017-09-06 | 7:00 | 1.7842 | 0 | 0 | 1.5 | 0 | 79.6383
2017-09-06 | 7:05 | 1.7483 | 0 |  | 1.5
2017-09-06 | 7:10 | 1.7663 | 0 |  | 1.5
2017-09-06 | 7:15 | 1.7709 | 0 | 0 | 1.5 | 0 | 79.0928
2017-09-06 | 7:20 | 1.6812 | 0 |  | 1.5
2017-09-06 | 7:25 | 1.7023 | 0 |  | 1.5
2017-09-06 | 7:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 79.8476
2017-09-06 | 7:35 | 1.7156 | 0 |  | 1.5
2017-09-06 | 7:40 | 1.7156 | 0 |  | 1.5
2017-09-06 | 7:45 | 1.7491 | 0 | 0 | 1.5 | 0 | 80.3303
2017-09-06 | 7:50 | 1.7265 | 0 |  | 1.5
2017-09-06 | 7:55 | 1.7397 | 0 |  | 1.5
2017-09-06 | 8:00 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.4536
2017-09-06 | 8:05 | 1.7327 | 0 |  | 1.5
2017-09-06 | 8:10 | 1.7382 | 0 |  | 1.5
2017-09-06 | 8:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 80.6358
2017-09-06 | 8:20 | 1.7374 | 0 |  | 1.5
2017-09-06 | 8:25 | 1.7592 | 0 |  | 1.5
2017-09-06 | 8:30 | 1.728 | 0 | 0 | 1.5 | 0 | 81.0254
2017-09-06 | 8:35 | 1.7538 | 0 |  | 1.5
2017-09-06 | 8:40 | 1.7678 | 0 |  | 1.5
2017-09-06 | 8:45 | 1.7709 | 0 | 0 | 1.5 | 0 | 81.2219
2017-09-06 | 8:50 | 1.7397 | 0 |  | 1.5
2017-09-06 | 8:55 | 1.7366 | 0 |  | 1.5
2017-09-06 | 9:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 81.5532
2017-09-06 | 9:05 | 1.7522 | 0 |  | 1.5
2017-09-06 | 9:10 | 1.7288 | 0 |  | 1.5
2017-09-06 | 9:15 | 1.7358 | 0 | 0 | 1.5 | 0 | 81.9522
2017-09-06 | 9:20 | 1.7257 | 0 |  | 1.5
2017-09-06 | 9:25 | 1.7273 | 0 |  | 1.5
2017-09-06 | 9:30 | 1.7265 | 0 | 0 | 1.5 | 0 | 82.6012
2017-09-06 | 9:35 | 1.7733 | 0 |  | 1.5
2017-09-06 | 9:40 | 1.7507 | 0 |  | 1.5
2017-09-06 | 9:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 82.3495
2017-09-06 | 9:50 | 1.7631 | 0 |  | 1.5
2017-09-06 | 9:55 | 1.7429 | 0 |  | 1.5
2017-09-06 | 10:00 | 1.7031 | 0 | 0 | 1.5 | 0 | 82.4865
2017-09-06 | 10:05 | 1.7343 | 0 |  | 1.5
2017-09-06 | 10:10 | 1.739 | 0 |  | 1.5
2017-09-06 | 10:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 83.0245
2017-09-06 | 10:20 | 1.7335 | 0 |  | 1.5
2017-09-06 | 10:25 | 1.7483 | 0 |  | 1.5
2017-09-06 | 10:30 | 1.6922 | 0 | 0 | 1.5 | 0 | 83.4376
2017-09-06 | 10:35 | 1.7351 | 0 |  | 1.5
2017-09-06 | 10:40 | 1.7397 | 0 |  | 1.5
2017-09-06 | 10:45 | 1.7109 | 0 | 0 | 1.5 | 0 | 83.6675
2017-09-06 | 10:50 | 1.7101 | 0 |  | 1.5
2017-09-06 | 10:55 | 1.714 | 0 |  | 1.5
2017-09-06 | 11:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 84.3831
2017-09-06 | 11:05 | 1.7304 | 0 |  | 1.5
2017-09-06 | 11:10 | 1.767 | 0 |  | 1.5
2017-09-06 | 11:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 84.5235
2017-09-06 | 11:20 | 1.7491 | 0 |  | 1.5
2017-09-06 | 11:25 | 1.7561 | 0 |  | 1.5
2017-09-06 | 11:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 84.617
2017-09-06 | 11:35 | 1.6976 | 0 |  | 1.5
2017-09-06 | 11:40 | 1.7358 | 0 |  | 1.5
2017-09-06 | 11:45 | 1.7132 | 0 | 0 | 1.5 | 0 | 85.1881
2017-09-06 | 11:50 | 1.7514 | 0 |  | 1.5
2017-09-06 | 11:55 | 1.7296 | 0 |  | 1.5
2017-09-06 | 12:00 | 1.7795 | 0 | 0 | 1.5 | 0 | 84.8982
2017-09-06 | 12:05 | 1.7694 | 0 |  | 1.5
2017-09-06 | 12:10 | 1.7546 | 0 |  | 1.5
2017-09-06 | 12:15 | 1.8045 | 0 | 0 | 1.5 | 0 | 84.4592
2017-09-06 | 12:20 | 1.7561 | 0 |  | 1.5
2017-09-06 | 12:25 | 1.7561 | 0 |  | 1.5
2017-09-06 | 12:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 83.9631
2017-09-06 | 12:35 | 1.7616 | 0 |  | 1.5
2017-09-06 | 12:40 | 1.7405 | 0 |  | 1.5
2017-09-06 | 12:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 83.7247
2017-09-06 | 12:50 | 1.7655 | 0 |  | 1.5
2017-09-06 | 12:55 | 1.7709 | 0 |  | 1.5
2017-09-06 | 13:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 83.2166
2017-09-06 | 13:05 | 1.7507 | 0 |  | 1.5
2017-09-06 | 13:10 | 1.7374 | 0 |  | 1.5
2017-09-06 | 13:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 83.1492
2017-09-06 | 13:20 | 1.7351 | 0 |  | 1.5
2017-09-06 | 13:25 | 1.7748 | 0 |  | 1.5
2017-09-06 | 13:30 | 1.7577 | 0 | 0 | 1.5 | 0 | 83.118
2017-09-06 | 13:35 | 1.7374 | 0 |  | 1.5
2017-09-06 | 13:40 | 1.7787 | 0 |  | 1.5
2017-09-06 | 13:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 83.2252
2017-09-06 | 13:50 | 1.7405 | 0 |  | 1.5
2017-09-06 | 13:55 | 1.7397 | 0 |  | 1.5
2017-09-06 | 14:00 | 1.7312 | 0 | 0 | 1.5 | 0 | 83.2348
2017-09-06 | 14:05 | 1.7405 | 0 |  | 1.5
2017-09-06 | 14:10 | 1.7452 | 0 |  | 1.5
2017-09-06 | 14:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 83.4505
2017-09-06 | 14:20 | 1.7163 | 0 |  | 1.5
2017-09-06 | 14:25 | 1.7366 | 0 |  | 1.5
2017-09-06 | 14:30 | 1.7421 | 0 | 0 | 1.5 | 0 | 83.6423
2017-09-06 | 14:35 | 1.7234 | 0 |  | 1.5
2017-09-06 | 14:40 | 1.7499 | 0 |  | 1.5
2017-09-06 | 14:45 | 1.7288 | 0 | 0 | 1.5 | 0 | 83.8609
2017-09-06 | 14:50 | 1.7124 | 0 |  | 1.5
2017-09-06 | 14:55 | 1.7421 | 0 |  | 1.5
2017-09-06 | 15:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 84.4439
2017-09-06 | 15:05 | 1.7163 | 0 |  | 1.5
2017-09-06 | 15:10 | 1.7257 | 0 |  | 1.5
2017-09-06 | 15:15 | 1.7366 | 0 | 0 | 1.5 | 0 | 84.989
2017-09-06 | 15:20 | 1.7702 | 0 |  | 1.5
2017-09-06 | 15:25 | 1.7249 | 0 |  | 1.5
2017-09-06 | 15:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 85.2733
2017-09-06 | 15:35 | 1.7265 | 0 |  | 1.5
2017-09-06 | 15:40 | 1.7507 | 0 |  | 1.5
2017-09-06 | 15:45 | 1.7413 | 0 | 0 | 1.5 | 0 | 85.4727
2017-09-06 | 15:50 | 1.7374 | 0 |  | 1.5
2017-09-06 | 15:55 | 1.7655 | 0 |  | 1.5
2017-09-06 | 16:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 85.485
2017-09-06 | 16:05 | 1.792 | 0 |  | 1.5
2017-09-06 | 16:10 | 1.7483 | 0 |  | 1.5
2017-09-06 | 16:15 | 1.7834 | 0 | 0 | 1.5 | 0 | 85.1967
2017-09-06 | 16:20 | 1.7312 | 0 |  | 1.5
2017-09-06 | 16:25 | 1.7569 | 0 |  | 1.5
2017-09-06 | 16:30 | 1.7881 | 0 | 0 | 1.5 | 0 | 84.6508
2017-09-06 | 16:35 | 1.7358 | 0 |  | 1.5
2017-09-06 | 16:40 | 1.7678 | 0 |  | 1.5
2017-09-06 | 16:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 84.3675
2017-09-06 | 16:50 | 1.7803 | 0 |  | 1.5
2017-09-06 | 16:55 | 1.7312 | 0 |  | 1.5
2017-09-06 | 17:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 84.0555
2017-09-06 | 17:05 | 1.7585 | 0 |  | 1.5
2017-09-06 | 17:10 | 1.7351 | 0 |  | 1.5
2017-09-06 | 17:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 83.9167
2017-09-06 | 17:20 | 1.7811 | 0 |  | 1.5
2017-09-06 | 17:25 | 1.7787 | 0 |  | 1.5
2017-09-06 | 17:30 | 1.7834 | 0 | 0 | 1.5 | 0 | 83.1844
2017-09-06 | 17:35 | 1.7912 | 0 |  | 1.5
2017-09-06 | 17:40 | 1.792 | 0 |  | 1.5
2017-09-06 | 17:45 | 1.7772 | 0 | 0 | 1.5 | 0 | 82.4676
2017-09-06 | 17:50 | 1.7624 | 0 |  | 1.5
2017-09-06 | 17:55 | 1.7717 | 0 |  | 1.5
2017-09-06 | 18:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.131
2017-09-06 | 18:05 | 1.7842 | 0 |  | 1.5
2017-09-06 | 18:10 | 1.7553 | 0 |  | 1.5
2017-09-06 | 18:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 81.7684
2017-09-06 | 18:20 | 1.76 | 0 |  | 1.5
2017-09-06 | 18:25 | 1.7717 | 0 |  | 1.5
2017-09-06 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.3847
2017-09-06 | 18:35 | 1.7655 | 0 |  | 1.5
2017-09-06 | 18:40 | 1.7647 | 0 |  | 1.5
2017-09-06 | 18:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.1174
2017-09-06 | 18:50 | 1.7475 | 0 |  | 1.5
2017-09-06 | 18:55 | 1.7647 | 0 |  | 1.5
2017-09-06 | 19:00 | 1.739 | 0 | 0 | 1.5 | 0 | 81.1269
2017-09-06 | 19:05 | 1.7538 | 0 |  | 1.5
2017-09-06 | 19:10 | 1.7694 | 0 |  | 1.5
2017-09-06 | 19:15 | 1.7733 | 0 | 0 | 1.5 | 0 | 80.8162
2017-09-06 | 19:20 | 1.767 | 0 |  | 1.5
2017-09-06 | 19:25 | 1.7842 | 0 |  | 1.5
2017-09-06 | 19:30 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.271
2017-09-06 | 19:35 | 1.7366 | 0 |  | 1.5
2017-09-06 | 19:40 | 1.7538 | 0 |  | 1.5
2017-09-06 | 19:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 80.0871
2017-09-06 | 19:50 | 1.7468 | 0 |  | 1.5
2017-09-06 | 19:55 | 1.7803 | 0 |  | 1.5
2017-09-06 | 20:00 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.6077
2017-09-06 | 20:05 | 1.7413 | 0 |  | 1.5
2017-09-06 | 20:10 | 1.7538 | 0 |  | 1.5
2017-09-06 | 20:15 | 1.7842 | 0 | 0 | 1.5 | 0 | 79.3418
2017-09-06 | 20:20 | 1.7678 | 0 |  | 1.5
2017-09-06 | 20:25 | 1.7592 | 0 |  | 1.5
2017-09-06 | 20:30 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.1768
2017-09-06 | 20:35 | 1.76 | 0 |  | 1.5
2017-09-06 | 20:40 | 1.7483 | 0 |  | 1.5
2017-09-06 | 20:45 | 1.7756 | 0 | 0 | 1.5 | 0 | 79.0427
2017-09-06 | 20:50 | 1.7413 | 0 |  | 1.5
2017-09-06 | 20:55 | 1.7499 | 0 |  | 1.5
2017-09-06 | 21:00 | 1.7912 | 0 | 0 | 1.5 | 0 | 78.8772
2017-09-06 | 21:05 | -0.1034 | 0 |  | 1.5
2017-09-06 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-06 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 21:20 | -0.10418 | 0 |  | 1.5
2017-09-06 | 21:25 | -0.10262 | 0 |  | 1.5
2017-09-06 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-06 | 21:40 | -0.10496 | 0 |  | 1.5
2017-09-06 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 21:50 | -0.10574 | 0 |  | 1.5
2017-09-06 | 21:55 | -0.10574 | 0 |  | 1.5
2017-09-06 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 22:05 | -0.10574 | 0 |  | 1.5
2017-09-06 | 22:10 | -0.10574 | 0 |  | 1.5
2017-09-06 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 22:20 | -0.10574 | 0 |  | 1.5
2017-09-06 | 22:25 | -0.10496 | 0 |  | 1.5
2017-09-06 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 22:35 | -0.10496 | 0 |  | 1.5
2017-09-06 | 22:40 | -0.10496 | 0 |  | 1.5
2017-09-06 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 22:50 | -0.10496 | 0 |  | 1.5
2017-09-06 | 22:55 | -0.10496 | 0 |  | 1.5
2017-09-06 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 23:05 | -0.10496 | 0 |  | 1.5
2017-09-06 | 23:10 | -0.10496 | 0 |  | 1.5
2017-09-06 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 23:20 | -0.10496 | 0 |  | 1.5
2017-09-06 | 23:25 | -0.10496 | 0 |  | 1.5
2017-09-06 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 23:35 | -0.10418 | 0 |  | 1.5
2017-09-06 | 23:40 | -0.10418 | 0 |  | 1.5
2017-09-06 | 23:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-06 | 23:50 | -0.1034 | 0 |  | 1.5
2017-09-06 | 23:55 | -0.10418 | 0 |  | 1.5
2017-09-07 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 0:05 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:10 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 0:20 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:25 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 0:35 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:40 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 0:50 | -0.1034 | 0 |  | 1.5
2017-09-07 | 0:55 | -0.1034 | 0 |  | 1.5
2017-09-07 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 1:05 | -0.1034 | 0 |  | 1.5
2017-09-07 | 1:10 | -0.1034 | 0 |  | 1.5
2017-09-07 | 1:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 1:20 | -0.10496 | 0 |  | 1.5
2017-09-07 | 1:25 | -0.10574 | 0 |  | 1.5
2017-09-07 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 1:35 | -0.10652 | 0 |  | 1.5
2017-09-07 | 1:40 | -0.10652 | 0 |  | 1.5
2017-09-07 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 1:50 | -0.10652 | 0 |  | 1.5
2017-09-07 | 1:55 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 2:05 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:10 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 2:20 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:25 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 2:35 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:40 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 2:50 | -0.10652 | 0 |  | 1.5
2017-09-07 | 2:55 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 3:05 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:10 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 3:20 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:25 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 3:35 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:40 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 3:50 | -0.10652 | 0 |  | 1.5
2017-09-07 | 3:55 | -0.10652 | 0 |  | 1.5
2017-09-07 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 4:05 | -0.10652 | 0 |  | 1.5
2017-09-07 | 4:10 | -0.1073 | 0 |  | 1.5
2017-09-07 | 4:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 4:20 | -0.1073 | 0 |  | 1.5
2017-09-07 | 4:25 | -0.1073 | 0 |  | 1.5
2017-09-07 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 4:35 | -0.1073 | 0 |  | 1.5
2017-09-07 | 4:40 | -0.1073 | 0 |  | 1.5
2017-09-07 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 4:50 | -0.1073 | 0 |  | 1.5
2017-09-07 | 4:55 | -0.1073 | 0 |  | 1.5
2017-09-07 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 5:05 | 1.494 | 0 |  | 1.5
2017-09-07 | 5:10 | 1.7538 | 0 |  | 1.5
2017-09-07 | 5:15 | 1.8029 | 0 | 0 | 1.5 | 0 | 99.3889
2017-09-07 | 5:20 | 1.8427 | 0 |  | 1.5
2017-09-07 | 5:25 | 1.8989 | 0 |  | 1.5
2017-09-07 | 5:30 | 1.9113 | 0 | 0 | 1.5 | 0 | 96.3778
2017-09-07 | 5:35 | 1.9605 | 0 |  | 1.5
2017-09-07 | 5:40 | 1.9917 | 0 |  | 1.5
2017-09-07 | 5:45 | 1.9737 | 0 | 0 | 1.5 | 0 | 90.2744
2017-09-07 | 5:50 | 1.9316 | 0 |  | 1.5
2017-09-07 | 5:55 | 1.9035 | 0 |  | 1.5
2017-09-07 | 6:00 | 1.845 | 0 | 0 | 1.5 | 0 | 85.8481
2017-09-07 | 6:05 | 1.8599 | 0 |  | 1.5
2017-09-07 | 6:10 | 1.8411 | 0 |  | 1.5
2017-09-07 | 6:15 | 1.8201 | 0 | 0 | 1.5 | 0 | 83.1521
2017-09-07 | 6:20 | 1.8326 | 0 |  | 1.5
2017-09-07 | 6:25 | 1.817 | 0 |  | 1.5
2017-09-07 | 6:30 | 1.8029 | 0 | 0 | 1.5 | 0 | 81.4684
2017-09-07 | 6:35 | 1.8053 | 0 |  | 1.5
2017-09-07 | 6:40 | 1.7998 | 0 |  | 1.5
2017-09-07 | 6:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 80.4094
2017-09-07 | 6:50 | 1.7725 | 0 |  | 1.5
2017-09-07 | 6:55 | 1.7631 | 0 |  | 1.5
2017-09-07 | 7:00 | 1.7819 | 0 | 0 | 1.5 | 0 | 79.7367
2017-09-07 | 7:05 | 1.7397 | 0 |  | 1.5
2017-09-07 | 7:10 | 1.7741 | 0 |  | 1.5
2017-09-07 | 7:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.6588
2017-09-07 | 7:20 | 1.7475 | 0 |  | 1.5
2017-09-07 | 7:25 | 1.7483 | 0 |  | 1.5
2017-09-07 | 7:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 79.5399
2017-09-07 | 7:35 | 1.7538 | 0 |  | 1.5
2017-09-07 | 7:40 | 1.7436 | 0 |  | 1.5
2017-09-07 | 7:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 79.6373
2017-09-07 | 7:50 | 1.7787 | 0 |  | 1.5
2017-09-07 | 7:55 | 1.7421 | 0 |  | 1.5
2017-09-07 | 8:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 79.3557
2017-09-07 | 8:05 | 1.7468 | 0 |  | 1.5
2017-09-07 | 8:10 | 1.7686 | 0 |  | 1.5
2017-09-07 | 8:15 | 1.7436 | 0 | 0 | 1.5 | 0 | 79.4213
2017-09-07 | 8:20 | 1.7475 | 0 |  | 1.5
2017-09-07 | 8:25 | 1.7717 | 0 |  | 1.5
2017-09-07 | 8:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 79.4465
2017-09-07 | 8:35 | 1.7507 | 0 |  | 1.5
2017-09-07 | 8:40 | 1.7694 | 0 |  | 1.5
2017-09-07 | 8:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 79.3996
2017-09-07 | 8:50 | 1.7514 | 0 |  | 1.5
2017-09-07 | 8:55 | 1.767 | 0 |  | 1.5
2017-09-07 | 9:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 79.6501
2017-09-07 | 9:05 | 1.7273 | 0 |  | 1.5
2017-09-07 | 9:10 | 1.7374 | 0 |  | 1.5
2017-09-07 | 9:15 | 1.7273 | 0 | 0 | 1.5 | 0 | 79.972
2017-09-07 | 9:20 | 1.7826 | 0 |  | 1.5
2017-09-07 | 9:25 | 1.7366 | 0 |  | 1.5
2017-09-07 | 9:30 | 1.7218 | 0 | 0 | 1.5 | 0 | 80.4675
2017-09-07 | 9:35 | 1.7499 | 0 |  | 1.5
2017-09-07 | 9:40 | 1.753 | 0 |  | 1.5
2017-09-07 | 9:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 80.4901
2017-09-07 | 9:50 | 1.7436 | 0 |  | 1.5
2017-09-07 | 9:55 | 1.7351 | 0 |  | 1.5
2017-09-07 | 10:00 | 1.7468 | 0 | 0 | 1.5 | 0 | 80.7662
2017-09-07 | 10:05 | 1.7631 | 0 |  | 1.5
2017-09-07 | 10:10 | 1.714 | 0 |  | 1.5
2017-09-07 | 10:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 80.9572
2017-09-07 | 10:20 | 1.7312 | 0 |  | 1.5
2017-09-07 | 10:25 | 1.7304 | 0 |  | 1.5
2017-09-07 | 10:30 | 1.7179 | 0 | 0 | 1.5 | 0 | 81.839
2017-09-07 | 10:35 | 1.7608 | 0 |  | 1.5
2017-09-07 | 10:40 | 1.7343 | 0 |  | 1.5
2017-09-07 | 10:45 | 1.7257 | 0 | 0 | 1.5 | 0 | 82.0421
2017-09-07 | 10:50 | 1.7436 | 0 |  | 1.5
2017-09-07 | 10:55 | 1.7647 | 0 |  | 1.5
2017-09-07 | 11:00 | 1.7499 | 0 | 0 | 1.5 | 0 | 81.9435
2017-09-07 | 11:05 | 1.7756 | 0 |  | 1.5
2017-09-07 | 11:10 | 1.7826 | 0 |  | 1.5
2017-09-07 | 11:15 | 1.7351 | 0 | 0 | 1.5 | 0 | 81.6662
2017-09-07 | 11:20 | 1.707 | 0 |  | 1.5
2017-09-07 | 11:25 | 1.7179 | 0 |  | 1.5
2017-09-07 | 11:30 | 1.7343 | 0 | 0 | 1.5 | 0 | 82.5383
2017-09-07 | 11:35 | 1.7226 | 0 |  | 1.5
2017-09-07 | 11:40 | 1.7195 | 0 |  | 1.5
2017-09-07 | 11:45 | 1.8131 | 0 | 0 | 1.5 | 0 | 82.7389
2017-09-07 | 11:50 | 1.8045 | 0 |  | 1.5
2017-09-07 | 11:55 | 1.7741 | 0 |  | 1.5
2017-09-07 | 12:00 | 1.7304 | 0 | 0 | 1.5 | 0 | 82.278
2017-09-07 | 12:05 | 1.7608 | 0 |  | 1.5
2017-09-07 | 12:10 | 1.746 | 0 |  | 1.5
2017-09-07 | 12:15 | 1.7132 | 0 | 0 | 1.5 | 0 | 82.2762
2017-09-07 | 12:20 | 1.6961 | 0 |  | 1.5
2017-09-07 | 12:25 | 1.7522 | 0 |  | 1.5
2017-09-07 | 12:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 82.1303
2017-09-07 | 12:35 | 1.7046 | 0 |  | 1.5
2017-09-07 | 12:40 | 1.7553 | 0 |  | 1.5
2017-09-07 | 12:45 | 1.7296 | 0 | 0 | 1.5 | 0 | 82.3227
2017-09-07 | 12:50 | 1.746 | 0 |  | 1.5
2017-09-07 | 12:55 | 1.7335 | 0 |  | 1.5
2017-09-07 | 13:00 | 1.7171 | 0 | 0 | 1.5 | 0 | 82.6824
2017-09-07 | 13:05 | 1.7124 | 0 |  | 1.5
2017-09-07 | 13:10 | 1.7694 | 0 |  | 1.5
2017-09-07 | 13:15 | 1.7327 | 0 | 0 | 1.5 | 0 | 83.0242
2017-09-07 | 13:20 | 1.6961 | 0 |  | 1.5
2017-09-07 | 13:25 | 1.6656 | 0 |  | 1.5
2017-09-07 | 13:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 84.0036
2017-09-07 | 13:35 | 1.6633 | 0 |  | 1.5
2017-09-07 | 13:40 | 1.6898 | 0 |  | 1.5
2017-09-07 | 13:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 85.0331
2017-09-07 | 13:50 | 1.7343 | 0 |  | 1.5
2017-09-07 | 13:55 | 1.7218 | 0 |  | 1.5
2017-09-07 | 14:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 85.2782
2017-09-07 | 14:05 | 1.7491 | 0 |  | 1.5
2017-09-07 | 14:10 | 1.7101 | 0 |  | 1.5
2017-09-07 | 14:15 | 1.7202 | 0 | 0 | 1.5 | 0 | 85.8674
2017-09-07 | 14:20 | 1.7156 | 0 |  | 1.5
2017-09-07 | 14:25 | 1.7725 | 0 |  | 1.5
2017-09-07 | 14:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 86.1373
2017-09-07 | 14:35 | 1.7156 | 0 |  | 1.5
2017-09-07 | 14:40 | 1.7296 | 0 |  | 1.5
2017-09-07 | 14:45 | 1.7218 | 0 | 0 | 1.5 | 0 | 87.032
2017-09-07 | 14:50 | 1.7304 | 0 |  | 1.5
2017-09-07 | 14:55 | 1.7273 | 0 |  | 1.5
2017-09-07 | 15:00 | 1.7015 | 0 | 0 | 1.5 | 0 | 87.9654
2017-09-07 | 15:05 | 1.7257 | 0 |  | 1.5
2017-09-07 | 15:10 | 1.6656 | 0 |  | 1.5
2017-09-07 | 15:15 | 1.728 | 0 | 0 | 1.5 | 0 | 89.0899
2017-09-07 | 15:20 | 1.7085 | 0 |  | 1.5
2017-09-07 | 15:25 | 1.7202 | 0 |  | 1.5
2017-09-07 | 15:30 | 1.753 | 0 | 0 | 1.5 | 0 | 89.712
2017-09-07 | 15:35 | 1.7608 | 0 |  | 1.5
2017-09-07 | 15:40 | 1.7748 | 0 |  | 1.5
2017-09-07 | 15:45 | 1.7265 | 0 | 0 | 1.5 | 0 | 89.6393
2017-09-07 | 15:50 | 1.778 | 0 |  | 1.5
2017-09-07 | 15:55 | 1.7959 | 0 |  | 1.5
2017-09-07 | 16:00 | 1.7912 | 0 | 0 | 1.5 | 0 | 88.7707
2017-09-07 | 16:05 | 1.7928 | 0 |  | 1.5
2017-09-07 | 16:10 | 1.7624 | 0 |  | 1.5
2017-09-07 | 16:15 | 1.7881 | 0 | 0 | 1.5 | 0 | 88.2924
2017-09-07 | 16:20 | 1.8037 | 0 |  | 1.5
2017-09-07 | 16:25 | 1.7756 | 0 |  | 1.5
2017-09-07 | 16:30 | 1.8162 | 0 | 0 | 1.5 | 0 | 87.1114
2017-09-07 | 16:35 | 1.8287 | 0 |  | 1.5
2017-09-07 | 16:40 | 1.8037 | 0 |  | 1.5
2017-09-07 | 16:45 | 1.7702 | 0 | 0 | 1.5 | 0 | 85.642
2017-09-07 | 16:50 | 1.7624 | 0 |  | 1.5
2017-09-07 | 16:55 | 1.76 | 0 |  | 1.5
2017-09-07 | 17:00 | 1.8021 | 0 | 0 | 1.5 | 0 | 84.7502
2017-09-07 | 17:05 | 1.817 | 0 |  | 1.5
2017-09-07 | 17:10 | 1.7982 | 0 |  | 1.5
2017-09-07 | 17:15 | 1.7772 | 0 | 0 | 1.5 | 0 | 83.9085
2017-09-07 | 17:20 | 1.7826 | 0 |  | 1.5
2017-09-07 | 17:25 | 1.7748 | 0 |  | 1.5
2017-09-07 | 17:30 | 1.7616 | 0 | 0 | 1.5 | 0 | 83.1918
2017-09-07 | 17:35 | 1.7694 | 0 |  | 1.5
2017-09-07 | 17:40 | 1.7733 | 0 |  | 1.5
2017-09-07 | 17:45 | 1.7561 | 0 | 0 | 1.5 | 0 | 82.512
2017-09-07 | 17:50 | 1.7819 | 0 |  | 1.5
2017-09-07 | 17:55 | 1.8021 | 0 |  | 1.5
2017-09-07 | 18:00 | 1.7865 | 0 | 0 | 1.5 | 0 | 81.8608
2017-09-07 | 18:05 | 1.7436 | 0 |  | 1.5
2017-09-07 | 18:10 | 1.7678 | 0 |  | 1.5
2017-09-07 | 18:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 81.3107
2017-09-07 | 18:20 | 1.785 | 0 |  | 1.5
2017-09-07 | 18:25 | 1.739 | 0 |  | 1.5
2017-09-07 | 18:30 | 1.76 | 0 | 0 | 1.5 | 0 | 80.9734
2017-09-07 | 18:35 | 1.7522 | 0 |  | 1.5
2017-09-07 | 18:40 | 1.7764 | 0 |  | 1.5
2017-09-07 | 18:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 80.7781
2017-09-07 | 18:50 | 1.7499 | 0 |  | 1.5
2017-09-07 | 18:55 | 1.7538 | 0 |  | 1.5
2017-09-07 | 19:00 | 1.739 | 0 | 0 | 1.5 | 0 | 80.4243
2017-09-07 | 19:05 | 1.7741 | 0 |  | 1.5
2017-09-07 | 19:10 | 1.7553 | 0 |  | 1.5
2017-09-07 | 19:15 | 1.7811 | 0 | 0 | 1.5 | 0 | 80.1091
2017-09-07 | 19:20 | 1.767 | 0 |  | 1.5
2017-09-07 | 19:25 | 1.7624 | 0 |  | 1.5
2017-09-07 | 19:30 | 1.7694 | 0 | 0 | 1.5 | 0 | 79.7374
2017-09-07 | 19:35 | 1.7647 | 0 |  | 1.5
2017-09-07 | 19:40 | 1.7686 | 0 |  | 1.5
2017-09-07 | 19:45 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.1798
2017-09-07 | 19:50 | 1.7686 | 0 |  | 1.5
2017-09-07 | 19:55 | 1.7585 | 0 |  | 1.5
2017-09-07 | 20:00 | 1.7795 | 0 | 0 | 1.5 | 0 | 78.6471
2017-09-07 | 20:05 | 1.7577 | 0 |  | 1.5
2017-09-07 | 20:10 | 1.7577 | 0 |  | 1.5
2017-09-07 | 20:15 | 1.753 | 0 | 0 | 1.5 | 0 | 78.4633
2017-09-07 | 20:20 | 1.7631 | 0 |  | 1.5
2017-09-07 | 20:25 | 1.7522 | 0 |  | 1.5
2017-09-07 | 20:30 | 1.7904 | 0 | 0 | 1.5 | 0 | 78.2365
2017-09-07 | 20:35 | 1.7678 | 0 |  | 1.5
2017-09-07 | 20:40 | 1.7546 | 0 |  | 1.5
2017-09-07 | 20:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 78.1618
2017-09-07 | 20:50 | 1.7483 | 0 |  | 1.5
2017-09-07 | 20:55 | 1.7436 | 0 |  | 1.5
2017-09-07 | 21:00 | 1.753 | 0 | 0 | 1.5 | 0 | 78.3597
2017-09-07 | 21:05 | -0.1034 | 0 |  | 1.5
2017-09-07 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-07 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 21:20 | -0.10496 | 0 |  | 1.5
2017-09-07 | 21:25 | -0.10496 | 0 |  | 1.5
2017-09-07 | 21:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-07 | 21:40 | -0.10574 | 0 |  | 1.5
2017-09-07 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 21:50 | -0.10574 | 0 |  | 1.5
2017-09-07 | 21:55 | -0.10574 | 0 |  | 1.5
2017-09-07 | 22:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 22:05 | -0.10574 | 0 |  | 1.5
2017-09-07 | 22:10 | -0.10652 | 0 |  | 1.5
2017-09-07 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 22:20 | -0.10652 | 0 |  | 1.5
2017-09-07 | 22:25 | -0.10574 | 0 |  | 1.5
2017-09-07 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 22:35 | -0.10574 | 0 |  | 1.5
2017-09-07 | 22:40 | -0.10496 | 0 |  | 1.5
2017-09-07 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 22:50 | -0.10496 | 0 |  | 1.5
2017-09-07 | 22:55 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 23:05 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:10 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 23:20 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:25 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 23:35 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:40 | -0.10418 | 0 |  | 1.5
2017-09-07 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-07 | 23:50 | -0.10496 | 0 |  | 1.5
2017-09-07 | 23:55 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 0:05 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:10 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 0:20 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:25 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 0:35 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:40 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 0:50 | -0.10496 | 0 |  | 1.5
2017-09-08 | 0:55 | -0.10496 | 0 |  | 1.5
2017-09-08 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 1:05 | -0.10496 | 0 |  | 1.5
2017-09-08 | 1:10 | -0.10496 | 0 |  | 1.5
2017-09-08 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 1:20 | -0.10808 | 0 |  | 1.5
2017-09-08 | 1:25 | -0.10886 | 0 |  | 1.5
2017-09-08 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 1:35 | -0.10808 | 0 |  | 1.5
2017-09-08 | 1:40 | -0.10808 | 0 |  | 1.5
2017-09-08 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 1:50 | -0.10808 | 0 |  | 1.5
2017-09-08 | 1:55 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 2:05 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:10 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 2:20 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:25 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 2:35 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:40 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-08 | 2:55 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 3:05 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:10 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 3:20 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:25 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 3:35 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:40 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 3:50 | -0.10808 | 0 |  | 1.5
2017-09-08 | 3:55 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 4:05 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:10 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 4:20 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:25 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 4:35 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:40 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 4:50 | -0.10808 | 0 |  | 1.5
2017-09-08 | 4:55 | -0.10808 | 0 |  | 1.5
2017-09-08 | 5:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 5:05 | 1.7366 | 0 |  | 1.5
2017-09-08 | 5:10 | 2.0455 | 0 |  | 1.5
2017-09-08 | 5:15 | 1.9948 | 0 | 0 | 1.5 | 0 | 94.0941
2017-09-08 | 5:20 | 1.8926 | 0 |  | 1.5
2017-09-08 | 5:25 | 1.9363 | 0 |  | 1.5
2017-09-08 | 5:30 | 1.9301 | 0 | 0 | 1.5 | 0 | 89.2686
2017-09-08 | 5:35 | 1.8957 | 0 |  | 1.5
2017-09-08 | 5:40 | 1.8505 | 0 |  | 1.5
2017-09-08 | 5:45 | 1.838 | 0 | 0 | 1.5 | 0 | 85.7123
2017-09-08 | 5:50 | 1.838 | 0 |  | 1.5
2017-09-08 | 5:55 | 1.824 | 0 |  | 1.5
2017-09-08 | 6:00 | 1.8029 | 0 | 0 | 1.5 | 0 | 84.0032
2017-09-08 | 6:05 | 1.8006 | 0 |  | 1.5
2017-09-08 | 6:10 | 1.806 | 0 |  | 1.5
2017-09-08 | 6:15 | 1.7764 | 0 | 0 | 1.5 | 0 | 82.6698
2017-09-08 | 6:20 | 1.7803 | 0 |  | 1.5
2017-09-08 | 6:25 | 1.7811 | 0 |  | 1.5
2017-09-08 | 6:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 81.858
2017-09-08 | 6:35 | 1.7592 | 0 |  | 1.5
2017-09-08 | 6:40 | 1.7756 | 0 |  | 1.5
2017-09-08 | 6:45 | 1.7686 | 0 | 0 | 1.5 | 0 | 81.4786
2017-09-08 | 6:50 | 1.7967 | 0 |  | 1.5
2017-09-08 | 6:55 | 1.8209 | 0 |  | 1.5
2017-09-08 | 7:00 | 1.7631 | 0 | 0 | 1.5 | 0 | 80.7775
2017-09-08 | 7:05 | 1.7928 | 0 |  | 1.5
2017-09-08 | 7:10 | 1.7639 | 0 |  | 1.5
2017-09-08 | 7:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 80.025
2017-09-08 | 7:20 | 1.7702 | 0 |  | 1.5
2017-09-08 | 7:25 | 1.778 | 0 |  | 1.5
2017-09-08 | 7:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.3797
2017-09-08 | 7:35 | 1.746 | 0 |  | 1.5
2017-09-08 | 7:40 | 1.7795 | 0 |  | 1.5
2017-09-08 | 7:45 | 1.746 | 0 | 0 | 1.5 | 0 | 79.0897
2017-09-08 | 7:50 | 1.7748 | 0 |  | 1.5
2017-09-08 | 7:55 | 1.7717 | 0 |  | 1.5
2017-09-08 | 8:00 | 1.7842 | 0 | 0 | 1.5 | 0 | 78.7458
2017-09-08 | 8:05 | 1.7608 | 0 |  | 1.5
2017-09-08 | 8:10 | 1.7733 | 0 |  | 1.5
2017-09-08 | 8:15 | 1.7132 | 0 | 0 | 1.5 | 0 | 78.7292
2017-09-08 | 8:20 | 1.7171 | 0 |  | 1.5
2017-09-08 | 8:25 | 1.6922 | 0 |  | 1.5
2017-09-08 | 8:30 | 1.7288 | 0 | 0 | 1.5 | 0 | 79.6302
2017-09-08 | 8:35 | 1.7366 | 0 |  | 1.5
2017-09-08 | 8:40 | 1.7265 | 0 |  | 1.5
2017-09-08 | 8:45 | 1.739 | 0 | 0 | 1.5 | 0 | 80.024
2017-09-08 | 8:50 | 1.7592 | 0 |  | 1.5
2017-09-08 | 8:55 | 1.7179 | 0 |  | 1.5
2017-09-08 | 9:00 | 1.7358 | 0 | 0 | 1.5 | 0 | 80.5731
2017-09-08 | 9:05 | 1.7288 | 0 |  | 1.5
2017-09-08 | 9:10 | 1.7764 | 0 |  | 1.5
2017-09-08 | 9:15 | 1.7694 | 0 | 0 | 1.5 | 0 | 81.0509
2017-09-08 | 9:20 | 1.7585 | 0 |  | 1.5
2017-09-08 | 9:25 | 1.7514 | 0 |  | 1.5
2017-09-08 | 9:30 | 1.7218 | 0 | 0 | 1.5 | 0 | 81.2861
2017-09-08 | 9:35 | 1.721 | 0 |  | 1.5
2017-09-08 | 9:40 | 1.7444 | 0 |  | 1.5
2017-09-08 | 9:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 81.4077
2017-09-08 | 9:50 | 1.7374 | 0 |  | 1.5
2017-09-08 | 9:55 | 1.7475 | 0 |  | 1.5
2017-09-08 | 10:00 | 1.7187 | 0 | 0 | 1.5 | 0 | 81.8765
2017-09-08 | 10:05 | 1.7351 | 0 |  | 1.5
2017-09-08 | 10:10 | 1.7156 | 0 |  | 1.5
2017-09-08 | 10:15 | 1.7288 | 0 | 0 | 1.5 | 0 | 82.5164
2017-09-08 | 10:20 | 1.7538 | 0 |  | 1.5
2017-09-08 | 10:25 | 1.7452 | 0 |  | 1.5
2017-09-08 | 10:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 82.9493
2017-09-08 | 10:35 | 1.6844 | 0 |  | 1.5
2017-09-08 | 10:40 | 1.7015 | 0 |  | 1.5
2017-09-08 | 10:45 | 1.7319 | 0 | 0 | 1.5 | 0 | 83.9962
2017-09-08 | 10:50 | 1.7468 | 0 |  | 1.5
2017-09-08 | 10:55 | 1.753 | 0 |  | 1.5
2017-09-08 | 11:00 | 1.7218 | 0 | 0 | 1.5 | 0 | 84.2638
2017-09-08 | 11:05 | 1.7522 | 0 |  | 1.5
2017-09-08 | 11:10 | 1.6851 | 0 |  | 1.5
2017-09-08 | 11:15 | 1.7202 | 0 | 0 | 1.5 | 0 | 85.1945
2017-09-08 | 11:20 | 1.6836 | 0 |  | 1.5
2017-09-08 | 11:25 | 1.7085 | 0 |  | 1.5
2017-09-08 | 11:30 | 1.753 | 0 | 0 | 1.5 | 0 | 85.6675
2017-09-08 | 11:35 | 1.7507 | 0 |  | 1.5
2017-09-08 | 11:40 | 1.7312 | 0 |  | 1.5
2017-09-08 | 11:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 85.8188
2017-09-08 | 11:50 | 1.7592 | 0 |  | 1.5
2017-09-08 | 11:55 | 1.799 | 0 |  | 1.5
2017-09-08 | 12:00 | 1.806 | 0 | 0 | 1.5 | 0 | 85.0036
2017-09-08 | 12:05 | 1.7943 | 0 |  | 1.5
2017-09-08 | 12:10 | 1.7834 | 0 |  | 1.5
2017-09-08 | 12:15 | 1.753 | 0 | 0 | 1.5 | 0 | 84.3442
2017-09-08 | 12:20 | 1.7967 | 0 |  | 1.5
2017-09-08 | 12:25 | 1.7546 | 0 |  | 1.5
2017-09-08 | 12:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 83.8037
2017-09-08 | 12:35 | 1.7429 | 0 |  | 1.5
2017-09-08 | 12:40 | 1.7647 | 0 |  | 1.5
2017-09-08 | 12:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 83.6759
2017-09-08 | 12:50 | 1.7491 | 0 |  | 1.5
2017-09-08 | 12:55 | 1.7382 | 0 |  | 1.5
2017-09-08 | 13:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 83.6762
2017-09-08 | 13:05 | 1.7694 | 0 |  | 1.5
2017-09-08 | 13:10 | 1.7421 | 0 |  | 1.5
2017-09-08 | 13:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 83.8024
2017-09-08 | 13:20 | 1.7421 | 0 |  | 1.5
2017-09-08 | 13:25 | 1.7631 | 0 |  | 1.5
2017-09-08 | 13:30 | 1.7702 | 0 | 0 | 1.5 | 0 | 83.653
2017-09-08 | 13:35 | 1.7335 | 0 |  | 1.5
2017-09-08 | 13:40 | 1.7507 | 0 |  | 1.5
2017-09-08 | 13:45 | 1.7819 | 0 | 0 | 1.5 | 0 | 83.5704
2017-09-08 | 13:50 | 1.7631 | 0 |  | 1.5
2017-09-08 | 13:55 | 1.7319 | 0 |  | 1.5
2017-09-08 | 14:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 83.455
2017-09-08 | 14:05 | 1.7639 | 0 |  | 1.5
2017-09-08 | 14:10 | 1.7452 | 0 |  | 1.5
2017-09-08 | 14:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 83.4708
2017-09-08 | 14:20 | 1.7366 | 0 |  | 1.5
2017-09-08 | 14:25 | 1.7273 | 0 |  | 1.5
2017-09-08 | 14:30 | 1.7195 | 0 | 0 | 1.5 | 0 | 83.9335
2017-09-08 | 14:35 | 1.7179 | 0 |  | 1.5
2017-09-08 | 14:40 | 1.7351 | 0 |  | 1.5
2017-09-08 | 14:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 84.4582
2017-09-08 | 14:50 | 1.7148 | 0 |  | 1.5
2017-09-08 | 14:55 | 1.7351 | 0 |  | 1.5
2017-09-08 | 15:00 | 1.7436 | 0 | 0 | 1.5 | 0 | 84.7278
2017-09-08 | 15:05 | 1.7725 | 0 |  | 1.5
2017-09-08 | 15:10 | 1.7826 | 0 |  | 1.5
2017-09-08 | 15:15 | 1.7811 | 0 | 0 | 1.5 | 0 | 84.1154
2017-09-08 | 15:20 | 1.792 | 0 |  | 1.5
2017-09-08 | 15:25 | 1.7468 | 0 |  | 1.5
2017-09-08 | 15:30 | 1.7226 | 0 | 0 | 1.5 | 0 | 84.0617
2017-09-08 | 15:35 | 1.7507 | 0 |  | 1.5
2017-09-08 | 15:40 | 1.7343 | 0 |  | 1.5
2017-09-08 | 15:45 | 1.753 | 0 | 0 | 1.5 | 0 | 83.8337
2017-09-08 | 15:50 | 1.7725 | 0 |  | 1.5
2017-09-08 | 15:55 | 1.7686 | 0 |  | 1.5
2017-09-08 | 16:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 83.5325
2017-09-08 | 16:05 | 1.7655 | 0 |  | 1.5
2017-09-08 | 16:10 | 1.7468 | 0 |  | 1.5
2017-09-08 | 16:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 83.3664
2017-09-08 | 16:20 | 1.7335 | 0 |  | 1.5
2017-09-08 | 16:25 | 1.7546 | 0 |  | 1.5
2017-09-08 | 16:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 83.264
2017-09-08 | 16:35 | 1.7327 | 0 |  | 1.5
2017-09-08 | 16:40 | 1.746 | 0 |  | 1.5
2017-09-08 | 16:45 | 1.7358 | 0 | 0 | 1.5 | 0 | 83.5263
2017-09-08 | 16:50 | 1.7226 | 0 |  | 1.5
2017-09-08 | 16:55 | 1.7694 | 0 |  | 1.5
2017-09-08 | 17:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 83.5479
2017-09-08 | 17:05 | 1.7881 | 0 |  | 1.5
2017-09-08 | 17:10 | 1.7569 | 0 |  | 1.5
2017-09-08 | 17:15 | 1.7928 | 0 | 0 | 1.5 | 0 | 82.8342
2017-09-08 | 17:20 | 1.7819 | 0 |  | 1.5
2017-09-08 | 17:25 | 1.7787 | 0 |  | 1.5
2017-09-08 | 17:30 | 1.7764 | 0 | 0 | 1.5 | 0 | 82.0021
2017-09-08 | 17:35 | 1.7592 | 0 |  | 1.5
2017-09-08 | 17:40 | 1.7678 | 0 |  | 1.5
2017-09-08 | 17:45 | 1.7772 | 0 | 0 | 1.5 | 0 | 81.3383
2017-09-08 | 17:50 | 1.7928 | 0 |  | 1.5
2017-09-08 | 17:55 | 1.7546 | 0 |  | 1.5
2017-09-08 | 18:00 | 1.7733 | 0 | 0 | 1.5 | 0 | 80.7771
2017-09-08 | 18:05 | 1.7819 | 0 |  | 1.5
2017-09-08 | 18:10 | 1.7928 | 0 |  | 1.5
2017-09-08 | 18:15 | 1.7967 | 0 | 0 | 1.5 | 0 | 80.0119
2017-09-08 | 18:20 | 1.7881 | 0 |  | 1.5
2017-09-08 | 18:25 | 1.7592 | 0 |  | 1.5
2017-09-08 | 18:30 | 1.7421 | 0 | 0 | 1.5 | 0 | 79.5401
2017-09-08 | 18:35 | 1.7491 | 0 |  | 1.5
2017-09-08 | 18:40 | 1.7998 | 0 |  | 1.5
2017-09-08 | 18:45 | 1.7795 | 0 | 0 | 1.5 | 0 | 79.2445
2017-09-08 | 18:50 | 1.7725 | 0 |  | 1.5
2017-09-08 | 18:55 | 1.7655 | 0 |  | 1.5
2017-09-08 | 19:00 | 1.7663 | 0 | 0 | 1.5 | 0 | 78.9256
2017-09-08 | 19:05 | 1.7928 | 0 |  | 1.5
2017-09-08 | 19:10 | 1.7374 | 0 |  | 1.5
2017-09-08 | 19:15 | 1.8037 | 0 | 0 | 1.5 | 0 | 78.3027
2017-09-08 | 19:20 | 1.7819 | 0 |  | 1.5
2017-09-08 | 19:25 | 1.7553 | 0 |  | 1.5
2017-09-08 | 19:30 | 1.7819 | 0 | 0 | 1.5 | 0 | 77.8972
2017-09-08 | 19:35 | 1.7858 | 0 |  | 1.5
2017-09-08 | 19:40 | 1.7522 | 0 |  | 1.5
2017-09-08 | 19:45 | 1.7647 | 0 | 0 | 1.5 | 0 | 77.7305
2017-09-08 | 19:50 | 1.7312 | 0 |  | 1.5
2017-09-08 | 19:55 | 1.7483 | 0 |  | 1.5
2017-09-08 | 20:00 | 1.76 | 0 | 0 | 1.5 | 0 | 77.9307
2017-09-08 | 20:05 | 1.76 | 0 |  | 1.5
2017-09-08 | 20:10 | 1.7405 | 0 |  | 1.5
2017-09-08 | 20:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 78.1021
2017-09-08 | 20:20 | 1.7413 | 0 |  | 1.5
2017-09-08 | 20:25 | 1.7296 | 0 |  | 1.5
2017-09-08 | 20:30 | 1.7132 | 0 | 0 | 1.5 | 0 | 78.3412
2017-09-08 | 20:35 | 1.7382 | 0 |  | 1.5
2017-09-08 | 20:40 | 1.7522 | 0 |  | 1.5
2017-09-08 | 20:45 | 1.7343 | 0 | 0 | 1.5 | 0 | 78.3433
2017-09-08 | 20:50 | 1.7491 | 0 |  | 1.5
2017-09-08 | 20:55 | 1.7475 | 0 |  | 1.5
2017-09-08 | 21:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 78.285
2017-09-08 | 21:05 | -0.1034 | 0 |  | 1.5
2017-09-08 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-08 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 21:20 | -0.1073 | 0 |  | 1.5
2017-09-08 | 21:25 | -0.10574 | 0 |  | 1.5
2017-09-08 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 21:35 | -0.10574 | 0 |  | 1.5
2017-09-08 | 21:40 | -0.10574 | 0 |  | 1.5
2017-09-08 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 21:50 | -0.10574 | 0 |  | 1.5
2017-09-08 | 21:55 | -0.10574 | 0 |  | 1.5
2017-09-08 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 22:05 | -0.10652 | 0 |  | 1.5
2017-09-08 | 22:10 | -0.10652 | 0 |  | 1.5
2017-09-08 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 22:20 | -0.10652 | 0 |  | 1.5
2017-09-08 | 22:25 | -0.10574 | 0 |  | 1.5
2017-09-08 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 22:35 | -0.10808 | 0 |  | 1.5
2017-09-08 | 22:40 | -0.10574 | 0 |  | 1.5
2017-09-08 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 22:50 | -0.10574 | 0 |  | 1.5
2017-09-08 | 22:55 | -0.10574 | 0 |  | 1.5
2017-09-08 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 23:05 | -0.10574 | 0 |  | 1.5
2017-09-08 | 23:10 | -0.10496 | 0 |  | 1.5
2017-09-08 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 23:20 | -0.10574 | 0 |  | 1.5
2017-09-08 | 23:25 | -0.10574 | 0 |  | 1.5
2017-09-08 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 23:35 | -0.10496 | 0 |  | 1.5
2017-09-08 | 23:40 | -0.10496 | 0 |  | 1.5
2017-09-08 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-08 | 23:50 | -0.10496 | 0 |  | 1.5
2017-09-08 | 23:55 | -0.10496 | 0 |  | 1.5
2017-09-09 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 0:05 | -0.10496 | 0 |  | 1.5
2017-09-09 | 0:10 | -0.10496 | 0 |  | 1.5
2017-09-09 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 0:20 | -0.10496 | 0 |  | 1.5
2017-09-09 | 0:25 | -0.10496 | 0 |  | 1.5
2017-09-09 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 0:35 | -0.10418 | 0 |  | 1.5
2017-09-09 | 0:40 | -0.10418 | 0 |  | 1.5
2017-09-09 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 0:50 | -0.10418 | 0 |  | 1.5
2017-09-09 | 0:55 | -0.10496 | 0 |  | 1.5
2017-09-09 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 1:05 | -0.10418 | 0 |  | 1.5
2017-09-09 | 1:10 | -0.10418 | 0 |  | 1.5
2017-09-09 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 1:20 | -0.10808 | 0 |  | 1.5
2017-09-09 | 1:25 | -0.1073 | 0 |  | 1.5
2017-09-09 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 1:35 | -0.10808 | 0 |  | 1.5
2017-09-09 | 1:40 | -0.10808 | 0 |  | 1.5
2017-09-09 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 1:50 | -0.10808 | 0 |  | 1.5
2017-09-09 | 1:55 | -0.10808 | 0 |  | 1.5
2017-09-09 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 2:05 | -0.1073 | 0 |  | 1.5
2017-09-09 | 2:10 | -0.1073 | 0 |  | 1.5
2017-09-09 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 2:20 | -0.10808 | 0 |  | 1.5
2017-09-09 | 2:25 | -0.10808 | 0 |  | 1.5
2017-09-09 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 2:35 | -0.1073 | 0 |  | 1.5
2017-09-09 | 2:40 | -0.1073 | 0 |  | 1.5
2017-09-09 | 2:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-09 | 2:55 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 3:05 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:10 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 3:20 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:25 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 3:35 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:40 | -0.10808 | 0 |  | 1.5
2017-09-09 | 3:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 3:50 | -0.1073 | 0 |  | 1.5
2017-09-09 | 3:55 | -0.10808 | 0 |  | 1.5
2017-09-09 | 4:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 4:05 | -0.1073 | 0 |  | 1.5
2017-09-09 | 4:10 | -0.10808 | 0 |  | 1.5
2017-09-09 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 4:20 | -0.10808 | 0 |  | 1.5
2017-09-09 | 4:25 | -0.10808 | 0 |  | 1.5
2017-09-09 | 4:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 4:35 | -0.10808 | 0 |  | 1.5
2017-09-09 | 4:40 | -0.1073 | 0 |  | 1.5
2017-09-09 | 4:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 4:50 | -0.10808 | 0 |  | 1.5
2017-09-09 | 4:55 | -0.1073 | 0 |  | 1.5
2017-09-09 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 5:05 | 1.7226 | 0 |  | 1.5
2017-09-09 | 5:10 | 2.0783 | 0 |  | 1.5
2017-09-09 | 5:15 | 1.9535 | 0 | 0 | 1.5 | 0 | 94.3704
2017-09-09 | 5:20 | 1.8918 | 0 |  | 1.5
2017-09-09 | 5:25 | 1.9418 | 0 |  | 1.5
2017-09-09 | 5:30 | 1.9589 | 0 | 0 | 1.5 | 0 | 89.2107
2017-09-09 | 5:35 | 1.9293 | 0 |  | 1.5
2017-09-09 | 5:40 | 1.8653 | 0 |  | 1.5
2017-09-09 | 5:45 | 1.8419 | 0 | 0 | 1.5 | 0 | 85.248
2017-09-09 | 5:50 | 1.8489 | 0 |  | 1.5
2017-09-09 | 5:55 | 1.8037 | 0 |  | 1.5
2017-09-09 | 6:00 | 1.8053 | 0 | 0 | 1.5 | 0 | 83.3853
2017-09-09 | 6:05 | 1.8084 | 0 |  | 1.5
2017-09-09 | 6:10 | 1.8201 | 0 |  | 1.5
2017-09-09 | 6:15 | 1.8045 | 0 | 0 | 1.5 | 0 | 81.8823
2017-09-09 | 6:20 | 1.7764 | 0 |  | 1.5
2017-09-09 | 6:25 | 1.7912 | 0 |  | 1.5
2017-09-09 | 6:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 80.8256
2017-09-09 | 6:35 | 1.7561 | 0 |  | 1.5
2017-09-09 | 6:40 | 1.7951 | 0 |  | 1.5
2017-09-09 | 6:45 | 1.7787 | 0 | 0 | 1.5 | 0 | 80.3217
2017-09-09 | 6:50 | 1.7624 | 0 |  | 1.5
2017-09-09 | 6:55 | 1.76 | 0 |  | 1.5
2017-09-09 | 7:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 79.6176
2017-09-09 | 7:05 | 1.7585 | 0 |  | 1.5
2017-09-09 | 7:10 | 1.7249 | 0 |  | 1.5
2017-09-09 | 7:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 79.2385
2017-09-09 | 7:20 | 1.7405 | 0 |  | 1.5
2017-09-09 | 7:25 | 1.76 | 0 |  | 1.5
2017-09-09 | 7:30 | 1.7608 | 0 | 0 | 1.5 | 0 | 78.9975
2017-09-09 | 7:35 | 1.7616 | 0 |  | 1.5
2017-09-09 | 7:40 | 1.7421 | 0 |  | 1.5
2017-09-09 | 7:45 | 1.7507 | 0 | 0 | 1.5 | 0 | 78.8604
2017-09-09 | 7:50 | 1.7608 | 0 |  | 1.5
2017-09-09 | 7:55 | 1.7702 | 0 |  | 1.5
2017-09-09 | 8:00 | 1.753 | 0 | 0 | 1.5 | 0 | 78.5544
2017-09-09 | 8:05 | 1.7678 | 0 |  | 1.5
2017-09-09 | 8:10 | 1.7631 | 0 |  | 1.5
2017-09-09 | 8:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 78.3549
2017-09-09 | 8:20 | 1.7429 | 0 |  | 1.5
2017-09-09 | 8:25 | 1.7546 | 0 |  | 1.5
2017-09-09 | 8:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 78.196
2017-09-09 | 8:35 | 1.7429 | 0 |  | 1.5
2017-09-09 | 8:40 | 1.7436 | 0 |  | 1.5
2017-09-09 | 8:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 78.054
2017-09-09 | 8:50 | 1.7663 | 0 |  | 1.5
2017-09-09 | 8:55 | 1.7546 | 0 |  | 1.5
2017-09-09 | 9:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 78.1464
2017-09-09 | 9:05 | 1.7522 | 0 |  | 1.5
2017-09-09 | 9:10 | 1.76 | 0 |  | 1.5
2017-09-09 | 9:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 77.9274
2017-09-09 | 9:20 | 1.7702 | 0 |  | 1.5
2017-09-09 | 9:25 | 1.7538 | 0 |  | 1.5
2017-09-09 | 9:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 77.8641
2017-09-09 | 9:35 | 1.7343 | 0 |  | 1.5
2017-09-09 | 9:40 | 1.7366 | 0 |  | 1.5
2017-09-09 | 9:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 77.7371
2017-09-09 | 9:50 | 1.7335 | 0 |  | 1.5
2017-09-09 | 9:55 | 1.7522 | 0 |  | 1.5
2017-09-09 | 10:00 | 1.7351 | 0 | 0 | 1.5 | 0 | 77.9501
2017-09-09 | 10:05 | 1.7483 | 0 |  | 1.5
2017-09-09 | 10:10 | 1.7733 | 0 |  | 1.5
2017-09-09 | 10:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 77.9316
2017-09-09 | 10:20 | 1.7319 | 0 |  | 1.5
2017-09-09 | 10:25 | 1.7273 | 0 |  | 1.5
2017-09-09 | 10:30 | 1.721 | 0 | 0 | 1.5 | 0 | 78.3196
2017-09-09 | 10:35 | 1.7647 | 0 |  | 1.5
2017-09-09 | 10:40 | 1.7319 | 0 |  | 1.5
2017-09-09 | 10:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 78.3636
2017-09-09 | 10:50 | 1.7429 | 0 |  | 1.5
2017-09-09 | 10:55 | 1.7483 | 0 |  | 1.5
2017-09-09 | 11:00 | 1.739 | 0 | 0 | 1.5 | 0 | 78.5537
2017-09-09 | 11:05 | 1.7507 | 0 |  | 1.5
2017-09-09 | 11:10 | 1.7413 | 0 |  | 1.5
2017-09-09 | 11:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 78.7413
2017-09-09 | 11:20 | 1.7382 | 0 |  | 1.5
2017-09-09 | 11:25 | 1.721 | 0 |  | 1.5
2017-09-09 | 11:30 | 1.7132 | 0 | 0 | 1.5 | 0 | 79.1864
2017-09-09 | 11:35 | 1.7296 | 0 |  | 1.5
2017-09-09 | 11:40 | 1.7514 | 0 |  | 1.5
2017-09-09 | 11:45 | 1.7187 | 0 | 0 | 1.5 | 0 | 79.7268
2017-09-09 | 11:50 | 1.7413 | 0 |  | 1.5
2017-09-09 | 11:55 | 1.6906 | 0 |  | 1.5
2017-09-09 | 12:00 | 1.7062 | 0 | 0 | 1.5 | 0 | 80.6088
2017-09-09 | 12:05 | 1.7 | 0 |  | 1.5
2017-09-09 | 12:10 | 1.6906 | 0 |  | 1.5
2017-09-09 | 12:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 81.7788
2017-09-09 | 12:20 | 1.7156 | 0 |  | 1.5
2017-09-09 | 12:25 | 1.7117 | 0 |  | 1.5
2017-09-09 | 12:30 | 1.7062 | 0 | 0 | 1.5 | 0 | 82.6814
2017-09-09 | 12:35 | 1.7468 | 0 |  | 1.5
2017-09-09 | 12:40 | 1.6953 | 0 |  | 1.5
2017-09-09 | 12:45 | 1.7491 | 0 | 0 | 1.5 | 0 | 83.4582
2017-09-09 | 12:50 | 1.7 | 0 |  | 1.5
2017-09-09 | 12:55 | 1.7374 | 0 |  | 1.5
2017-09-09 | 13:00 | 1.7366 | 0 | 0 | 1.5 | 0 | 84.3704
2017-09-09 | 13:05 | 1.7553 | 0 |  | 1.5
2017-09-09 | 13:10 | 1.753 | 0 |  | 1.5
2017-09-09 | 13:15 | 1.714 | 0 | 0 | 1.5 | 0 | 85.0352
2017-09-09 | 13:20 | 1.728 | 0 |  | 1.5
2017-09-09 | 13:25 | 1.7288 | 0 |  | 1.5
2017-09-09 | 13:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 85.5783
2017-09-09 | 13:35 | 1.7702 | 0 |  | 1.5
2017-09-09 | 13:40 | 1.7748 | 0 |  | 1.5
2017-09-09 | 13:45 | 1.778 | 0 | 0 | 1.5 | 0 | 84.9805
2017-09-09 | 13:50 | 1.8068 | 0 |  | 1.5
2017-09-09 | 13:55 | 1.7975 | 0 |  | 1.5
2017-09-09 | 14:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 83.9289
2017-09-09 | 14:05 | 1.7475 | 0 |  | 1.5
2017-09-09 | 14:10 | 1.7647 | 0 |  | 1.5
2017-09-09 | 14:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 83.4281
2017-09-09 | 14:20 | 1.7475 | 0 |  | 1.5
2017-09-09 | 14:25 | 1.7514 | 0 |  | 1.5
2017-09-09 | 14:30 | 1.7405 | 0 | 0 | 1.5 | 0 | 83.3691
2017-09-09 | 14:35 | 1.7452 | 0 |  | 1.5
2017-09-09 | 14:40 | 1.7429 | 0 |  | 1.5
2017-09-09 | 14:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 83.3302
2017-09-09 | 14:50 | 1.746 | 0 |  | 1.5
2017-09-09 | 14:55 | 1.7452 | 0 |  | 1.5
2017-09-09 | 15:00 | 1.7756 | 0 | 0 | 1.5 | 0 | 83.12
2017-09-09 | 15:05 | 1.7647 | 0 |  | 1.5
2017-09-09 | 15:10 | 1.7858 | 0 |  | 1.5
2017-09-09 | 15:15 | 1.7772 | 0 | 0 | 1.5 | 0 | 82.3403
2017-09-09 | 15:20 | 1.7694 | 0 |  | 1.5
2017-09-09 | 15:25 | 1.7873 | 0 |  | 1.5
2017-09-09 | 15:30 | 1.7468 | 0 | 0 | 1.5 | 0 | 81.4969
2017-09-09 | 15:35 | 1.7772 | 0 |  | 1.5
2017-09-09 | 15:40 | 1.7959 | 0 |  | 1.5
2017-09-09 | 15:45 | 1.7904 | 0 | 0 | 1.5 | 0 | 80.6241
2017-09-09 | 15:50 | 1.7733 | 0 |  | 1.5
2017-09-09 | 15:55 | 1.7686 | 0 |  | 1.5
2017-09-09 | 16:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.9309
2017-09-09 | 16:05 | 1.7803 | 0 |  | 1.5
2017-09-09 | 16:10 | 1.7499 | 0 |  | 1.5
2017-09-09 | 16:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.523
2017-09-09 | 16:20 | 1.746 | 0 |  | 1.5
2017-09-09 | 16:25 | 1.7756 | 0 |  | 1.5
2017-09-09 | 16:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 79.2399
2017-09-09 | 16:35 | 1.7429 | 0 |  | 1.5
2017-09-09 | 16:40 | 1.7709 | 0 |  | 1.5
2017-09-09 | 16:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 79.1096
2017-09-09 | 16:50 | 1.7725 | 0 |  | 1.5
2017-09-09 | 16:55 | 1.7483 | 0 |  | 1.5
2017-09-09 | 17:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.6939
2017-09-09 | 17:05 | 1.7569 | 0 |  | 1.5
2017-09-09 | 17:10 | 1.7678 | 0 |  | 1.5
2017-09-09 | 17:15 | 1.7351 | 0 | 0 | 1.5 | 0 | 78.3248
2017-09-09 | 17:20 | 1.7709 | 0 |  | 1.5
2017-09-09 | 17:25 | 1.7444 | 0 |  | 1.5
2017-09-09 | 17:30 | 1.7202 | 0 | 0 | 1.5 | 0 | 78.2735
2017-09-09 | 17:35 | 1.7834 | 0 |  | 1.5
2017-09-09 | 17:40 | 1.7117 | 0 |  | 1.5
2017-09-09 | 17:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 78.2804
2017-09-09 | 17:50 | 1.7421 | 0 |  | 1.5
2017-09-09 | 17:55 | 1.7444 | 0 |  | 1.5
2017-09-09 | 18:00 | 1.7405 | 0 | 0 | 1.5 | 0 | 78.4117
2017-09-09 | 18:05 | 1.714 | 0 |  | 1.5
2017-09-09 | 18:10 | 1.7187 | 0 |  | 1.5
2017-09-09 | 18:15 | 1.753 | 0 | 0 | 1.5 | 0 | 78.5486
2017-09-09 | 18:20 | 1.7312 | 0 |  | 1.5
2017-09-09 | 18:25 | 1.7483 | 0 |  | 1.5
2017-09-09 | 18:30 | 1.7865 | 0 | 0 | 1.5 | 0 | 78.4428
2017-09-09 | 18:35 | 1.7499 | 0 |  | 1.5
2017-09-09 | 18:40 | 1.7702 | 0 |  | 1.5
2017-09-09 | 18:45 | 1.7756 | 0 | 0 | 1.5 | 0 | 78.2516
2017-09-09 | 18:50 | 1.767 | 0 |  | 1.5
2017-09-09 | 18:55 | 1.7475 | 0 |  | 1.5
2017-09-09 | 19:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.2109
2017-09-09 | 19:05 | 1.7538 | 0 |  | 1.5
2017-09-09 | 19:10 | 1.7514 | 0 |  | 1.5
2017-09-09 | 19:15 | 1.7413 | 0 | 0 | 1.5 | 0 | 78.0659
2017-09-09 | 19:20 | 1.7546 | 0 |  | 1.5
2017-09-09 | 19:25 | 1.7561 | 0 |  | 1.5
2017-09-09 | 19:30 | 1.7491 | 0 | 0 | 1.5 | 0 | 77.7984
2017-09-09 | 19:35 | 1.7639 | 0 |  | 1.5
2017-09-09 | 19:40 | 1.7655 | 0 |  | 1.5
2017-09-09 | 19:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 77.6234
2017-09-09 | 19:50 | 1.7803 | 0 |  | 1.5
2017-09-09 | 19:55 | 1.7772 | 0 |  | 1.5
2017-09-09 | 20:00 | 1.7663 | 0 | 0 | 1.5 | 0 | 77.4373
2017-09-09 | 20:05 | 1.7733 | 0 |  | 1.5
2017-09-09 | 20:10 | 1.7499 | 0 |  | 1.5
2017-09-09 | 20:15 | 1.753 | 0 | 0 | 1.5 | 0 | 77.2958
2017-09-09 | 20:20 | 1.7343 | 0 |  | 1.5
2017-09-09 | 20:25 | 1.7655 | 0 |  | 1.5
2017-09-09 | 20:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 77.2244
2017-09-09 | 20:35 | 1.7249 | 0 |  | 1.5
2017-09-09 | 20:40 | 1.7585 | 0 |  | 1.5
2017-09-09 | 20:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 77.1414
2017-09-09 | 20:50 | 1.7577 | 0 |  | 1.5
2017-09-09 | 20:55 | 1.7514 | 0 |  | 1.5
2017-09-09 | 21:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 76.9249
2017-09-09 | 21:05 | -0.1034 | 0 |  | 1.5
2017-09-09 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-09 | 21:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 21:20 | -0.10496 | 0 |  | 1.5
2017-09-09 | 21:25 | -0.10496 | 0 |  | 1.5
2017-09-09 | 21:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 21:35 | -0.10574 | 0 |  | 1.5
2017-09-09 | 21:40 | -0.10574 | 0 |  | 1.5
2017-09-09 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 21:50 | -0.10574 | 0 |  | 1.5
2017-09-09 | 21:55 | -0.10574 | 0 |  | 1.5
2017-09-09 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 22:05 | -0.10574 | 0 |  | 1.5
2017-09-09 | 22:10 | -0.10574 | 0 |  | 1.5
2017-09-09 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 22:20 | -0.10652 | 0 |  | 1.5
2017-09-09 | 22:25 | -0.10574 | 0 |  | 1.5
2017-09-09 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 22:35 | -0.10652 | 0 |  | 1.5
2017-09-09 | 22:40 | -0.10652 | 0 |  | 1.5
2017-09-09 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 22:50 | -0.10652 | 0 |  | 1.5
2017-09-09 | 22:55 | -0.10574 | 0 |  | 1.5
2017-09-09 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 23:05 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:10 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 23:20 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:25 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 23:35 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:40 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-09 | 23:50 | -0.10652 | 0 |  | 1.5
2017-09-09 | 23:55 | -0.10652 | 0 |  | 1.5
2017-09-10 | 0:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 0:05 | -0.10652 | 0 |  | 1.5
2017-09-10 | 0:10 | -0.10652 | 0 |  | 1.5
2017-09-10 | 0:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 0:20 | -0.10652 | 0 |  | 1.5
2017-09-10 | 0:25 | -0.10652 | 0 |  | 1.5
2017-09-10 | 0:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 0:35 | -0.1073 | 0 |  | 1.5
2017-09-10 | 0:40 | -0.10652 | 0 |  | 1.5
2017-09-10 | 0:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 0:50 | -0.1073 | 0 |  | 1.5
2017-09-10 | 0:55 | -0.1073 | 0 |  | 1.5
2017-09-10 | 1:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 1:05 | -0.1073 | 0 |  | 1.5
2017-09-10 | 1:10 | -0.1073 | 0 |  | 1.5
2017-09-10 | 1:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 1:20 | -0.1112 | 0 |  | 1.5
2017-09-10 | 1:25 | -0.11042 | 0 |  | 1.5
2017-09-10 | 1:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 1:35 | -0.11042 | 0 |  | 1.5
2017-09-10 | 1:40 | -0.11042 | 0 |  | 1.5
2017-09-10 | 1:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 1:50 | -0.11042 | 0 |  | 1.5
2017-09-10 | 1:55 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 2:05 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:10 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 2:20 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:25 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 2:35 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:40 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 2:50 | -0.11042 | 0 |  | 1.5
2017-09-10 | 2:55 | -0.1112 | 0 |  | 1.5
2017-09-10 | 3:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 3:05 | -0.11042 | 0 |  | 1.5
2017-09-10 | 3:10 | -0.1112 | 0 |  | 1.5
2017-09-10 | 3:15 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 3:20 | -0.11042 | 0 |  | 1.5
2017-09-10 | 3:25 | -0.1112 | 0 |  | 1.5
2017-09-10 | 3:30 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 3:35 | -0.11042 | 0 |  | 1.5
2017-09-10 | 3:40 | -0.1112 | 0 |  | 1.5
2017-09-10 | 3:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 3:50 | -0.1112 | 0 |  | 1.5
2017-09-10 | 3:55 | -0.11042 | 0 |  | 1.5
2017-09-10 | 4:00 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 4:05 | -0.1112 | 0 |  | 1.5
2017-09-10 | 4:10 | -0.1112 | 0 |  | 1.5
2017-09-10 | 4:15 | -0.1112 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 4:20 | -0.1112 | 0 |  | 1.5
2017-09-10 | 4:25 | -0.1112 | 0 |  | 1.5
2017-09-10 | 4:30 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 4:35 | -0.11042 | 0 |  | 1.5
2017-09-10 | 4:40 | -0.11042 | 0 |  | 1.5
2017-09-10 | 4:45 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 4:50 | -0.11042 | 0 |  | 1.5
2017-09-10 | 4:55 | -0.11042 | 0 |  | 1.5
2017-09-10 | 5:00 | -0.11042 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 5:05 | 2.1664 | 0 |  | 1.5
2017-09-10 | 5:10 | 2.2132 | 0 |  | 1.5
2017-09-10 | 5:15 | 2.0728 | 0 | 0 | 1.5 | 0 | 90.1681
2017-09-10 | 5:20 | 1.9706 | 0 |  | 1.5
2017-09-10 | 5:25 | 1.8981 | 0 |  | 1.5
2017-09-10 | 5:30 | 1.877 | 0 | 0 | 1.5 | 0 | 84.9669
2017-09-10 | 5:35 | 1.8692 | 0 |  | 1.5
2017-09-10 | 5:40 | 1.8177 | 0 |  | 1.5
2017-09-10 | 5:45 | 1.8357 | 0 | 0 | 1.5 | 0 | 82.6383
2017-09-10 | 5:50 | 1.8224 | 0 |  | 1.5
2017-09-10 | 5:55 | 1.8162 | 0 |  | 1.5
2017-09-10 | 6:00 | 1.7936 | 0 | 0 | 1.5 | 0 | 80.7606
2017-09-10 | 6:05 | 1.7959 | 0 |  | 1.5
2017-09-10 | 6:10 | 1.7678 | 0 |  | 1.5
2017-09-10 | 6:15 | 1.7733 | 0 | 0 | 1.5 | 0 | 79.8064
2017-09-10 | 6:20 | 1.7897 | 0 |  | 1.5
2017-09-10 | 6:25 | 1.7803 | 0 |  | 1.5
2017-09-10 | 6:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 79.1564
2017-09-10 | 6:35 | 1.7608 | 0 |  | 1.5
2017-09-10 | 6:40 | 1.7475 | 0 |  | 1.5
2017-09-10 | 6:45 | 1.7717 | 0 | 0 | 1.5 | 0 | 78.8519
2017-09-10 | 6:50 | 1.7702 | 0 |  | 1.5
2017-09-10 | 6:55 | 1.7842 | 0 |  | 1.5
2017-09-10 | 7:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 78.322
2017-09-10 | 7:05 | 1.7702 | 0 |  | 1.5
2017-09-10 | 7:10 | 1.7592 | 0 |  | 1.5
2017-09-10 | 7:15 | 1.7725 | 0 | 0 | 1.5 | 0 | 77.7739
2017-09-10 | 7:20 | 1.7499 | 0 |  | 1.5
2017-09-10 | 7:25 | 1.7717 | 0 |  | 1.5
2017-09-10 | 7:30 | 1.7436 | 0 | 0 | 1.5 | 0 | 77.3472
2017-09-10 | 7:35 | 1.7475 | 0 |  | 1.5
2017-09-10 | 7:40 | 1.7826 | 0 |  | 1.5
2017-09-10 | 7:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 77.1119
2017-09-10 | 7:50 | 1.7577 | 0 |  | 1.5
2017-09-10 | 7:55 | 1.739 | 0 |  | 1.5
2017-09-10 | 8:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 76.7535
2017-09-10 | 8:05 | 1.7663 | 0 |  | 1.5
2017-09-10 | 8:10 | 1.7366 | 0 |  | 1.5
2017-09-10 | 8:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 76.5255
2017-09-10 | 8:20 | 1.767 | 0 |  | 1.5
2017-09-10 | 8:25 | 1.7616 | 0 |  | 1.5
2017-09-10 | 8:30 | 1.7343 | 0 | 0 | 1.5 | 0 | 76.4402
2017-09-10 | 8:35 | 1.7631 | 0 |  | 1.5
2017-09-10 | 8:40 | 1.7468 | 0 |  | 1.5
2017-09-10 | 8:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 76.3491
2017-09-10 | 8:50 | 1.7561 | 0 |  | 1.5
2017-09-10 | 8:55 | 1.7343 | 0 |  | 1.5
2017-09-10 | 9:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 76.4003
2017-09-10 | 9:05 | 1.7499 | 0 |  | 1.5
2017-09-10 | 9:10 | 1.7429 | 0 |  | 1.5
2017-09-10 | 9:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 76.4527
2017-09-10 | 9:20 | 1.753 | 0 |  | 1.5
2017-09-10 | 9:25 | 1.76 | 0 |  | 1.5
2017-09-10 | 9:30 | 1.7358 | 0 | 0 | 1.5 | 0 | 76.4582
2017-09-10 | 9:35 | 1.7522 | 0 |  | 1.5
2017-09-10 | 9:40 | 1.7335 | 0 |  | 1.5
2017-09-10 | 9:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 76.6675
2017-09-10 | 9:50 | 1.7078 | 0 |  | 1.5
2017-09-10 | 9:55 | 1.7241 | 0 |  | 1.5
2017-09-10 | 10:00 | 1.7748 | 0 | 0 | 1.5 | 0 | 76.7067
2017-09-10 | 10:05 | 1.7382 | 0 |  | 1.5
2017-09-10 | 10:10 | 1.7366 | 0 |  | 1.5
2017-09-10 | 10:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 76.7987
2017-09-10 | 10:20 | 1.7631 | 0 |  | 1.5
2017-09-10 | 10:25 | 1.7499 | 0 |  | 1.5
2017-09-10 | 10:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 76.8347
2017-09-10 | 10:35 | 1.7218 | 0 |  | 1.5
2017-09-10 | 10:40 | 1.7647 | 0 |  | 1.5
2017-09-10 | 10:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 76.9687
2017-09-10 | 10:50 | 1.7405 | 0 |  | 1.5
2017-09-10 | 10:55 | 1.7304 | 0 |  | 1.5
2017-09-10 | 11:00 | 1.7273 | 0 | 0 | 1.5 | 0 | 77.1978
2017-09-10 | 11:05 | 1.7288 | 0 |  | 1.5
2017-09-10 | 11:10 | 1.7733 | 0 |  | 1.5
2017-09-10 | 11:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 77.2545
2017-09-10 | 11:20 | 1.7514 | 0 |  | 1.5
2017-09-10 | 11:25 | 1.7226 | 0 |  | 1.5
2017-09-10 | 11:30 | 1.7351 | 0 | 0 | 1.5 | 0 | 77.7094
2017-09-10 | 11:35 | 1.7156 | 0 |  | 1.5
2017-09-10 | 11:40 | 1.7319 | 0 |  | 1.5
2017-09-10 | 11:45 | 1.7054 | 0 | 0 | 1.5 | 0 | 78.3651
2017-09-10 | 11:50 | 1.7405 | 0 |  | 1.5
2017-09-10 | 11:55 | 1.7023 | 0 |  | 1.5
2017-09-10 | 12:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 78.7919
2017-09-10 | 12:05 | 1.7312 | 0 |  | 1.5
2017-09-10 | 12:10 | 1.7226 | 0 |  | 1.5
2017-09-10 | 12:15 | 1.7202 | 0 | 0 | 1.5 | 0 | 79.4159
2017-09-10 | 12:20 | 1.7062 | 0 |  | 1.5
2017-09-10 | 12:25 | 1.721 | 0 |  | 1.5
2017-09-10 | 12:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 80.228
2017-09-10 | 12:35 | 1.7171 | 0 |  | 1.5
2017-09-10 | 12:40 | 1.7187 | 0 |  | 1.5
2017-09-10 | 12:45 | 1.7218 | 0 | 0 | 1.5 | 0 | 80.9019
2017-09-10 | 12:50 | 1.7226 | 0 |  | 1.5
2017-09-10 | 12:55 | 1.7171 | 0 |  | 1.5
2017-09-10 | 13:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 81.512
2017-09-10 | 13:05 | 1.7475 | 0 |  | 1.5
2017-09-10 | 13:10 | 1.7546 | 0 |  | 1.5
2017-09-10 | 13:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.7375
2017-09-10 | 13:20 | 1.7319 | 0 |  | 1.5
2017-09-10 | 13:25 | 1.7483 | 0 |  | 1.5
2017-09-10 | 13:30 | 1.7616 | 0 | 0 | 1.5 | 0 | 81.818
2017-09-10 | 13:35 | 1.7538 | 0 |  | 1.5
2017-09-10 | 13:40 | 1.7358 | 0 |  | 1.5
2017-09-10 | 13:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 81.548
2017-09-10 | 13:50 | 1.7585 | 0 |  | 1.5
2017-09-10 | 13:55 | 1.7405 | 0 |  | 1.5
2017-09-10 | 14:00 | 1.7468 | 0 | 0 | 1.5 | 0 | 81.5194
2017-09-10 | 14:05 | 1.7538 | 0 |  | 1.5
2017-09-10 | 14:10 | 1.7241 | 0 |  | 1.5
2017-09-10 | 14:15 | 1.728 | 0 | 0 | 1.5 | 0 | 81.7822
2017-09-10 | 14:20 | 1.7366 | 0 |  | 1.5
2017-09-10 | 14:25 | 1.7335 | 0 |  | 1.5
2017-09-10 | 14:30 | 1.7226 | 0 | 0 | 1.5 | 0 | 82.1153
2017-09-10 | 14:35 | 1.7405 | 0 |  | 1.5
2017-09-10 | 14:40 | 1.7429 | 0 |  | 1.5
2017-09-10 | 14:45 | 1.7483 | 0 | 0 | 1.5 | 0 | 82.5389
2017-09-10 | 14:50 | 1.7421 | 0 |  | 1.5
2017-09-10 | 14:55 | 1.7304 | 0 |  | 1.5
2017-09-10 | 15:00 | 1.739 | 0 | 0 | 1.5 | 0 | 82.9357
2017-09-10 | 15:05 | 1.7382 | 0 |  | 1.5
2017-09-10 | 15:10 | 1.767 | 0 |  | 1.5
2017-09-10 | 15:15 | 1.7382 | 0 | 0 | 1.5 | 0 | 83.3044
2017-09-10 | 15:20 | 1.7624 | 0 |  | 1.5
2017-09-10 | 15:25 | 1.767 | 0 |  | 1.5
2017-09-10 | 15:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 83.296
2017-09-10 | 15:35 | 1.7585 | 0 |  | 1.5
2017-09-10 | 15:40 | 1.799 | 0 |  | 1.5
2017-09-10 | 15:45 | 1.7826 | 0 | 0 | 1.5 | 0 | 82.948
2017-09-10 | 15:50 | 1.7904 | 0 |  | 1.5
2017-09-10 | 15:55 | 1.7436 | 0 |  | 1.5
2017-09-10 | 16:00 | 1.7975 | 0 | 0 | 1.5 | 0 | 82.2497
2017-09-10 | 16:05 | 1.7631 | 0 |  | 1.5
2017-09-10 | 16:10 | 1.7826 | 0 |  | 1.5
2017-09-10 | 16:15 | 1.7936 | 0 | 0 | 1.5 | 0 | 81.6046
2017-09-10 | 16:20 | 1.7546 | 0 |  | 1.5
2017-09-10 | 16:25 | 1.7717 | 0 |  | 1.5
2017-09-10 | 16:30 | 1.7569 | 0 | 0 | 1.5 | 0 | 81.1573
2017-09-10 | 16:35 | 1.7741 | 0 |  | 1.5
2017-09-10 | 16:40 | 1.7585 | 0 |  | 1.5
2017-09-10 | 16:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 80.8321
2017-09-10 | 16:50 | 1.7257 | 0 |  | 1.5
2017-09-10 | 16:55 | 1.7499 | 0 |  | 1.5
2017-09-10 | 17:00 | 1.7904 | 0 | 0 | 1.5 | 0 | 80.326
2017-09-10 | 17:05 | 1.7725 | 0 |  | 1.5
2017-09-10 | 17:10 | 1.7585 | 0 |  | 1.5
2017-09-10 | 17:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.9594
2017-09-10 | 17:20 | 1.767 | 0 |  | 1.5
2017-09-10 | 17:25 | 1.7522 | 0 |  | 1.5
2017-09-10 | 17:30 | 1.778 | 0 | 0 | 1.5 | 0 | 79.5819
2017-09-10 | 17:35 | 1.7561 | 0 |  | 1.5
2017-09-10 | 17:40 | 1.7569 | 0 |  | 1.5
2017-09-10 | 17:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 79.174
2017-09-10 | 17:50 | 1.7366 | 0 |  | 1.5
2017-09-10 | 17:55 | 1.7655 | 0 |  | 1.5
2017-09-10 | 18:00 | 1.7733 | 0 | 0 | 1.5 | 0 | 78.88
2017-09-10 | 18:05 | 1.7452 | 0 |  | 1.5
2017-09-10 | 18:10 | 1.7592 | 0 |  | 1.5
2017-09-10 | 18:15 | 1.7764 | 0 | 0 | 1.5 | 0 | 78.6633
2017-09-10 | 18:20 | 1.767 | 0 |  | 1.5
2017-09-10 | 18:25 | 1.7592 | 0 |  | 1.5
2017-09-10 | 18:30 | 1.7624 | 0 | 0 | 1.5 | 0 | 78.6369
2017-09-10 | 18:35 | 1.7631 | 0 |  | 1.5
2017-09-10 | 18:40 | 1.7514 | 0 |  | 1.5
2017-09-10 | 18:45 | 1.7881 | 0 | 0 | 1.5 | 0 | 78.3367
2017-09-10 | 18:50 | 1.7382 | 0 |  | 1.5
2017-09-10 | 18:55 | 1.7436 | 0 |  | 1.5
2017-09-10 | 19:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 78.0527
2017-09-10 | 19:05 | 1.7725 | 0 |  | 1.5
2017-09-10 | 19:10 | 1.7202 | 0 |  | 1.5
2017-09-10 | 19:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 77.7981
2017-09-10 | 19:20 | 1.7663 | 0 |  | 1.5
2017-09-10 | 19:25 | 1.7787 | 0 |  | 1.5
2017-09-10 | 19:30 | 1.7694 | 0 | 0 | 1.5 | 0 | 77.4574
2017-09-10 | 19:35 | 1.7569 | 0 |  | 1.5
2017-09-10 | 19:40 | 1.785 | 0 |  | 1.5
2017-09-10 | 19:45 | 1.7202 | 0 | 0 | 1.5 | 0 | 77.2756
2017-09-10 | 19:50 | 1.7491 | 0 |  | 1.5
2017-09-10 | 19:55 | 1.7569 | 0 |  | 1.5
2017-09-10 | 20:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 77.1172
2017-09-10 | 20:05 | 1.7608 | 0 |  | 1.5
2017-09-10 | 20:10 | 1.7577 | 0 |  | 1.5
2017-09-10 | 20:15 | 1.76 | 0 | 0 | 1.5 | 0 | 76.853
2017-09-10 | 20:20 | 1.7655 | 0 |  | 1.5
2017-09-10 | 20:25 | 1.7639 | 0 |  | 1.5
2017-09-10 | 20:30 | 1.7327 | 0 | 0 | 1.5 | 0 | 76.5607
2017-09-10 | 20:35 | 1.7764 | 0 |  | 1.5
2017-09-10 | 20:40 | 1.7514 | 0 |  | 1.5
2017-09-10 | 20:45 | 1.76 | 0 | 0 | 1.5 | 0 | 76.5342
2017-09-10 | 20:50 | 1.7195 | 0 |  | 1.5
2017-09-10 | 20:55 | 1.7522 | 0 |  | 1.5
2017-09-10 | 21:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 76.5063
2017-09-10 | 21:05 | -0.10184 | 0 |  | 1.5
2017-09-10 | 21:10 | -0.10262 | 0 |  | 1.5
2017-09-10 | 21:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 21:20 | -0.1034 | 0 |  | 1.5
2017-09-10 | 21:25 | -0.10262 | 0 |  | 1.5
2017-09-10 | 21:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 21:35 | -0.1034 | 0 |  | 1.5
2017-09-10 | 21:40 | -0.1034 | 0 |  | 1.5
2017-09-10 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 21:50 | -0.10418 | 0 |  | 1.5
2017-09-10 | 21:55 | -0.10418 | 0 |  | 1.5
2017-09-10 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 22:05 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:10 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 22:20 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:25 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 22:35 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:40 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 22:50 | -0.10496 | 0 |  | 1.5
2017-09-10 | 22:55 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 23:05 | -0.10574 | 0 |  | 1.5
2017-09-10 | 23:10 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 23:20 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:25 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 23:35 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:40 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-10 | 23:50 | -0.10496 | 0 |  | 1.5
2017-09-10 | 23:55 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 0:05 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:10 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 0:20 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:25 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 0:35 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:40 | -0.10496 | 0 |  | 1.5
2017-09-11 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 0:50 | -0.10418 | 0 |  | 1.5
2017-09-11 | 0:55 | -0.10418 | 0 |  | 1.5
2017-09-11 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 1:05 | -0.10496 | 0 |  | 1.5
2017-09-11 | 1:10 | -0.10496 | 0 |  | 1.5
2017-09-11 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 1:20 | -0.10808 | 0 |  | 1.5
2017-09-11 | 1:25 | -0.10808 | 0 |  | 1.5
2017-09-11 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 1:35 | -0.10808 | 0 |  | 1.5
2017-09-11 | 1:40 | -0.10808 | 0 |  | 1.5
2017-09-11 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 1:50 | -0.10808 | 0 |  | 1.5
2017-09-11 | 1:55 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 2:05 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:10 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 2:20 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:25 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 2:35 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:40 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-11 | 2:55 | -0.10886 | 0 |  | 1.5
2017-09-11 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 3:05 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:10 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 3:20 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:25 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 3:35 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:40 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 3:50 | -0.10808 | 0 |  | 1.5
2017-09-11 | 3:55 | -0.10808 | 0 |  | 1.5
2017-09-11 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 4:05 | -0.10808 | 0 |  | 1.5
2017-09-11 | 4:10 | -0.10886 | 0 |  | 1.5
2017-09-11 | 4:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 4:20 | -0.10808 | 0 |  | 1.5
2017-09-11 | 4:25 | -0.10808 | 0 |  | 1.5
2017-09-11 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 4:35 | -0.10886 | 0 |  | 1.5
2017-09-11 | 4:40 | -0.10808 | 0 |  | 1.5
2017-09-11 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 4:50 | -0.10886 | 0 |  | 1.5
2017-09-11 | 4:55 | -0.10886 | 0 |  | 1.5
2017-09-11 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 5:05 | 2.2163 | 0 |  | 1.5
2017-09-11 | 5:10 | 2.2943 | 0 |  | 1.5
2017-09-11 | 5:15 | 2.0759 | 0 | 0 | 1.5 | 0 | 88.7867
2017-09-11 | 5:20 | 1.948 | 0 |  | 1.5
2017-09-11 | 5:25 | 1.8567 | 0 |  | 1.5
2017-09-11 | 5:30 | 1.845 | 0 | 0 | 1.5 | 0 | 84.3694
2017-09-11 | 5:35 | 1.8365 | 0 |  | 1.5
2017-09-11 | 5:40 | 1.8146 | 0 |  | 1.5
2017-09-11 | 5:45 | 1.8209 | 0 | 0 | 1.5 | 0 | 82.2939
2017-09-11 | 5:50 | 1.7928 | 0 |  | 1.5
2017-09-11 | 5:55 | 1.8014 | 0 |  | 1.5
2017-09-11 | 6:00 | 1.8084 | 0 | 0 | 1.5 | 0 | 80.5357
2017-09-11 | 6:05 | 1.7897 | 0 |  | 1.5
2017-09-11 | 6:10 | 1.7998 | 0 |  | 1.5
2017-09-11 | 6:15 | 1.7678 | 0 | 0 | 1.5 | 0 | 79.638
2017-09-11 | 6:20 | 1.7226 | 0 |  | 1.5
2017-09-11 | 6:25 | 1.7405 | 0 |  | 1.5
2017-09-11 | 6:30 | 1.7124 | 0 | 0 | 1.5 | 0 | 80.159
2017-09-11 | 6:35 | 1.6937 | 0 |  | 1.5
2017-09-11 | 6:40 | 1.7273 | 0 |  | 1.5
2017-09-11 | 6:45 | 1.76 | 0 | 0 | 1.5 | 0 | 81.0633
2017-09-11 | 6:50 | 1.7296 | 0 |  | 1.5
2017-09-11 | 6:55 | 1.7218 | 0 |  | 1.5
2017-09-11 | 7:00 | 1.7304 | 0 | 0 | 1.5 | 0 | 81.7257
2017-09-11 | 7:05 | 1.7343 | 0 |  | 1.5
2017-09-11 | 7:10 | 1.7499 | 0 |  | 1.5
2017-09-11 | 7:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 82.0824
2017-09-11 | 7:20 | 1.7507 | 0 |  | 1.5
2017-09-11 | 7:25 | 1.7304 | 0 |  | 1.5
2017-09-11 | 7:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 82.2014
2017-09-11 | 7:35 | 1.7195 | 0 |  | 1.5
2017-09-11 | 7:40 | 1.746 | 0 |  | 1.5
2017-09-11 | 7:45 | 1.7171 | 0 | 0 | 1.5 | 0 | 82.4514
2017-09-11 | 7:50 | 1.7148 | 0 |  | 1.5
2017-09-11 | 7:55 | 1.6929 | 0 |  | 1.5
2017-09-11 | 8:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 82.9679
2017-09-11 | 8:05 | 1.7865 | 0 |  | 1.5
2017-09-11 | 8:10 | 1.7624 | 0 |  | 1.5
2017-09-11 | 8:15 | 1.8029 | 0 | 0 | 1.5 | 0 | 82.0563
2017-09-11 | 8:20 | 1.7585 | 0 |  | 1.5
2017-09-11 | 8:25 | 1.746 | 0 |  | 1.5
2017-09-11 | 8:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 81.7093
2017-09-11 | 8:35 | 1.7569 | 0 |  | 1.5
2017-09-11 | 8:40 | 1.7327 | 0 |  | 1.5
2017-09-11 | 8:45 | 1.7865 | 0 | 0 | 1.5 | 0 | 81.5008
2017-09-11 | 8:50 | 1.7663 | 0 |  | 1.5
2017-09-11 | 8:55 | 1.7608 | 0 |  | 1.5
2017-09-11 | 9:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 81.2298
2017-09-11 | 9:05 | 1.7678 | 0 |  | 1.5
2017-09-11 | 9:10 | 1.7608 | 0 |  | 1.5
2017-09-11 | 9:15 | 1.7686 | 0 | 0 | 1.5 | 0 | 81.0293
2017-09-11 | 9:20 | 1.7561 | 0 |  | 1.5
2017-09-11 | 9:25 | 1.7624 | 0 |  | 1.5
2017-09-11 | 9:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 81.0947
2017-09-11 | 9:35 | 1.7483 | 0 |  | 1.5
2017-09-11 | 9:40 | 1.7452 | 0 |  | 1.5
2017-09-11 | 9:45 | 1.778 | 0 | 0 | 1.5 | 0 | 81.1416
2017-09-11 | 9:50 | 1.7592 | 0 |  | 1.5
2017-09-11 | 9:55 | 1.7514 | 0 |  | 1.5
2017-09-11 | 10:00 | 1.7351 | 0 | 0 | 1.5 | 0 | 81.1731
2017-09-11 | 10:05 | 1.7358 | 0 |  | 1.5
2017-09-11 | 10:10 | 1.7483 | 0 |  | 1.5
2017-09-11 | 10:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 81.0368
2017-09-11 | 10:20 | 1.7475 | 0 |  | 1.5
2017-09-11 | 10:25 | 1.7694 | 0 |  | 1.5
2017-09-11 | 10:30 | 1.7374 | 0 | 0 | 1.5 | 0 | 80.8778
2017-09-11 | 10:35 | 1.7577 | 0 |  | 1.5
2017-09-11 | 10:40 | 1.7249 | 0 |  | 1.5
2017-09-11 | 10:45 | 1.7366 | 0 | 0 | 1.5 | 0 | 81.2605
2017-09-11 | 10:50 | 1.7397 | 0 |  | 1.5
2017-09-11 | 10:55 | 1.7296 | 0 |  | 1.5
2017-09-11 | 11:00 | 1.6812 | 0 | 0 | 1.5 | 0 | 82.0265
2017-09-11 | 11:05 | 1.6758 | 0 |  | 1.5
2017-09-11 | 11:10 | 1.6727 | 0 |  | 1.5
2017-09-11 | 11:15 | 1.6399 | 0 | 0 | 1.5 | 0 | 84.2493
2017-09-11 | 11:20 | 1.6485 | 0 |  | 1.5
2017-09-11 | 11:25 | 1.6867 | 0 |  | 1.5
2017-09-11 | 11:30 | 1.7078 | 0 | 0 | 1.5 | 0 | 86.3976
2017-09-11 | 11:35 | 1.6883 | 0 |  | 1.5
2017-09-11 | 11:40 | 1.6742 | 0 |  | 1.5
2017-09-11 | 11:45 | 1.7187 | 0 | 0 | 1.5 | 0 | 87.6638
2017-09-11 | 11:50 | 1.7358 | 0 |  | 1.5
2017-09-11 | 11:55 | 1.7756 | 0 |  | 1.5
2017-09-11 | 12:00 | 1.8263 | 0 | 0 | 1.5 | 0 | 87.1696
2017-09-11 | 12:05 | 1.785 | 0 |  | 1.5
2017-09-11 | 12:10 | 1.7491 | 0 |  | 1.5
2017-09-11 | 12:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 86.4332
2017-09-11 | 12:20 | 1.7694 | 0 |  | 1.5
2017-09-11 | 12:25 | 1.7702 | 0 |  | 1.5
2017-09-11 | 12:30 | 1.7452 | 0 | 0 | 1.5 | 0 | 86.5233
2017-09-11 | 12:35 | 1.7553 | 0 |  | 1.5
2017-09-11 | 12:40 | 1.7288 | 0 |  | 1.5
2017-09-11 | 12:45 | 1.7273 | 0 | 0 | 1.5 | 0 | 86.7442
2017-09-11 | 12:50 | 1.7234 | 0 |  | 1.5
2017-09-11 | 12:55 | 1.728 | 0 |  | 1.5
2017-09-11 | 13:00 | 1.7327 | 0 | 0 | 1.5 | 0 | 87.1893
2017-09-11 | 13:05 | 1.7413 | 0 |  | 1.5
2017-09-11 | 13:10 | 1.7265 | 0 |  | 1.5
2017-09-11 | 13:15 | 1.6953 | 0 | 0 | 1.5 | 0 | 87.994
2017-09-11 | 13:20 | 1.7109 | 0 |  | 1.5
2017-09-11 | 13:25 | 1.7078 | 0 |  | 1.5
2017-09-11 | 13:30 | 1.728 | 0 | 0 | 1.5 | 0 | 88.9251
2017-09-11 | 13:35 | 1.7156 | 0 |  | 1.5
2017-09-11 | 13:40 | 1.7421 | 0 |  | 1.5
2017-09-11 | 13:45 | 1.7171 | 0 | 0 | 1.5 | 0 | 89.5894
2017-09-11 | 13:50 | 1.7444 | 0 |  | 1.5
2017-09-11 | 13:55 | 1.753 | 0 |  | 1.5
2017-09-11 | 14:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 89.9883
2017-09-11 | 14:05 | 1.7234 | 0 |  | 1.5
2017-09-11 | 14:10 | 1.721 | 0 |  | 1.5
2017-09-11 | 14:15 | 1.7234 | 0 | 0 | 1.5 | 0 | 90.6589
2017-09-11 | 14:20 | 1.7023 | 0 |  | 1.5
2017-09-11 | 14:25 | 1.7296 | 0 |  | 1.5
2017-09-11 | 14:30 | 1.7288 | 0 | 0 | 1.5 | 0 | 91.7119
2017-09-11 | 14:35 | 1.707 | 0 |  | 1.5
2017-09-11 | 14:40 | 1.721 | 0 |  | 1.5
2017-09-11 | 14:45 | 1.7234 | 0 | 0 | 1.5 | 0 | 92.5066
2017-09-11 | 14:50 | 1.728 | 0 |  | 1.5
2017-09-11 | 14:55 | 1.7163 | 0 |  | 1.5
2017-09-11 | 15:00 | 1.7319 | 0 | 0 | 1.5 | 0 | 92.9734
2017-09-11 | 15:05 | 1.7514 | 0 |  | 1.5
2017-09-11 | 15:10 | 1.728 | 0 |  | 1.5
2017-09-11 | 15:15 | 1.7351 | 0 | 0 | 1.5 | 0 | 93.189
2017-09-11 | 15:20 | 1.7546 | 0 |  | 1.5
2017-09-11 | 15:25 | 1.7078 | 0 |  | 1.5
2017-09-11 | 15:30 | 1.7382 | 0 | 0 | 1.5 | 0 | 93.4109
2017-09-11 | 15:35 | 1.7327 | 0 |  | 1.5
2017-09-11 | 15:40 | 1.7156 | 0 |  | 1.5
2017-09-11 | 15:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 93.8557
2017-09-11 | 15:50 | 1.753 | 0 |  | 1.5
2017-09-11 | 15:55 | 1.7787 | 0 |  | 1.5
2017-09-11 | 16:00 | 1.7881 | 0 | 0 | 1.5 | 0 | 93.1893
2017-09-11 | 16:05 | 1.7709 | 0 |  | 1.5
2017-09-11 | 16:10 | 1.7468 | 0 |  | 1.5
2017-09-11 | 16:15 | 1.7546 | 0 | 0 | 1.5 | 0 | 92.7027
2017-09-11 | 16:20 | 1.7858 | 0 |  | 1.5
2017-09-11 | 16:25 | 1.7553 | 0 |  | 1.5
2017-09-11 | 16:30 | 1.7561 | 0 | 0 | 1.5 | 0 | 92.1717
2017-09-11 | 16:35 | 1.7733 | 0 |  | 1.5
2017-09-11 | 16:40 | 1.8154 | 0 |  | 1.5
2017-09-11 | 16:45 | 1.7889 | 0 | 0 | 1.5 | 0 | 91.221
2017-09-11 | 16:50 | 1.8489 | 0 |  | 1.5
2017-09-11 | 16:55 | 1.8115 | 0 |  | 1.5
2017-09-11 | 17:00 | 1.8427 | 0 | 0 | 1.5 | 0 | 89.3012
2017-09-11 | 17:05 | 1.8224 | 0 |  | 1.5
2017-09-11 | 17:10 | 1.8591 | 0 |  | 1.5
2017-09-11 | 17:15 | 1.8271 | 0 | 0 | 1.5 | 0 | 87.269
2017-09-11 | 17:20 | 1.8544 | 0 |  | 1.5
2017-09-11 | 17:25 | 1.8489 | 0 |  | 1.5
2017-09-11 | 17:30 | 1.8341 | 0 | 0 | 1.5 | 0 | 84.8197
2017-09-11 | 17:35 | 1.8271 | 0 |  | 1.5
2017-09-11 | 17:40 | 1.8037 | 0 |  | 1.5
2017-09-11 | 17:45 | 1.7998 | 0 | 0 | 1.5 | 0 | 83.0937
2017-09-11 | 17:50 | 1.7936 | 0 |  | 1.5
2017-09-11 | 17:55 | 1.7795 | 0 |  | 1.5
2017-09-11 | 18:00 | 1.7702 | 0 | 0 | 1.5 | 0 | 82.0692
2017-09-11 | 18:05 | 1.7912 | 0 |  | 1.5
2017-09-11 | 18:10 | 1.799 | 0 |  | 1.5
2017-09-11 | 18:15 | 1.8045 | 0 | 0 | 1.5 | 0 | 81.3395
2017-09-11 | 18:20 | 1.767 | 0 |  | 1.5
2017-09-11 | 18:25 | 1.739 | 0 |  | 1.5
2017-09-11 | 18:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 80.7068
2017-09-11 | 18:35 | 1.7514 | 0 |  | 1.5
2017-09-11 | 18:40 | 1.7585 | 0 |  | 1.5
2017-09-11 | 18:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 80.4822
2017-09-11 | 18:50 | 1.76 | 0 |  | 1.5
2017-09-11 | 18:55 | 1.7561 | 0 |  | 1.5
2017-09-11 | 19:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 80.3148
2017-09-11 | 19:05 | 1.7366 | 0 |  | 1.5
2017-09-11 | 19:10 | 1.7561 | 0 |  | 1.5
2017-09-11 | 19:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 80.0788
2017-09-11 | 19:20 | 1.7507 | 0 |  | 1.5
2017-09-11 | 19:25 | 1.7429 | 0 |  | 1.5
2017-09-11 | 19:30 | 1.7702 | 0 | 0 | 1.5 | 0 | 79.9468
2017-09-11 | 19:35 | 1.7468 | 0 |  | 1.5
2017-09-11 | 19:40 | 1.7639 | 0 |  | 1.5
2017-09-11 | 19:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.6982
2017-09-11 | 19:50 | 1.7514 | 0 |  | 1.5
2017-09-11 | 19:55 | 1.7491 | 0 |  | 1.5
2017-09-11 | 20:00 | 1.7787 | 0 | 0 | 1.5 | 0 | 79.2579
2017-09-11 | 20:05 | 1.7873 | 0 |  | 1.5
2017-09-11 | 20:10 | 1.7569 | 0 |  | 1.5
2017-09-11 | 20:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 79.1017
2017-09-11 | 20:20 | 1.7312 | 0 |  | 1.5
2017-09-11 | 20:25 | 1.7327 | 0 |  | 1.5
2017-09-11 | 20:30 | 1.7499 | 0 | 0 | 1.5 | 0 | 79.3394
2017-09-11 | 20:35 | 1.7351 | 0 |  | 1.5
2017-09-11 | 20:40 | 1.7585 | 0 |  | 1.5
2017-09-11 | 20:45 | 1.7741 | 0 | 0 | 1.5 | 0 | 79.3205
2017-09-11 | 20:50 | 1.7343 | 0 |  | 1.5
2017-09-11 | 20:55 | 1.7358 | 0 |  | 1.5
2017-09-11 | 21:00 | 1.7444 | 0 | 0 | 1.5 | 0 | 79.3715
2017-09-11 | 21:05 | -0.10262 | 0 |  | 1.5
2017-09-11 | 21:10 | -0.1034 | 0 |  | 1.5
2017-09-11 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 21:20 | -0.10496 | 0 |  | 1.5
2017-09-11 | 21:25 | -0.10574 | 0 |  | 1.5
2017-09-11 | 21:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-11 | 21:40 | -0.10574 | 0 |  | 1.5
2017-09-11 | 21:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 21:50 | -0.10652 | 0 |  | 1.5
2017-09-11 | 21:55 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 22:05 | -0.1073 | 0 |  | 1.5
2017-09-11 | 22:10 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 22:20 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:25 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 22:35 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:40 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 22:50 | -0.10652 | 0 |  | 1.5
2017-09-11 | 22:55 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 23:05 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:10 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 23:20 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:25 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 23:35 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:40 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-11 | 23:50 | -0.10574 | 0 |  | 1.5
2017-09-11 | 23:55 | -0.10574 | 0 |  | 1.5
2017-09-12 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 0:05 | -0.10574 | 0 |  | 1.5
2017-09-12 | 0:10 | -0.10496 | 0 |  | 1.5
2017-09-12 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 0:20 | -0.10496 | 0 |  | 1.5
2017-09-12 | 0:25 | -0.10496 | 0 |  | 1.5
2017-09-12 | 0:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 0:35 | -0.10496 | 0 |  | 1.5
2017-09-12 | 0:40 | -0.10496 | 0 |  | 1.5
2017-09-12 | 0:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 0:50 | -0.10496 | 0 |  | 1.5
2017-09-12 | 0:55 | -0.10418 | 0 |  | 1.5
2017-09-12 | 1:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 1:05 | -0.10496 | 0 |  | 1.5
2017-09-12 | 1:10 | -0.10496 | 0 |  | 1.5
2017-09-12 | 1:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 1:20 | -0.10808 | 0 |  | 1.5
2017-09-12 | 1:25 | -0.10808 | 0 |  | 1.5
2017-09-12 | 1:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 1:35 | -0.10808 | 0 |  | 1.5
2017-09-12 | 1:40 | -0.10808 | 0 |  | 1.5
2017-09-12 | 1:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 1:50 | -0.10808 | 0 |  | 1.5
2017-09-12 | 1:55 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 2:05 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:10 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 2:20 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:25 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 2:35 | -0.10886 | 0 |  | 1.5
2017-09-12 | 2:40 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 2:50 | -0.10808 | 0 |  | 1.5
2017-09-12 | 2:55 | -0.10886 | 0 |  | 1.5
2017-09-12 | 3:00 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 3:05 | -0.10886 | 0 |  | 1.5
2017-09-12 | 3:10 | -0.10808 | 0 |  | 1.5
2017-09-12 | 3:15 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 3:20 | -0.10886 | 0 |  | 1.5
2017-09-12 | 3:25 | -0.10808 | 0 |  | 1.5
2017-09-12 | 3:30 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 3:35 | -0.10808 | 0 |  | 1.5
2017-09-12 | 3:40 | -0.10808 | 0 |  | 1.5
2017-09-12 | 3:45 | -0.10808 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 3:50 | -0.10808 | 0 |  | 1.5
2017-09-12 | 3:55 | -0.10808 | 0 |  | 1.5
2017-09-12 | 4:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 4:05 | -0.1073 | 0 |  | 1.5
2017-09-12 | 4:10 | -0.1073 | 0 |  | 1.5
2017-09-12 | 4:15 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 4:20 | -0.1073 | 0 |  | 1.5
2017-09-12 | 4:25 | -0.10652 | 0 |  | 1.5
2017-09-12 | 4:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 4:35 | -0.1073 | 0 |  | 1.5
2017-09-12 | 4:40 | -0.1073 | 0 |  | 1.5
2017-09-12 | 4:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 4:50 | -0.10808 | 0 |  | 1.5
2017-09-12 | 4:55 | -0.1073 | 0 |  | 1.5
2017-09-12 | 5:00 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 5:05 | 2.0135 | 0 |  | 1.5
2017-09-12 | 5:10 | 2.0931 | 0 |  | 1.5
2017-09-12 | 5:15 | 2.012 | 0 | 0 | 1.5 | 0 | 92.4704
2017-09-12 | 5:20 | 1.9176 | 0 |  | 1.5
2017-09-12 | 5:25 | 1.9496 | 0 |  | 1.5
2017-09-12 | 5:30 | 1.9152 | 0 | 0 | 1.5 | 0 | 87.3232
2017-09-12 | 5:35 | 1.8614 | 0 |  | 1.5
2017-09-12 | 5:40 | 1.8435 | 0 |  | 1.5
2017-09-12 | 5:45 | 1.8076 | 0 | 0 | 1.5 | 0 | 84.7396
2017-09-12 | 5:50 | 1.7982 | 0 |  | 1.5
2017-09-12 | 5:55 | 1.7803 | 0 |  | 1.5
2017-09-12 | 6:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 83.6256
2017-09-12 | 6:05 | 1.7787 | 0 |  | 1.5
2017-09-12 | 6:10 | 1.7725 | 0 |  | 1.5
2017-09-12 | 6:15 | 1.76 | 0 | 0 | 1.5 | 0 | 82.855
2017-09-12 | 6:20 | 1.7842 | 0 |  | 1.5
2017-09-12 | 6:25 | 1.7733 | 0 |  | 1.5
2017-09-12 | 6:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 82.2355
2017-09-12 | 6:35 | 1.7514 | 0 |  | 1.5
2017-09-12 | 6:40 | 1.7787 | 0 |  | 1.5
2017-09-12 | 6:45 | 1.7678 | 0 | 0 | 1.5 | 0 | 81.6468
2017-09-12 | 6:50 | 1.7834 | 0 |  | 1.5
2017-09-12 | 6:55 | 1.7569 | 0 |  | 1.5
2017-09-12 | 7:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 81.0678
2017-09-12 | 7:05 | 1.7881 | 0 |  | 1.5
2017-09-12 | 7:10 | 1.7663 | 0 |  | 1.5
2017-09-12 | 7:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 80.7124
2017-09-12 | 7:20 | 1.7507 | 0 |  | 1.5
2017-09-12 | 7:25 | 1.7967 | 0 |  | 1.5
2017-09-12 | 7:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 80.2977
2017-09-12 | 7:35 | 1.7639 | 0 |  | 1.5
2017-09-12 | 7:40 | 1.7335 | 0 |  | 1.5
2017-09-12 | 7:45 | 1.7733 | 0 | 0 | 1.5 | 0 | 80.1301
2017-09-12 | 7:50 | 1.7663 | 0 |  | 1.5
2017-09-12 | 7:55 | 1.7374 | 0 |  | 1.5
2017-09-12 | 8:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 79.7621
2017-09-12 | 8:05 | 1.7452 | 0 |  | 1.5
2017-09-12 | 8:10 | 1.7397 | 0 |  | 1.5
2017-09-12 | 8:15 | 1.7514 | 0 | 0 | 1.5 | 0 | 79.7264
2017-09-12 | 8:20 | 1.7374 | 0 |  | 1.5
2017-09-12 | 8:25 | 1.7585 | 0 |  | 1.5
2017-09-12 | 8:30 | 1.7101 | 0 | 0 | 1.5 | 0 | 80.0356
2017-09-12 | 8:35 | 1.7366 | 0 |  | 1.5
2017-09-12 | 8:40 | 1.7639 | 0 |  | 1.5
2017-09-12 | 8:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 80.1581
2017-09-12 | 8:50 | 1.7296 | 0 |  | 1.5
2017-09-12 | 8:55 | 1.7015 | 0 |  | 1.5
2017-09-12 | 9:00 | 1.7179 | 0 | 0 | 1.5 | 0 | 80.5852
2017-09-12 | 9:05 | 1.7273 | 0 |  | 1.5
2017-09-12 | 9:10 | 1.7803 | 0 |  | 1.5
2017-09-12 | 9:15 | 1.7421 | 0 | 0 | 1.5 | 0 | 80.652
2017-09-12 | 9:20 | 1.7195 | 0 |  | 1.5
2017-09-12 | 9:25 | 1.746 | 0 |  | 1.5
2017-09-12 | 9:30 | 1.7093 | 0 | 0 | 1.5 | 0 | 80.9285
2017-09-12 | 9:35 | 1.7062 | 0 |  | 1.5
2017-09-12 | 9:40 | 1.7195 | 0 |  | 1.5
2017-09-12 | 9:45 | 1.7101 | 0 | 0 | 1.5 | 0 | 81.7525
2017-09-12 | 9:50 | 1.7397 | 0 |  | 1.5
2017-09-12 | 9:55 | 1.7561 | 0 |  | 1.5
2017-09-12 | 10:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 81.8105
2017-09-12 | 10:05 | 1.7374 | 0 |  | 1.5
2017-09-12 | 10:10 | 1.739 | 0 |  | 1.5
2017-09-12 | 10:15 | 1.7327 | 0 | 0 | 1.5 | 0 | 82.2414
2017-09-12 | 10:20 | 1.7171 | 0 |  | 1.5
2017-09-12 | 10:25 | 1.7273 | 0 |  | 1.5
2017-09-12 | 10:30 | 1.7015 | 0 | 0 | 1.5 | 0 | 83.0789
2017-09-12 | 10:35 | 1.6961 | 0 |  | 1.5
2017-09-12 | 10:40 | 1.7109 | 0 |  | 1.5
2017-09-12 | 10:45 | 1.6929 | 0 | 0 | 1.5 | 0 | 84.1609
2017-09-12 | 10:50 | 1.6984 | 0 |  | 1.5
2017-09-12 | 10:55 | 1.7007 | 0 |  | 1.5
2017-09-12 | 11:00 | 1.6961 | 0 | 0 | 1.5 | 0 | 85.6653
2017-09-12 | 11:05 | 1.8131 | 0 |  | 1.5
2017-09-12 | 11:10 | 1.7756 | 0 |  | 1.5
2017-09-12 | 11:15 | 1.7436 | 0 | 0 | 1.5 | 0 | 84.8093
2017-09-12 | 11:20 | 1.7733 | 0 |  | 1.5
2017-09-12 | 11:25 | 1.728 | 0 |  | 1.5
2017-09-12 | 11:30 | 1.7023 | 0 | 0 | 1.5 | 0 | 85.2673
2017-09-12 | 11:35 | 1.6851 | 0 |  | 1.5
2017-09-12 | 11:40 | 1.7179 | 0 |  | 1.5
2017-09-12 | 11:45 | 1.746 | 0 | 0 | 1.5 | 0 | 86.1992
2017-09-12 | 11:50 | 1.767 | 0 |  | 1.5
2017-09-12 | 11:55 | 1.7772 | 0 |  | 1.5
2017-09-12 | 12:00 | 1.7858 | 0 | 0 | 1.5 | 0 | 85.8846
2017-09-12 | 12:05 | 1.7382 | 0 |  | 1.5
2017-09-12 | 12:10 | 1.7553 | 0 |  | 1.5
2017-09-12 | 12:15 | 1.7405 | 0 | 0 | 1.5 | 0 | 86.0115
2017-09-12 | 12:20 | 1.753 | 0 |  | 1.5
2017-09-12 | 12:25 | 1.7413 | 0 |  | 1.5
2017-09-12 | 12:30 | 1.7397 | 0 | 0 | 1.5 | 0 | 86.187
2017-09-12 | 12:35 | 1.7397 | 0 |  | 1.5
2017-09-12 | 12:40 | 1.7358 | 0 |  | 1.5
2017-09-12 | 12:45 | 1.7304 | 0 | 0 | 1.5 | 0 | 86.5048
2017-09-12 | 12:50 | 1.7234 | 0 |  | 1.5
2017-09-12 | 12:55 | 1.7507 | 0 |  | 1.5
2017-09-12 | 13:00 | 1.7936 | 0 | 0 | 1.5 | 0 | 86.7627
2017-09-12 | 13:05 | 1.7858 | 0 |  | 1.5
2017-09-12 | 13:10 | 1.7522 | 0 |  | 1.5
2017-09-12 | 13:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 86.3681
2017-09-12 | 13:20 | 1.7148 | 0 |  | 1.5
2017-09-12 | 13:25 | 1.6586 | 0 |  | 1.5
2017-09-12 | 13:30 | 1.6976 | 0 | 0 | 1.5 | 0 | 87.8095
2017-09-12 | 13:35 | 2.3255 | 0 |  | 1.5
2017-09-12 | 13:40 | 1.5541 | 0 |  | 1.5
2017-09-12 | 13:45 | 1.6352 | 0 | 0 | 1.5 | 0 | 89.3033
2017-09-12 | 13:50 | 1.9082 | 0 |  | 1.5
2017-09-12 | 13:55 | 1.5861 | 0 |  | 1.5
2017-09-12 | 14:00 | 1.6703 | 0 | 0 | 1.5 | 0 | 90.6287
2017-09-12 | 14:05 | 2.462 | 0 |  | 1.5
2017-09-12 | 14:10 | 1.5767 | 0 |  | 1.5
2017-09-12 | 14:15 | 1.6376 | 0 | 0 | 1.5 | 0 | 90.015
2017-09-12 | 14:20 | 1.5759 | 0 |  | 1.5
2017-09-12 | 14:25 | 1.6641 | 0 |  | 1.5
2017-09-12 | 14:30 | 1.6649 | 0 | 0 | 1.5 | 0 | 90.862
2017-09-12 | 14:35 | 1.6812 | 0 |  | 1.5
2017-09-12 | 14:40 | 1.6844 | 0 |  | 1.5
2017-09-12 | 14:45 | 1.6859 | 0 | 0 | 1.5 | 0 | 92.7347
2017-09-12 | 14:50 | 1.6539 | 0 |  | 1.5
2017-09-12 | 14:55 | 1.6781 | 0 |  | 1.5
2017-09-12 | 15:00 | 1.7226 | 0 | 0 | 1.5 | 0 | 94.4771
2017-09-12 | 15:05 | 1.746 | 0 |  | 1.5
2017-09-12 | 15:10 | 1.7553 | 0 |  | 1.5
2017-09-12 | 15:15 | 1.785 | 0 | 0 | 1.5 | 0 | 94.3908
2017-09-12 | 15:20 | 1.7764 | 0 |  | 1.5
2017-09-12 | 15:25 | 1.7756 | 0 |  | 1.5
2017-09-12 | 15:30 | 1.7756 | 0 | 0 | 1.5 | 0 | 93.764
2017-09-12 | 15:35 | 1.7748 | 0 |  | 1.5
2017-09-12 | 15:40 | 1.7912 | 0 |  | 1.5
2017-09-12 | 15:45 | 1.8006 | 0 | 0 | 1.5 | 0 | 93.1271
2017-09-12 | 15:50 | 1.7733 | 0 |  | 1.5
2017-09-12 | 15:55 | 1.7787 | 0 |  | 1.5
2017-09-12 | 16:00 | 1.7889 | 0 | 0 | 1.5 | 0 | 92.2996
2017-09-12 | 16:05 | 1.7889 | 0 |  | 1.5
2017-09-12 | 16:10 | 1.8053 | 0 |  | 1.5
2017-09-12 | 16:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 91.1593
2017-09-12 | 16:20 | 1.7756 | 0 |  | 1.5
2017-09-12 | 16:25 | 1.767 | 0 |  | 1.5
2017-09-12 | 16:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 90.5724
2017-09-12 | 16:35 | 1.7678 | 0 |  | 1.5
2017-09-12 | 16:40 | 1.7928 | 0 |  | 1.5
2017-09-12 | 16:45 | 1.785 | 0 | 0 | 1.5 | 0 | 89.8367
2017-09-12 | 16:50 | 1.7694 | 0 |  | 1.5
2017-09-12 | 16:55 | 1.7382 | 0 |  | 1.5
2017-09-12 | 17:00 | 1.7413 | 0 | 0 | 1.5 | 0 | 89.7986
2017-09-12 | 17:05 | 1.7655 | 0 |  | 1.5
2017-09-12 | 17:10 | 1.7967 | 0 |  | 1.5
2017-09-12 | 17:15 | 1.8006 | 0 | 0 | 1.5 | 0 | 89.2083
2017-09-12 | 17:20 | 1.7904 | 0 |  | 1.5
2017-09-12 | 17:25 | 1.7951 | 0 |  | 1.5
2017-09-12 | 17:30 | 1.7717 | 0 | 0 | 1.5 | 0 | 88.3056
2017-09-12 | 17:35 | 1.8053 | 0 |  | 1.5
2017-09-12 | 17:40 | 1.7904 | 0 |  | 1.5
2017-09-12 | 17:45 | 1.7928 | 0 | 0 | 1.5 | 0 | 87.137
2017-09-12 | 17:50 | 1.7943 | 0 |  | 1.5
2017-09-12 | 17:55 | 1.7717 | 0 |  | 1.5
2017-09-12 | 18:00 | 1.7936 | 0 | 0 | 1.5 | 0 | 85.9795
2017-09-12 | 18:05 | 1.778 | 0 |  | 1.5
2017-09-12 | 18:10 | 1.7904 | 0 |  | 1.5
2017-09-12 | 18:15 | 1.7803 | 0 | 0 | 1.5 | 0 | 84.9812
2017-09-12 | 18:20 | 1.785 | 0 |  | 1.5
2017-09-12 | 18:25 | 1.8029 | 0 |  | 1.5
2017-09-12 | 18:30 | 1.8294 | 0 | 0 | 1.5 | 0 | 83.7197
2017-09-12 | 18:35 | 1.7717 | 0 |  | 1.5
2017-09-12 | 18:40 | 1.7834 | 0 |  | 1.5
2017-09-12 | 18:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 82.8511
2017-09-12 | 18:50 | 1.7858 | 0 |  | 1.5
2017-09-12 | 18:55 | 1.7694 | 0 |  | 1.5
2017-09-12 | 19:00 | 1.7725 | 0 | 0 | 1.5 | 0 | 82.1621
2017-09-12 | 19:05 | 1.7842 | 0 |  | 1.5
2017-09-12 | 19:10 | 1.7327 | 0 |  | 1.5
2017-09-12 | 19:15 | 1.7436 | 0 | 0 | 1.5 | 0 | 81.9505
2017-09-12 | 19:20 | 1.7429 | 0 |  | 1.5
2017-09-12 | 19:25 | 1.7429 | 0 |  | 1.5
2017-09-12 | 19:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 81.6052
2017-09-12 | 19:35 | 1.7694 | 0 |  | 1.5
2017-09-12 | 19:40 | 1.7826 | 0 |  | 1.5
2017-09-12 | 19:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 80.899
2017-09-12 | 19:50 | 1.7709 | 0 |  | 1.5
2017-09-12 | 19:55 | 1.7928 | 0 |  | 1.5
2017-09-12 | 20:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 80.1288
2017-09-12 | 20:05 | 1.7655 | 0 |  | 1.5
2017-09-12 | 20:10 | 1.767 | 0 |  | 1.5
2017-09-12 | 20:15 | 1.7756 | 0 | 0 | 1.5 | 0 | 79.644
2017-09-12 | 20:20 | 1.7748 | 0 |  | 1.5
2017-09-12 | 20:25 | 1.7405 | 0 |  | 1.5
2017-09-12 | 20:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.7973
2017-09-12 | 20:35 | 1.76 | 0 |  | 1.5
2017-09-12 | 20:40 | 1.7202 | 0 |  | 1.5
2017-09-12 | 20:45 | 1.7382 | 0 | 0 | 1.5 | 0 | 79.9484
2017-09-12 | 20:50 | 1.7288 | 0 |  | 1.5
2017-09-12 | 20:55 | 1.7694 | 0 |  | 1.5
2017-09-12 | 21:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.7493
2017-09-12 | 21:05 | -0.10184 | 0 |  | 1.5
2017-09-12 | 21:10 | -0.10262 | 0 |  | 1.5
2017-09-12 | 21:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 21:20 | -0.10418 | 0 |  | 1.5
2017-09-12 | 21:25 | -0.10418 | 0 |  | 1.5
2017-09-12 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-12 | 21:40 | -0.10496 | 0 |  | 1.5
2017-09-12 | 21:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 21:50 | -0.10418 | 0 |  | 1.5
2017-09-12 | 21:55 | -0.10496 | 0 |  | 1.5
2017-09-12 | 22:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 22:05 | -0.10496 | 0 |  | 1.5
2017-09-12 | 22:10 | -0.10496 | 0 |  | 1.5
2017-09-12 | 22:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 22:20 | -0.10496 | 0 |  | 1.5
2017-09-12 | 22:25 | -0.1034 | 0 |  | 1.5
2017-09-12 | 22:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 22:35 | -0.1034 | 0 |  | 1.5
2017-09-12 | 22:40 | -0.1034 | 0 |  | 1.5
2017-09-12 | 22:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 22:50 | -0.1034 | 0 |  | 1.5
2017-09-12 | 22:55 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 23:05 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:10 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 23:20 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:25 | -0.10262 | 0 |  | 1.5
2017-09-12 | 23:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 23:35 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:40 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-12 | 23:50 | -0.1034 | 0 |  | 1.5
2017-09-12 | 23:55 | -0.1034 | 0 |  | 1.5
2017-09-13 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 0:05 | -0.1034 | 0 |  | 1.5
2017-09-13 | 0:10 | -0.10262 | 0 |  | 1.5
2017-09-13 | 0:15 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 0:20 | -0.1034 | 0 |  | 1.5
2017-09-13 | 0:25 | -0.10262 | 0 |  | 1.5
2017-09-13 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 0:35 | -0.10262 | 0 |  | 1.5
2017-09-13 | 0:40 | -0.10574 | 0 |  | 1.5
2017-09-13 | 0:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 0:50 | -0.10262 | 0 |  | 1.5
2017-09-13 | 0:55 | -0.1034 | 0 |  | 1.5
2017-09-13 | 1:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 1:05 | -0.10262 | 0 |  | 1.5
2017-09-13 | 1:10 | -0.10262 | 0 |  | 1.5
2017-09-13 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 1:20 | -0.10652 | 0 |  | 1.5
2017-09-13 | 1:25 | -0.10574 | 0 |  | 1.5
2017-09-13 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 1:35 | -0.10574 | 0 |  | 1.5
2017-09-13 | 1:40 | -0.10574 | 0 |  | 1.5
2017-09-13 | 1:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 1:50 | -0.10574 | 0 |  | 1.5
2017-09-13 | 1:55 | -0.10574 | 0 |  | 1.5
2017-09-13 | 2:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 2:05 | -0.10574 | 0 |  | 1.5
2017-09-13 | 2:10 | -0.10574 | 0 |  | 1.5
2017-09-13 | 2:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 2:20 | -0.10574 | 0 |  | 1.5
2017-09-13 | 2:25 | -0.10574 | 0 |  | 1.5
2017-09-13 | 2:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 2:35 | -0.10652 | 0 |  | 1.5
2017-09-13 | 2:40 | -0.10652 | 0 |  | 1.5
2017-09-13 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 2:50 | -0.10652 | 0 |  | 1.5
2017-09-13 | 2:55 | -0.10652 | 0 |  | 1.5
2017-09-13 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 3:05 | -0.10652 | 0 |  | 1.5
2017-09-13 | 3:10 | -0.10652 | 0 |  | 1.5
2017-09-13 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 3:20 | -0.10652 | 0 |  | 1.5
2017-09-13 | 3:25 | -0.10652 | 0 |  | 1.5
2017-09-13 | 3:30 | -0.10886 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 3:35 | -0.1073 | 0 |  | 1.5
2017-09-13 | 3:40 | -0.1073 | 0 |  | 1.5
2017-09-13 | 3:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 3:50 | -0.10652 | 0 |  | 1.5
2017-09-13 | 3:55 | -0.1073 | 0 |  | 1.5
2017-09-13 | 4:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 4:05 | -0.1073 | 0 |  | 1.5
2017-09-13 | 4:10 | -0.10652 | 0 |  | 1.5
2017-09-13 | 4:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 4:20 | -0.10652 | 0 |  | 1.5
2017-09-13 | 4:25 | -0.10652 | 0 |  | 1.5
2017-09-13 | 4:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 4:35 | -0.10964 | 0 |  | 1.5
2017-09-13 | 4:40 | -0.10652 | 0 |  | 1.5
2017-09-13 | 4:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 4:50 | -0.10652 | 0 |  | 1.5
2017-09-13 | 4:55 | -0.10652 | 0 |  | 1.5
2017-09-13 | 5:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 5:05 | 2.2811 | 0 |  | 1.5
2017-09-13 | 5:10 | 2.2811 | 0 |  | 1.5
2017-09-13 | 5:15 | 2.0361 | 0 | 0 | 1.5 | 0 | 88.8733
2017-09-13 | 5:20 | 1.9301 | 0 |  | 1.5
2017-09-13 | 5:25 | 1.8521 | 0 |  | 1.5
2017-09-13 | 5:30 | 1.8146 | 0 | 0 | 1.5 | 0 | 85.115
2017-09-13 | 5:35 | 1.7873 | 0 |  | 1.5
2017-09-13 | 5:40 | 1.7717 | 0 |  | 1.5
2017-09-13 | 5:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 84.5304
2017-09-13 | 5:50 | 1.7585 | 0 |  | 1.5
2017-09-13 | 5:55 | 1.7483 | 0 |  | 1.5
2017-09-13 | 6:00 | 1.7569 | 0 | 0 | 1.5 | 0 | 84.4504
2017-09-13 | 6:05 | 1.746 | 0 |  | 1.5
2017-09-13 | 6:10 | 1.7202 | 0 |  | 1.5
2017-09-13 | 6:15 | 1.7218 | 0 | 0 | 1.5 | 0 | 84.6722
2017-09-13 | 6:20 | 1.7343 | 0 |  | 1.5
2017-09-13 | 6:25 | 1.7397 | 0 |  | 1.5
2017-09-13 | 6:30 | 1.753 | 0 | 0 | 1.5 | 0 | 84.7831
2017-09-13 | 6:35 | 1.7444 | 0 |  | 1.5
2017-09-13 | 6:40 | 1.7522 | 0 |  | 1.5
2017-09-13 | 6:45 | 1.7553 | 0 | 0 | 1.5 | 0 | 84.842
2017-09-13 | 6:50 | 1.7655 | 0 |  | 1.5
2017-09-13 | 6:55 | 1.7296 | 0 |  | 1.5
2017-09-13 | 7:00 | 1.739 | 0 | 0 | 1.5 | 0 | 85.0015
2017-09-13 | 7:05 | 1.7312 | 0 |  | 1.5
2017-09-13 | 7:10 | 1.739 | 0 |  | 1.5
2017-09-13 | 7:15 | 1.7358 | 0 | 0 | 1.5 | 0 | 85.1426
2017-09-13 | 7:20 | 1.7421 | 0 |  | 1.5
2017-09-13 | 7:25 | 1.7226 | 0 |  | 1.5
2017-09-13 | 7:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 85.6247
2017-09-13 | 7:35 | 1.7397 | 0 |  | 1.5
2017-09-13 | 7:40 | 1.7468 | 0 |  | 1.5
2017-09-13 | 7:45 | 1.7273 | 0 | 0 | 1.5 | 0 | 86.0923
2017-09-13 | 7:50 | 1.7218 | 0 |  | 1.5
2017-09-13 | 7:55 | 1.7312 | 0 |  | 1.5
2017-09-13 | 8:00 | 1.7257 | 0 | 0 | 1.5 | 0 | 86.6131
2017-09-13 | 8:05 | 1.7015 | 0 |  | 1.5
2017-09-13 | 8:10 | 1.7163 | 0 |  | 1.5
2017-09-13 | 8:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 87.1921
2017-09-13 | 8:20 | 1.7226 | 0 |  | 1.5
2017-09-13 | 8:25 | 1.7296 | 0 |  | 1.5
2017-09-13 | 8:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 87.6903
2017-09-13 | 8:35 | 1.721 | 0 |  | 1.5
2017-09-13 | 8:40 | 1.7803 | 0 |  | 1.5
2017-09-13 | 8:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 87.6589
2017-09-13 | 8:50 | 1.824 | 0 |  | 1.5
2017-09-13 | 8:55 | 1.8489 | 0 |  | 1.5
2017-09-13 | 9:00 | 1.8599 | 0 | 0 | 1.5 | 0 | 85.1615
2017-09-13 | 9:05 | 1.856 | 0 |  | 1.5
2017-09-13 | 9:10 | 1.824 | 0 |  | 1.5
2017-09-13 | 9:15 | 1.817 | 0 | 0 | 1.5 | 0 | 83.3039
2017-09-13 | 9:20 | 1.8006 | 0 |  | 1.5
2017-09-13 | 9:25 | 1.7631 | 0 |  | 1.5
2017-09-13 | 9:30 | 1.7639 | 0 | 0 | 1.5 | 0 | 82.6367
2017-09-13 | 9:35 | 1.76 | 0 |  | 1.5
2017-09-13 | 9:40 | 1.7694 | 0 |  | 1.5
2017-09-13 | 9:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.359
2017-09-13 | 9:50 | 1.7382 | 0 |  | 1.5
2017-09-13 | 9:55 | 1.739 | 0 |  | 1.5
2017-09-13 | 10:00 | 1.7124 | 0 | 0 | 1.5 | 0 | 82.3264
2017-09-13 | 10:05 | 1.7241 | 0 |  | 1.5
2017-09-13 | 10:10 | 1.7655 | 0 |  | 1.5
2017-09-13 | 10:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 82.4504
2017-09-13 | 10:20 | 1.7647 | 0 |  | 1.5
2017-09-13 | 10:25 | 1.7608 | 0 |  | 1.5
2017-09-13 | 10:30 | 1.7421 | 0 | 0 | 1.5 | 0 | 82.3458
2017-09-13 | 10:35 | 1.7397 | 0 |  | 1.5
2017-09-13 | 10:40 | 1.7031 | 0 |  | 1.5
2017-09-13 | 10:45 | 1.739 | 0 | 0 | 1.5 | 0 | 82.8331
2017-09-13 | 10:50 | 1.721 | 0 |  | 1.5
2017-09-13 | 10:55 | 1.7335 | 0 |  | 1.5
2017-09-13 | 11:00 | 1.7202 | 0 | 0 | 1.5 | 0 | 83.0284
2017-09-13 | 11:05 | 1.7421 | 0 |  | 1.5
2017-09-13 | 11:10 | 1.746 | 0 |  | 1.5
2017-09-13 | 11:15 | 1.7343 | 0 | 0 | 1.5 | 0 | 83.1451
2017-09-13 | 11:20 | 1.7569 | 0 |  | 1.5
2017-09-13 | 11:25 | 1.7327 | 0 |  | 1.5
2017-09-13 | 11:30 | 1.707 | 0 | 0 | 1.5 | 0 | 83.1612
2017-09-13 | 11:35 | 1.7499 | 0 |  | 1.5
2017-09-13 | 11:40 | 1.7491 | 0 |  | 1.5
2017-09-13 | 11:45 | 1.7296 | 0 | 0 | 1.5 | 0 | 83.1756
2017-09-13 | 11:50 | 1.7124 | 0 |  | 1.5
2017-09-13 | 11:55 | 1.7195 | 0 |  | 1.5
2017-09-13 | 12:00 | 1.7257 | 0 | 0 | 1.5 | 0 | 83.3811
2017-09-13 | 12:05 | 1.7561 | 0 |  | 1.5
2017-09-13 | 12:10 | 1.7499 | 0 |  | 1.5
2017-09-13 | 12:15 | 1.7296 | 0 | 0 | 1.5 | 0 | 83.3299
2017-09-13 | 12:20 | 1.7421 | 0 |  | 1.5
2017-09-13 | 12:25 | 1.7421 | 0 |  | 1.5
2017-09-13 | 12:30 | 1.7085 | 0 | 0 | 1.5 | 0 | 84.0441
2017-09-13 | 12:35 | 1.7062 | 0 |  | 1.5
2017-09-13 | 12:40 | 1.7156 | 0 |  | 1.5
2017-09-13 | 12:45 | 1.7257 | 0 | 0 | 1.5 | 0 | 84.902
2017-09-13 | 12:50 | 1.7585 | 0 |  | 1.5
2017-09-13 | 12:55 | 1.739 | 0 |  | 1.5
2017-09-13 | 13:00 | 1.7234 | 0 | 0 | 1.5 | 0 | 85.2265
2017-09-13 | 13:05 | 1.6851 | 0 |  | 1.5
2017-09-13 | 13:10 | 1.6875 | 0 |  | 1.5
2017-09-13 | 13:15 | 1.6844 | 0 | 0 | 1.5 | 0 | 86.6758
2017-09-13 | 13:20 | 1.7046 | 0 |  | 1.5
2017-09-13 | 13:25 | 1.7273 | 0 |  | 1.5
2017-09-13 | 13:30 | 1.6914 | 0 | 0 | 1.5 | 0 | 88.0977
2017-09-13 | 13:35 | 1.7195 | 0 |  | 1.5
2017-09-13 | 13:40 | 1.7577 | 0 |  | 1.5
2017-09-13 | 13:45 | 1.7772 | 0 | 0 | 1.5 | 0 | 88.1451
2017-09-13 | 13:50 | 1.7975 | 0 |  | 1.5
2017-09-13 | 13:55 | 1.7858 | 0 |  | 1.5
2017-09-13 | 14:00 | 1.8154 | 0 | 0 | 1.5 | 0 | 86.8181
2017-09-13 | 14:05 | 1.7795 | 0 |  | 1.5
2017-09-13 | 14:10 | 1.7889 | 0 |  | 1.5
2017-09-13 | 14:15 | 1.7631 | 0 | 0 | 1.5 | 0 | 85.9941
2017-09-13 | 14:20 | 1.7795 | 0 |  | 1.5
2017-09-13 | 14:25 | 1.767 | 0 |  | 1.5
2017-09-13 | 14:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 85.3401
2017-09-13 | 14:35 | 1.7538 | 0 |  | 1.5
2017-09-13 | 14:40 | 1.7858 | 0 |  | 1.5
2017-09-13 | 14:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 84.8542
2017-09-13 | 14:50 | 1.739 | 0 |  | 1.5
2017-09-13 | 14:55 | 1.7733 | 0 |  | 1.5
2017-09-13 | 15:00 | 1.7733 | 0 | 0 | 1.5 | 0 | 84.6569
2017-09-13 | 15:05 | 1.7343 | 0 |  | 1.5
2017-09-13 | 15:10 | 1.7475 | 0 |  | 1.5
2017-09-13 | 15:15 | 1.785 | 0 | 0 | 1.5 | 0 | 84.0549
2017-09-13 | 15:20 | 1.7678 | 0 |  | 1.5
2017-09-13 | 15:25 | 1.7702 | 0 |  | 1.5
2017-09-13 | 15:30 | 1.7842 | 0 | 0 | 1.5 | 0 | 83.6436
2017-09-13 | 15:35 | 1.7717 | 0 |  | 1.5
2017-09-13 | 15:40 | 1.7608 | 0 |  | 1.5
2017-09-13 | 15:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 83.2619
2017-09-13 | 15:50 | 1.7655 | 0 |  | 1.5
2017-09-13 | 15:55 | 1.7546 | 0 |  | 1.5
2017-09-13 | 16:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 82.9655
2017-09-13 | 16:05 | 1.7491 | 0 |  | 1.5
2017-09-13 | 16:10 | 1.7561 | 0 |  | 1.5
2017-09-13 | 16:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 82.6342
2017-09-13 | 16:20 | 1.739 | 0 |  | 1.5
2017-09-13 | 16:25 | 1.7452 | 0 |  | 1.5
2017-09-13 | 16:30 | 1.7811 | 0 | 0 | 1.5 | 0 | 82.1855
2017-09-13 | 16:35 | 1.7826 | 0 |  | 1.5
2017-09-13 | 16:40 | 1.7741 | 0 |  | 1.5
2017-09-13 | 16:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 81.6886
2017-09-13 | 16:50 | 1.7663 | 0 |  | 1.5
2017-09-13 | 16:55 | 1.7585 | 0 |  | 1.5
2017-09-13 | 17:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 81.64
2017-09-13 | 17:05 | 1.7561 | 0 |  | 1.5
2017-09-13 | 17:10 | 1.7561 | 0 |  | 1.5
2017-09-13 | 17:15 | 1.7889 | 0 | 0 | 1.5 | 0 | 81.1747
2017-09-13 | 17:20 | 1.7912 | 0 |  | 1.5
2017-09-13 | 17:25 | 1.7382 | 0 |  | 1.5
2017-09-13 | 17:30 | 1.7904 | 0 | 0 | 1.5 | 0 | 80.6471
2017-09-13 | 17:35 | 1.7709 | 0 |  | 1.5
2017-09-13 | 17:40 | 1.7585 | 0 |  | 1.5
2017-09-13 | 17:45 | 1.7787 | 0 | 0 | 1.5 | 0 | 80.1427
2017-09-13 | 17:50 | 1.7405 | 0 |  | 1.5
2017-09-13 | 17:55 | 1.7717 | 0 |  | 1.5
2017-09-13 | 18:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 79.9419
2017-09-13 | 18:05 | 1.7327 | 0 |  | 1.5
2017-09-13 | 18:10 | 1.7764 | 0 |  | 1.5
2017-09-13 | 18:15 | 1.7748 | 0 | 0 | 1.5 | 0 | 80.1426
2017-09-13 | 18:20 | 1.7546 | 0 |  | 1.5
2017-09-13 | 18:25 | 1.7436 | 0 |  | 1.5
2017-09-13 | 18:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 80.2058
2017-09-13 | 18:35 | 1.7507 | 0 |  | 1.5
2017-09-13 | 18:40 | 1.7444 | 0 |  | 1.5
2017-09-13 | 18:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 80.1479
2017-09-13 | 18:50 | 1.7592 | 0 |  | 1.5
2017-09-13 | 18:55 | 1.7639 | 0 |  | 1.5
2017-09-13 | 19:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 80.0616
2017-09-13 | 19:05 | 1.7522 | 0 |  | 1.5
2017-09-13 | 19:10 | 1.7429 | 0 |  | 1.5
2017-09-13 | 19:15 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.8708
2017-09-13 | 19:20 | 1.7647 | 0 |  | 1.5
2017-09-13 | 19:25 | 1.7624 | 0 |  | 1.5
2017-09-13 | 19:30 | 1.785 | 0 | 0 | 1.5 | 0 | 79.5115
2017-09-13 | 19:35 | 1.7585 | 0 |  | 1.5
2017-09-13 | 19:40 | 1.7553 | 0 |  | 1.5
2017-09-13 | 19:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 79.2615
2017-09-13 | 19:50 | 1.778 | 0 |  | 1.5
2017-09-13 | 19:55 | 1.7686 | 0 |  | 1.5
2017-09-13 | 20:00 | 1.7647 | 0 | 0 | 1.5 | 0 | 78.9243
2017-09-13 | 20:05 | 1.7608 | 0 |  | 1.5
2017-09-13 | 20:10 | 1.7686 | 0 |  | 1.5
2017-09-13 | 20:15 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.8485
2017-09-13 | 20:20 | 1.7858 | 0 |  | 1.5
2017-09-13 | 20:25 | 1.7592 | 0 |  | 1.5
2017-09-13 | 20:30 | 1.76 | 0 | 0 | 1.5 | 0 | 78.5828
2017-09-13 | 20:35 | 1.778 | 0 |  | 1.5
2017-09-13 | 20:40 | 1.7639 | 0 |  | 1.5
2017-09-13 | 20:45 | 1.7842 | 0 | 0 | 1.5 | 0 | 78.2475
2017-09-13 | 20:50 | 1.7468 | 0 |  | 1.5
2017-09-13 | 20:55 | 1.7569 | 0 |  | 1.5
2017-09-13 | 21:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 78.1038
2017-09-13 | 21:05 | -0.10106 | 0 |  | 1.5
2017-09-13 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-13 | 21:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 21:20 | -0.10262 | 0 |  | 1.5
2017-09-13 | 21:25 | -0.10262 | 0 |  | 1.5
2017-09-13 | 21:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 21:35 | -0.10262 | 0 |  | 1.5
2017-09-13 | 21:40 | -0.1034 | 0 |  | 1.5
2017-09-13 | 21:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 21:50 | -0.10418 | 0 |  | 1.5
2017-09-13 | 21:55 | -0.1034 | 0 |  | 1.5
2017-09-13 | 22:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 22:05 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:10 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 22:20 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:25 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 22:35 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:40 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 22:50 | -0.10418 | 0 |  | 1.5
2017-09-13 | 22:55 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 23:05 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:10 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 23:20 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:25 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 23:35 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:40 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-13 | 23:50 | -0.10418 | 0 |  | 1.5
2017-09-13 | 23:55 | -0.10418 | 0 |  | 1.5
2017-09-14 | 0:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 0:05 | -0.10418 | 0 |  | 1.5
2017-09-14 | 0:10 | -0.1034 | 0 |  | 1.5
2017-09-14 | 0:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 0:20 | -0.1034 | 0 |  | 1.5
2017-09-14 | 0:25 | -0.10418 | 0 |  | 1.5
2017-09-14 | 0:30 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 0:35 | -0.10418 | 0 |  | 1.5
2017-09-14 | 0:40 | -0.1034 | 0 |  | 1.5
2017-09-14 | 0:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 0:50 | -0.1034 | 0 |  | 1.5
2017-09-14 | 0:55 | -0.1034 | 0 |  | 1.5
2017-09-14 | 1:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 1:05 | -0.10262 | 0 |  | 1.5
2017-09-14 | 1:10 | -0.1034 | 0 |  | 1.5
2017-09-14 | 1:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 1:20 | -0.10652 | 0 |  | 1.5
2017-09-14 | 1:25 | -0.10652 | 0 |  | 1.5
2017-09-14 | 1:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 1:35 | -0.10652 | 0 |  | 1.5
2017-09-14 | 1:40 | -0.10652 | 0 |  | 1.5
2017-09-14 | 1:45 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 1:50 | -0.10652 | 0 |  | 1.5
2017-09-14 | 1:55 | -0.10652 | 0 |  | 1.5
2017-09-14 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 2:05 | -0.10652 | 0 |  | 1.5
2017-09-14 | 2:10 | -0.1073 | 0 |  | 1.5
2017-09-14 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 2:20 | -0.10652 | 0 |  | 1.5
2017-09-14 | 2:25 | -0.10652 | 0 |  | 1.5
2017-09-14 | 2:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 2:35 | -0.10652 | 0 |  | 1.5
2017-09-14 | 2:40 | -0.1073 | 0 |  | 1.5
2017-09-14 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 2:50 | -0.10652 | 0 |  | 1.5
2017-09-14 | 2:55 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 3:05 | -0.1073 | 0 |  | 1.5
2017-09-14 | 3:10 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 3:20 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:25 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 3:35 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:40 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 3:50 | -0.10652 | 0 |  | 1.5
2017-09-14 | 3:55 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 4:05 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:10 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 4:20 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:25 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 4:35 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:40 | -0.10652 | 0 |  | 1.5
2017-09-14 | 4:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 4:50 | -0.1073 | 0 |  | 1.5
2017-09-14 | 4:55 | -0.10652 | 0 |  | 1.5
2017-09-14 | 5:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 5:05 | 2.2304 | 0 |  | 1.5
2017-09-14 | 5:10 | 2.2428 | 0 |  | 1.5
2017-09-14 | 5:15 | 2.0845 | 0 | 0 | 1.5 | 0 | 89.3402
2017-09-14 | 5:20 | 1.9948 | 0 |  | 1.5
2017-09-14 | 5:25 | 1.9605 | 0 |  | 1.5
2017-09-14 | 5:30 | 1.8731 | 0 | 0 | 1.5 | 0 | 83.6737
2017-09-14 | 5:35 | 1.8294 | 0 |  | 1.5
2017-09-14 | 5:40 | 1.8396 | 0 |  | 1.5
2017-09-14 | 5:45 | 1.7967 | 0 | 0 | 1.5 | 0 | 81.4997
2017-09-14 | 5:50 | 1.792 | 0 |  | 1.5
2017-09-14 | 5:55 | 1.8006 | 0 |  | 1.5
2017-09-14 | 6:00 | 1.7959 | 0 | 0 | 1.5 | 0 | 80.1861
2017-09-14 | 6:05 | 1.7717 | 0 |  | 1.5
2017-09-14 | 6:10 | 1.7421 | 0 |  | 1.5
2017-09-14 | 6:15 | 1.7795 | 0 | 0 | 1.5 | 0 | 79.3924
2017-09-14 | 6:20 | 1.7702 | 0 |  | 1.5
2017-09-14 | 6:25 | 1.7522 | 0 |  | 1.5
2017-09-14 | 6:30 | 1.7686 | 0 | 0 | 1.5 | 0 | 78.803
2017-09-14 | 6:35 | 1.7686 | 0 |  | 1.5
2017-09-14 | 6:40 | 1.7702 | 0 |  | 1.5
2017-09-14 | 6:45 | 1.7561 | 0 | 0 | 1.5 | 0 | 78.137
2017-09-14 | 6:50 | 1.7702 | 0 |  | 1.5
2017-09-14 | 6:55 | 1.7756 | 0 |  | 1.5
2017-09-14 | 7:00 | 1.739 | 0 | 0 | 1.5 | 0 | 77.728
2017-09-14 | 7:05 | 1.7787 | 0 |  | 1.5
2017-09-14 | 7:10 | 1.7514 | 0 |  | 1.5
2017-09-14 | 7:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 77.6855
2017-09-14 | 7:20 | 1.6602 | 0 |  | 1.5
2017-09-14 | 7:25 | 1.6688 | 0 |  | 1.5
2017-09-14 | 7:30 | 1.6828 | 0 | 0 | 1.5 | 0 | 79.3188
2017-09-14 | 7:35 | 1.6563 | 0 |  | 1.5
2017-09-14 | 7:40 | 1.6929 | 0 |  | 1.5
2017-09-14 | 7:45 | 1.6968 | 0 | 0 | 1.5 | 0 | 81.0365
2017-09-14 | 7:50 | 1.7218 | 0 |  | 1.5
2017-09-14 | 7:55 | 1.7202 | 0 |  | 1.5
2017-09-14 | 8:00 | 1.7195 | 0 | 0 | 1.5 | 0 | 81.9116
2017-09-14 | 8:05 | 1.7241 | 0 |  | 1.5
2017-09-14 | 8:10 | 1.707 | 0 |  | 1.5
2017-09-14 | 8:15 | 1.7444 | 0 | 0 | 1.5 | 0 | 82.5144
2017-09-14 | 8:20 | 1.7608 | 0 |  | 1.5
2017-09-14 | 8:25 | 1.7663 | 0 |  | 1.5
2017-09-14 | 8:30 | 1.739 | 0 | 0 | 1.5 | 0 | 82.3626
2017-09-14 | 8:35 | 1.7405 | 0 |  | 1.5
2017-09-14 | 8:40 | 1.7951 | 0 |  | 1.5
2017-09-14 | 8:45 | 1.7733 | 0 | 0 | 1.5 | 0 | 81.7341
2017-09-14 | 8:50 | 1.7733 | 0 |  | 1.5
2017-09-14 | 8:55 | 1.7452 | 0 |  | 1.5
2017-09-14 | 9:00 | 1.7904 | 0 | 0 | 1.5 | 0 | 81.1856
2017-09-14 | 9:05 | 1.7499 | 0 |  | 1.5
2017-09-14 | 9:10 | 1.8053 | 0 |  | 1.5
2017-09-14 | 9:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 80.8415
2017-09-14 | 9:20 | 1.7273 | 0 |  | 1.5
2017-09-14 | 9:25 | 1.7507 | 0 |  | 1.5
2017-09-14 | 9:30 | 1.7257 | 0 | 0 | 1.5 | 0 | 80.9992
2017-09-14 | 9:35 | 1.7374 | 0 |  | 1.5
2017-09-14 | 9:40 | 1.7538 | 0 |  | 1.5
2017-09-14 | 9:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 80.9095
2017-09-14 | 9:50 | 1.7569 | 0 |  | 1.5
2017-09-14 | 9:55 | 1.76 | 0 |  | 1.5
2017-09-14 | 10:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 81.1949
2017-09-14 | 10:05 | 1.7156 | 0 |  | 1.5
2017-09-14 | 10:10 | 1.7257 | 0 |  | 1.5
2017-09-14 | 10:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 81.6238
2017-09-14 | 10:20 | 1.7288 | 0 |  | 1.5
2017-09-14 | 10:25 | 1.7304 | 0 |  | 1.5
2017-09-14 | 10:30 | 1.7288 | 0 | 0 | 1.5 | 0 | 82.2756
2017-09-14 | 10:35 | 1.7577 | 0 |  | 1.5
2017-09-14 | 10:40 | 1.7647 | 0 |  | 1.5
2017-09-14 | 10:45 | 1.7374 | 0 | 0 | 1.5 | 0 | 82.6274
2017-09-14 | 10:50 | 1.7343 | 0 |  | 1.5
2017-09-14 | 10:55 | 1.7748 | 0 |  | 1.5
2017-09-14 | 11:00 | 1.7787 | 0 | 0 | 1.5 | 0 | 82.0559
2017-09-14 | 11:05 | 1.7499 | 0 |  | 1.5
2017-09-14 | 11:10 | 1.7811 | 0 |  | 1.5
2017-09-14 | 11:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 81.7452
2017-09-14 | 11:20 | 1.7351 | 0 |  | 1.5
2017-09-14 | 11:25 | 1.7179 | 0 |  | 1.5
2017-09-14 | 11:30 | 1.7031 | 0 | 0 | 1.5 | 0 | 82.6359
2017-09-14 | 11:35 | 1.7062 | 0 |  | 1.5
2017-09-14 | 11:40 | 1.7148 | 0 |  | 1.5
2017-09-14 | 11:45 | 1.707 | 0 | 0 | 1.5 | 0 | 83.7456
2017-09-14 | 11:50 | 1.7265 | 0 |  | 1.5
2017-09-14 | 11:55 | 1.7546 | 0 |  | 1.5
2017-09-14 | 12:00 | 1.7163 | 0 | 0 | 1.5 | 0 | 84.3631
2017-09-14 | 12:05 | 1.7195 | 0 |  | 1.5
2017-09-14 | 12:10 | 1.7616 | 0 |  | 1.5
2017-09-14 | 12:15 | 1.7522 | 0 | 0 | 1.5 | 0 | 84.6023
2017-09-14 | 12:20 | 1.7444 | 0 |  | 1.5
2017-09-14 | 12:25 | 1.7468 | 0 |  | 1.5
2017-09-14 | 12:30 | 1.7046 | 0 | 0 | 1.5 | 0 | 84.8838
2017-09-14 | 12:35 | 1.7241 | 0 |  | 1.5
2017-09-14 | 12:40 | 1.7265 | 0 |  | 1.5
2017-09-14 | 12:45 | 1.7132 | 0 | 0 | 1.5 | 0 | 85.6225
2017-09-14 | 12:50 | 1.6976 | 0 |  | 1.5
2017-09-14 | 12:55 | 1.7078 | 0 |  | 1.5
2017-09-14 | 13:00 | 1.675 | 0 | 0 | 1.5 | 0 | 86.688
2017-09-14 | 13:05 | 1.7351 | 0 |  | 1.5
2017-09-14 | 13:10 | 1.7351 | 0 |  | 1.5
2017-09-14 | 13:15 | 1.6844 | 0 | 0 | 1.5 | 0 | 87.2828
2017-09-14 | 13:20 | 1.6875 | 0 |  | 1.5
2017-09-14 | 13:25 | 1.707 | 0 |  | 1.5
2017-09-14 | 13:30 | 1.7429 | 0 | 0 | 1.5 | 0 | 88.2624
2017-09-14 | 13:35 | 1.7343 | 0 |  | 1.5
2017-09-14 | 13:40 | 1.7881 | 0 |  | 1.5
2017-09-14 | 13:45 | 1.7608 | 0 | 0 | 1.5 | 0 | 87.6205
2017-09-14 | 13:50 | 1.7514 | 0 |  | 1.5
2017-09-14 | 13:55 | 1.7468 | 0 |  | 1.5
2017-09-14 | 14:00 | 1.7429 | 0 | 0 | 1.5 | 0 | 87.7483
2017-09-14 | 14:05 | 1.753 | 0 |  | 1.5
2017-09-14 | 14:10 | 1.7756 | 0 |  | 1.5
2017-09-14 | 14:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 87.5854
2017-09-14 | 14:20 | 1.7241 | 0 |  | 1.5
2017-09-14 | 14:25 | 1.707 | 0 |  | 1.5
2017-09-14 | 14:30 | 1.7265 | 0 | 0 | 1.5 | 0 | 88.1652
2017-09-14 | 14:35 | 1.7421 | 0 |  | 1.5
2017-09-14 | 14:40 | 1.7725 | 0 |  | 1.5
2017-09-14 | 14:45 | 1.7421 | 0 | 0 | 1.5 | 0 | 88.6337
2017-09-14 | 14:50 | 1.7101 | 0 |  | 1.5
2017-09-14 | 14:55 | 1.6961 | 0 |  | 1.5
2017-09-14 | 15:00 | 1.7366 | 0 | 0 | 1.5 | 0 | 89.3759
2017-09-14 | 15:05 | 1.7265 | 0 |  | 1.5
2017-09-14 | 15:10 | 1.7624 | 0 |  | 1.5
2017-09-14 | 15:15 | 1.7725 | 0 | 0 | 1.5 | 0 | 89.3011
2017-09-14 | 15:20 | 1.7975 | 0 |  | 1.5
2017-09-14 | 15:25 | 1.8099 | 0 |  | 1.5
2017-09-14 | 15:30 | 1.838 | 0 | 0 | 1.5 | 0 | 87.516
2017-09-14 | 15:35 | 1.8497 | 0 |  | 1.5
2017-09-14 | 15:40 | 1.8341 | 0 |  | 1.5
2017-09-14 | 15:45 | 1.8006 | 0 | 0 | 1.5 | 0 | 85.3298
2017-09-14 | 15:50 | 1.8232 | 0 |  | 1.5
2017-09-14 | 15:55 | 1.8006 | 0 |  | 1.5
2017-09-14 | 16:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 84.1771
2017-09-14 | 16:05 | 1.7943 | 0 |  | 1.5
2017-09-14 | 16:10 | 1.7858 | 0 |  | 1.5
2017-09-14 | 16:15 | 1.7943 | 0 | 0 | 1.5 | 0 | 83.515
2017-09-14 | 16:20 | 1.7897 | 0 |  | 1.5
2017-09-14 | 16:25 | 1.7351 | 0 |  | 1.5
2017-09-14 | 16:30 | 1.7023 | 0 | 0 | 1.5 | 0 | 83.5366
2017-09-14 | 16:35 | 1.7608 | 0 |  | 1.5
2017-09-14 | 16:40 | 1.7507 | 0 |  | 1.5
2017-09-14 | 16:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 83.4465
2017-09-14 | 16:50 | 1.7468 | 0 |  | 1.5
2017-09-14 | 16:55 | 1.7694 | 0 |  | 1.5
2017-09-14 | 17:00 | 1.7764 | 0 | 0 | 1.5 | 0 | 83.0002
2017-09-14 | 17:05 | 1.7787 | 0 |  | 1.5
2017-09-14 | 17:10 | 1.7943 | 0 |  | 1.5
2017-09-14 | 17:15 | 1.7655 | 0 | 0 | 1.5 | 0 | 82.2326
2017-09-14 | 17:20 | 1.7943 | 0 |  | 1.5
2017-09-14 | 17:25 | 1.7717 | 0 |  | 1.5
2017-09-14 | 17:30 | 1.7998 | 0 | 0 | 1.5 | 0 | 81.1159
2017-09-14 | 17:35 | 1.7702 | 0 |  | 1.5
2017-09-14 | 17:40 | 1.7803 | 0 |  | 1.5
2017-09-14 | 17:45 | 1.7842 | 0 | 0 | 1.5 | 0 | 80.0752
2017-09-14 | 17:50 | 1.7663 | 0 |  | 1.5
2017-09-14 | 17:55 | 1.7413 | 0 |  | 1.5
2017-09-14 | 18:00 | 1.767 | 0 | 0 | 1.5 | 0 | 79.7757
2017-09-14 | 18:05 | 1.7436 | 0 |  | 1.5
2017-09-14 | 18:10 | 1.7663 | 0 |  | 1.5
2017-09-14 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 79.7298
2017-09-14 | 18:20 | 1.785 | 0 |  | 1.5
2017-09-14 | 18:25 | 1.7912 | 0 |  | 1.5
2017-09-14 | 18:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 79.5433
2017-09-14 | 18:35 | 1.7655 | 0 |  | 1.5
2017-09-14 | 18:40 | 1.7304 | 0 |  | 1.5
2017-09-14 | 18:45 | 1.7577 | 0 | 0 | 1.5 | 0 | 79.3693
2017-09-14 | 18:50 | 1.7561 | 0 |  | 1.5
2017-09-14 | 18:55 | 1.7514 | 0 |  | 1.5
2017-09-14 | 19:00 | 1.7686 | 0 | 0 | 1.5 | 0 | 79.281
2017-09-14 | 19:05 | 1.7741 | 0 |  | 1.5
2017-09-14 | 19:10 | 1.7819 | 0 |  | 1.5
2017-09-14 | 19:15 | 1.7592 | 0 | 0 | 1.5 | 0 | 78.9028
2017-09-14 | 19:20 | 1.7569 | 0 |  | 1.5
2017-09-14 | 19:25 | 1.7585 | 0 |  | 1.5
2017-09-14 | 19:30 | 1.7436 | 0 | 0 | 1.5 | 0 | 78.6561
2017-09-14 | 19:35 | 1.7553 | 0 |  | 1.5
2017-09-14 | 19:40 | 1.7616 | 0 |  | 1.5
2017-09-14 | 19:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 78.4064
2017-09-14 | 19:50 | 1.7702 | 0 |  | 1.5
2017-09-14 | 19:55 | 1.7717 | 0 |  | 1.5
2017-09-14 | 20:00 | 1.7616 | 0 | 0 | 1.5 | 0 | 77.9369
2017-09-14 | 20:05 | 1.7748 | 0 |  | 1.5
2017-09-14 | 20:10 | 1.7873 | 0 |  | 1.5
2017-09-14 | 20:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 77.5373
2017-09-14 | 20:20 | 1.7382 | 0 |  | 1.5
2017-09-14 | 20:25 | 1.7413 | 0 |  | 1.5
2017-09-14 | 20:30 | 1.746 | 0 | 0 | 1.5 | 0 | 77.4493
2017-09-14 | 20:35 | 1.7475 | 0 |  | 1.5
2017-09-14 | 20:40 | 1.7366 | 0 |  | 1.5
2017-09-14 | 20:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 77.2242
2017-09-14 | 20:50 | 1.7686 | 0 |  | 1.5
2017-09-14 | 20:55 | 1.7741 | 0 |  | 1.5
2017-09-14 | 21:00 | 1.7561 | 0 | 0 | 1.5 | 0 | 76.8217
2017-09-14 | 21:05 | -0.10028 | 0 |  | 1.5
2017-09-14 | 21:10 | -0.10106 | 0 |  | 1.5
2017-09-14 | 21:15 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 21:20 | -0.10184 | 0 |  | 1.5
2017-09-14 | 21:25 | -0.10184 | 0 |  | 1.5
2017-09-14 | 21:30 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 21:35 | -0.10262 | 0 |  | 1.5
2017-09-14 | 21:40 | -0.10262 | 0 |  | 1.5
2017-09-14 | 21:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 21:50 | -0.10262 | 0 |  | 1.5
2017-09-14 | 21:55 | -0.10262 | 0 |  | 1.5
2017-09-14 | 22:00 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 22:05 | -0.10262 | 0 |  | 1.5
2017-09-14 | 22:10 | -0.1034 | 0 |  | 1.5
2017-09-14 | 22:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 22:20 | -0.10262 | 0 |  | 1.5
2017-09-14 | 22:25 | -0.1034 | 0 |  | 1.5
2017-09-14 | 22:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 22:35 | -0.10184 | 0 |  | 1.5
2017-09-14 | 22:40 | -0.1034 | 0 |  | 1.5
2017-09-14 | 22:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 22:50 | -0.10262 | 0 |  | 1.5
2017-09-14 | 22:55 | -0.1034 | 0 |  | 1.5
2017-09-14 | 23:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 23:05 | -0.10262 | 0 |  | 1.5
2017-09-14 | 23:10 | -0.10262 | 0 |  | 1.5
2017-09-14 | 23:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 23:20 | -0.1034 | 0 |  | 1.5
2017-09-14 | 23:25 | -0.10262 | 0 |  | 1.5
2017-09-14 | 23:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 23:35 | -0.10262 | 0 |  | 1.5
2017-09-14 | 23:40 | -0.10262 | 0 |  | 1.5
2017-09-14 | 23:45 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-14 | 23:50 | -0.10262 | 0 |  | 1.5
2017-09-14 | 23:55 | -0.10262 | 0 |  | 1.5
2017-09-15 | 0:00 | -0.1034 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 0:05 | -0.10262 | 0 |  | 1.5
2017-09-15 | 0:10 | -0.1034 | 0 |  | 1.5
2017-09-15 | 0:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 0:20 | -0.10262 | 0 |  | 1.5
2017-09-15 | 0:25 | -0.10262 | 0 |  | 1.5
2017-09-15 | 0:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 0:35 | -0.10262 | 0 |  | 1.5
2017-09-15 | 0:40 | -0.10262 | 0 |  | 1.5
2017-09-15 | 0:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 0:50 | -0.1034 | 0 |  | 1.5
2017-09-15 | 0:55 | -0.10262 | 0 |  | 1.5
2017-09-15 | 1:00 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 1:05 | -0.10262 | 0 |  | 1.5
2017-09-15 | 1:10 | -0.1034 | 0 |  | 1.5
2017-09-15 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 1:20 | -0.10574 | 0 |  | 1.5
2017-09-15 | 1:25 | -0.10574 | 0 |  | 1.5
2017-09-15 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 1:35 | -0.10574 | 0 |  | 1.5
2017-09-15 | 1:40 | -0.10574 | 0 |  | 1.5
2017-09-15 | 1:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 1:50 | -0.10574 | 0 |  | 1.5
2017-09-15 | 1:55 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 2:05 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:10 | -0.10652 | 0 |  | 1.5
2017-09-15 | 2:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 2:20 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:25 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 2:35 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:40 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 2:50 | -0.10574 | 0 |  | 1.5
2017-09-15 | 2:55 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 3:05 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:10 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 3:20 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:25 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 3:35 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:40 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 3:50 | -0.10574 | 0 |  | 1.5
2017-09-15 | 3:55 | -0.10574 | 0 |  | 1.5
2017-09-15 | 4:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 4:05 | -0.10574 | 0 |  | 1.5
2017-09-15 | 4:10 | -0.10574 | 0 |  | 1.5
2017-09-15 | 4:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 4:20 | -0.10652 | 0 |  | 1.5
2017-09-15 | 4:25 | -0.10574 | 0 |  | 1.5
2017-09-15 | 4:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 4:35 | -0.10652 | 0 |  | 1.5
2017-09-15 | 4:40 | -0.10652 | 0 |  | 1.5
2017-09-15 | 4:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 4:50 | -0.10574 | 0 |  | 1.5
2017-09-15 | 4:55 | -0.10574 | 0 |  | 1.5
2017-09-15 | 5:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 5:05 | 2.3091 | 0 |  | 1.5
2017-09-15 | 5:10 | 2.3302 | 0 |  | 1.5
2017-09-15 | 5:15 | 2.0673 | 0 | 0 | 1.5 | 0 | 87.5915
2017-09-15 | 5:20 | 1.9659 | 0 |  | 1.5
2017-09-15 | 5:25 | 1.8739 | 0 |  | 1.5
2017-09-15 | 5:30 | 1.8076 | 0 | 0 | 1.5 | 0 | 83.1693
2017-09-15 | 5:35 | 1.7897 | 0 |  | 1.5
2017-09-15 | 5:40 | 1.7811 | 0 |  | 1.5
2017-09-15 | 5:45 | 1.753 | 0 | 0 | 1.5 | 0 | 82.2459
2017-09-15 | 5:50 | 1.7397 | 0 |  | 1.5
2017-09-15 | 5:55 | 1.7546 | 0 |  | 1.5
2017-09-15 | 6:00 | 1.7865 | 0 | 0 | 1.5 | 0 | 82.056
2017-09-15 | 6:05 | 1.7351 | 0 |  | 1.5
2017-09-15 | 6:10 | 1.7195 | 0 |  | 1.5
2017-09-15 | 6:15 | 1.7624 | 0 | 0 | 1.5 | 0 | 82.2415
2017-09-15 | 6:20 | 1.7421 | 0 |  | 1.5
2017-09-15 | 6:25 | 1.7483 | 0 |  | 1.5
2017-09-15 | 6:30 | 1.753 | 0 | 0 | 1.5 | 0 | 82.5014
2017-09-15 | 6:35 | 1.7327 | 0 |  | 1.5
2017-09-15 | 6:40 | 1.7366 | 0 |  | 1.5
2017-09-15 | 6:45 | 1.739 | 0 | 0 | 1.5 | 0 | 82.7135
2017-09-15 | 6:50 | 1.7249 | 0 |  | 1.5
2017-09-15 | 6:55 | 1.753 | 0 |  | 1.5
2017-09-15 | 7:00 | 1.7265 | 0 | 0 | 1.5 | 0 | 83.0792
2017-09-15 | 7:05 | 1.7483 | 0 |  | 1.5
2017-09-15 | 7:10 | 1.7444 | 0 |  | 1.5
2017-09-15 | 7:15 | 1.7327 | 0 | 0 | 1.5 | 0 | 83.2415
2017-09-15 | 7:20 | 1.7444 | 0 |  | 1.5
2017-09-15 | 7:25 | 1.7319 | 0 |  | 1.5
2017-09-15 | 7:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 83.3484
2017-09-15 | 7:35 | 1.7421 | 0 |  | 1.5
2017-09-15 | 7:40 | 1.746 | 0 |  | 1.5
2017-09-15 | 7:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 83.6394
2017-09-15 | 7:50 | 1.7413 | 0 |  | 1.5
2017-09-15 | 7:55 | 1.7382 | 0 |  | 1.5
2017-09-15 | 8:00 | 1.7124 | 0 | 0 | 1.5 | 0 | 84.0061
2017-09-15 | 8:05 | 1.7163 | 0 |  | 1.5
2017-09-15 | 8:10 | 1.6695 | 0 |  | 1.5
2017-09-15 | 8:15 | 1.6711 | 0 | 0 | 1.5 | 0 | 85.5173
2017-09-15 | 8:20 | 1.6984 | 0 |  | 1.5
2017-09-15 | 8:25 | 1.6976 | 0 |  | 1.5
2017-09-15 | 8:30 | 1.7062 | 0 | 0 | 1.5 | 0 | 86.8463
2017-09-15 | 8:35 | 1.6992 | 0 |  | 1.5
2017-09-15 | 8:40 | 1.7124 | 0 |  | 1.5
2017-09-15 | 8:45 | 1.7093 | 0 | 0 | 1.5 | 0 | 87.9659
2017-09-15 | 8:50 | 1.7304 | 0 |  | 1.5
2017-09-15 | 8:55 | 1.707 | 0 |  | 1.5
2017-09-15 | 9:00 | 1.7015 | 0 | 0 | 1.5 | 0 | 89.0604
2017-09-15 | 9:05 | 1.7101 | 0 |  | 1.5
2017-09-15 | 9:10 | 1.7132 | 0 |  | 1.5
2017-09-15 | 9:15 | 1.721 | 0 | 0 | 1.5 | 0 | 89.7846
2017-09-15 | 9:20 | 1.7561 | 0 |  | 1.5
2017-09-15 | 9:25 | 1.7764 | 0 |  | 1.5
2017-09-15 | 9:30 | 1.8528 | 0 | 0 | 1.5 | 0 | 89.296
2017-09-15 | 9:35 | 1.8903 | 0 |  | 1.5
2017-09-15 | 9:40 | 1.9035 | 0 |  | 1.5
2017-09-15 | 9:45 | 1.884 | 0 | 0 | 1.5 | 0 | 85.1302
2017-09-15 | 9:50 | 1.8489 | 0 |  | 1.5
2017-09-15 | 9:55 | 1.8029 | 0 |  | 1.5
2017-09-15 | 10:00 | 1.7257 | 0 | 0 | 1.5 | 0 | 83.841
2017-09-15 | 10:05 | 1.7304 | 0 |  | 1.5
2017-09-15 | 10:10 | 1.7187 | 0 |  | 1.5
2017-09-15 | 10:15 | 1.7358 | 0 | 0 | 1.5 | 0 | 84.2357
2017-09-15 | 10:20 | 1.7491 | 0 |  | 1.5
2017-09-15 | 10:25 | 1.7491 | 0 |  | 1.5
2017-09-15 | 10:30 | 1.7265 | 0 | 0 | 1.5 | 0 | 84.1442
2017-09-15 | 10:35 | 1.76 | 0 |  | 1.5
2017-09-15 | 10:40 | 1.7663 | 0 |  | 1.5
2017-09-15 | 10:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 83.7347
2017-09-15 | 10:50 | 1.7436 | 0 |  | 1.5
2017-09-15 | 10:55 | 1.8248 | 0 |  | 1.5
2017-09-15 | 11:00 | 1.8154 | 0 | 0 | 1.5 | 0 | 82.5989
2017-09-15 | 11:05 | 1.7943 | 0 |  | 1.5
2017-09-15 | 11:10 | 1.767 | 0 |  | 1.5
2017-09-15 | 11:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 81.7085
2017-09-15 | 11:20 | 1.7413 | 0 |  | 1.5
2017-09-15 | 11:25 | 1.7631 | 0 |  | 1.5
2017-09-15 | 11:30 | 1.7616 | 0 | 0 | 1.5 | 0 | 81.6743
2017-09-15 | 11:35 | 1.7507 | 0 |  | 1.5
2017-09-15 | 11:40 | 1.7234 | 0 |  | 1.5
2017-09-15 | 11:45 | 1.8006 | 0 | 0 | 1.5 | 0 | 81.3313
2017-09-15 | 11:50 | 1.7514 | 0 |  | 1.5
2017-09-15 | 11:55 | 1.7148 | 0 |  | 1.5
2017-09-15 | 12:00 | 1.714 | 0 | 0 | 1.5 | 0 | 81.7247
2017-09-15 | 12:05 | 1.7475 | 0 |  | 1.5
2017-09-15 | 12:10 | 1.7335 | 0 |  | 1.5
2017-09-15 | 12:15 | 1.7335 | 0 | 0 | 1.5 | 0 | 82.5737
2017-09-15 | 12:20 | 1.7343 | 0 |  | 1.5
2017-09-15 | 12:25 | 1.7452 | 0 |  | 1.5
2017-09-15 | 12:30 | 1.739 | 0 | 0 | 1.5 | 0 | 83.0398
2017-09-15 | 12:35 | 1.7335 | 0 |  | 1.5
2017-09-15 | 12:40 | 1.714 | 0 |  | 1.5
2017-09-15 | 12:45 | 1.7522 | 0 | 0 | 1.5 | 0 | 83.6489
2017-09-15 | 12:50 | 1.721 | 0 |  | 1.5
2017-09-15 | 12:55 | 1.7093 | 0 |  | 1.5
2017-09-15 | 13:00 | 1.7163 | 0 | 0 | 1.5 | 0 | 84.4023
2017-09-15 | 13:05 | 1.7124 | 0 |  | 1.5
2017-09-15 | 13:10 | 1.7195 | 0 |  | 1.5
2017-09-15 | 13:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 85.3417
2017-09-15 | 13:20 | 1.7585 | 0 |  | 1.5
2017-09-15 | 13:25 | 1.7218 | 0 |  | 1.5
2017-09-15 | 13:30 | 1.6773 | 0 | 0 | 1.5 | 0 | 85.7347
2017-09-15 | 13:35 | 1.7023 | 0 |  | 1.5
2017-09-15 | 13:40 | 1.7421 | 0 |  | 1.5
2017-09-15 | 13:45 | 1.7585 | 0 | 0 | 1.5 | 0 | 86.6886
2017-09-15 | 13:50 | 1.7702 | 0 |  | 1.5
2017-09-15 | 13:55 | 1.7499 | 0 |  | 1.5
2017-09-15 | 14:00 | 1.7717 | 0 | 0 | 1.5 | 0 | 86.7785
2017-09-15 | 14:05 | 1.7491 | 0 |  | 1.5
2017-09-15 | 14:10 | 1.7468 | 0 |  | 1.5
2017-09-15 | 14:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 86.5784
2017-09-15 | 14:20 | 1.7491 | 0 |  | 1.5
2017-09-15 | 14:25 | 1.7795 | 0 |  | 1.5
2017-09-15 | 14:30 | 1.7842 | 0 | 0 | 1.5 | 0 | 86.0894
2017-09-15 | 14:35 | 1.7538 | 0 |  | 1.5
2017-09-15 | 14:40 | 1.7499 | 0 |  | 1.5
2017-09-15 | 14:45 | 1.7624 | 0 | 0 | 1.5 | 0 | 85.6609
2017-09-15 | 14:50 | 1.7694 | 0 |  | 1.5
2017-09-15 | 14:55 | 1.7865 | 0 |  | 1.5
2017-09-15 | 15:00 | 1.7655 | 0 | 0 | 1.5 | 0 | 84.9916
2017-09-15 | 15:05 | 1.7561 | 0 |  | 1.5
2017-09-15 | 15:10 | 1.753 | 0 |  | 1.5
2017-09-15 | 15:15 | 1.7756 | 0 | 0 | 1.5 | 0 | 84.4679
2017-09-15 | 15:20 | 1.7803 | 0 |  | 1.5
2017-09-15 | 15:25 | 1.7616 | 0 |  | 1.5
2017-09-15 | 15:30 | 1.8029 | 0 | 0 | 1.5 | 0 | 83.8717
2017-09-15 | 15:35 | 1.7725 | 0 |  | 1.5
2017-09-15 | 15:40 | 1.7569 | 0 |  | 1.5
2017-09-15 | 15:45 | 1.7124 | 0 | 0 | 1.5 | 0 | 83.4595
2017-09-15 | 15:50 | 1.7647 | 0 |  | 1.5
2017-09-15 | 15:55 | 1.7507 | 0 |  | 1.5
2017-09-15 | 16:00 | 1.7631 | 0 | 0 | 1.5 | 0 | 82.7399
2017-09-15 | 16:05 | 1.76 | 0 |  | 1.5
2017-09-15 | 16:10 | 1.7663 | 0 |  | 1.5
2017-09-15 | 16:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 82.5844
2017-09-15 | 16:20 | 1.7663 | 0 |  | 1.5
2017-09-15 | 16:25 | 1.7647 | 0 |  | 1.5
2017-09-15 | 16:30 | 1.7709 | 0 | 0 | 1.5 | 0 | 81.9396
2017-09-15 | 16:35 | 1.7998 | 0 |  | 1.5
2017-09-15 | 16:40 | 1.7694 | 0 |  | 1.5
2017-09-15 | 16:45 | 1.785 | 0 | 0 | 1.5 | 0 | 81.0379
2017-09-15 | 16:50 | 1.7374 | 0 |  | 1.5
2017-09-15 | 16:55 | 1.7998 | 0 |  | 1.5
2017-09-15 | 17:00 | 1.7756 | 0 | 0 | 1.5 | 0 | 80.367
2017-09-15 | 17:05 | 1.7717 | 0 |  | 1.5
2017-09-15 | 17:10 | 1.7592 | 0 |  | 1.5
2017-09-15 | 17:15 | 1.7741 | 0 | 0 | 1.5 | 0 | 80.5026
2017-09-15 | 17:20 | 1.7561 | 0 |  | 1.5
2017-09-15 | 17:25 | 1.753 | 0 |  | 1.5
2017-09-15 | 17:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 80.242
2017-09-15 | 17:35 | 1.7475 | 0 |  | 1.5
2017-09-15 | 17:40 | 1.7702 | 0 |  | 1.5
2017-09-15 | 17:45 | 1.7826 | 0 | 0 | 1.5 | 0 | 79.9007
2017-09-15 | 17:50 | 1.7686 | 0 |  | 1.5
2017-09-15 | 17:55 | 1.7475 | 0 |  | 1.5
2017-09-15 | 18:00 | 1.746 | 0 | 0 | 1.5 | 0 | 79.6455
2017-09-15 | 18:05 | 1.7709 | 0 |  | 1.5
2017-09-15 | 18:10 | 1.7546 | 0 |  | 1.5
2017-09-15 | 18:15 | 1.7663 | 0 | 0 | 1.5 | 0 | 79.4394
2017-09-15 | 18:20 | 1.7561 | 0 |  | 1.5
2017-09-15 | 18:25 | 1.7561 | 0 |  | 1.5
2017-09-15 | 18:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 79.3694
2017-09-15 | 18:35 | 1.7538 | 0 |  | 1.5
2017-09-15 | 18:40 | 1.778 | 0 |  | 1.5
2017-09-15 | 18:45 | 1.7397 | 0 | 0 | 1.5 | 0 | 79.3461
2017-09-15 | 18:50 | 1.7616 | 0 |  | 1.5
2017-09-15 | 18:55 | 1.7858 | 0 |  | 1.5
2017-09-15 | 19:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 79.2153
2017-09-15 | 19:05 | 1.7592 | 0 |  | 1.5
2017-09-15 | 19:10 | 1.7397 | 0 |  | 1.5
2017-09-15 | 19:15 | 1.7889 | 0 | 0 | 1.5 | 0 | 78.889
2017-09-15 | 19:20 | 1.7312 | 0 |  | 1.5
2017-09-15 | 19:25 | 1.7522 | 0 |  | 1.5
2017-09-15 | 19:30 | 1.7413 | 0 | 0 | 1.5 | 0 | 78.7774
2017-09-15 | 19:35 | 1.7585 | 0 |  | 1.5
2017-09-15 | 19:40 | 1.7522 | 0 |  | 1.5
2017-09-15 | 19:45 | 1.7616 | 0 | 0 | 1.5 | 0 | 78.5798
2017-09-15 | 19:50 | 1.7608 | 0 |  | 1.5
2017-09-15 | 19:55 | 1.7624 | 0 |  | 1.5
2017-09-15 | 20:00 | 1.7748 | 0 | 0 | 1.5 | 0 | 78.1869
2017-09-15 | 20:05 | 1.7826 | 0 |  | 1.5
2017-09-15 | 20:10 | 1.7585 | 0 |  | 1.5
2017-09-15 | 20:15 | 1.7514 | 0 | 0 | 1.5 | 0 | 77.8256
2017-09-15 | 20:20 | 1.7522 | 0 |  | 1.5
2017-09-15 | 20:25 | 1.7483 | 0 |  | 1.5
2017-09-15 | 20:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 77.6661
2017-09-15 | 20:35 | 1.7787 | 0 |  | 1.5
2017-09-15 | 20:40 | 1.7819 | 0 |  | 1.5
2017-09-15 | 20:45 | 1.7686 | 0 | 0 | 1.5 | 0 | 77.2096
2017-09-15 | 20:50 | 1.7436 | 0 |  | 1.5
2017-09-15 | 20:55 | 1.7678 | 0 |  | 1.5
2017-09-15 | 21:00 | 1.7538 | 0 | 0 | 1.5 | 0 | 76.8346
2017-09-15 | 21:05 | -0.0995 | 0 |  | 1.5
2017-09-15 | 21:10 | -0.10028 | 0 |  | 1.5
2017-09-15 | 21:15 | -0.0995 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 21:20 | -0.0995 | 0 |  | 1.5
2017-09-15 | 21:25 | -0.0995 | 0 |  | 1.5
2017-09-15 | 21:30 | -0.10028 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 21:35 | -0.10028 | 0 |  | 1.5
2017-09-15 | 21:40 | -0.10028 | 0 |  | 1.5
2017-09-15 | 21:45 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 21:50 | -0.10106 | 0 |  | 1.5
2017-09-15 | 21:55 | -0.10184 | 0 |  | 1.5
2017-09-15 | 22:00 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 22:05 | -0.10106 | 0 |  | 1.5
2017-09-15 | 22:10 | -0.10106 | 0 |  | 1.5
2017-09-15 | 22:15 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 22:20 | -0.10106 | 0 |  | 1.5
2017-09-15 | 22:25 | -0.10028 | 0 |  | 1.5
2017-09-15 | 22:30 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 22:35 | -0.10106 | 0 |  | 1.5
2017-09-15 | 22:40 | -0.10106 | 0 |  | 1.5
2017-09-15 | 22:45 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 22:50 | -0.10028 | 0 |  | 1.5
2017-09-15 | 22:55 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:00 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 23:05 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:10 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:15 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 23:20 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:25 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:30 | -0.10028 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 23:35 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:40 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:45 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-15 | 23:50 | -0.10106 | 0 |  | 1.5
2017-09-15 | 23:55 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:00 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 0:05 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:10 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:15 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 0:20 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:25 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:30 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 0:35 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:40 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:45 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 0:50 | -0.10106 | 0 |  | 1.5
2017-09-16 | 0:55 | -0.10106 | 0 |  | 1.5
2017-09-16 | 1:00 | -0.10028 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 1:05 | -0.10106 | 0 |  | 1.5
2017-09-16 | 1:10 | -0.10106 | 0 |  | 1.5
2017-09-16 | 1:15 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 1:20 | -0.10418 | 0 |  | 1.5
2017-09-16 | 1:25 | -0.10418 | 0 |  | 1.5
2017-09-16 | 1:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 1:35 | -0.10418 | 0 |  | 1.5
2017-09-16 | 1:40 | -0.10496 | 0 |  | 1.5
2017-09-16 | 1:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 1:50 | -0.10418 | 0 |  | 1.5
2017-09-16 | 1:55 | -0.10418 | 0 |  | 1.5
2017-09-16 | 2:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 2:05 | -0.11042 | 0 |  | 1.5
2017-09-16 | 2:10 | -0.10418 | 0 |  | 1.5
2017-09-16 | 2:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 2:20 | -0.10418 | 0 |  | 1.5
2017-09-16 | 2:25 | -0.10418 | 0 |  | 1.5
2017-09-16 | 2:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 2:35 | -0.10418 | 0 |  | 1.5
2017-09-16 | 2:40 | -0.10418 | 0 |  | 1.5
2017-09-16 | 2:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 2:50 | -0.10496 | 0 |  | 1.5
2017-09-16 | 2:55 | -0.10418 | 0 |  | 1.5
2017-09-16 | 3:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 3:05 | -0.10418 | 0 |  | 1.5
2017-09-16 | 3:10 | -0.10418 | 0 |  | 1.5
2017-09-16 | 3:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 3:20 | -0.10418 | 0 |  | 1.5
2017-09-16 | 3:25 | -0.10496 | 0 |  | 1.5
2017-09-16 | 3:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 3:35 | -0.10418 | 0 |  | 1.5
2017-09-16 | 3:40 | -0.10418 | 0 |  | 1.5
2017-09-16 | 3:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 3:50 | -0.10496 | 0 |  | 1.5
2017-09-16 | 3:55 | -0.10418 | 0 |  | 1.5
2017-09-16 | 4:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 4:05 | -0.10418 | 0 |  | 1.5
2017-09-16 | 4:10 | -0.10496 | 0 |  | 1.5
2017-09-16 | 4:15 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 4:20 | -0.10496 | 0 |  | 1.5
2017-09-16 | 4:25 | -0.10418 | 0 |  | 1.5
2017-09-16 | 4:30 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 4:35 | -0.10496 | 0 |  | 1.5
2017-09-16 | 4:40 | -0.10496 | 0 |  | 1.5
2017-09-16 | 4:45 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 4:50 | -0.10496 | 0 |  | 1.5
2017-09-16 | 4:55 | -0.10496 | 0 |  | 1.5
2017-09-16 | 5:00 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 5:05 | 2.3403 | 0 |  | 1.5
2017-09-16 | 5:10 | 2.313 | 0 |  | 1.5
2017-09-16 | 5:15 | 2.0806 | 0 | 0 | 1.5 | 0 | 87.7349
2017-09-16 | 5:20 | 1.9464 | 0 |  | 1.5
2017-09-16 | 5:25 | 1.856 | 0 |  | 1.5
2017-09-16 | 5:30 | 1.7982 | 0 | 0 | 1.5 | 0 | 84.0231
2017-09-16 | 5:35 | 1.7639 | 0 |  | 1.5
2017-09-16 | 5:40 | 1.7499 | 0 |  | 1.5
2017-09-16 | 5:45 | 1.7015 | 0 | 0 | 1.5 | 0 | 83.631
2017-09-16 | 5:50 | 1.7452 | 0 |  | 1.5
2017-09-16 | 5:55 | 1.7226 | 0 |  | 1.5
2017-09-16 | 6:00 | 1.7343 | 0 | 0 | 1.5 | 0 | 83.8242
2017-09-16 | 6:05 | 1.7273 | 0 |  | 1.5
2017-09-16 | 6:10 | 1.7257 | 0 |  | 1.5
2017-09-16 | 6:15 | 1.7312 | 0 | 0 | 1.5 | 0 | 84.0941
2017-09-16 | 6:20 | 1.7444 | 0 |  | 1.5
2017-09-16 | 6:25 | 1.7468 | 0 |  | 1.5
2017-09-16 | 6:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 84.2571
2017-09-16 | 6:35 | 1.7577 | 0 |  | 1.5
2017-09-16 | 6:40 | 1.7475 | 0 |  | 1.5
2017-09-16 | 6:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 84.4249
2017-09-16 | 6:50 | 1.7514 | 0 |  | 1.5
2017-09-16 | 6:55 | 1.7538 | 0 |  | 1.5
2017-09-16 | 7:00 | 1.753 | 0 | 0 | 1.5 | 0 | 84.5834
2017-09-16 | 7:05 | 1.7514 | 0 |  | 1.5
2017-09-16 | 7:10 | 1.7429 | 0 |  | 1.5
2017-09-16 | 7:15 | 1.7569 | 0 | 0 | 1.5 | 0 | 84.7478
2017-09-16 | 7:20 | 1.7366 | 0 |  | 1.5
2017-09-16 | 7:25 | 1.778 | 0 |  | 1.5
2017-09-16 | 7:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 85.011
2017-09-16 | 7:35 | 1.7265 | 0 |  | 1.5
2017-09-16 | 7:40 | 1.7296 | 0 |  | 1.5
2017-09-16 | 7:45 | 1.7327 | 0 | 0 | 1.5 | 0 | 85.2206
2017-09-16 | 7:50 | 1.7491 | 0 |  | 1.5
2017-09-16 | 7:55 | 1.7343 | 0 |  | 1.5
2017-09-16 | 8:00 | 1.7132 | 0 | 0 | 1.5 | 0 | 85.4896
2017-09-16 | 8:05 | 1.707 | 0 |  | 1.5
2017-09-16 | 8:10 | 1.753 | 0 |  | 1.5
2017-09-16 | 8:15 | 1.7756 | 0 | 0 | 1.5 | 0 | 85.5955
2017-09-16 | 8:20 | 1.8045 | 0 |  | 1.5
2017-09-16 | 8:25 | 1.9121 | 0 |  | 1.5
2017-09-16 | 8:30 | 1.8747 | 0 | 0 | 1.5 | 0 | 82.8802
2017-09-16 | 8:35 | 1.845 | 0 |  | 1.5
2017-09-16 | 8:40 | 1.792 | 0 |  | 1.5
2017-09-16 | 8:45 | 1.7834 | 0 | 0 | 1.5 | 0 | 80.8284
2017-09-16 | 8:50 | 1.7959 | 0 |  | 1.5
2017-09-16 | 8:55 | 1.7748 | 0 |  | 1.5
2017-09-16 | 9:00 | 1.8006 | 0 | 0 | 1.5 | 0 | 79.785
2017-09-16 | 9:05 | 1.8115 | 0 |  | 1.5
2017-09-16 | 9:10 | 1.7772 | 0 |  | 1.5
2017-09-16 | 9:15 | 1.746 | 0 | 0 | 1.5 | 0 | 79.0744
2017-09-16 | 9:20 | 1.7569 | 0 |  | 1.5
2017-09-16 | 9:25 | 1.7585 | 0 |  | 1.5
2017-09-16 | 9:30 | 1.7772 | 0 | 0 | 1.5 | 0 | 78.5018
2017-09-16 | 9:35 | 1.7343 | 0 |  | 1.5
2017-09-16 | 9:40 | 1.7343 | 0 |  | 1.5
2017-09-16 | 9:45 | 1.7725 | 0 | 0 | 1.5 | 0 | 78.1939
2017-09-16 | 9:50 | 1.7585 | 0 |  | 1.5
2017-09-16 | 9:55 | 1.7725 | 0 |  | 1.5
2017-09-16 | 10:00 | 1.7826 | 0 | 0 | 1.5 | 0 | 77.8101
2017-09-16 | 10:05 | 1.7842 | 0 |  | 1.5
2017-09-16 | 10:10 | 1.7889 | 0 |  | 1.5
2017-09-16 | 10:15 | 1.7702 | 0 | 0 | 1.5 | 0 | 77.4035
2017-09-16 | 10:20 | 1.7631 | 0 |  | 1.5
2017-09-16 | 10:25 | 1.7624 | 0 |  | 1.5
2017-09-16 | 10:30 | 1.7273 | 0 | 0 | 1.5 | 0 | 77.0479
2017-09-16 | 10:35 | 1.7491 | 0 |  | 1.5
2017-09-16 | 10:40 | 1.7709 | 0 |  | 1.5
2017-09-16 | 10:45 | 1.7741 | 0 | 0 | 1.5 | 0 | 76.8825
2017-09-16 | 10:50 | 1.7382 | 0 |  | 1.5
2017-09-16 | 10:55 | 1.7538 | 0 |  | 1.5
2017-09-16 | 11:00 | 1.7585 | 0 | 0 | 1.5 | 0 | 76.7792
2017-09-16 | 11:05 | 1.7273 | 0 |  | 1.5
2017-09-16 | 11:10 | 1.739 | 0 |  | 1.5
2017-09-16 | 11:15 | 1.7257 | 0 | 0 | 1.5 | 0 | 76.9126
2017-09-16 | 11:20 | 1.7592 | 0 |  | 1.5
2017-09-16 | 11:25 | 1.7624 | 0 |  | 1.5
2017-09-16 | 11:30 | 1.746 | 0 | 0 | 1.5 | 0 | 76.9138
2017-09-16 | 11:35 | 1.7608 | 0 |  | 1.5
2017-09-16 | 11:40 | 1.7803 | 0 |  | 1.5
2017-09-16 | 11:45 | 1.767 | 0 | 0 | 1.5 | 0 | 76.9103
2017-09-16 | 11:50 | 1.7561 | 0 |  | 1.5
2017-09-16 | 11:55 | 1.7475 | 0 |  | 1.5
2017-09-16 | 12:00 | 1.7569 | 0 | 0 | 1.5 | 0 | 76.9359
2017-09-16 | 12:05 | 1.7507 | 0 |  | 1.5
2017-09-16 | 12:10 | 1.7577 | 0 |  | 1.5
2017-09-16 | 12:15 | 1.7639 | 0 | 0 | 1.5 | 0 | 76.9954
2017-09-16 | 12:20 | 1.7561 | 0 |  | 1.5
2017-09-16 | 12:25 | 1.7382 | 0 |  | 1.5
2017-09-16 | 12:30 | 1.7663 | 0 | 0 | 1.5 | 0 | 77.2393
2017-09-16 | 12:35 | 1.7241 | 0 |  | 1.5
2017-09-16 | 12:40 | 1.76 | 0 |  | 1.5
2017-09-16 | 12:45 | 1.753 | 0 | 0 | 1.5 | 0 | 77.337
2017-09-16 | 12:50 | 1.7413 | 0 |  | 1.5
2017-09-16 | 12:55 | 1.7117 | 0 |  | 1.5
2017-09-16 | 13:00 | 1.7234 | 0 | 0 | 1.5 | 0 | 77.7597
2017-09-16 | 13:05 | 1.7218 | 0 |  | 1.5
2017-09-16 | 13:10 | 1.7717 | 0 |  | 1.5
2017-09-16 | 13:15 | 1.7507 | 0 | 0 | 1.5 | 0 | 77.9334
2017-09-16 | 13:20 | 1.7514 | 0 |  | 1.5
2017-09-16 | 13:25 | 1.7475 | 0 |  | 1.5
2017-09-16 | 13:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 78.051
2017-09-16 | 13:35 | 1.7452 | 0 |  | 1.5
2017-09-16 | 13:40 | 1.7468 | 0 |  | 1.5
2017-09-16 | 13:45 | 1.7436 | 0 | 0 | 1.5 | 0 | 78.4152
2017-09-16 | 13:50 | 1.7257 | 0 |  | 1.5
2017-09-16 | 13:55 | 1.7429 | 0 |  | 1.5
2017-09-16 | 14:00 | 1.7382 | 0 | 0 | 1.5 | 0 | 78.6612
2017-09-16 | 14:05 | 1.7148 | 0 |  | 1.5
2017-09-16 | 14:10 | 1.7405 | 0 |  | 1.5
2017-09-16 | 14:15 | 1.7397 | 0 | 0 | 1.5 | 0 | 78.9484
2017-09-16 | 14:20 | 1.7569 | 0 |  | 1.5
2017-09-16 | 14:25 | 1.7616 | 0 |  | 1.5
2017-09-16 | 14:30 | 1.7514 | 0 | 0 | 1.5 | 0 | 78.8293
2017-09-16 | 14:35 | 1.7624 | 0 |  | 1.5
2017-09-16 | 14:40 | 1.7421 | 0 |  | 1.5
2017-09-16 | 14:45 | 1.7413 | 0 | 0 | 1.5 | 0 | 78.914
2017-09-16 | 14:50 | 1.746 | 0 |  | 1.5
2017-09-16 | 14:55 | 1.7397 | 0 |  | 1.5
2017-09-16 | 15:00 | 1.7179 | 0 | 0 | 1.5 | 0 | 79.0923
2017-09-16 | 15:05 | 1.7608 | 0 |  | 1.5
2017-09-16 | 15:10 | 1.739 | 0 |  | 1.5
2017-09-16 | 15:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 78.9756
2017-09-16 | 15:20 | 1.792 | 0 |  | 1.5
2017-09-16 | 15:25 | 1.7585 | 0 |  | 1.5
2017-09-16 | 15:30 | 1.7351 | 0 | 0 | 1.5 | 0 | 78.8963
2017-09-16 | 15:35 | 1.7452 | 0 |  | 1.5
2017-09-16 | 15:40 | 1.7358 | 0 |  | 1.5
2017-09-16 | 15:45 | 1.7663 | 0 | 0 | 1.5 | 0 | 78.9553
2017-09-16 | 15:50 | 1.76 | 0 |  | 1.5
2017-09-16 | 15:55 | 1.7468 | 0 |  | 1.5
2017-09-16 | 16:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 78.7824
2017-09-16 | 16:05 | 1.7475 | 0 |  | 1.5
2017-09-16 | 16:10 | 1.746 | 0 |  | 1.5
2017-09-16 | 16:15 | 1.7335 | 0 | 0 | 1.5 | 0 | 78.8399
2017-09-16 | 16:20 | 1.7592 | 0 |  | 1.5
2017-09-16 | 16:25 | 1.7717 | 0 |  | 1.5
2017-09-16 | 16:30 | 1.7733 | 0 | 0 | 1.5 | 0 | 78.6036
2017-09-16 | 16:35 | 1.7483 | 0 |  | 1.5
2017-09-16 | 16:40 | 1.7616 | 0 |  | 1.5
2017-09-16 | 16:45 | 1.7491 | 0 | 0 | 1.5 | 0 | 78.6643
2017-09-16 | 16:50 | 1.7421 | 0 |  | 1.5
2017-09-16 | 16:55 | 1.753 | 0 |  | 1.5
2017-09-16 | 17:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 78.5775
2017-09-16 | 17:05 | 1.7569 | 0 |  | 1.5
2017-09-16 | 17:10 | 1.7421 | 0 |  | 1.5
2017-09-16 | 17:15 | 1.7616 | 0 | 0 | 1.5 | 0 | 78.4835
2017-09-16 | 17:20 | 1.7733 | 0 |  | 1.5
2017-09-16 | 17:25 | 1.7873 | 0 |  | 1.5
2017-09-16 | 17:30 | 1.7795 | 0 | 0 | 1.5 | 0 | 77.7585
2017-09-16 | 17:35 | 1.7647 | 0 |  | 1.5
2017-09-16 | 17:40 | 1.7561 | 0 |  | 1.5
2017-09-16 | 17:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 77.4436
2017-09-16 | 17:50 | 1.7678 | 0 |  | 1.5
2017-09-16 | 17:55 | 1.7429 | 0 |  | 1.5
2017-09-16 | 18:00 | 1.7592 | 0 | 0 | 1.5 | 0 | 77.2226
2017-09-16 | 18:05 | 1.7663 | 0 |  | 1.5
2017-09-16 | 18:10 | 1.7678 | 0 |  | 1.5
2017-09-16 | 18:15 | 1.7608 | 0 | 0 | 1.5 | 0 | 76.923
2017-09-16 | 18:20 | 1.7585 | 0 |  | 1.5
2017-09-16 | 18:25 | 1.7351 | 0 |  | 1.5
2017-09-16 | 18:30 | 1.7078 | 0 | 0 | 1.5 | 0 | 76.9478
2017-09-16 | 18:35 | 1.7468 | 0 |  | 1.5
2017-09-16 | 18:40 | 1.7663 | 0 |  | 1.5
2017-09-16 | 18:45 | 1.7694 | 0 | 0 | 1.5 | 0 | 76.8253
2017-09-16 | 18:50 | 1.7468 | 0 |  | 1.5
2017-09-16 | 18:55 | 1.767 | 0 |  | 1.5
2017-09-16 | 19:00 | 1.7577 | 0 | 0 | 1.5 | 0 | 76.5425
2017-09-16 | 19:05 | 1.7499 | 0 |  | 1.5
2017-09-16 | 19:10 | 1.7468 | 0 |  | 1.5
2017-09-16 | 19:15 | 1.7702 | 0 | 0 | 1.5 | 0 | 76.5592
2017-09-16 | 19:20 | 1.7592 | 0 |  | 1.5
2017-09-16 | 19:25 | 1.7452 | 0 |  | 1.5
2017-09-16 | 19:30 | 1.7764 | 0 | 0 | 1.5 | 0 | 76.4813
2017-09-16 | 19:35 | 1.7429 | 0 |  | 1.5
2017-09-16 | 19:40 | 1.7304 | 0 |  | 1.5
2017-09-16 | 19:45 | 1.7631 | 0 | 0 | 1.5 | 0 | 76.2437
2017-09-16 | 19:50 | 1.7452 | 0 |  | 1.5
2017-09-16 | 19:55 | 1.7569 | 0 |  | 1.5
2017-09-16 | 20:00 | 1.7546 | 0 | 0 | 1.5 | 0 | 76.0981
2017-09-16 | 20:05 | 1.7811 | 0 |  | 1.5
2017-09-16 | 20:10 | 1.7585 | 0 |  | 1.5
2017-09-16 | 20:15 | 1.7382 | 0 | 0 | 1.5 | 0 | 76.0295
2017-09-16 | 20:20 | 1.7678 | 0 |  | 1.5
2017-09-16 | 20:25 | 1.7561 | 0 |  | 1.5
2017-09-16 | 20:30 | 1.7577 | 0 | 0 | 1.5 | 0 | 76.1579
2017-09-16 | 20:35 | 1.7663 | 0 |  | 1.5
2017-09-16 | 20:40 | 1.7561 | 0 |  | 1.5
2017-09-16 | 20:45 | 1.7475 | 0 | 0 | 1.5 | 0 | 75.9672
2017-09-16 | 20:50 | 1.7592 | 0 |  | 1.5
2017-09-16 | 20:55 | 1.7312 | 0 |  | 1.5
2017-09-16 | 21:00 | 1.7249 | 0 | 0 | 1.5 | 0 | 76.0647
2017-09-16 | 21:05 | -0.10106 | 0 |  | 1.5
2017-09-16 | 21:10 | -0.10106 | 0 |  | 1.5
2017-09-16 | 21:15 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 21:20 | -0.10262 | 0 |  | 1.5
2017-09-16 | 21:25 | -0.10262 | 0 |  | 1.5
2017-09-16 | 21:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 21:35 | -0.10262 | 0 |  | 1.5
2017-09-16 | 21:40 | -0.10262 | 0 |  | 1.5
2017-09-16 | 21:45 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 21:50 | -0.10184 | 0 |  | 1.5
2017-09-16 | 21:55 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:00 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 22:05 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:10 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:15 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 22:20 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:25 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:30 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 22:35 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:40 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:45 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 22:50 | -0.10184 | 0 |  | 1.5
2017-09-16 | 22:55 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:00 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 23:05 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:10 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:15 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 23:20 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:25 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:30 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 23:35 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:40 | -0.10262 | 0 |  | 1.5
2017-09-16 | 23:45 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-16 | 23:50 | -0.10184 | 0 |  | 1.5
2017-09-16 | 23:55 | -0.10184 | 0 |  | 1.5
2017-09-17 | 0:00 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 0:05 | -0.10184 | 0 |  | 1.5
2017-09-17 | 0:10 | -0.10184 | 0 |  | 1.5
2017-09-17 | 0:15 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 0:20 | -0.10184 | 0 |  | 1.5
2017-09-17 | 0:25 | -0.10184 | 0 |  | 1.5
2017-09-17 | 0:30 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 0:35 | -0.10184 | 0 |  | 1.5
2017-09-17 | 0:40 | -0.10262 | 0 |  | 1.5
2017-09-17 | 0:45 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 0:50 | -0.10262 | 0 |  | 1.5
2017-09-17 | 0:55 | -0.10262 | 0 |  | 1.5
2017-09-17 | 1:00 | -0.10184 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 1:05 | -0.10262 | 0 |  | 1.5
2017-09-17 | 1:10 | -0.10262 | 0 |  | 1.5
2017-09-17 | 1:15 | -0.10262 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 1:20 | -0.10652 | 0 |  | 1.5
2017-09-17 | 1:25 | -0.10574 | 0 |  | 1.5
2017-09-17 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 1:35 | -0.10652 | 0 |  | 1.5
2017-09-17 | 1:40 | -0.10652 | 0 |  | 1.5
2017-09-17 | 1:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 1:50 | -0.10652 | 0 |  | 1.5
2017-09-17 | 1:55 | -0.10574 | 0 |  | 1.5
2017-09-17 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 2:05 | -0.10652 | 0 |  | 1.5
2017-09-17 | 2:10 | -0.10574 | 0 |  | 1.5
2017-09-17 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 2:20 | -0.10652 | 0 |  | 1.5
2017-09-17 | 2:25 | -0.10574 | 0 |  | 1.5
2017-09-17 | 2:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 2:35 | -0.10652 | 0 |  | 1.5
2017-09-17 | 2:40 | -0.10652 | 0 |  | 1.5
2017-09-17 | 2:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 2:50 | -0.10652 | 0 |  | 1.5
2017-09-17 | 2:55 | -0.10574 | 0 |  | 1.5
2017-09-17 | 3:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 3:05 | -0.10574 | 0 |  | 1.5
2017-09-17 | 3:10 | -0.10574 | 0 |  | 1.5
2017-09-17 | 3:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 3:20 | -0.10652 | 0 |  | 1.5
2017-09-17 | 3:25 | -0.10652 | 0 |  | 1.5
2017-09-17 | 3:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 3:35 | -0.10652 | 0 |  | 1.5
2017-09-17 | 3:40 | -0.10652 | 0 |  | 1.5
2017-09-17 | 3:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 3:50 | -0.10574 | 0 |  | 1.5
2017-09-17 | 3:55 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 4:05 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:10 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 4:20 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:25 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 4:35 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:40 | -0.11354 | 0 |  | 1.5
2017-09-17 | 4:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 4:50 | -0.10652 | 0 |  | 1.5
2017-09-17 | 4:55 | -0.10652 | 0 |  | 1.5
2017-09-17 | 5:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 5:05 | 2.3645 | 0 |  | 1.5
2017-09-17 | 5:10 | 2.3013 | 0 |  | 1.5
2017-09-17 | 5:15 | 2.1134 | 0 | 0 | 1.5 | 0 | 87.563
2017-09-17 | 5:20 | 2.012 | 0 |  | 1.5
2017-09-17 | 5:25 | 1.9246 | 0 |  | 1.5
2017-09-17 | 5:30 | 1.8739 | 0 | 0 | 1.5 | 0 | 82.0338
2017-09-17 | 5:35 | 1.856 | 0 |  | 1.5
2017-09-17 | 5:40 | 1.8411 | 0 |  | 1.5
2017-09-17 | 5:45 | 1.8302 | 0 | 0 | 1.5 | 0 | 79.8772
2017-09-17 | 5:50 | 1.8053 | 0 |  | 1.5
2017-09-17 | 5:55 | 1.8076 | 0 |  | 1.5
2017-09-17 | 6:00 | 1.7756 | 0 | 0 | 1.5 | 0 | 78.363
2017-09-17 | 6:05 | 1.7678 | 0 |  | 1.5
2017-09-17 | 6:10 | 1.7842 | 0 |  | 1.5
2017-09-17 | 6:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 77.73
2017-09-17 | 6:20 | 1.7514 | 0 |  | 1.5
2017-09-17 | 6:25 | 1.7912 | 0 |  | 1.5
2017-09-17 | 6:30 | 1.7748 | 0 | 0 | 1.5 | 0 | 77.2599
2017-09-17 | 6:35 | 1.7702 | 0 |  | 1.5
2017-09-17 | 6:40 | 1.7702 | 0 |  | 1.5
2017-09-17 | 6:45 | 1.7569 | 0 | 0 | 1.5 | 0 | 76.7375
2017-09-17 | 6:50 | 1.7608 | 0 |  | 1.5
2017-09-17 | 6:55 | 1.7374 | 0 |  | 1.5
2017-09-17 | 7:00 | 1.7257 | 0 | 0 | 1.5 | 0 | 76.6605
2017-09-17 | 7:05 | 1.7273 | 0 |  | 1.5
2017-09-17 | 7:10 | 1.7444 | 0 |  | 1.5
2017-09-17 | 7:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 76.9781
2017-09-17 | 7:20 | 1.7421 | 0 |  | 1.5
2017-09-17 | 7:25 | 1.7436 | 0 |  | 1.5
2017-09-17 | 7:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 77.1748
2017-09-17 | 7:35 | 1.7405 | 0 |  | 1.5
2017-09-17 | 7:40 | 1.7421 | 0 |  | 1.5
2017-09-17 | 7:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 77.1424
2017-09-17 | 7:50 | 1.7717 | 0 |  | 1.5
2017-09-17 | 7:55 | 1.7468 | 0 |  | 1.5
2017-09-17 | 8:00 | 1.7358 | 0 | 0 | 1.5 | 0 | 77.206
2017-09-17 | 8:05 | 1.7616 | 0 |  | 1.5
2017-09-17 | 8:10 | 1.7553 | 0 |  | 1.5
2017-09-17 | 8:15 | 1.7499 | 0 | 0 | 1.5 | 0 | 77.21
2017-09-17 | 8:20 | 1.7483 | 0 |  | 1.5
2017-09-17 | 8:25 | 1.7382 | 0 |  | 1.5
2017-09-17 | 8:30 | 1.7553 | 0 | 0 | 1.5 | 0 | 77.2779
2017-09-17 | 8:35 | 1.7585 | 0 |  | 1.5
2017-09-17 | 8:40 | 1.739 | 0 |  | 1.5
2017-09-17 | 8:45 | 1.7085 | 0 | 0 | 1.5 | 0 | 77.4436
2017-09-17 | 8:50 | 1.7507 | 0 |  | 1.5
2017-09-17 | 8:55 | 1.7421 | 0 |  | 1.5
2017-09-17 | 9:00 | 1.7382 | 0 | 0 | 1.5 | 0 | 77.8936
2017-09-17 | 9:05 | 1.7499 | 0 |  | 1.5
2017-09-17 | 9:10 | 1.7483 | 0 |  | 1.5
2017-09-17 | 9:15 | 1.7647 | 0 | 0 | 1.5 | 0 | 78.0471
2017-09-17 | 9:20 | 1.7429 | 0 |  | 1.5
2017-09-17 | 9:25 | 1.7631 | 0 |  | 1.5
2017-09-17 | 9:30 | 1.7312 | 0 | 0 | 1.5 | 0 | 78.0997
2017-09-17 | 9:35 | 1.7257 | 0 |  | 1.5
2017-09-17 | 9:40 | 1.753 | 0 |  | 1.5
2017-09-17 | 9:45 | 1.7405 | 0 | 0 | 1.5 | 0 | 78.2623
2017-09-17 | 9:50 | 1.7663 | 0 |  | 1.5
2017-09-17 | 9:55 | 1.746 | 0 |  | 1.5
2017-09-17 | 10:00 | 1.7483 | 0 | 0 | 1.5 | 0 | 78.2808
2017-09-17 | 10:05 | 1.7304 | 0 |  | 1.5
2017-09-17 | 10:10 | 1.7834 | 0 |  | 1.5
2017-09-17 | 10:15 | 1.753 | 0 | 0 | 1.5 | 0 | 78.3837
2017-09-17 | 10:20 | 1.7624 | 0 |  | 1.5
2017-09-17 | 10:25 | 1.721 | 0 |  | 1.5
2017-09-17 | 10:30 | 1.7444 | 0 | 0 | 1.5 | 0 | 78.4632
2017-09-17 | 10:35 | 1.7179 | 0 |  | 1.5
2017-09-17 | 10:40 | 1.7132 | 0 |  | 1.5
2017-09-17 | 10:45 | 1.7444 | 0 | 0 | 1.5 | 0 | 78.6675
2017-09-17 | 10:50 | 1.7374 | 0 |  | 1.5
2017-09-17 | 10:55 | 1.7491 | 0 |  | 1.5
2017-09-17 | 11:00 | 1.7358 | 0 | 0 | 1.5 | 0 | 78.8348
2017-09-17 | 11:05 | 1.76 | 0 |  | 1.5
2017-09-17 | 11:10 | 1.7624 | 0 |  | 1.5
2017-09-17 | 11:15 | 1.7538 | 0 | 0 | 1.5 | 0 | 78.9682
2017-09-17 | 11:20 | 1.7499 | 0 |  | 1.5
2017-09-17 | 11:25 | 1.7546 | 0 |  | 1.5
2017-09-17 | 11:30 | 1.767 | 0 | 0 | 1.5 | 0 | 78.7111
2017-09-17 | 11:35 | 1.76 | 0 |  | 1.5
2017-09-17 | 11:40 | 1.7717 | 0 |  | 1.5
2017-09-17 | 11:45 | 1.7592 | 0 | 0 | 1.5 | 0 | 78.4089
2017-09-17 | 11:50 | 1.7655 | 0 |  | 1.5
2017-09-17 | 11:55 | 1.7655 | 0 |  | 1.5
2017-09-17 | 12:00 | 1.7678 | 0 | 0 | 1.5 | 0 | 78.0337
2017-09-17 | 12:05 | 1.7663 | 0 |  | 1.5
2017-09-17 | 12:10 | 1.7772 | 0 |  | 1.5
2017-09-17 | 12:15 | 1.7468 | 0 | 0 | 1.5 | 0 | 77.856
2017-09-17 | 12:20 | 1.7413 | 0 |  | 1.5
2017-09-17 | 12:25 | 1.7491 | 0 |  | 1.5
2017-09-17 | 12:30 | 1.7631 | 0 | 0 | 1.5 | 0 | 77.7571
2017-09-17 | 12:35 | 1.7522 | 0 |  | 1.5
2017-09-17 | 12:40 | 1.7741 | 0 |  | 1.5
2017-09-17 | 12:45 | 1.7546 | 0 | 0 | 1.5 | 0 | 77.5562
2017-09-17 | 12:50 | 1.7585 | 0 |  | 1.5
2017-09-17 | 12:55 | 1.767 | 0 |  | 1.5
2017-09-17 | 13:00 | 1.7397 | 0 | 0 | 1.5 | 0 | 77.5423
2017-09-17 | 13:05 | 1.7413 | 0 |  | 1.5
2017-09-17 | 13:10 | 1.7413 | 0 |  | 1.5
2017-09-17 | 13:15 | 1.7249 | 0 | 0 | 1.5 | 0 | 77.4411
2017-09-17 | 13:20 | 1.7499 | 0 |  | 1.5
2017-09-17 | 13:25 | 1.7522 | 0 |  | 1.5
2017-09-17 | 13:30 | 1.7717 | 0 | 0 | 1.5 | 0 | 77.3731
2017-09-17 | 13:35 | 1.7452 | 0 |  | 1.5
2017-09-17 | 13:40 | 1.7483 | 0 |  | 1.5
2017-09-17 | 13:45 | 1.7514 | 0 | 0 | 1.5 | 0 | 77.2848
2017-09-17 | 13:50 | 1.7631 | 0 |  | 1.5
2017-09-17 | 13:55 | 1.7468 | 0 |  | 1.5
2017-09-17 | 14:00 | 1.7296 | 0 | 0 | 1.5 | 0 | 77.1198
2017-09-17 | 14:05 | 1.7678 | 0 |  | 1.5
2017-09-17 | 14:10 | 1.7569 | 0 |  | 1.5
2017-09-17 | 14:15 | 1.7335 | 0 | 0 | 1.5 | 0 | 77.1522
2017-09-17 | 14:20 | 1.7304 | 0 |  | 1.5
2017-09-17 | 14:25 | 1.7382 | 0 |  | 1.5
2017-09-17 | 14:30 | 1.7475 | 0 | 0 | 1.5 | 0 | 77.1909
2017-09-17 | 14:35 | 1.7678 | 0 |  | 1.5
2017-09-17 | 14:40 | 1.7475 | 0 |  | 1.5
2017-09-17 | 14:45 | 1.7335 | 0 | 0 | 1.5 | 0 | 77.0403
2017-09-17 | 14:50 | 1.7639 | 0 |  | 1.5
2017-09-17 | 14:55 | 1.7499 | 0 |  | 1.5
2017-09-17 | 15:00 | 1.7663 | 0 | 0 | 1.5 | 0 | 76.9567
2017-09-17 | 15:05 | 1.7483 | 0 |  | 1.5
2017-09-17 | 15:10 | 1.7663 | 0 |  | 1.5
2017-09-17 | 15:15 | 1.76 | 0 | 0 | 1.5 | 0 | 76.7702
2017-09-17 | 15:20 | 1.753 | 0 |  | 1.5
2017-09-17 | 15:25 | 1.7436 | 0 |  | 1.5
2017-09-17 | 15:30 | 1.7819 | 0 | 0 | 1.5 | 0 | 76.6558
2017-09-17 | 15:35 | 1.7546 | 0 |  | 1.5
2017-09-17 | 15:40 | 1.7499 | 0 |  | 1.5
2017-09-17 | 15:45 | 1.7639 | 0 | 0 | 1.5 | 0 | 76.6709
2017-09-17 | 15:50 | 1.7374 | 0 |  | 1.5
2017-09-17 | 15:55 | 1.7413 | 0 |  | 1.5
2017-09-17 | 16:00 | 1.7561 | 0 | 0 | 1.5 | 0 | 76.6869
2017-09-17 | 16:05 | 1.7405 | 0 |  | 1.5
2017-09-17 | 16:10 | 1.7616 | 0 |  | 1.5
2017-09-17 | 16:15 | 1.7553 | 0 | 0 | 1.5 | 0 | 76.5773
2017-09-17 | 16:20 | 1.7616 | 0 |  | 1.5
2017-09-17 | 16:25 | 1.7413 | 0 |  | 1.5
2017-09-17 | 16:30 | 1.753 | 0 | 0 | 1.5 | 0 | 76.5324
2017-09-17 | 16:35 | 1.7436 | 0 |  | 1.5
2017-09-17 | 16:40 | 1.7358 | 0 |  | 1.5
2017-09-17 | 16:45 | 1.753 | 0 | 0 | 1.5 | 0 | 76.5598
2017-09-17 | 16:50 | 1.7499 | 0 |  | 1.5
2017-09-17 | 16:55 | 1.7452 | 0 |  | 1.5
2017-09-17 | 17:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 76.6699
2017-09-17 | 17:05 | 1.7452 | 0 |  | 1.5
2017-09-17 | 17:10 | 1.7468 | 0 |  | 1.5
2017-09-17 | 17:15 | 1.7475 | 0 | 0 | 1.5 | 0 | 76.4453
2017-09-17 | 17:20 | 1.7663 | 0 |  | 1.5
2017-09-17 | 17:25 | 1.7499 | 0 |  | 1.5
2017-09-17 | 17:30 | 1.753 | 0 | 0 | 1.5 | 0 | 76.2976
2017-09-17 | 17:35 | 1.7585 | 0 |  | 1.5
2017-09-17 | 17:40 | 1.746 | 0 |  | 1.5
2017-09-17 | 17:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 76.3201
2017-09-17 | 17:50 | 1.785 | 0 |  | 1.5
2017-09-17 | 17:55 | 1.7655 | 0 |  | 1.5
2017-09-17 | 18:00 | 1.7514 | 0 | 0 | 1.5 | 0 | 76.315
2017-09-17 | 18:05 | 1.7733 | 0 |  | 1.5
2017-09-17 | 18:10 | 1.7397 | 0 |  | 1.5
2017-09-17 | 18:15 | 1.7452 | 0 | 0 | 1.5 | 0 | 76.094
2017-09-17 | 18:20 | 1.7678 | 0 |  | 1.5
2017-09-17 | 18:25 | 1.7351 | 0 |  | 1.5
2017-09-17 | 18:30 | 1.7546 | 0 | 0 | 1.5 | 0 | 76.2093
2017-09-17 | 18:35 | 1.7452 | 0 |  | 1.5
2017-09-17 | 18:40 | 1.7569 | 0 |  | 1.5
2017-09-17 | 18:45 | 1.7327 | 0 | 0 | 1.5 | 0 | 76.2435
2017-09-17 | 18:50 | 1.7507 | 0 |  | 1.5
2017-09-17 | 18:55 | 1.7436 | 0 |  | 1.5
2017-09-17 | 19:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 76.2295
2017-09-17 | 19:05 | 1.7507 | 0 |  | 1.5
2017-09-17 | 19:10 | 1.7507 | 0 |  | 1.5
2017-09-17 | 19:15 | 1.753 | 0 | 0 | 1.5 | 0 | 76.1632
2017-09-17 | 19:20 | 1.7382 | 0 |  | 1.5
2017-09-17 | 19:25 | 1.7585 | 0 |  | 1.5
2017-09-17 | 19:30 | 1.7538 | 0 | 0 | 1.5 | 0 | 76.1852
2017-09-17 | 19:35 | 1.76 | 0 |  | 1.5
2017-09-17 | 19:40 | 1.7358 | 0 |  | 1.5
2017-09-17 | 19:45 | 1.7296 | 0 | 0 | 1.5 | 0 | 76.0683
2017-09-17 | 19:50 | 1.7226 | 0 |  | 1.5
2017-09-17 | 19:55 | 1.7475 | 0 |  | 1.5
2017-09-17 | 20:00 | 1.7624 | 0 | 0 | 1.5 | 0 | 76.1561
2017-09-17 | 20:05 | 1.7522 | 0 |  | 1.5
2017-09-17 | 20:10 | 1.7468 | 0 |  | 1.5
2017-09-17 | 20:15 | 1.7561 | 0 | 0 | 1.5 | 0 | 76.2171
2017-09-17 | 20:20 | 1.7413 | 0 |  | 1.5
2017-09-17 | 20:25 | 1.7577 | 0 |  | 1.5
2017-09-17 | 20:30 | 1.7585 | 0 | 0 | 1.5 | 0 | 76.2601
2017-09-17 | 20:35 | 1.7499 | 0 |  | 1.5
2017-09-17 | 20:40 | 1.7405 | 0 |  | 1.5
2017-09-17 | 20:45 | 1.7499 | 0 | 0 | 1.5 | 0 | 76.2797
2017-09-17 | 20:50 | 1.7343 | 0 |  | 1.5
2017-09-17 | 20:55 | 1.7647 | 0 |  | 1.5
2017-09-17 | 21:00 | 1.7522 | 0 | 0 | 1.5 | 0 | 76.2848
2017-09-17 | 21:05 | -0.10262 | 0 |  | 1.5
2017-09-17 | 21:10 | -0.10418 | 0 |  | 1.5
2017-09-17 | 21:15 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 21:20 | -0.10418 | 0 |  | 1.5
2017-09-17 | 21:25 | -0.10418 | 0 |  | 1.5
2017-09-17 | 21:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 21:35 | -0.10496 | 0 |  | 1.5
2017-09-17 | 21:40 | -0.10496 | 0 |  | 1.5
2017-09-17 | 21:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 21:50 | -0.10496 | 0 |  | 1.5
2017-09-17 | 21:55 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 22:05 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:10 | -0.10496 | 0 |  | 1.5
2017-09-17 | 22:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 22:20 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:25 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 22:35 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:40 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 22:50 | -0.10574 | 0 |  | 1.5
2017-09-17 | 22:55 | -0.10574 | 0 |  | 1.5
2017-09-17 | 23:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 23:05 | -0.10574 | 0 |  | 1.5
2017-09-17 | 23:10 | -0.10574 | 0 |  | 1.5
2017-09-17 | 23:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 23:20 | -0.10652 | 0 |  | 1.5
2017-09-17 | 23:25 | -0.10652 | 0 |  | 1.5
2017-09-17 | 23:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 23:35 | -0.10652 | 0 |  | 1.5
2017-09-17 | 23:40 | -0.10652 | 0 |  | 1.5
2017-09-17 | 23:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-17 | 23:50 | -0.10574 | 0 |  | 1.5
2017-09-17 | 23:55 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-18 | 0:05 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:10 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-18 | 0:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 0:20 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:25 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:30 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-18 | 0:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 0:35 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:40 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:45 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-18 | 0:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 0:50 | -0.10574 | 0 |  | 1.5
2017-09-18 | 0:55 | -0.10574 | 0 |  | 1.5
2017-09-18 | 1:00 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-18 | 1:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 1:05 | -0.10574 | 0 |  | 1.5
2017-09-18 | 1:10 | -0.10574 | 0 |  | 1.5
2017-09-18 | 1:15 | -0.10652 | 0 | 0 | 1.5 | 0
2017-09-18 | 1:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 1:20 | -0.10964 | 0 |  | 1.5
2017-09-18 | 1:25 | -0.10886 | 0 |  | 1.5
2017-09-18 | 1:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 1:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 1:35 | -0.10886 | 0 |  | 1.5
2017-09-18 | 1:40 | -0.10886 | 0 |  | 1.5
2017-09-18 | 1:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 1:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 1:50 | -0.10886 | 0 |  | 1.5
2017-09-18 | 1:55 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 2:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 2:05 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:10 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 2:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 2:20 | -0.10808 | 0 |  | 1.5
2017-09-18 | 2:25 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 2:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 2:35 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:40 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 2:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 2:50 | -0.10886 | 0 |  | 1.5
2017-09-18 | 2:55 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 3:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 3:05 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:10 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 3:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 3:20 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:25 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:30 | -0.10964 | 0 | 0 | 1.5 | 0
2017-09-18 | 3:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 3:35 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:40 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 3:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 3:50 | -0.10886 | 0 |  | 1.5
2017-09-18 | 3:55 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 4:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 4:05 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:10 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:15 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 4:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 4:20 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:25 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:30 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 4:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 4:35 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:40 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:45 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 4:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 4:50 | -0.10886 | 0 |  | 1.5
2017-09-18 | 4:55 | -0.10886 | 0 |  | 1.5
2017-09-18 | 5:00 | -0.10886 | 0 | 0 | 1.5 | 0
2017-09-18 | 5:00 |  |  |  | 1.5 |  | 25
2017-09-18 | 5:05 | 2.4238 | 0 |  | 1.5
2017-09-18 | 5:10 | 2.3232 | 0 |  | 1.5
2017-09-18 | 5:15 | 2.0884 | 0 | 0 | 1.5 | 0
2017-09-18 | 5:15 |  |  |  | 1.5 |  | 87.2736
2017-09-18 | 5:20 | 1.9714 | 0 |  | 1.5
2017-09-18 | 5:25 | 1.9012 | 0 |  | 1.5
2017-09-18 | 5:30 | 1.8396 | 0 | 0 | 1.5 | 0
2017-09-18 | 5:30 |  |  |  | 1.5 |  | 82.8755
2017-09-18 | 5:35 | 1.7912 | 0 |  | 1.5
2017-09-18 | 5:40 | 1.7616 | 0 |  | 1.5
2017-09-18 | 5:45 | 1.7741 | 0 | 0 | 1.5 | 0
2017-09-18 | 5:45 |  |  |  | 1.5 |  | 81.9084
2017-09-18 | 5:50 | 1.7624 | 0 |  | 1.5
2017-09-18 | 5:55 | 1.7514 | 0 |  | 1.5
2017-09-18 | 6:00 | 1.7335 | 0 | 0 | 1.5 | 0
2017-09-18 | 6:00 |  |  |  | 1.5 |  | 81.8372
2017-09-18 | 6:05 | 1.7444 | 0 |  | 1.5
2017-09-18 | 6:10 | 1.7444 | 0 |  | 1.5
2017-09-18 | 6:15 | 1.7062 | 0 | 0 | 1.5 | 0
2017-09-18 | 6:15 |  |  |  | 1.5 |  | 82.2217
2017-09-18 | 6:20 | 1.7327 | 0 |  | 1.5
2017-09-18 | 6:25 | 1.746 | 0 |  | 1.5
2017-09-18 | 6:30 | 1.7553 | 0 | 0 | 1.5 | 0
2017-09-18 | 6:30 |  |  |  | 1.5 |  | 82.8376
2017-09-18 | 6:35 | 1.7319 | 0 |  | 1.5
2017-09-18 | 6:40 | 1.7397 | 0 |  | 1.5
2017-09-18 | 6:45 | 1.7436 | 0 | 0 | 1.5 | 0
2017-09-18 | 6:45 |  |  |  | 1.5 |  | 83.1801
2017-09-18 | 6:50 | 1.7273 | 0 |  | 1.5
2017-09-18 | 6:55 | 1.7413 | 0 |  | 1.5
2017-09-18 | 7:00 | 1.7319 | 0 | 0 | 1.5 | 0
2017-09-18 | 7:00 |  |  |  | 1.5 |  | 83.3407
2017-09-18 | 7:05 | 1.7327 | 0 |  | 1.5
2017-09-18 | 7:10 | 1.7663 | 0 |  | 1.5
2017-09-18 | 7:15 | 1.7405 | 0 | 0 | 1.5 | 0
2017-09-18 | 7:15 |  |  |  | 1.5 |  | 83.5694
2017-09-18 | 7:20 | 1.7226 | 0 |  | 1.5
2017-09-18 | 7:25 | 1.7405 | 0 |  | 1.5
2017-09-18 | 7:30 | 1.7413 | 0 | 0 | 1.5 | 0
2017-09-18 | 7:30 |  |  |  | 1.5 |  | 83.9073
2017-09-18 | 7:35 | 1.6898 | 0 |  | 1.5
2017-09-18 | 7:40 | 1.689 | 0 |  | 1.5
2017-09-18 | 7:45 | 1.7163 | 0 | 0 | 1.5 | 0
2017-09-18 | 7:45 |  |  |  | 1.5 |  | 85.3457
2017-09-18 | 7:50 | 1.7312 | 0 |  | 1.5
2017-09-18 | 7:55 | 1.7655 | 0 |  | 1.5
2017-09-18 | 8:00 | 1.7078 | 0 | 0 | 1.5 | 0
2017-09-18 | 8:00 |  |  |  | 1.5 |  | 85.9013
2017-09-18 | 8:05 | 1.728 | 0 |  | 1.5
2017-09-18 | 8:10 | 1.7452 | 0 |  | 1.5
2017-09-18 | 8:15 | 1.721 | 0 | 0 | 1.5 | 0
2017-09-18 | 8:15 |  |  |  | 1.5 |  | 86.4645
2017-09-18 | 8:20 | 1.7296 | 0 |  | 1.5
2017-09-18 | 8:25 | 1.7413 | 0 |  | 1.5
2017-09-18 | 8:30 | 1.7475 | 0 | 0 | 1.5 | 0
2017-09-18 | 8:30 |  |  |  | 1.5 |  | 86.8468
2017-09-18 | 8:35 | 1.7491 | 0 |  | 1.5
2017-09-18 | 8:40 | 1.7085 | 0 |  | 1.5
2017-09-18 | 8:45 | 1.721 | 0 | 0 | 1.5 | 0
2017-09-18 | 8:45 |  |  |  | 1.5 |  | 87.705
2017-09-18 | 8:50 | 1.728 | 0 |  | 1.5
2017-09-18 | 8:55 | 1.6976 | 0 |  | 1.5
2017-09-18 | 9:00 | 1.6649 | 0 | 0 | 1.5 | 0
2017-09-18 | 9:00 |  |  |  | 1.5 |  | 88.845
2017-09-18 | 9:05 | 1.6867 | 0 |  | 1.5
2017-09-18 | 9:10 | 1.6898 | 0 |  | 1.5
2017-09-18 | 9:15 | 1.689 | 0 | 0 | 1.5 | 0
2017-09-18 | 9:15 | [5 empty] | 90.3849
2017-09-18 | 9:20 | 1.7132 | 0 |  | 1.5
2017-09-18 | 9:25 | 1.6727 | 0 |  | 1.5
2017-09-18 | 9:30 | 1.6968 | 0 | 0 | 1.5 | 0
2017-09-18 | 9:30 |  |  |  | 1.5 |  | 91.4435
2017-09-18 | 9:35 | 1.721 | 0 |  | 1.5
2017-09-18 | 9:40 | 1.721 | 0 |  | 1.5
2017-09-18 | 9:45 | 1.7319 | 0 | 0 | 1.5 | 0
2017-09-18 | 9:45 |  |  |  | 1.5 |  | 92.3455
2017-09-18 | 9:50 | 1.8123 | 0 |  | 1.5
2017-09-18 | 9:55 | 1.7819 | 0 |  | 1.5
2017-09-18 | 10:00 | 1.8544 | 0 | 0 | 1.5 | 0
2017-09-18 | 10:00 |  |  |  | 1.5 |  | 91.4164
2017-09-18 | 10:05 | 1.9589 | 0 |  | 1.5
2017-09-18 | 10:10 | 1.8934 | 0 |  | 1.5
2017-09-18 | 10:15 | 1.8965 | 0 | 0 | 1.5 | 0
2017-09-18 | 10:15 |  |  |  | 1.5 |  | 87.0754
2017-09-18 | 10:20 | 1.8575 | 0 |  | 1.5
2017-09-18 | 10:25 | 1.806 | 0 |  | 1.5
2017-09-18 | 10:30 | 1.8372 | 0 | 0 | 1.5 | 0
2017-09-18 | 10:30 |  |  |  | 1.5 |  | 84.7297
2017-09-18 | 10:35 | 1.8279 | 0 |  | 1.5
2017-09-18 | 10:40 | 1.8053 | 0 |  | 1.5
2017-09-18 | 10:45 | 1.7834 | 0 | 0 | 1.5 | 0
2017-09-18 | 10:45 |  |  |  | 1.5 |  | 83.3306
2017-09-18 | 10:50 | 1.8333 | 0 |  | 1.5
2017-09-18 | 10:55 | 1.7881 | 0 |  | 1.5
2017-09-18 | 11:00 | 1.7842 | 0 | 0 | 1.5 | 0
2017-09-18 | 11:00 |  |  |  | 1.5 |  | 82.2602
2017-09-18 | 11:05 | 1.7694 | 0 |  | 1.5
2017-09-18 | 11:10 | 1.7936 | 0 |  | 1.5
2017-09-18 | 11:15 | 1.8068 | 0 | 0 | 1.5 | 0
2017-09-18 | 11:15 |  |  |  | 1.5 |  | 81.6554
2017-09-18 | 11:20 | 1.7163 | 0 |  | 1.5
2017-09-18 | 11:25 | 1.7413 | 0 |  | 1.5
2017-09-18 | 11:30 | 1.7569 | 0 | 0 | 1.5 | 0
2017-09-18 | 11:30 |  |  |  | 1.5 |  | 81.4785
2017-09-18 | 11:35 | 1.7834 | 0 |  | 1.5
2017-09-18 | 11:40 | 1.7834 | 0 |  | 1.5
2017-09-18 | 11:45 | 1.7647 | 0 | 0 | 1.5 | 0
2017-09-18 | 11:45 |  | 0 |  | 1.5 |  | 80.9374
2017-09-18 | 11:50 | 1.7624 | 0 |  | 1.5
2017-09-18 | 11:55 | 1.7421 | 0 |  | 1.5
2017-09-18 | 12:00 | 1.7553 | 0 | 0 | 1.5 | 0
2017-09-18 | 12:00 |  |  |  | 1.5 |  | 81.1178
2017-09-18 | 12:05 | 1.7444 | 0 |  | 1.5
2017-09-18 | 12:10 | 1.7561 | 0 |  | 1.5
2017-09-18 | 12:15 | 1.7585 | 0 | 0 | 1.5 | 0
2017-09-18 | 12:15 |  |  |  | 1.5 |  | 80.9268
2017-09-18 | 12:20 | 1.7421 | 0 |  | 1.5
2017-09-18 | 12:25 | 1.7748 | 0 |  | 1.5
2017-09-18 | 12:30 | 1.7678 | 0 | 0 | 1.5 | 0
2017-09-18 | 12:30 |  |  |  | 1.5 |  | 80.6451
2017-09-18 | 12:35 | 1.767 | 0 |  | 1.5
2017-09-18 | 12:40 | 1.7569 | 0 |  | 1.5
2017-09-18 | 12:45 | 1.7795 | 0 | 0 | 1.5 | 0
2017-09-18 | 12:45 |  |  |  | 1.5 |  | 80.4219
2017-09-18 | 12:50 | 1.7491 | 0 |  | 1.5
2017-09-18 | 12:55 | 1.7553 | 0 |  | 1.5
2017-09-18 | 13:00 | 1.746 | 0 | 0 | 1.5 | 0
2017-09-18 | 13:00 |  |  |  | 1.5 |  | 80.346
2017-09-18 | 13:05 | 1.7358 | 0 |  | 1.5
2017-09-18 | 13:10 | 1.7226 | 0 |  | 1.5
2017-09-18 | 13:15 | 1.721 | 0 | 0 | 1.5 | 0
2017-09-18 | 13:15 |  |  |  | 1.5 |  | 80.8899
2017-09-18 | 13:20 | 1.7 | 0 |  | 1.5
2017-09-18 | 13:25 | 1.7 | 0 |  | 1.5
2017-09-18 | 13:30 | 1.7405 | 0 | 0 | 1.5 | 0
2017-09-18 | 13:30 |  |  |  | 1.5 |  | 81.8597
2017-09-18 | 13:35 | 1.7475 | 0 |  | 1.5
2017-09-18 | 13:40 | 1.7741 | 0 |  | 1.5
2017-09-18 | 13:45 | 1.7171 | 0 | 0 | 1.5 | 0
2017-09-18 | 13:45 |  |  |  | 1.5 |  | 81.7729
2017-09-18 | 13:50 | 1.7226 | 0 |  | 1.5
2017-09-18 | 13:55 | 1.7101 | 0 |  | 1.5
2017-09-18 | 14:00 | 1.7273 | 0 | 0 | 1.5 | 0
2017-09-18 | 14:00 |  |  |  | 1.5 |  | 82.4612
2017-09-18 | 14:05 | 1.7374 | 0 |  | 1.5
2017-09-18 | 14:10 | 1.7616 | 0 |  | 1.5
2017-09-18 | 14:15 | 1.7054 | 0 | 0 | 1.5 | 0
2017-09-18 | 14:15 |  |  |  | 1.5 |  | 82.9145
2017-09-18 | 14:20 | 1.7444 | 0 |  | 1.5
2017-09-18 | 14:25 | 1.7358 | 0 |  | 1.5
2017-09-18 | 14:30 | 1.7592 | 0 | 0 | 1.5 | 0
2017-09-18 | 14:30 |  |  |  | 1.5 |  | 83.0912
2017-09-18 | 14:35 | 1.7171 | 0 |  | 1.5
2017-09-18 | 14:40 | 1.7491 | 0 |  | 1.5
2017-09-18 | 14:45 | 1.7444 | 0 | 0 | 1.5 | 0
2017-09-18 | 14:45 |  |  |  | 1.5 |  | 83.6162
2017-09-18 | 14:50 | 1.7592 | 0 |  | 1.5
2017-09-18 | 14:55 | 1.7756 | 0 |  | 1.5
2017-09-18 | 15:00 | 1.7514 | 0 | 0 | 1.5 | 0
2017-09-18 | 15:00 |  |  |  | 1.5 |  | 83.5631
2017-09-18 | 15:05 | 1.7787 | 0 |  | 1.5
2017-09-18 | 15:10 | 1.7366 | 0 |  | 1.5
2017-09-18 | 15:15 | 1.7475 | 0 | 0 | 1.5 | 0
2017-09-18 | 15:15 | [5 empty] | 83.4574
2017-09-18 | 15:20 | 1.7608 | 0 |  | 1.5
2017-09-18 | 15:25 | 1.7335 | 0 |  | 1.5
2017-09-18 | 15:30 | 1.7421 | 0 | 0 | 1.5 | 0
2017-09-18 | 15:30 |  |  |  | 1.5 |  | 83.246
2017-09-18 | 15:35 | 1.8014 | 0 |  | 1.5
2017-09-18 | 15:40 | 1.7608 | 0 |  | 1.5
2017-09-18 | 15:45 | 1.7538 | 0 | 0 | 1.5 | 0
2017-09-18 | 15:45 |  |  |  | 1.5 |  | 82.8454
2017-09-18 | 15:50 | 1.7616 | 0 |  | 1.5
2017-09-18 | 15:55 | 1.7709 | 0 |  | 1.5
2017-09-18 | 16:00 | 1.7678 | 0 | 0 | 1.5 | 0
2017-09-18 | 16:00 |  |  |  | 1.5 |  | 82.505
2017-09-18 | 16:05 | 1.714 | 0 |  | 1.5
2017-09-18 | 16:10 | 1.7561 | 0 |  | 1.5
2017-09-18 | 16:15 | 1.7522 | 0 | 0 | 1.5 | 0
2017-09-18 | 16:15 |  |  |  | 1.5 |  | 82.2613
2017-09-18 | 16:20 | 1.7483 | 0 |  | 1.5
2017-09-18 | 16:25 | 1.7647 | 0 |  | 1.5
2017-09-18 | 16:30 | 1.7085 | 0 | 0 | 1.5 | 0
2017-09-18 | 16:30 |  |  |  | 1.5 |  | 82.2121
2017-09-18 | 16:35 | 1.7585 | 0 |  | 1.5
2017-09-18 | 16:40 | 1.7249 | 0 |  | 1.5
2017-09-18 | 16:45 | 1.7117 | 0 | 0 | 1.5 | 0
2017-09-18 | 16:45 |  |  |  | 1.5 |  | 82.3492
2017-09-18 | 16:50 | 1.7241 | 0 |  | 1.5
2017-09-18 | 16:55 | 1.7296 | 0 |  | 1.5
2017-09-18 | 17:00 | 1.7351 | 0 | 0 | 1.5 | 0
2017-09-18 | 17:00 |  |  |  | 1.5 |  | 82.8064
2017-09-18 | 17:05 | 1.7132 | 0 |  | 1.5
2017-09-18 | 17:10 | 1.7694 | 0 |  | 1.5
2017-09-18 | 17:15 | 1.7756 | 0 | 0 | 1.5 | 0
2017-09-18 | 17:15 |  |  |  | 1.5 |  | 82.8082
2017-09-18 | 17:20 | 1.746 | 0 |  | 1.5
2017-09-18 | 17:25 | 1.7928 | 0 |  | 1.5
2017-09-18 | 17:30 | 1.7366 | 0 | 0 | 1.5 | 0
2017-09-18 | 17:30 |  |  |  | 1.5 |  | 82.2664
2017-09-18 | 17:35 | 1.7546 | 0 |  | 1.5
2017-09-18 | 17:40 | 1.7663 | 0 |  | 1.5
2017-09-18 | 17:45 | 1.76 | 0 | 0 | 1.5 | 0
2017-09-18 | 17:45 |  |  |  | 1.5 |  | 81.7344
2017-09-18 | 17:50 | 1.7881 | 0 |  | 1.5
2017-09-18 | 17:55 | 1.7811 | 0 |  | 1.5
2017-09-18 | 18:00 | 1.7756 | 0 | 0 | 1.5 | 0
2017-09-18 | 18:00 |  |  |  | 1.5 |  | 81.0632
2017-09-18 | 18:05 | 1.7694 | 0 |  | 1.5
2017-09-18 | 18:10 | 1.7678 | 0 |  | 1.5
2017-09-18 | 18:15 | 1.7631 | 0 | 0 | 1.5 | 0
2017-09-18 | 18:15 |  |  |  | 1.5 |  | 80.6962
2017-09-18 | 18:20 | 1.7499 | 0 |  | 1.5
2017-09-18 | 18:25 | 1.7429 | 0 |  | 1.5
2017-09-18 | 18:30 | 1.76 | 0 | 0 | 1.5 | 0
2017-09-18 | 18:30 |  |  |  | 1.5 |  | 80.3329
2017-09-18 | 18:35 | 1.7616 | 0 |  | 1.5
2017-09-18 | 18:40 | 1.7889 | 0 |  | 1.5
2017-09-18 | 18:45 | 1.7553 | 0 | 0 | 1.5 | 0
2017-09-18 | 18:45 |  |  |  | 1.5 |  | 80.0939
2017-09-18 | 18:50 | 1.7741 | 0 |  | 1.5
2017-09-18 | 18:55 | 1.7639 | 0 |  | 1.5
2017-09-18 | 19:00 | 1.7709 | 0 | 0 | 1.5 | 0
2017-09-18 | 19:00 |  |  |  | 1.5 |  | 79.7289
2017-09-18 | 19:05 | 1.7327 | 0 |  | 1.5
2017-09-18 | 19:10 | 1.7631 | 0 |  | 1.5
2017-09-18 | 19:15 | 1.7405 | 0 | 0 | 1.5 | 0
2017-09-18 | 19:15 |  |  |  | 1.5 |  | 79.6581
2017-09-18 | 19:20 | 1.7358 | 0 |  | 1.5
2017-09-18 | 19:25 | 1.7663 | 0 |  | 1.5
2017-09-18 | 19:30 | 1.7655 | 0 | 0 | 1.5 | 0
2017-09-18 | 19:30 |  |  |  | 1.5 |  | 79.3974
2017-09-18 | 19:35 | 1.7273 | 0 |  | 1.5
2017-09-18 | 19:40 | 1.7366 | 0 |  | 1.5
2017-09-18 | 19:45 | 1.7226 | 0 | 0 | 1.5 | 0
2017-09-18 | 19:45 |  |  |  | 1.5 |  | 79.9737
2017-09-18 | 19:50 | 1.7109 | 0 |  | 1.5
2017-09-18 | 19:55 | 1.707 | 0 |  | 1.5
2017-09-18 | 20:00 | 1.7117 | 0 | 0 | 1.5 | 0
2017-09-18 | 20:00 |  |  |  | 1.5 |  | 80.817
2017-09-18 | 20:05 | 1.7351 | 0 |  | 1.5
2017-09-18 | 20:10 | 1.7319 | 0 |  | 1.5
2017-09-18 | 20:15 | 1.7585 | 0 | 0 | 1.5 | 0
2017-09-18 | 20:15 |  |  |  | 1.5 |  | 81.1345
2017-09-18 | 20:20 | 1.7429 | 0 |  | 1.5
2017-09-18 | 20:25 | 1.7452 | 0 |  | 1.5
2017-09-18 | 20:30 | 1.746 | 0 | 0 | 1.5 | 0
2017-09-18 | 20:30 |  |  |  | 1.5 |  | 81.383
2017-09-18 | 20:35 | 1.7366 | 0 |  | 1.5
2017-09-18 | 20:40 | 1.7429 | 0 |  | 1.5
2017-09-18 | 20:45 | 1.7304 | 0 | 0 | 1.5 | 0
2017-09-18 | 20:45 |  |  |  | 1.5 |  | 81.6777
2017-09-18 | 20:50 | 1.7327 | 0 |  | 1.5
2017-09-18 | 20:55 | 1.7265 | 0 |  | 1.5
2017-09-18 | 21:00 | 1.7436 | 0 | 0 | 1.5 | 0
2017-09-18 | 21:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 21:05 | -0.10106 | 0 |  | 1.5
2017-09-18 | 21:10 | -0.10184 | 0 |  | 1.5
2017-09-18 | 21:15 | -0.10106 | 0 | 0 | 1.5 | 0
2017-09-18 | 21:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 21:20 | -0.10262 | 0 |  | 1.5
2017-09-18 | 21:25 | -0.10106 | 0 |  | 1.5
2017-09-18 | 21:30 | -0.10106 | 0 | 0 | 1.5 | 0
2017-09-18 | 21:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 21:35 | -0.10106 | 0 |  | 1.5
2017-09-18 | 21:40 | -0.10106 | 0 |  | 1.5
2017-09-18 | 21:45 | -0.10106 | 0 | 0 | 1.5 | 0
2017-09-18 | 21:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 21:50 | -0.10184 | 0 |  | 1.5
2017-09-18 | 21:55 | -0.10028 | 0 |  | 1.5
2017-09-18 | 22:00 | -0.0995 | 0 | 0 | 1.5 | 0
2017-09-18 | 22:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 22:05 | -0.11978 | 0 |  | 1.5
2017-09-18 | 22:10 | -0.11666 | 0 |  | 1.5
2017-09-18 | 22:15 | -0.11432 | 0 | 0 | 1.5 | 0
2017-09-18 | 22:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 22:20 | -0.10106 | 0 |  | 1.5
2017-09-18 | 22:25 | -0.09872 | 0 |  | 1.5
2017-09-18 | 22:30 | -0.09872 | 0 | 0 | 1.5 | 0
2017-09-18 | 22:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 22:35 | -0.0995 | 0 |  | 1.5
2017-09-18 | 22:40 | -0.10106 | 0 |  | 1.5
2017-09-18 | 22:45 | -0.0995 | 0 | 0 | 1.5 | 0
2017-09-18 | 22:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 22:50 | -0.10028 | 0 |  | 1.5
2017-09-18 | 22:55 | -0.09794 | 0 |  | 1.5
2017-09-18 | 23:00 | -0.0995 | 0 | 0 | 1.5 | 0
2017-09-18 | 23:00 |  |  |  | 1.5 |  | 0
2017-09-18 | 23:05 | -0.09794 | 0 |  | 1.5
2017-09-18 | 23:10 | -0.09716 | 0 |  | 1.5
2017-09-18 | 23:15 | -0.10574 | 0 | 0 | 1.5 | 0
2017-09-18 | 23:15 |  |  |  | 1.5 |  | 0
2017-09-18 | 23:20 | -0.0995 | 0 |  | 1.5
2017-09-18 | 23:25 | -0.09872 | 0 |  | 1.5
2017-09-18 | 23:30 | -0.10184 | 0 | 0 | 1.5 | 0
2017-09-18 | 23:30 |  |  |  | 1.5 |  | 0
2017-09-18 | 23:35 | -0.09794 | 0 |  | 1.5
2017-09-18 | 23:40 | -0.10496 | 0 |  | 1.5
2017-09-18 | 23:45 | -0.10028 | 0 | 0 | 1.5 | 0
2017-09-18 | 23:45 |  |  |  | 1.5 |  | 0
2017-09-18 | 23:50 | -0.10418 | 0 |  | 1.5
2017-09-18 | 23:55 | -0.09872 | 0 |  | 1.5
2017-09-19 | 0:00 | -0.09794 | 0 | 0 | 1.5 | 0
2017-09-19 | 0:00 |  |  |  | 1.5 |  | 0
2017-09-19 | 0:05 | -0.09872 | 0 |  | 1.5
2017-09-19 | 0:10 | -0.0995 | 0 |  | 1.5
2017-09-19 | 0:15 | -0.09872 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 0:20 | -0.0995 | 0 |  | 1.5
2017-09-19 | 0:25 | -0.0995 | 0 |  | 1.5
2017-09-19 | 0:30 | -0.0995 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 0:35 | -0.10262 | 0 |  | 1.5
2017-09-19 | 0:40 | -0.09872 | 0 |  | 1.5
2017-09-19 | 0:45 | -0.09872 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 0:50 | -0.09794 | 0 |  | 1.5
2017-09-19 | 0:55 | -0.09794 | 0 |  | 1.5
2017-09-19 | 1:00 | -0.09794 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 1:05 | -0.10106 | 0 |  | 1.5
2017-09-19 | 1:10 | -0.0995 | 0 |  | 1.5
2017-09-19 | 1:15 | -0.0995 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 1:20 | -0.10028 | 0 |  | 1.5
2017-09-19 | 1:25 | -0.10106 | 0 |  | 1.5
2017-09-19 | 1:30 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 1:35 | -0.10496 | 0 |  | 1.5
2017-09-19 | 1:40 | -0.10574 | 0 |  | 1.5
2017-09-19 | 1:45 | -0.10496 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 1:50 | -0.10652 | 0 |  | 1.5
2017-09-19 | 1:55 | -0.10652 | 0 |  | 1.5
2017-09-19 | 2:00 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 2:05 | -0.10652 | 0 |  | 1.5
2017-09-19 | 2:10 | -0.10574 | 0 |  | 1.5
2017-09-19 | 2:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 2:20 | -0.10652 | 0 |  | 1.5
2017-09-19 | 2:25 | -0.10652 | 0 |  | 1.5
2017-09-19 | 2:30 | -0.1073 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 2:35 | -0.10652 | 0 |  | 1.5
2017-09-19 | 2:40 | -0.10886 | 0 |  | 1.5
2017-09-19 | 2:45 | -0.10106 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 2:50 | -0.10184 | 0 |  | 1.5
2017-09-19 | 2:55 | -0.10106 | 0 |  | 1.5
2017-09-19 | 3:00 | -0.0995 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 3:05 | -0.10652 | 0 |  | 1.5
2017-09-19 | 3:10 | -0.10574 | 0 |  | 1.5
2017-09-19 | 3:15 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 3:20 | -0.10574 | 0 |  | 1.5
2017-09-19 | 3:25 | -0.10652 | 0 |  | 1.5
2017-09-19 | 3:30 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 3:35 | -0.10574 | 0 |  | 1.5
2017-09-19 | 3:40 | -0.10808 | 0 |  | 1.5
2017-09-19 | 3:45 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 3:50 | -0.10574 | 0 |  | 1.5
2017-09-19 | 3:55 | -0.1073 | 0 |  | 1.5
2017-09-19 | 4:00 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 4:05 | -0.10652 | 0 |  | 1.5
2017-09-19 | 4:10 | -0.10574 | 0 |  | 1.5
2017-09-19 | 4:15 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 4:20 | -0.10574 | 0 |  | 1.5
2017-09-19 | 4:25 | -0.10886 | 0 |  | 1.5
2017-09-19 | 4:30 | -0.10418 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 4:35 | -0.10106 | 0 |  | 1.5
2017-09-19 | 4:40 | -0.10028 | 0 |  | 1.5
2017-09-19 | 4:45 | -0.10652 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 4:50 | -0.10496 | 0 |  | 1.5
2017-09-19 | 4:55 | -0.10652 | 0 |  | 1.5
2017-09-19 | 5:00 | -0.10574 | 0 | 0 | 1.5 | 0 | 0
2017-09-19 | 5:05 | 2.5439 | 0 |  | 1.5
2017-09-19 | 5:10 | 2.3403 | 0 |  | 1.5
2017-09-19 | 5:15 | 2.0853 | 0 | 0 | 1.5 | 0 | 86.1967
2017-09-19 | 5:20 | 1.9324 | 0 |  | 1.5
2017-09-19 | 5:25 | 1.8723 | 0 |  | 1.5
2017-09-19 | 5:30 | 1.8287 | 0 | 0 | 1.5 | 0 | 81.8762
2017-09-19 | 5:35 | 1.8099 | 0 |  | 1.5
2017-09-19 | 5:40 | 1.7686 | 0 |  | 1.5
2017-09-19 | 5:45 | 1.7429 | 0 | 0 | 1.5 | 0 | 80.9326
2017-09-19 | 5:50 | 1.7639 | 0 |  | 1.5
2017-09-19 | 5:55 | 1.7608 | 0 |  | 1.5
2017-09-19 | 6:00 | 1.7491 | 0 | 0 | 1.5 | 0 | 80.7586
2017-09-19 | 6:05 | 1.7444 | 0 |  | 1.5
2017-09-19 | 6:10 | 1.7405 | 0 |  | 1.5
2017-09-19 | 6:15 | 1.7577 | 0 | 0 | 1.5 | 0 | 80.7551
2017-09-19 | 6:20 | 1.7553 | 0 |  | 1.5
2017-09-19 | 6:25 | 1.7444 | 0 |  | 1.5
2017-09-19 | 6:30 | 1.7483 | 0 | 0 | 1.5 | 0 | 80.8414
2017-09-19 | 6:35 | 1.7507 | 0 |  | 1.5
2017-09-19 | 6:40 | 1.7772 | 0 |  | 1.5
2017-09-19 | 6:45 | 1.7468 | 0 | 0 | 1.5 | 0 | 80.9224
2017-09-19 | 6:50 | 1.7382 | 0 |  | 1.5
2017-09-19 | 6:55 | 1.7569 | 0 |  | 1.5
2017-09-19 | 7:00 | 1.7507 | 0 | 0 | 1.5 | 0 | 80.9506
2017-09-19 | 7:05 | 1.7553 | 0 |  | 1.5
2017-09-19 | 7:10 | 1.7592 | 0 |  | 1.5
2017-09-19 | 7:15 | 1.7483 | 0 | 0 | 1.5 | 0 | 80.9612
2017-09-19 | 7:20 | 1.7702 | 0 |  | 1.5
2017-09-19 | 7:25 | 1.7499 | 0 |  | 1.5
2017-09-19 | 7:30 | 1.7187 | 0 | 0 | 1.5 | 0 | 81.1182
2017-09-19 | 7:35 | 1.6968 | 0 |  | 1.5
2017-09-19 | 7:40 | 1.7062 | 0 |  | 1.5
2017-09-19 | 7:45 | 1.7351 | 0 | 0 | 1.5 | 0 | 82.1091
2017-09-19 | 7:50 | 1.7078 | 0 |  | 1.5
2017-09-19 | 7:55 | 1.7397 | 0 |  | 1.5
2017-09-19 | 8:00 | 1.7156 | 0 | 0 | 1.5 | 0 | 82.8084
2017-09-19 | 8:05 | 1.728 | 0 |  | 1.5
2017-09-19 | 8:10 | 1.7054 | 0 |  | 1.5
2017-09-19 | 8:15 | 1.728 | 0 | 0 | 1.5 | 0 | 83.7898
2017-09-19 | 8:20 | 1.7109 | 0 |  | 1.5
2017-09-19 | 8:25 | 1.7163 | 0 |  | 1.5
2017-09-19 | 8:30 | 1.7249 | 0 | 0 | 1.5 | 0 | 84.4501
2017-09-19 | 8:35 | 1.7257 | 0 |  | 1.5
2017-09-19 | 8:40 | 1.7405 | 0 |  | 1.5
2017-09-19 | 8:45 | 1.7265 | 0 | 0 | 1.5 | 0 | 84.6134
2017-09-19 | 8:50 | 1.7124 | 0 |  | 1.5
2017-09-19 | 8:55 | 1.7475 | 0 |  | 1.5
2017-09-19 | 9:00 | 1.7483 | 0 | 0 | 1.5 | 0 | 84.8612
2017-09-19 | 9:05 | 1.7452 | 0 |  | 1.5
2017-09-19 | 9:10 | 1.7187 | 0 |  | 1.5
2017-09-19 | 9:15 | 1.7429 | 0 | 0 | 1.5 | 0 | 85.4038
2017-09-19 | 9:20 | 1.721 | 0 |  | 1.5
2017-09-19 | 9:25 | 1.7031 | 0 |  | 1.5
2017-09-19 | 9:30 | 1.7117 | 0 | 0 | 1.5 | 0 | 86.3386
2017-09-19 | 9:35 | 1.6766 | 0 |  | 1.5
2017-09-19 | 9:40 | 1.6851 | 0 |  | 1.5
2017-09-19 | 9:45 | 1.6703 | 0 | 0 | 1.5 | 0 | 88.1926
2017-09-19 | 9:50 | 1.6898 | 0 |  | 1.5
2017-09-19 | 9:55 | 1.6992 | 0 |  | 1.5
2017-09-19 | 10:00 | 1.6929 | 0 | 0 | 1.5 | 0 | 89.8214
2017-09-19 | 10:05 | 1.7257 | 0 |  | 1.5
2017-09-19 | 10:10 | 1.7335 | 0 |  | 1.5
2017-09-19 | 10:15 | 1.7202 | 0 | 0 | 1.5 | 0 | 90.8018
2017-09-19 | 10:20 | 1.792 | 0 |  | 1.5
2017-09-19 | 10:25 | 1.7741 | 0 |  | 1.5
2017-09-19 | 10:30 | 1.806 | 0 | 0 | 1.5 | 0 | 90.4489
2017-09-19 | 10:35 | 1.7881 | 0 |  | 1.5
2017-09-19 | 10:40 | 1.7748 | 0 |  | 1.5
2017-09-19 | 10:45 | 1.8029 | 0 | 0 | 1.5 | 0 | 88.5366
2017-09-19 | 10:50 | 1.7858 | 0 |  | 1.5
2017-09-19 | 10:55 | 1.8216 | 0 |  | 1.5
2017-09-19 | 11:00 | 1.7982 | 0 | 0 | 1.5 | 0 | 87.3825
2017-09-19 | 11:05 | 1.7811 | 0 |  | 1.5
2017-09-19 | 11:10 | 1.7655 | 0 |  | 1.5
2017-09-19 | 11:15 | 1.8131 | 0 | 0 | 1.5 | 0 | 86.8993
2017-09-19 | 11:20 | 1.7249 | 0 |  | 1.5
2017-09-19 | 11:25 | 1.7577 | 0 |  | 1.5
2017-09-19 | 11:30 | 1.7709 | 0 | 0 | 1.5 | 0 | 86.7639
2017-09-19 | 11:35 | 1.7522 | 0 |  | 1.5
2017-09-19 | 11:40 | 1.7553 | 0 |  | 1.5
2017-09-19 | 11:45 | 1.7538 | 0 | 0 | 1.5 | 0 | 86.5401
2017-09-19 | 11:50 | 1.7842 | 0 |  | 1.5
2017-09-19 | 11:55 | 1.8037 | 0 |  | 1.5
2017-09-19 | 12:00 | 1.7452 | 0 | 0 | 1.5 | 0 | 86.0211
2017-09-19 | 12:05 | 1.7475 | 0 |  | 1.5
2017-09-19 | 12:10 | 1.7187 | 0 |  | 1.5
2017-09-19 | 12:15 | 1.7319 | 0 | 0 | 1.5 | 0 | 86.0364
2017-09-19 | 12:20 | 1.7249 | 0 |  | 1.5
2017-09-19 | 12:25 | 1.7226 | 0 |  | 1.5
2017-09-19 | 12:30 | 1.7171 | 0 | 0 | 1.5 | 0 | 86.5978
2017-09-19 | 12:35 | 1.8996 | 0 |  | 1.5
2017-09-19 | 12:40 | 1.5159 | 0 |  | 1.5
2017-09-19 | 12:45 | 1.6142 | 0 | 0 | 1.5 | 0 | 84.8696
2017-09-19 | 12:50 | 1.6727 | 0 |  | 1.5
2017-09-19 | 12:55 | 1.7015 | 0 |  | 1.5
2017-09-19 | 13:00 | 1.7335 | 0 | 0 | 1.5 | 0 | 86.5734
2017-09-19 | 13:05 | 1.7163 | 0 |  | 1.5
2017-09-19 | 13:10 | 1.7171 | 0 |  | 1.5
2017-09-19 | 13:15 | 1.7241 | 0 | 0 | 1.5 | 0 | 86.3626
2017-09-19 | 13:20 | 1.7335 | 0 |  | 1.5
2017-09-19 | 13:25 | 1.7421 | 0 |  | 1.5
2017-09-19 | 13:30 | 1.792 | 0 | 0 | 1.5 | 0 | 86.4323
2017-09-19 | 13:35 | 1.7616 | 0 |  | 1.5
2017-09-19 | 13:40 | 1.7897 | 0 |  | 1.5
2017-09-19 | 13:45 | 1.7858 | 0 | 0 | 1.5 | 0 | 85.6219
2017-09-19 | 13:50 | 1.7616 | 0 |  | 1.5
2017-09-19 | 13:55 | 1.7819 | 0 |  | 1.5
2017-09-19 | 14:00 | 1.753 | 0 | 0 | 1.5 | 0 | 85.2024
2017-09-19 | 14:05 | 1.7452 | 0 |  | 1.5
2017-09-19 | 14:10 | 1.7998 | 0 |  | 1.5
2017-09-19 | 14:15 | 1.7265 | 0 | 0 | 1.5 | 0 | 84.8497
2017-09-19 | 14:20 | 1.7452 | 0 |  | 1.5
2017-09-19 | 14:25 | 1.7335 | 0 |  | 1.5
2017-09-19 | 14:30 | 1.7842 | 0 | 0 | 1.5 | 0 | 84.766
2017-09-19 | 14:35 | 1.7397 | 0 |  | 1.5
2017-09-19 | 14:40 | 1.7538 | 0 |  | 1.5
2017-09-19 | 14:45 | 1.7904 | 0 | 0 | 1.5 | 0 | 84.4526
2017-09-19 | 14:50 | 1.7538 | 0 |  | 1.5
2017-09-19 | 14:55 | 1.7717 | 0 |  | 1.5
2017-09-19 | 15:00 | 1.7904 | 0 | 0 | 1.5 | 0 | 84.0017
2017-09-19 | 15:05 |  |  |  | 1.5