**MERIDIAN PARK – STEAM BOILER UPGRADE**

- BLOW DOWN STORAGE – CONFIRM SIZING. DRAIN SIZE IS 2”, BUT THE DRAIN FROM THE COOLING KIT IS 3”. EXISTING LINE TO TRENCH IS 2-1/2”.

-Steam control valve to DA. Does it need little PRV in front of it???

-HPS SIZED FOR 3000 LBS/HR, @ 75 PSI, 8000 FPM AND 1 PSI/100FT P.D.

- IMPROVE WIRING DIAGRAM

- master Controller location.

-CONFIRM HOUSE GAS PRESSURE.

-The gas PRV serves the existing steam boilers, and the pilot lights to the existing boilers. We need to confirm that it doesn’t serve anything else.