## PART 1   GENERAL

1.1	DESCRIPTION

A.	The Access Control system shall provide the interaction to the door controls and locks provided by others.

B.	The proximity reader is to work in conjunction with an electronic door controller refer to door hardware section.

C.	All components needed for a complete and functional install are to be part of the bid, sized for number of doors indicated on plans. Verify number of users with architect prior to bid.

1.2	QUALITY ASSURANCE

A.	Underwriters Laboratories, Inc., listed, and NEC approved.

1.3	SUBMITTAL AND RECORD DOCUMENTATION

A.	Submit product data describing all components whether listed in specifications or on plans needed for a complete installation.

B.	Submit shop drawings which shall include complete wiring and schematic diagrams for equipment furnished, equipment layout, and other details.

C.	Include performance field test reports with operation and maintenance manuals.

## PART 2   PRODUCTS

2.1	MATERIALS

A.	Proximity Reader

1.	Mount to single gang Junction box.

2.	Have a read range of up to 8”.

3.	Black finish with Red LED indicating system power.

4.	Interior or exterior grade depending on mounting location as shown on plans.

5.	12v or 24v compatible.

B.	System

1.	Ability to monitor number of doors shown on plans.

2.	Network capable for programming and monitoring.

3.	Software shall be compatible with current operating systems

4.	System software will have the documentation fields for entering persons name, division, card number, date of issue, date to shut down access.

C.	Proximity Cards

1.	Cards shall be capable of reprogramming onsite with proper equipment.

## PART 3   EXECUTION

3.1	GENERAL INSTALLATION

A.	Wiring Method:  Install wiring in raceways except in accessible indoor ceiling spaces and attics, and as otherwise indicated.  Conceal raceways and wiring except in unfinished spaces and at terminal boards.

B.	Wiring Within Enclosures:  Bundle, lace, and train the conductors to terminal points with no excess.  Provide and use lacing bars and distribution spools.

C.	Pulling Cables:  Do not exceed manufacturer’s recommended pulling tensions.  Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between indicated termination, tap, or junction points.  Remove and discard cable where damaged during installation and replace it with new cable.

D.	Splices, Taps, and Terminations:  For power and control wiring use numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.  Tighten connections to comply with torque tightening requirements specified in UL 486A.

E.	Grounding:  Provide independent signal circuit grounding recommended by manufacturer.

3.2	Operation

A.	When card is read by proximity reader it will unlock the door associated with that particular reader and no other door. The system shall record date, time, and person who has accessed the door.

3.3	IDENTIFICATION

A.	Identify system components, wiring, cabling, and terminals according to Division 26, Electrical Identification.

3.4	FIELD QUALITY CONTROL

A.	Manufacturer’s Field Service:  Provide services of a factory-authorized service representative to supervise the field assembly and component connections and the pretesting, testing, and adjusting of the system.

B.	Inspection:  Verify that units and controls are properly installed, connected, labeled and that interconnecting wires and terminals are identified.

C.	Pretesting:  Align and adjust the system and pretest all components, wiring, and functions to verify they conform to specified requirements.  Replace malfunctioning or damaged items with new items.  Retest until satisfactory performance and conditions are achieved.

D.	Acceptance Test Schedule:  Schedule tests after pretesting has been successfully completed and system has been in normal functional operation for at least two weeks.  Provide a minimum of 10 days’ notice of acceptance test performance schedule.

3.5	CLEANING

A.	Clean installed items using methods and materials recommended by manufacturer.

3.6	DEMONSTRATION

A.	Training:  Arrange and pay for the services of a factory-authorized service representative to demonstrate adjustment, operation, and maintenance of the system and to train Owner’s personnel.

B.	Conduct a minimum of six hours of training.

C.	Schedule demonstration, training, and adjustment with Owner of at least seven days’ advance notice.

3.7	ON-SITE ASSISTANCE

A.	Occupancy Adjustments:  When requested within one year of substantial completion, provide on-site assistance in tuning and adjusting the system to suit actual occupied conditions and to optimize performance.  Provide up to two requested adjustment periods at the site for this purpose without additional cost.

END OF SECTION